{"text_format":"1","workbook":"xlsx","n_sheets":39,"sheets":["Instructions","Updates Log","TMYx","ECMs","Project Info","ECM Summary","PA Impacts","Workspace","Bldg Envelope","Interior Lighting","Exterior Lighting","Unitary HVAC (RTU, AC, HP, VRF)","High Efficiency Chillers","Variable Frequency Drives","Energy Recovery","Demand Control Ventilation","Variable Flow Kitchen Hood","Condensing Boilers","DHW Heaters","Low Flow DHW Fixtures","17","18","19","20","Unitary HVAC (RTU, AC, HP OLD)","User Defined 1","User Defined 2","User Defined 3","User Defined 4","Report","Sheet5","Sheet4","DX and HP Systems","High Efficiency VRF Systems","Sheet2","Sheet1","Sheet3","ERV Eff Calculator","AirCooled Chiller Sample Data"],"not_rendered":{"charts":17,"images":26,"macros":1,"external_links":8,"defined_names":1755,"comments":16,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Instructions","index":0,"n_rows":9,"n_cols":20,"rows_kept":9,"cut":false,"hidden":false,"merged":[[1,0,38,15]]}
["General Instructions for Use of the Streamlined Savings Calculation Tool",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"General Cell Color Designations"]
["The primary intended use of this tool is for energy savings and incentives analysis for buildings being considered through the NHSaves's New Construction incentive program.\nThe tool is designed for use ONLY on New Construction/Major Renovation studies where baselines for energy saving calculations are defined by the local energy code and state-specific modifications for industry standard practice.  It is NOT capable of analyzing retrofit measures with existing condition baselines.\nAll baseline assumptions are automated by the tool based on State, Program Year, and selected energy code standard.  Baseline values for individual measures cannot be revised by the user. \n\nDISCLAIMERS:\n   · Only designated input cell values should be adjusted when completing this tool.  All other cells are protected and should remain protected and unchanged. Altering the protected cell values and formulas could create unintended results.  If there is a suspected error in the tool's protected values and formulas, the Program Administrator should be informed.\n   · Results of this tool are not binding on any party.  The PA is not obligated to provide an incentive for any measure at any time and may consider other factors outside of this tool when making decisions on how to proceed, or not proceed, with a project.  Savings entered into the tool are not necessarily vetted, approved, or guaranteed by the PA.\n   · Ultimately it is the prerogative of the PA to decide the amount of incentive that will be offered to the customer.\n\nSTEP 1: Enter General Project Information\nGeneral Project Information inputs must be entered in the \"Project Info\" sheet as the first step when starting any new project with this tool. Many of the inputs in this sheet are referenced and used in the savings calculations for individual measures, so the calculations will not work properly until the Project Info inputs are complete.\n\nSTEP 2: Select ECMs and Enter Specific ECM Input Data\nOnce the \"Project Info\" inputs are complete, ECM-specific data can be entered into the tool:\n    · The tool includes 12 pre-set ECMs with automated savings calculations based on the applicable user inputs.\n    · To open and access individual measure sheets/tabs for direct inputs, go to the \"ECM Summary\" sheet and select \"Yes\" next to the applicable measure.\n    · Up to 4 User-Defined ECMs can also be added. Enabling a User-Defined ECM will open a blank sheet with pre-populated bin model and designated cells\n      to enter the base and proposed case descriptions and calculated savings for the measure.\n\nThe \"Workspace\" sheet is a blank, unprotected sheet that can be used to add any supplemental data, calculations, notes, etc.\n\nSTEP 3: Print Report\nOnce all ECM information has been entered and reviewed, a project summary report can be printed using the \"Print Report\" button on the \"ECM Summary\" sheet. The \"Select Report Version\" input cell should be set to either \"Draft\" or \"Final\" before generating the report.\n",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Protected Cell; information and/or formulas in these cells cannot be edited"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Input Cell; these cells can be edited"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Required Input Cell; denotes an input that is required for the tool to function properly.  These cells should turn white once an input is entered."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Input/Summary Table Cells; highlights the tables where User Inputs can be entered or summary information is provided"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Input Cell Not Required; denotes input cells that are not needed based on other input selections"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Tool Version:","v2026.02.19"]

{"sheet":"Updates Log","index":1,"n_rows":75,"n_cols":3,"rows_kept":75,"cut":false,"hidden":true,"merged":[]}
["v02.2 Updates"]
["General"]
[null,"·","Calculation of custom incentive for each ECM revised so that ECM incentives are not limited by the ECM's incremental cost."]
[null,"·","Revised % Peak savings distribution calculation for each ECM; rounded values to ensure 100% total for copying into screening tool."]
["Project Info Sheet"]
[null,"·","Added user input to select Program Path (Path 3 or Path 4) and automation to set the default incentive rates based on the Path number."]
[null,"·","Added Facility Description input section."]
[null,"·","Added a cell to indicate that all required Project Info inputs have been entered."]
[null,"·","Added Input for Design and Construction schedule/dates"]
["ECM Summary Sheet"]
[null,"·","Moved incentive rate overrides to the ECM Summary sheet."]
[null,"·","Added columns to Summary Table showing separate electric and gas incentives."]
[null,"·","Added optional column to select ECMs included in current design (for use with design assistance, charrettes, design reviews)."]
["PA Impacts Sheet"]
[null,"·","Formatting allowed to enable copying screening tool data."]
[null,"·","Added Heat Pump Metrics Summary Table"]
["Bldg Envelope Sheet"]
[null,"·","Updated Default Incremental Cost calculation so that value can only be ≥ 0."]
["Interior Lighting Sheet"]
[null,"·","Added input option for Certified Lighting Designer to override DLC/ES requirement."]
[null,"·","Added \"Notes\" input section."]
[null,"·","Added data validation check on Design Total Watts override cell to avoid values for LPD being entered (Input must be Total Watts)."]
["Exterior Lighting Sheet"]
[null,"·","Fixed Exterior Lighting baseline automation - baseline watts now set to equal proposed for non-eligible fixtures."]
[null,"·","Added \"Notes\" input section."]
[null,"·","Added input option for Certified Lighting Designer to override DLC/ES requirement."]
["Unitary HVAC (RTU, AC, HP, VRF) Sheet"]
[null,"·","Added guidance to use AHRI performance ratings for inputs."]
[null,"·","Added guidance for the heating performance COP inputs (high condensing and low condensing temperatures)."]
[null,"·","Revised calculations to only use the low condensing temp (i.e. COP 17) performance input value for air-source heat pumps."]
[null,"·","Revised VRF Baseline performance values per ASHRAE 90.1-2013 addendum."]
[null,"·","Changed default peak load % to 85% of entered capacity (was previously set to 90%)."]
[null,"·","Added table showing breakdown of measure savings by heating vs. cooling energy and HVAC vs. constant/IT loads."]
[null,"·","Added a limit for the maximum IEER used in the savings calculations - max IEER in calculations is 25.0."]
[null,"·","Added Calculation of Heat Pump Metrics for program records (Qty, Savings, Incr Cost, Incentive, Summer/Winter kW)."]
[null,"·","Reduced Avg % load for IT/Elec load cooling equipment to 25%."]
["High Efficiency Chillers Sheet"]
[null,"·","No changes"]
["Variable Frequency Drives Sheet"]
[null,"·","Correct error with TRM savings rates for Chilled Water Pumps and Cooling Tower Pumps."]
["Energy Recovery Sheet"]
[null,"·","Corrected error in baseline effectiveness automation."]
[null,"·","Added guidance that the tool is not designed to analyze ISMRE performance ratings."]
[null,"·","Revised the optional Effectiveness Calculator to simplify the inputs and add direction and guidance for the calculator's use."]
["Demand Control Ventilation Sheet"]
[null,"·","No changes"]
["Variable Flow Kitchen Hood Sheet"]
[null,"·","Revised Incremental Cost calculation."]
[null,"·","Revised calculations to use balanced infiltration for heating/cooling savings if no Make-up Air CFM is entered."]
["Condensing Boilers Sheet"]
[null,"·","Added incentive calculation for boilers >2,000 MBH; incentive is the larger of the custom calculated incentive and $10,000 per boiler."]
["DHW Heaters Sheet"]
[null,"·","Revised calculations to limit peak DHW load based on total capacity of the heaters,"]
[null,"·","Added guidance on the default gallons per day calculation (based on bldg type and area, not on operating hours)."]
[null,"·","Added guidance to show calculation of Optional Override gallons per day input in the Workspace sheet."]
["Low Flow DHW Fixtures Sheet"]
[null,"·","No changes"]
[null,"·","Added guidance on the default gallons per day calculation (based on bldg type and area, not on operating hours)."]
[null,"·","Added guidance to show calculation of Optional Override gallons per day input in the Workspace sheet."]
["User Defined Measures Sheet"]
[null,"·","Added incentive override input if the custom calculated incentive does not apply."]
[null,"·","Formatting enabled in all cells."]
[]
["v02.3 Updates"]
[]
[null,"·","Interior Lighting Sheet – For NH sites, added logic so that no incentive is calculated when < 50% of the proposed wattage is DLC/Energy Star listed.  "]
[null,"·","Condensing Boiler Sheet – For NH sites, updated baseline boiler efficiency to be 85% for boilers ≤ 2,500 MBH (per the recent NH TRM updates)"]
[null,"·","PA Impacts Sheet – added calculation for equivalent kWh savings associated with the propane/oil MMBTU savings measures. (For NH)"]
[null,"·","DCV Sheet - corrected MBH to kW conversion error."]
[null,"·","Revised ECM Summary to make \"Included in Current Design\" cells open for inputs."]
[]
["v02.3 Updates"]
[null,"·","Boilers - Revised RI prescriptive incentives"]
[null,"·","Boilers - Added two incentive tiers for boilers ≤ 300 MBH based on avg. efficiency"]
[null,"·","ECM Summary - corrected boiler gas PA incentive to be the total incentive value"]

{"sheet":"TMYx","index":2,"n_rows":8765,"n_cols":85,"rows_kept":2250,"cut":true,"hidden":true,"merged":[],"bounds":{"rows_first":1000,"rows_last":250,"rows_between":1000,"halvings":1}}
[null,null,null,null,null,null,null,null,null,"DRY BULB TEMPERATURE DATA"]
[null,null,null,null,null,null,null,null,null,{"$f":"1*(J3=$V$4)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!$C$102","v":"Berlin"},{"$f":"'Project Info'!$C$103","v":"Concord"},{"$f":"'Project Info'!$C$104","v":"Keene"},{"$f":"'Project Info'!$C$105","v":"Laconia"},{"$f":"'Project Info'!$C$106","v":"Lebanon"},{"$f":"'Project Info'!$C$107","v":"Manchester"},{"$f":"'Project Info'!$C$108","v":"Mt. Washington"},{"$f":"'Project Info'!$C$109","v":"Nashua"},{"$f":"'Project Info'!$C$110","v":"Plymouth"},{"$f":"'Project Info'!$C$111","v":"Portsmouth"},{"$f":"'Project Info'!$C$112","v":"Rochester"},null,"Location:"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!$C$16","v":0},null,null,"Winter","Winter","Summer","Summer","Winter","Summer","Non-Holiday/Non-Break Hours",null,null,null,null,"Monthly/Seasonal","Occupied",null,"Calculation Year",null,2018,null,null,"Total Bin Hours Check",null,null,null,null,null,"Occ Hours",null,{"$f":"SUM(AT15:AT38)","v":0}]
["Date (MM/DD/YYYY)","Month","Day","Year",null,"Weekday","Holiday","Time (HH:MM)","Hour","DB (°F)","DB (°F)","DB (°F)","DB (°F)","DB (°F)","DB (°F)","DB (°F)","DB (°F)","DB (°F)","DB (°F)","DB (°F)",null,"DB (°F)",null,null,"On Peak","Off Peak","On Peak","Off Peak","Demand","Demand","1-Standard US Holidays","2-No Holidays","3-School w/ Breaks","4-Seasonal-Summer Peak","5-Seasonal-Winter Peak","Diversity","Hour",null,"Hours of Operation",null,null,null,null,"Annual Hours",null,null,{"$f":"SUM(AU15:AX38,BE15:BH38)","v":8760},8760,null,"Unocc Hours",null,{"$f":"SUM(BD15:BD38)","v":8760}]
["1976-01-01",1,1,{"$f":"$AO$4","v":2018},{"$f":"DATE(D6,B6,C6)","v":"2018-01-01"},{"$f":"WEEKDAY(E6,2)","v":1},{"$f":"COUNTIF($AM$34:$AM$43,E6)","v":1},"01:00:00",{"$f":"H6*24","v":1},-11.019999999999996,28.04,23,30.2,-14.080000000000005,30.92,8.5999999999999979,21.2,28.58,31.46,24.98,null,{"$f":"SUMPRODUCT($J$2:$T$2,J6:T6)","v":0},null,null,{"$f":"OR(B6<=$AO$14,B6>=$AN$14)*(F6<6)*(I6>$AN$15)*(I6<=$AO$15)*(G6<>1)","v":0},{"$f":"OR(B6<=$AO$14,B6>=$AN$14)*(Y6=0)","v":1},{"$f":"AND(B6>=$AN$24,B6<=$AO$24)*(F6<6)*(I6>$AN$25)*(I6<=$AO$25)*(G6<>1)","v":0},{"$f":"AND(B6>=$AN$24,B6<=$AO$24)*(AA6=0)","v":0},{"$f":"OR(B6<=$AO$19,B6>=$AN$19)*(F6<6)*(I6>$AN$20)*(I6<=$AO$20)","v":0},{"$f":"AND(B6>=$AN$29,B6<=$AO$29)*(F6<6)*(I6>$AN$30)*(I6<=$AO$30)","v":0},{"$f":"IF(OR(E6=$AM$34,E6=$AM$35,E6=$AM$36,E6=$AM$37,E6=$AM$38,E6=$AM$39,E6=$AM$40,E6=$AM$41,E6=$AM$42,E6=$AM$43),0,1)","v":0},1,{"$f":"IF(OR(AND(E6>=$AM$47,E6<=$AN$47),AND(E6>=$AM$48,E6<=$AN$48),AND(E6>=$AM$49,E6<=$AN$49),AND(E6>=$AM$50,E6<=$AN$50),AND(E6>=$AM$51,E6<=$AN$51)),0,1)*AE6","v":0},{"$f":"(B6>=5)*(B6<=10)","v":0},{"$f":"1*OR(B6<=4,B6>=11)","v":1},{"$f":"LOOKUP(B6,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE6:AI6)*((F6<6)*(I6>$AO$7)*(I6<=$AP$7)+(F6=6)*(I6>$AO$8)*(I6<=$AP$8)+(F6>=7)*(I6>$AO$9)*(I6<=$AP$9))","v":0},null,null,null,"Start","End",null,"On Peak Hours",null,null,{"$f":"SUM(AU15:AU38,AW15:AW38,BE15:BE38,BG15:BG38)","v":4016},4016,null,"Total",null,{"$f":"AZ5+AZ4","v":8760}]
["1976-01-01",1,1,2018,{"$f":"DATE(D7,B7,C7)","v":"2018-01-01"},{"$f":"WEEKDAY(E7,2)","v":1},1,"02:00:00",{"$f":"H7*24","v":2},-9.9400000000000048,28.04,19.399999999999999,30.2,-14.980000000000004,32,8.5999999999999979,19.04,31.46,32.18,24.08,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0,null,"Weekdays",null,{"$f":"'Project Info'!I15","v":0},{"$f":"'Project Info'!J15","v":0},null,"Off Peak Hours",null,null,{"$f":"SUM(AV15:AV38,AX15:AX38,BF15:BF38,BH15:BH38)","v":4744},4744]
["1976-01-01",1,1,2018,"2018-01-01",1,1,"03:00:00",{"$f":"H8*24","v":3},-11.019999999999996,30.92,19.399999999999999,30.2,-20.019999999999996,32.18,8.5999999999999979,19.04,31.1,32.54,21.02,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0,null,"Saturday",null,{"$f":"'Project Info'!I16","v":0},{"$f":"'Project Info'!J16","v":0},null,"Winter Demand Hours",null,null,{"$f":"SUM(AY15:AY38,BI15:BI38)","v":88},88]
["1976-01-01",1,1,2018,"2018-01-01",1,1,"04:00:00",4,-11.019999999999996,32,17.600000000000001,33.799999999999997,-18.940000000000005,32.36,8.5999999999999979,18.14,30.92,32.9,19.939999999999998,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0,null,"Sunday",null,{"$f":"'Project Info'!I17","v":0},{"$f":"'Project Info'!J17","v":0},null,"Summer Demand Hours",null,null,{"$f":"SUM(AZ15:AZ38,BJ15:BJ38)","v":264},264]
["1976-01-01",1,1,2018,"2018-01-01",1,1,"05:00:00",5,-18.04,32,17.600000000000001,32,-16.96,33.08,6.8000000000000007,19.04,31.1,32.18,19.399999999999999,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0,null,"Annual Use Profile",null,{"$f":"'Project Info'!I18","v":"1-Standard US Holidays"}]
["1976-01-01",1,1,2018,"2018-01-01",1,1,"06:00:00",6,-20.92,32,15.8,32,-18.04,33.08,3.1999999999999993,17.059999999999999,32,32.18,17.600000000000001,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0,null,null,null,null,null,null,"Occupied Hours Peak Period Distribution",null,null,null,null,null,null,null,null,null,"Unoccupied Hours Peak Period Distribution",null,null,null,null,null,null,null,null,null,"All Hours Peak Period Distribution",null,null,null,null,null,null,null,null,null,null,null,null,null,"(Table used for Binx in Calculations)"]
["1976-01-01",1,1,2018,"2018-01-01",1,1,"07:00:00",7,-13,32,15.8,33.799999999999997,-23.980000000000004,33.979999999999997,-0.39999999999999858,17.059999999999999,31.1,31.82,19.04,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0,null,"Winter OnPeak Period Hours",null,null,null,null,"OA Drybulb",null,null,null,null,null,null,null,null,null,"OA Drybulb",null,null,null,null,null,null,null,null,null,"OA Drybulb",null,null,null,null,null,null,null,null,null,"Default Fill-In Values",null,null,null,"Avg. Ambient Conditions for this Project"]
["1976-01-01",1,1,2018,"2018-01-01",1,1,"08:00:00",8,-11.019999999999996,32,15.8,30.2,-20.019999999999996,35.06,-2.2000000000000028,19.04,28.4,32.18,19.04,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0,null,null,"Start","End",null,null,"Bin Range",null,"Total","Winter","Winter","Summer","Summer","Winter","Summer",null,"Bin Range",null,"Total","Winter","Winter","Summer","Summer","Winter","Summer",null,"Bin Range",null,"Total","Winter","Winter","Summer","Summer","Winter","Summer",null,"OA db","OA wb","OA Enth","Row","OA db","OA wb","OA Enth"]
["1976-01-01",1,1,2018,"2018-01-01",1,1,"09:00:00",9,-9.9400000000000048,30.92,17.600000000000001,28.4,-18.940000000000005,32,-5.8000000000000043,22.1,25.7,33.08,21.02,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0,null,"Months",10,5,null,null,"From","To","Hours","On Peak","Off Peak","On Peak","Off Peak","Demand","Demand",null,"From","To","Hours","On Peak","Off Peak","On Peak","Off Peak","Demand","Demand",null,"From","To","Hours","On Peak","Off Peak","On Peak","Off Peak","Demand","Demand",null,"°F","°F","Btu/lb",1,"°F","°F","Btu/lb"]
["1976-01-01",1,1,2018,"2018-01-01",1,1,"10:00:00",10,-7.9600000000000009,26.96,19.399999999999999,24.8,-7.0600000000000023,32,-7.6000000000000014,24.08,24.8,32.36,24.08,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0,null,"Peak Hrs",7,23,null,null,100,105,{"$f":"SUM(AU15:AX15)","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR15)*($V$6:$V$8765<$AS15)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR15)*($V$6:$V$8765<$AS15)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR15)*($V$6:$V$8765<$AS15)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR15)*($V$6:$V$8765<$AS15)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR15)*($V$6:$V$8765<$AS15)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR15)*($V$6:$V$8765<$AS15)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,100,105,{"$f":"SUM(BE15:BH15)","v":0},{"$f":"BO15-AU15","v":0},{"$f":"BP15-AV15","v":0},{"$f":"BQ15-AW15","v":0},{"$f":"BR15-AX15","v":0},{"$f":"BS15-AY15","v":0},{"$f":"BT15-AZ15","v":0},null,100,105,{"$f":"SUM(BO15:BR15)","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB15)*($V$6:$V$8765<$BC15)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB15)*($V$6:$V$8765<$BC15)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB15)*($V$6:$V$8765<$BC15)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB15)*($V$6:$V$8765<$BC15)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB15)*($V$6:$V$8765<$BC15)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB15)*($V$6:$V$8765<$BC15)*(AD$6:AD$8765))","v":0},null,102,76,40,2,{"$f":"IFERROR(HLOOKUP($V$4,$AU$44:$BE$68,BY15),BV15)","v":102},{"$f":"IFERROR(HLOOKUP($V$4,$BI$44:$BS$68,BY15),BW15)","v":76},{"$f":"IFERROR(HLOOKUP($V$4,$BW$44:$CG$68,BY15),BX15)","v":40}]
["1976-01-01",1,1,2018,"2018-01-01",1,1,"11:00:00",11,-7.0600000000000023,26.96,23,26.6,-5.980000000000004,32,-7.6000000000000014,27.14,24.08,31.28,28.04,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0,null,null,null,null,null,null,95,100,0,{"$f":"SUM(($V$6:$V$8765>=$AR16)*($V$6:$V$8765<$AS16)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR16)*($V$6:$V$8765<$AS16)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR16)*($V$6:$V$8765<$AS16)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR16)*($V$6:$V$8765<$AS16)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR16)*($V$6:$V$8765<$AS16)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR16)*($V$6:$V$8765<$AS16)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,95,100,0,0,0,0,0,0,0,null,95,100,0,{"$f":"SUM(($V$6:$V$8765>=$BB16)*($V$6:$V$8765<$BC16)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB16)*($V$6:$V$8765<$BC16)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB16)*($V$6:$V$8765<$BC16)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB16)*($V$6:$V$8765<$BC16)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB16)*($V$6:$V$8765<$BC16)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB16)*($V$6:$V$8765<$BC16)*(AD$6:AD$8765))","v":0},null,{"$f":"_xlfn.AGGREGATE(1,6,AU46:BE46)","v":95.219272727272724},{"$f":"_xlfn.AGGREGATE(1,6,BI46:BS46)","v":74.534025272781079},{"$f":"_xlfn.AGGREGATE(1,6,BW46:CG46)","v":37.923296058061368},3,{"$f":"IFERROR(HLOOKUP($V$4,$AU$44:$BE$68,BY16),BV16)","v":95.219272727272724},{"$f":"IFERROR(HLOOKUP($V$4,$BI$44:$BS$68,BY16),BW16)","v":74.534025272781079},{"$f":"IFERROR(HLOOKUP($V$4,$BW$44:$CG$68,BY16),BX16)","v":37.923296058061368}]
["1976-01-01",1,1,2018,"2018-01-01",1,1,"12:00:00",12,-5.980000000000004,26.96,24.8,24.8,1.9400000000000013,30.92,-7.6000000000000014,28.4,24.62,31.1,30.02,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0,null,"Winter Demand Period Hours",null,null,null,null,90,95,0,{"$f":"SUM(($V$6:$V$8765>=$AR17)*($V$6:$V$8765<$AS17)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR17)*($V$6:$V$8765<$AS17)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR17)*($V$6:$V$8765<$AS17)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR17)*($V$6:$V$8765<$AS17)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR17)*($V$6:$V$8765<$AS17)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR17)*($V$6:$V$8765<$AS17)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,90,95,0,0,0,0,0,0,0,null,90,95,0,{"$f":"SUM(($V$6:$V$8765>=$BB17)*($V$6:$V$8765<$BC17)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB17)*($V$6:$V$8765<$BC17)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB17)*($V$6:$V$8765<$BC17)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB17)*($V$6:$V$8765<$BC17)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB17)*($V$6:$V$8765<$BC17)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB17)*($V$6:$V$8765<$BC17)*(AD$6:AD$8765))","v":0},null,{"$f":"_xlfn.AGGREGATE(1,6,AU47:BE47)","v":92.016049160256074},{"$f":"_xlfn.AGGREGATE(1,6,BI47:BS47)","v":72.911561930607689},{"$f":"_xlfn.AGGREGATE(1,6,BW47:CG47)","v":36.467095439351091},4,92.016049160256074,72.911561930607689,36.467095439351091]
["1976-01-01",1,1,2018,"2018-01-01",1,1,"13:00:00",13,-4,26.96,28.4,23.9,5,30.92,-7.6000000000000014,30.2,23.72,30.02,30.2,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0,null,null,"Start","End",null,null,85,90,0,{"$f":"SUM(($V$6:$V$8765>=$AR18)*($V$6:$V$8765<$AS18)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR18)*($V$6:$V$8765<$AS18)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR18)*($V$6:$V$8765<$AS18)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR18)*($V$6:$V$8765<$AS18)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR18)*($V$6:$V$8765<$AS18)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR18)*($V$6:$V$8765<$AS18)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,85,90,0,0,0,0,0,0,0,null,85,90,0,{"$f":"SUM(($V$6:$V$8765>=$BB18)*($V$6:$V$8765<$BC18)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB18)*($V$6:$V$8765<$BC18)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB18)*($V$6:$V$8765<$BC18)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB18)*($V$6:$V$8765<$BC18)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB18)*($V$6:$V$8765<$BC18)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB18)*($V$6:$V$8765<$BC18)*(AD$6:AD$8765))","v":0},null,87.457811360655285,70.80538329449476,34.679413213566804,5,87.457811360655285,70.80538329449476,34.679413213566804]
["1976-01-01",1,1,2018,"2018-01-01",1,1,"14:00:00",14,-2.019999999999996,26.96,28.4,23,6.98,30.92,-9.3999999999999986,32,22.82,29.66,30.2,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0,null,"Months",12,1,null,null,80,85,0,{"$f":"SUM(($V$6:$V$8765>=$AR19)*($V$6:$V$8765<$AS19)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR19)*($V$6:$V$8765<$AS19)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR19)*($V$6:$V$8765<$AS19)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR19)*($V$6:$V$8765<$AS19)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR19)*($V$6:$V$8765<$AS19)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR19)*($V$6:$V$8765<$AS19)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,80,85,0,0,0,0,0,0,0,null,80,85,0,{"$f":"SUM(($V$6:$V$8765>=$BB19)*($V$6:$V$8765<$BC19)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB19)*($V$6:$V$8765<$BC19)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB19)*($V$6:$V$8765<$BC19)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB19)*($V$6:$V$8765<$BC19)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB19)*($V$6:$V$8765<$BC19)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB19)*($V$6:$V$8765<$BC19)*(AD$6:AD$8765))","v":0},null,82.136788830239965,67.872393622439333,32.296248223809314,6,82.136788830239965,67.872393622439333,32.296248223809314]
["1976-01-01",1,1,2018,"2018-01-01",1,1,"15:00:00",15,-0.94000000000000483,26.96,28.4,23,6.0799999999999983,30.02,-11.200000000000003,33.799999999999997,21.740000000000002,29.48,30.02,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0,null,"Peak Hrs",17,19,null,null,75,80,0,{"$f":"SUM(($V$6:$V$8765>=$AR20)*($V$6:$V$8765<$AS20)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR20)*($V$6:$V$8765<$AS20)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR20)*($V$6:$V$8765<$AS20)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR20)*($V$6:$V$8765<$AS20)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR20)*($V$6:$V$8765<$AS20)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR20)*($V$6:$V$8765<$AS20)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,75,80,0,0,0,0,0,0,0,null,75,80,0,{"$f":"SUM(($V$6:$V$8765>=$BB20)*($V$6:$V$8765<$BC20)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB20)*($V$6:$V$8765<$BC20)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB20)*($V$6:$V$8765<$BC20)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB20)*($V$6:$V$8765<$BC20)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB20)*($V$6:$V$8765<$BC20)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB20)*($V$6:$V$8765<$BC20)*(AD$6:AD$8765))","v":0},null,76.988400157585886,65.129261896908645,30.190476812806729,7,76.988400157585886,65.129261896908645,30.190476812806729]
["1976-01-01",1,1,2018,"2018-01-01",1,1,"16:00:00",16,-2.019999999999996,24.98,28.4,21.2,5,28.04,-11.200000000000003,32.36,21.740000000000002,27.86,30.92,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0,null,null,null,null,null,null,70,75,0,{"$f":"SUM(($V$6:$V$8765>=$AR21)*($V$6:$V$8765<$AS21)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR21)*($V$6:$V$8765<$AS21)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR21)*($V$6:$V$8765<$AS21)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR21)*($V$6:$V$8765<$AS21)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR21)*($V$6:$V$8765<$AS21)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR21)*($V$6:$V$8765<$AS21)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,70,75,0,0,0,0,0,0,0,null,70,75,0,{"$f":"SUM(($V$6:$V$8765>=$BB21)*($V$6:$V$8765<$BC21)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB21)*($V$6:$V$8765<$BC21)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB21)*($V$6:$V$8765<$BC21)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB21)*($V$6:$V$8765<$BC21)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB21)*($V$6:$V$8765<$BC21)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB21)*($V$6:$V$8765<$BC21)*(AD$6:AD$8765))","v":0},null,72.457982050814195,63.604425012889301,29.088683095945193,8,72.457982050814195,63.604425012889301,29.088683095945193]
["1976-01-01",1,1,2018,"2018-01-01",1,1,"17:00:00",17,-4,24.98,28.4,21.2,-3.9999999999999147E-2,26.060000000000002,-11.200000000000003,32.9,19.399999999999999,24.8,30.2,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0,null,"Summer OnPeak Period Hours",null,null,null,null,65,70,0,{"$f":"SUM(($V$6:$V$8765>=$AR22)*($V$6:$V$8765<$AS22)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR22)*($V$6:$V$8765<$AS22)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR22)*($V$6:$V$8765<$AS22)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR22)*($V$6:$V$8765<$AS22)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR22)*($V$6:$V$8765<$AS22)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR22)*($V$6:$V$8765<$AS22)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,65,70,0,0,0,0,0,0,0,null,65,70,0,{"$f":"SUM(($V$6:$V$8765>=$BB22)*($V$6:$V$8765<$BC22)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB22)*($V$6:$V$8765<$BC22)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB22)*($V$6:$V$8765<$BC22)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB22)*($V$6:$V$8765<$BC22)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB22)*($V$6:$V$8765<$BC22)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB22)*($V$6:$V$8765<$BC22)*(AD$6:AD$8765))","v":0},null,67.815831070966169,61.631331368130574,27.661514889731574,9,67.815831070966169,61.631331368130574,27.661514889731574]
["1976-01-01",1,1,2018,"2018-01-01",1,1,"18:00:00",18,-5.0800000000000054,19.939999999999998,28.4,19.399999999999999,-7.9600000000000009,24.08,-13,32.9,17.059999999999999,23,30.2,null,0,null,null,0,1,0,0,1,0,0,1,0,0,1,1,0,null,null,"Start","End",null,null,60,65,0,{"$f":"SUM(($V$6:$V$8765>=$AR23)*($V$6:$V$8765<$AS23)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR23)*($V$6:$V$8765<$AS23)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR23)*($V$6:$V$8765<$AS23)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR23)*($V$6:$V$8765<$AS23)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR23)*($V$6:$V$8765<$AS23)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR23)*($V$6:$V$8765<$AS23)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,60,65,0,0,0,0,0,0,0,null,60,65,0,{"$f":"SUM(($V$6:$V$8765>=$BB23)*($V$6:$V$8765<$BC23)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB23)*($V$6:$V$8765<$BC23)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB23)*($V$6:$V$8765<$BC23)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB23)*($V$6:$V$8765<$BC23)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB23)*($V$6:$V$8765<$BC23)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB23)*($V$6:$V$8765<$BC23)*(AD$6:AD$8765))","v":0},null,62.535961472271332,57.135476922863582,24.623037157728302,10,62.535961472271332,57.135476922863582,24.623037157728302]
["1976-01-01",1,1,2018,"2018-01-01",1,1,"19:00:00",19,-5.980000000000004,19.04,28.4,17.600000000000001,-14.980000000000004,23,-14.800000000000004,33.799999999999997,15.8,21.2,30.2,null,0,null,null,0,1,0,0,1,0,0,1,0,0,1,1,0,null,"Months",6,9,null,null,55,60,0,{"$f":"SUM(($V$6:$V$8765>=$AR24)*($V$6:$V$8765<$AS24)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR24)*($V$6:$V$8765<$AS24)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR24)*($V$6:$V$8765<$AS24)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR24)*($V$6:$V$8765<$AS24)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR24)*($V$6:$V$8765<$AS24)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR24)*($V$6:$V$8765<$AS24)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,55,60,0,0,0,0,0,0,0,null,55,60,0,{"$f":"SUM(($V$6:$V$8765>=$BB24)*($V$6:$V$8765<$BC24)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB24)*($V$6:$V$8765<$BC24)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB24)*($V$6:$V$8765<$BC24)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB24)*($V$6:$V$8765<$BC24)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB24)*($V$6:$V$8765<$BC24)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB24)*($V$6:$V$8765<$BC24)*(AD$6:AD$8765))","v":0},null,57.125792270740902,52.596971157053673,21.818001539159841,11,57.125792270740902,52.596971157053673,21.818001539159841]
["1976-01-01",1,1,2018,"2018-01-01",1,1,"20:00:00",20,-7.9600000000000009,19.04,26.6,15.8,-14.980000000000004,21.02,-14.800000000000004,31.1,14.719999999999999,19.759999999999998,32,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0,null,"Peak Hrs",7,23,null,null,50,55,0,{"$f":"SUM(($V$6:$V$8765>=$AR25)*($V$6:$V$8765<$AS25)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR25)*($V$6:$V$8765<$AS25)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR25)*($V$6:$V$8765<$AS25)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR25)*($V$6:$V$8765<$AS25)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR25)*($V$6:$V$8765<$AS25)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR25)*($V$6:$V$8765<$AS25)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,50,55,0,0,0,0,0,0,0,null,50,55,0,{"$f":"SUM(($V$6:$V$8765>=$BB25)*($V$6:$V$8765<$BC25)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB25)*($V$6:$V$8765<$BC25)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB25)*($V$6:$V$8765<$BC25)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB25)*($V$6:$V$8765<$BC25)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB25)*($V$6:$V$8765<$BC25)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB25)*($V$6:$V$8765<$BC25)*(AD$6:AD$8765))","v":0},null,52.235698854337961,48.022768090099298,19.246640192796217,12,52.235698854337961,48.022768090099298,19.246640192796217]
["1976-01-01",1,1,2018,"2018-01-01",1,1,"21:00:00",21,-9.9400000000000048,15.98,26.6,14,-14.080000000000005,19.939999999999998,-16.600000000000001,32.18,13.64,18.5,32.18,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0,null,null,null,null,null,null,45,50,0,{"$f":"SUM(($V$6:$V$8765>=$AR26)*($V$6:$V$8765<$AS26)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR26)*($V$6:$V$8765<$AS26)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR26)*($V$6:$V$8765<$AS26)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR26)*($V$6:$V$8765<$AS26)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR26)*($V$6:$V$8765<$AS26)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR26)*($V$6:$V$8765<$AS26)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,45,50,0,0,0,0,0,0,0,null,45,50,0,{"$f":"SUM(($V$6:$V$8765>=$BB26)*($V$6:$V$8765<$BC26)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB26)*($V$6:$V$8765<$BC26)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB26)*($V$6:$V$8765<$BC26)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB26)*($V$6:$V$8765<$BC26)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB26)*($V$6:$V$8765<$BC26)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB26)*($V$6:$V$8765<$BC26)*(AD$6:AD$8765))","v":0},null,47.459170258371508,43.465397050422162,16.894183241713304,13,47.459170258371508,43.465397050422162,16.894183241713304]
["1976-01-01",1,1,2018,"2018-01-01",1,1,"22:00:00",22,-14.980000000000004,15.079999999999998,26.6,14,-14.080000000000005,17.96,-16.600000000000001,30.2,12.740000000000002,17.059999999999999,28.4,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0,null,"Summer Demand Period Hours",null,null,null,null,40,45,0,{"$f":"SUM(($V$6:$V$8765>=$AR27)*($V$6:$V$8765<$AS27)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR27)*($V$6:$V$8765<$AS27)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR27)*($V$6:$V$8765<$AS27)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR27)*($V$6:$V$8765<$AS27)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR27)*($V$6:$V$8765<$AS27)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR27)*($V$6:$V$8765<$AS27)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,40,45,0,0,0,0,0,0,0,null,40,45,0,{"$f":"SUM(($V$6:$V$8765>=$BB27)*($V$6:$V$8765<$BC27)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB27)*($V$6:$V$8765<$BC27)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB27)*($V$6:$V$8765<$BC27)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB27)*($V$6:$V$8765<$BC27)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB27)*($V$6:$V$8765<$BC27)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB27)*($V$6:$V$8765<$BC27)*(AD$6:AD$8765))","v":0},null,42.677030404888129,38.812544504634097,14.690265649465921,14,42.677030404888129,38.812544504634097,14.690265649465921]
["1976-01-01",1,1,2018,"2018-01-01",1,1,"23:00:00",23,-16.060000000000002,15.079999999999998,21.2,12.2,-20.019999999999996,17.059999999999999,-16.600000000000001,23,12.2,15.8,28.4,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0,null,null,"Start","End",null,null,35,40,0,{"$f":"SUM(($V$6:$V$8765>=$AR28)*($V$6:$V$8765<$AS28)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR28)*($V$6:$V$8765<$AS28)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR28)*($V$6:$V$8765<$AS28)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR28)*($V$6:$V$8765<$AS28)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR28)*($V$6:$V$8765<$AS28)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR28)*($V$6:$V$8765<$AS28)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,35,40,0,0,0,0,0,0,0,null,35,40,0,{"$f":"SUM(($V$6:$V$8765>=$BB28)*($V$6:$V$8765<$BC28)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB28)*($V$6:$V$8765<$BC28)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB28)*($V$6:$V$8765<$BC28)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB28)*($V$6:$V$8765<$BC28)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB28)*($V$6:$V$8765<$BC28)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB28)*($V$6:$V$8765<$BC28)*(AD$6:AD$8765))","v":0},null,37.333046773755832,33.904706919479686,12.53841602318813,15,37.333046773755832,33.904706919479686,12.53841602318813]
["1976-01-01",1,1,2018,"2018-01-01",1,1,1,24,-18.940000000000005,10.039999999999999,23,12.2,-20.019999999999996,15.079999999999998,-16.600000000000001,23,11.84,15.079999999999998,28.4,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0,null,"Months",6,8,null,null,30,35,0,{"$f":"SUM(($V$6:$V$8765>=$AR29)*($V$6:$V$8765<$AS29)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR29)*($V$6:$V$8765<$AS29)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR29)*($V$6:$V$8765<$AS29)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR29)*($V$6:$V$8765<$AS29)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR29)*($V$6:$V$8765<$AS29)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR29)*($V$6:$V$8765<$AS29)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,30,35,0,0,0,0,0,0,0,null,30,35,0,{"$f":"SUM(($V$6:$V$8765>=$BB29)*($V$6:$V$8765<$BC29)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB29)*($V$6:$V$8765<$BC29)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB29)*($V$6:$V$8765<$BC29)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB29)*($V$6:$V$8765<$BC29)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB29)*($V$6:$V$8765<$BC29)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB29)*($V$6:$V$8765<$BC29)*(AD$6:AD$8765))","v":0},null,32.638179845662044,29.547170928664851,10.728972818165861,16,32.638179845662044,29.547170928664851,10.728972818165861]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"01:00:00",1,-20.92,8.9599999999999973,24.8,12.2,-16.96,14,-14.800000000000004,19.399999999999999,11.3,14,30.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0,null,"Peak Hrs",13,17,null,null,25,30,0,{"$f":"SUM(($V$6:$V$8765>=$AR30)*($V$6:$V$8765<$AS30)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR30)*($V$6:$V$8765<$AS30)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR30)*($V$6:$V$8765<$AS30)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR30)*($V$6:$V$8765<$AS30)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR30)*($V$6:$V$8765<$AS30)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR30)*($V$6:$V$8765<$AS30)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,25,30,0,0,0,0,0,0,0,null,25,30,0,{"$f":"SUM(($V$6:$V$8765>=$BB30)*($V$6:$V$8765<$BC30)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB30)*($V$6:$V$8765<$BC30)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB30)*($V$6:$V$8765<$BC30)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB30)*($V$6:$V$8765<$BC30)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB30)*($V$6:$V$8765<$BC30)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB30)*($V$6:$V$8765<$BC30)*(AD$6:AD$8765))","v":0},null,27.529264646850947,24.652717392657845,8.8041305482613303,17,27.529264646850947,24.652717392657845,8.8041305482613303]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"02:00:00",2,-23.980000000000004,8.9599999999999973,24.8,11.3,-13,14,-14.800000000000004,17.600000000000001,10.399999999999999,12.920000000000002,30.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0,null,null,null,null,null,null,20,25,0,{"$f":"SUM(($V$6:$V$8765>=$AR31)*($V$6:$V$8765<$AS31)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR31)*($V$6:$V$8765<$AS31)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR31)*($V$6:$V$8765<$AS31)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR31)*($V$6:$V$8765<$AS31)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR31)*($V$6:$V$8765<$AS31)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR31)*($V$6:$V$8765<$AS31)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,20,25,0,0,0,0,0,0,0,null,20,25,0,{"$f":"SUM(($V$6:$V$8765>=$BB31)*($V$6:$V$8765<$BC31)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB31)*($V$6:$V$8765<$BC31)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB31)*($V$6:$V$8765<$BC31)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB31)*($V$6:$V$8765<$BC31)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB31)*($V$6:$V$8765<$BC31)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB31)*($V$6:$V$8765<$BC31)*(AD$6:AD$8765))","v":0},null,22.998111483544687,20.383306659827422,7.246164547543378,18,22.998111483544687,20.383306659827422,7.246164547543378]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"03:00:00",3,-27.04,8.9599999999999973,24.8,10.399999999999999,-16.060000000000002,14,-14.800000000000004,19.399999999999999,10.219999999999999,12.2,30.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0,null,"Standard US Holidays 2018",null,null,null,null,15,20,0,{"$f":"SUM(($V$6:$V$8765>=$AR32)*($V$6:$V$8765<$AS32)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR32)*($V$6:$V$8765<$AS32)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR32)*($V$6:$V$8765<$AS32)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR32)*($V$6:$V$8765<$AS32)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR32)*($V$6:$V$8765<$AS32)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR32)*($V$6:$V$8765<$AS32)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,15,20,0,0,0,0,0,0,0,null,15,20,0,{"$f":"SUM(($V$6:$V$8765>=$BB32)*($V$6:$V$8765<$BC32)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB32)*($V$6:$V$8765<$BC32)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB32)*($V$6:$V$8765<$BC32)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB32)*($V$6:$V$8765<$BC32)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB32)*($V$6:$V$8765<$BC32)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB32)*($V$6:$V$8765<$BC32)*(AD$6:AD$8765))","v":0},null,17.808510327474309,15.420865796304254,5.5490484131518292,19,17.808510327474309,15.420865796304254,5.5490484131518292]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"04:00:00",4,-25.060000000000002,3.9200000000000017,26.6,8.5999999999999979,-23.080000000000005,12.920000000000002,-14.800000000000004,24.8,8.9599999999999973,12.2,30.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0,null,"Date","Holiday",null,null,null,10,15,0,{"$f":"SUM(($V$6:$V$8765>=$AR33)*($V$6:$V$8765<$AS33)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR33)*($V$6:$V$8765<$AS33)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR33)*($V$6:$V$8765<$AS33)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR33)*($V$6:$V$8765<$AS33)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR33)*($V$6:$V$8765<$AS33)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR33)*($V$6:$V$8765<$AS33)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,10,15,0,0,0,0,0,0,0,null,10,15,0,{"$f":"SUM(($V$6:$V$8765>=$BB33)*($V$6:$V$8765<$BC33)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB33)*($V$6:$V$8765<$BC33)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB33)*($V$6:$V$8765<$BC33)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB33)*($V$6:$V$8765<$BC33)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB33)*($V$6:$V$8765<$BC33)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB33)*($V$6:$V$8765<$BC33)*(AD$6:AD$8765))","v":0},null,12.269931130346862,10.318264913023604,3.9082824916941998,20,12.269931130346862,10.318264913023604,3.9082824916941998]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"05:00:00",5,-16.060000000000002,3.9200000000000017,24.8,8.5999999999999979,-23.080000000000005,12.920000000000002,-14.800000000000004,23,1.9400000000000013,11.48,28.4,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0,null,"2018-01-01","New Years Day",null,null,null,5,10,0,{"$f":"SUM(($V$6:$V$8765>=$AR34)*($V$6:$V$8765<$AS34)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR34)*($V$6:$V$8765<$AS34)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR34)*($V$6:$V$8765<$AS34)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR34)*($V$6:$V$8765<$AS34)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR34)*($V$6:$V$8765<$AS34)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR34)*($V$6:$V$8765<$AS34)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,5,10,0,0,0,0,0,0,0,null,5,10,0,{"$f":"SUM(($V$6:$V$8765>=$BB34)*($V$6:$V$8765<$BC34)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB34)*($V$6:$V$8765<$BC34)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB34)*($V$6:$V$8765<$BC34)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB34)*($V$6:$V$8765<$BC34)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB34)*($V$6:$V$8765<$BC34)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB34)*($V$6:$V$8765<$BC34)*(AD$6:AD$8765))","v":0},null,7.3137581369917548,5.7052382449247707,2.5019418419888937,21,7.3137581369917548,5.7052382449247707,2.5019418419888937]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"06:00:00",6,-20.92,-2.019999999999996,24.8,8.5999999999999979,-20.019999999999996,12.02,-14.800000000000004,19.04,-0.94000000000000483,12.379999999999999,26.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0,null,"2018-01-15","MLK Day",null,null,null,0,5,0,{"$f":"SUM(($V$6:$V$8765>=$AR35)*($V$6:$V$8765<$AS35)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR35)*($V$6:$V$8765<$AS35)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR35)*($V$6:$V$8765<$AS35)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR35)*($V$6:$V$8765<$AS35)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR35)*($V$6:$V$8765<$AS35)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR35)*($V$6:$V$8765<$AS35)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,0,5,8760,2672,3160,1344,1584,88,264,null,0,5,8760,{"$f":"SUM(($V$6:$V$8765>=$BB35)*($V$6:$V$8765<$BC35)*(Y$6:Y$8765))","v":2672},{"$f":"SUM(($V$6:$V$8765>=$BB35)*($V$6:$V$8765<$BC35)*(Z$6:Z$8765))","v":3160},{"$f":"SUM(($V$6:$V$8765>=$BB35)*($V$6:$V$8765<$BC35)*(AA$6:AA$8765))","v":1344},{"$f":"SUM(($V$6:$V$8765>=$BB35)*($V$6:$V$8765<$BC35)*(AB$6:AB$8765))","v":1584},{"$f":"SUM(($V$6:$V$8765>=$BB35)*($V$6:$V$8765<$BC35)*(AC$6:AC$8765))","v":88},{"$f":"SUM(($V$6:$V$8765>=$BB35)*($V$6:$V$8765<$BC35)*(AD$6:AD$8765))","v":264},null,2.6119461836144886,1.2699770062067783,1.2046477897733283,22,2.6119461836144886,1.2699770062067783,1.2046477897733283]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"07:00:00",7,-20.019999999999996,1.9400000000000013,24.8,10.399999999999999,-23.080000000000005,10.039999999999999,-14.800000000000004,19.399999999999999,1.0399999999999991,12.2,24.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0,null,"2018-02-19","Presidents Day",null,null,null,-5,0,0,{"$f":"SUM(($V$6:$V$8765>=$AR36)*($V$6:$V$8765<$AS36)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR36)*($V$6:$V$8765<$AS36)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR36)*($V$6:$V$8765<$AS36)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR36)*($V$6:$V$8765<$AS36)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR36)*($V$6:$V$8765<$AS36)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR36)*($V$6:$V$8765<$AS36)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,-5,0,0,0,0,0,0,0,0,null,-5,0,0,{"$f":"SUM(($V$6:$V$8765>=$BB36)*($V$6:$V$8765<$BC36)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB36)*($V$6:$V$8765<$BC36)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB36)*($V$6:$V$8765<$BC36)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB36)*($V$6:$V$8765<$BC36)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB36)*($V$6:$V$8765<$BC36)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB36)*($V$6:$V$8765<$BC36)*(AD$6:AD$8765))","v":0},null,-1.6731398516793925,-2.7083318773557807,7.9391832815876459E-2,23,-1.6731398516793925,-2.7083318773557807,7.9391832815876459E-2]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"08:00:00",8,-20.92,1.9400000000000013,23,12.2,-23.980000000000004,12.02,-11.200000000000003,24.08,3.9200000000000017,13.279999999999998,24.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0,null,"2018-05-28","Memorial Day",null,null,null,-10,-5,0,{"$f":"SUM(($V$6:$V$8765>=$AR37)*($V$6:$V$8765<$AS37)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR37)*($V$6:$V$8765<$AS37)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR37)*($V$6:$V$8765<$AS37)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR37)*($V$6:$V$8765<$AS37)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR37)*($V$6:$V$8765<$AS37)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR37)*($V$6:$V$8765<$AS37)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,-10,-5,0,0,0,0,0,0,0,null,-10,-5,0,{"$f":"SUM(($V$6:$V$8765>=$BB37)*($V$6:$V$8765<$BC37)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB37)*($V$6:$V$8765<$BC37)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB37)*($V$6:$V$8765<$BC37)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB37)*($V$6:$V$8765<$BC37)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB37)*($V$6:$V$8765<$BC37)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB37)*($V$6:$V$8765<$BC37)*(AD$6:AD$8765))","v":0},null,-6.5729865085377277,-7.2465935998252222,-1.168423365310433,24,-6.5729865085377277,-7.2465935998252222,-1.168423365310433]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"09:00:00",9,-18.04,10.940000000000001,21.2,12.2,-20.92,14,-11.200000000000003,27.14,6.259999999999998,15.440000000000001,24.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0,null,"2018-07-04","Independence Day",null,null,null,-30,-10,0,{"$f":"SUM(($V$6:$V$8765>=$AR38)*($V$6:$V$8765<$AS38)*(Y$6:Y$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR38)*($V$6:$V$8765<$AS38)*(Z$6:Z$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR38)*($V$6:$V$8765<$AS38)*(AA$6:AA$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR38)*($V$6:$V$8765<$AS38)*(AB$6:AB$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR38)*($V$6:$V$8765<$AS38)*(AC$6:AC$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$AR38)*($V$6:$V$8765<$AS38)*(AD$6:AD$8765)*($AK$6:$AK$8765)*($AJ$6:$AJ$8765))","v":0},null,-30,-10,0,0,0,0,0,0,0,null,-30,-10,0,{"$f":"SUM(($V$6:$V$8765>=$BB38)*($V$6:$V$8765<$BC38)*(Y$6:Y$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB38)*($V$6:$V$8765<$BC38)*(Z$6:Z$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB38)*($V$6:$V$8765<$BC38)*(AA$6:AA$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB38)*($V$6:$V$8765<$BC38)*(AB$6:AB$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB38)*($V$6:$V$8765<$BC38)*(AC$6:AC$8765))","v":0},{"$f":"SUM(($V$6:$V$8765>=$BB38)*($V$6:$V$8765<$BC38)*(AD$6:AD$8765))","v":0},null,-15.32570353422995,-15.707838211108999,-3.4051318156661381,25,-15.32570353422995,-15.707838211108999,-3.4051318156661381]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"10:00:00",10,-5.980000000000004,17.96,21.2,14,-13,19.04,-11.200000000000003,26.6,10.039999999999999,17.78,26.6,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0,null,"2018-09-03","Labor Day"]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"11:00:00",11,-3.9999999999999147E-2,17.96,21.2,15.8,-7.9600000000000009,21.92,-11.200000000000003,28.04,16.159999999999997,22.28,28.4,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0,null,"2018-10-08","Columbus Day"]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"12:00:00",12,1.0399999999999991,21.92,21.2,19.399999999999999,-2.019999999999996,24.98,-11.200000000000003,27.14,19.939999999999998,25.34,28.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0,null,"2018-11-12","Veterans Day"]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"13:00:00",13,3.019999999999996,23,21.2,23,3.9200000000000017,24.08,-13,26.060000000000002,20.12,24.259999999999998,28.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0,null,"2018-11-22","Thanksgiving",null,null,null,null,"OA Drybulb",null,null,null,null,null,null,null,null,null,null,null,null,null,"OA Drybulb",null,null,null,null,null,null,null,null,null,null,null,null,null,"OA Drybulb"]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"14:00:00",14,5,23,21.2,21.2,3.9200000000000017,24.08,-13,26.060000000000002,20.12,23.9,24.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0,null,"2018-12-25","Christmas",null,null,null,null,"Bin Range",null,"AVERAGE DRYBULB",null,null,null,null,null,null,null,null,null,null,null,"Bin Range",null,"AVERAGE WETBULB",null,null,null,null,null,null,null,null,null,null,null,"Bin Range",null,"AVERAGE BTU/LB"]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"15:00:00",15,3.9200000000000017,21.02,19.399999999999999,21.2,5,24.98,-16.600000000000001,24.08,18.86,24.439999999999998,23,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0,null,null,null,null,null,null,null,"From","To",{"$f":"J3","v":"Berlin"},"Concord","Keene","Laconia","Lebanon","Manchester","Mt. Washington","Nashua","Plymouth","Portsmouth","Rochester",null,"From","To",{"$f":"J3","v":"Berlin"},"Concord","Keene","Laconia","Lebanon","Manchester","Mt. Washington","Nashua","Plymouth","Portsmouth","Rochester",null,"From","To",{"$f":"J3","v":"Berlin"},"Concord","Keene","Laconia","Lebanon","Manchester","Mt. Washington","Nashua","Plymouth","Portsmouth","Rochester"]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"16:00:00",16,3.019999999999996,19.939999999999998,19.399999999999999,17.600000000000001,3.9200000000000017,23,-16.600000000000001,22.1,17.420000000000002,22.64,21.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0,null,"MA School Vacations 2018",null,null,null,null,null,100,105,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},null,100,105,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},null,100,105,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"17:00:00",17,-2.019999999999996,19.939999999999998,15.8,17.600000000000001,-0.94000000000000483,19.939999999999998,-18.399999999999999,19.04,13.82,20.479999999999997,17.059999999999999,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0,null,"Start","End",null,null,null,null,95,100,{"$error":"#DIV/0!"},95.215999999999994,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},95.36,{"$error":"#DIV/0!"},95.081818181818193,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},null,95,100,{"$error":"#DIV/0!"},75.596249492170017,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},74.623728345241631,{"$error":"#DIV/0!"},73.38209798093159,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},null,95,100,{"$error":"#DIV/0!"},38.961527027186293,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},37.993994697762503,{"$error":"#DIV/0!"},36.814366449235301,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"18:00:00",18,-5.980000000000004,15.98,14,14,-2.9200000000000017,19.04,-13,16.159999999999997,11.120000000000001,18.5,14,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0,null,"2018-02-19","2018-02-23","Feb Vacation",null,null,null,90,95,{"$error":"#DIV/0!"},92.31674418604652,91.940000000000012,{"$error":"#DIV/0!"},92.215294117647076,92.34714285714287,{"$error":"#DIV/0!"},92.106666666666626,91.28,91.868000000000023,92.054545454545462,null,90,95,{"$error":"#DIV/0!"},71.971223375844872,71.729493507756473,{"$error":"#DIV/0!"},73.149393207384279,72.06282764203695,{"$error":"#DIV/0!"},71.392636739602096,73.926269730359067,75.329896404279367,73.730754837598369,null,90,95,{"$error":"#DIV/0!"},35.566298043534012,35.358043116773082,{"$error":"#DIV/0!"},36.677569252196946,35.682603122822812,{"$error":"#DIV/0!"},35.114375136552674,37.377836811134962,38.7522650436525,37.20777298814177]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"19:00:00",19,-5.0800000000000054,12.02,12.2,10.399999999999999,-0.94000000000000483,17.059999999999999,-2.2000000000000028,12.02,8.0599999999999987,15.98,10.940000000000001,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0,null,"2018-04-16","2018-04-20","April Vacation",null,null,null,85,90,87.152765957446817,88.129464285714178,87.85842105263157,87.590000000000074,88.011874999999989,87.897226277372141,85.28,87.781999999999783,87.248888888888885,87.192499999999995,87.892783505154625,null,85,90,71.362609990520923,69.749547747804598,70.27203541760008,69.915301714523622,71.264846810230011,70.74887650491182,69.829923476789929,70.208508272076159,69.268824420961877,73.768030135459583,72.470711748563744,null,85,90,35.122604772047779,33.740045303883846,34.170653083244176,33.913984909016122,35.048148836310283,34.654228533510796,33.73066442038197,34.237247362969775,33.323940667456185,37.378183482833265,36.153843977580628]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"20:00:00",20,-2.2000000000000028,12.02,10.399999999999999,8.5999999999999979,-3.9999999999999147E-2,12.920000000000002,-13,10.039999999999999,5,13.459999999999997,8.0599999999999987,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0,null,"2018-06-25","2018-09-05","Summer Vacation",null,null,null,80,85,82.067931034482882,82.290363636363679,82.191685393258496,82.022895927601851,82.129606986899603,82.188913649025011,81.863000000000014,82.47421052631563,82.088000000000008,82.16972972972971,82.018340248962673,null,80,85,67.653466966867157,67.192064596728599,67.592199066465767,67.744565749905433,67.992693184311889,67.073659836136059,68.566363337786214,67.567245031979681,66.704148894816313,69.608052999894824,68.901870181940808,null,80,85,32.101867682512832,31.756922945602046,32.052813767313715,32.193803948627135,32.411520731962952,31.666513228082422,32.733926984909296,32.103795327407589,31.347286210759592,33.747391626247214,33.142888008477676]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"21:00:00",21,-0.94000000000000483,6.0799999999999983,8.5999999999999979,5,-2.019999999999996,10.039999999999999,-9.3999999999999986,8.0599999999999987,3.1999999999999993,10.940000000000001,6.0799999999999983,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0,null,"2018-11-21","2018-11-23","Thanksgiving Break",null,null,null,75,80,77.092884615384605,76.938164705882386,76.844084507042254,76.816043956044012,76.769807692307722,76.791094890510834,77.124000000000052,77.246877470355699,77.399082568807387,77.108641425389862,76.741719901719847,null,75,80,64.549801972961077,64.200363578197837,64.373999429549087,64.149647540519268,65.131682665912734,65.034471194303848,66.269301308718894,65.160005421940284,64.514522589322908,67.615020429936592,65.423064734632618,null,75,80,29.735553081532888,29.509507543552758,29.634097917360574,29.420897223835688,30.188844693240561,30.148836537806943,31.027950190838279,30.252399486352605,29.661683688208338,32.106581560434428,30.408893017710945]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"22:00:00",22,-3.9999999999999147E-2,3.9200000000000017,6.8000000000000007,3.1999999999999993,1.0399999999999991,8.0599999999999987,-9.3999999999999986,7.1599999999999966,1.759999999999998,7.879999999999999,5,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0,null,"2018-12-24","2018-12-31","Winter Break",null,null,null,70,75,72.5013688212928,72.392961165048646,72.486323529411834,72.503975903614446,72.440408163265289,72.410831792975969,72.392180451127814,72.507575150300511,72.549999999999983,72.353433395872372,72.49874418604648,null,70,75,62.651055959380258,63.337445828961982,62.589328148589537,63.196505258692447,63.419713512341417,63.916029798464187,63.896997376176778,63.946655569011625,62.433653102377278,65.723182773845821,64.538107813941011,null,70,75,28.357227055116255,28.938417712751217,28.369971809187831,28.750748023119844,28.983202194472504,29.317835396637772,29.280229629531217,29.375069785261456,28.217727509070716,30.634240367999251,29.750844572249022]
["1976-01-02",1,2,2018,"2018-01-02",2,0,"23:00:00",23,1.0399999999999991,3.9200000000000017,3.1999999999999993,3.1999999999999993,-2.019999999999996,6.0799999999999983,-5.8000000000000043,7.1599999999999966,0.5,6.259999999999998,5,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0,null,null,null,null,null,null,null,65,70,67.835704697986543,68.004688856729317,67.913066666666637,67.942996057818561,67.838785046728901,67.977048710601707,67.518406072106302,68.024507042253433,67.340477707006414,67.631307420494721,67.947153502235381,null,65,70,61.457667969586474,61.475548247555082,61.357128611209717,61.736414860801531,61.700992065626352,60.880829065043962,62.067649608450118,61.64261285074258,60.66247810558351,62.90545453389916,62.057869130937902,null,65,70,27.509967364829134,27.570204521010208,27.471881391274845,27.714004207625905,27.695533922930419,27.132108360255874,27.980029437150371,27.697676364142783,26.989127644386819,28.567992888842767,27.948137684598183]
["1976-01-02",1,2,2018,"2018-01-02",2,0,1,24,1.9400000000000013,1.9400000000000013,-0.39999999999999858,1.3999999999999986,-2.9200000000000017,5,-0.39999999999999858,6.0799999999999983,0.14000000000000057,4.6400000000000006,3.9200000000000017,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0,null,"Monthly/Seasonal Diversity",null,null,null,null,null,60,65,62.379404255319486,62.563116564417442,62.528513674197676,62.634965800273712,62.562024390244034,62.585319148936499,62.402647058823511,62.775687263556321,62.417478991596674,62.562133333333378,62.484285714285932,null,60,65,57.860982701013747,56.805552734741042,56.656133110387081,56.782025401716204,56.897637389595992,56.284620794392211,57.988267702236875,56.78542617638626,57.568832010862522,57.507650945554758,57.353117184612742,null,60,65,25.059139846924651,24.427979823309915,24.328030354188943,24.386910559425971,24.458567472014785,24.097328214458855,25.170371212944836,24.411666889373905,24.899450025647106,24.862000471169104,24.751963865553297]
["1976-01-03",1,3,2018,"2018-01-03",3,0,"01:00:00",1,-2.019999999999996,1.9400000000000013,-2.2000000000000028,1.3999999999999986,3.019999999999996,3.9200000000000017,3.1999999999999993,6.0799999999999983,0.31999999999999673,3.9200000000000017,3.9200000000000017,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0,null,"Seasonal Variation Used?",null,{"$f":"IF('Project Info'!I19='Project Info'!S103,\"Yes\", \"No\")","v":"No"},null,null,null,55,60,57.055051244509336,57.075210084033465,56.984335106383107,56.818769230769213,57.071057692307662,56.862659123055131,57.384939024390484,57.243043478260766,57.566782608695668,57.305606258148728,57.016261127596366,null,55,60,53.509157755629928,52.287525402520124,51.734624140158004,52.034268691865684,52.106068898110529,51.451524876111812,54.148172425567402,52.219999082888563,53.968275351975997,52.878053585728175,52.229012517034263,null,55,60,22.329812334686142,21.645152967067276,21.312487149309163,21.479782290817866,21.522424934504023,21.159602768104456,22.74609963847648,21.601171813180855,22.624717478144785,21.980582016179742,21.596183540287484]
["1976-01-03",1,3,2018,"2018-01-03",3,0,"02:00:00",2,1.9400000000000013,1.9400000000000013,-0.39999999999999858,1.3999999999999986,-3.9999999999999147E-2,3.9200000000000017,1.3999999999999986,5,0.31999999999999673,3.1999999999999993,3.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0,null,null,null,null,null,null,null,50,55,52.282430167597774,52.152566371681395,52.287218045112489,52.231232876712106,52.087363770250391,52.097715231788058,52.28297262059975,52.437609329446005,52.373717579250815,52.37939808481535,51.980463320463443,null,50,55,48.913941304289544,47.988763287135058,47.554362689229919,47.36397638834606,48.010035788203503,46.680521625522559,49.858587525084062,47.161236990954798,48.789278452912505,48.096858212124388,47.832886727289839,null,50,55,19.717769638609628,19.230213790123479,19.003776785773137,18.882451432176854,19.230493472698054,18.533904507359196,20.243425197903832,18.794404448835781,19.65518295554234,19.284438987254887,19.136980904481192]
["1976-01-03",1,3,2018,"2018-01-03",3,0,"03:00:00",3,3.9200000000000017,-3.9999999999999147E-2,-0.39999999999999858,1.3999999999999986,-3.9999999999999147E-2,3.9200000000000017,1.3999999999999986,4.0999999999999979,0.31999999999999673,2.84,3.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0,null,"Month","Usage Div.","Default",null,null,null,45,50,47.513661417322915,47.508439306358369,47.499617590822318,47.183043478260856,47.459918864097432,47.466121495327236,47.566655896607365,47.438058252427219,47.511398963730528,47.466293103448287,47.437664473684151,null,45,50,44.318193840109124,43.34969056055543,43.432793020222725,42.445437388730291,43.155702807893235,42.540155274771557,44.820465493150216,43.00151231614695,44.299888720746921,43.423767275849784,43.331760856467547,null,45,50,17.31457751729565,16.837825297483526,16.873758265728821,16.384028405758567,16.74135423213637,16.436498030270087,17.577659718926231,16.671662242385551,17.308841312010692,16.866908255403132,16.822902381447747]
["1976-01-03",1,3,2018,"2018-01-03",3,0,"04:00:00",4,3.9200000000000017,1.0399999999999991,-0.39999999999999858,1.3999999999999986,-2.9200000000000017,3.9200000000000017,-0.39999999999999858,4.0999999999999979,0.5,2.3000000000000007,1.9400000000000013,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0,null,1,{"$f":"IF($AO$54=\"Yes\",IF('Project Info'!M15=\"\",AO57,'Project Info'!M15),1)","v":1},1,null,null,null,40,45,42.54030769230765,42.72419410745232,42.748614864864685,42.81148217636018,42.814338983050824,42.736940789473643,42.589428571428492,42.641818181818145,42.590545454545392,42.44541723666201,42.804246395806068,null,40,45,39.076275658578425,38.489426331207746,38.550058107258089,38.376810434297312,38.720373370708266,37.88980280886026,40.045799807118527,38.614417618740426,39.824251222572308,38.547453879171009,38.803320312462688,null,40,45,14.805559352665874,14.544766525409621,14.569699923220238,14.485739766910248,14.649212812711088,14.274960263797587,15.256947540857698,14.601681775393814,15.153471629900199,14.568362374675186,14.682520178583589]
["1976-01-03",1,3,2018,"2018-01-03",3,0,"05:00:00",5,3.019999999999996,1.0399999999999991,-0.39999999999999858,3.1999999999999993,-4,3.9200000000000017,1.3999999999999986,3.019999999999996,1.2199999999999953,2.84,1.0399999999999991,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0,null,2,{"$f":"IF($AO$54=\"Yes\",IF('Project Info'!M16=\"\",AO58,'Project Info'!M16),1)","v":1},1,null,null,null,35,40,37.132983957219174,37.333356401384023,37.434925373134426,37.456372430471653,37.09895833333335,37.324291845493448,37.451162790697666,37.462554660529321,37.278540332906537,37.306673511293596,37.383694874850988,null,35,40,34.206645433247552,33.571747426237494,33.745554472185241,33.7820222869505,33.604917489237977,33.125959167157347,35.2339094730781,33.788922814757747,34.174569001791639,33.861021450324458,33.856507099308459,null,35,40,12.663787088757125,12.398078504661676,12.469461393041975,12.483709324650142,12.41058349712292,12.209707040671338,13.106260983555954,12.490724726397783,12.653204599094122,12.519566530461471,12.517492566654905]
["1976-01-03",1,3,2018,"2018-01-03",3,0,"06:00:00",6,-3.9999999999999147E-2,-2.9200000000000017,-0.39999999999999858,3.1999999999999993,-4,1.9400000000000013,1.3999999999999986,3.019999999999996,1.759999999999998,2.4800000000000004,1.0399999999999991,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0,null,3,{"$f":"IF($AO$54=\"Yes\",IF('Project Info'!M17=\"\",AO59,'Project Info'!M17),1)","v":1},1,null,null,null,30,35,32.668497109826646,32.572758620689747,32.559692898272644,32.529287646528481,32.490467625899342,32.524112829845421,33.011398601398682,32.729350649350728,32.671307484220037,32.939420625724338,32.323684210526388,null,30,35,30.052520750539614,29.30686784439202,29.340399947188267,29.198061083271714,29.489261292286141,28.981288160520201,30.99978878144109,29.291092842546536,29.870317212943526,29.590064250037422,28.899218050146818,null,30,35,10.931483581356455,10.631067099049934,10.647280790371376,10.583626122977916,10.704192853299539,10.500427745718238,11.320908539774747,10.631828093354246,10.857934771427553,10.744586251352315,10.465365151142151]
["1976-01-03",1,3,2018,"2018-01-03",3,0,"07:00:00",7,-5.0800000000000054,-4,-0.39999999999999858,1.3999999999999986,-5.980000000000004,1.9400000000000013,1.3999999999999986,3.019999999999996,1.3999999999999986,2.4800000000000004,1.0399999999999991,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0,null,4,{"$f":"IF($AO$54=\"Yes\",IF('Project Info'!M18=\"\",AO60,'Project Info'!M18),1)","v":1},1,null,null,null,25,30,27.426460807600936,27.568976377952762,27.533653516295022,27.755083798882701,27.516506550218395,27.659999999999986,27.416827586206889,27.458243243243217,27.410000000000032,27.574117647058824,27.502041587901665,null,25,30,25.006348426795014,24.494083320803654,24.570792105910623,25.084405878540519,24.466736507750085,24.113490995169133,25.737481255683278,24.148128531589169,24.932512716697982,24.185545359051947,24.440366221244837,null,25,30,8.9325063303926058,8.7453590732614011,8.7726466439889386,8.9649555500240368,8.7354332284523704,8.6016570426167487,9.210162028859445,8.6180649421806024,8.9092027386051473,8.6323227575456123,8.7231256949477309]
["1976-01-03",1,3,2018,"2018-01-03",3,0,"08:00:00",8,-7.0600000000000023,-4,-0.39999999999999858,1.3999999999999986,-2.019999999999996,3.9200000000000017,-0.39999999999999858,2.1199999999999974,1.3999999999999986,3.1999999999999993,1.0399999999999991,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0,null,5,{"$f":"IF($AO$54=\"Yes\",IF('Project Info'!M19=\"\",AO61,'Project Info'!M19),1)","v":1},1,null,null,null,20,25,23.111857142857133,23.208816705336385,23.041199999999996,23.145,23.035423340961085,23.088680351906142,22.647672131147527,22.754089935760152,22.729349397590358,22.844599999999982,23.372537313432776,null,20,25,21.065260686810852,20.463018345275255,20.453251987170212,20.378379511073046,20.184690108182352,19.630897263031624,21.36890697344823,19.884191927036483,20.289643435003129,19.82600371195095,20.672129309119487,null,20,25,7.4846066278317407,7.2740516417507415,7.2702223424526595,7.2442623147933274,7.174871980335678,6.9848954709621989,7.5926984436514822,7.0716151165803582,7.2097660953382352,7.0530472238803306,7.347772765400391]
["1976-01-03",1,3,2018,"2018-01-03",3,0,"09:00:00",9,-3.9999999999999147E-2,3.019999999999996,-2.2000000000000028,3.1999999999999993,1.0399999999999991,6.98,3.1999999999999993,3.019999999999996,0.85999999999999943,6.0799999999999983,1.9400000000000013,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0,null,6,{"$f":"IF($AO$54=\"Yes\",IF('Project Info'!M20=\"\",AO62,'Project Info'!M20),1)","v":1},1,null,null,null,15,20,17.843779527559001,17.934896142433196,17.932396166134172,17.870481283422439,17.881550802138982,18.067578124999979,17.428633093525217,17.736866359446989,17.562165605095544,17.517766497461935,18.117499999999989,null,15,20,15.897968137645046,15.245015805469786,15.911250671386474,15.493763598925121,15.488744443307075,14.757821536504698,16.304867962336687,15.108908433893037,15.624788766134376,14.350727948425897,15.445666455318614,null,15,20,5.7053068098870732,5.4939378798730125,5.7100391174140661,5.5720637305720375,5.5701324264681134,5.3339850472753243,5.8372185176025733,5.44832110942495,5.6130120632751881,5.1972372865923999,5.5582785562853898]
["1976-01-03",1,3,2018,"2018-01-03",3,0,"10:00:00",10,3.019999999999996,8.0599999999999987,-0.39999999999999858,6.8000000000000007,6.98,10.940000000000001,1.3999999999999986,5,3.019999999999996,8.5999999999999979,3.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0,null,7,{"$f":"IF($AO$54=\"Yes\",IF('Project Info'!M21=\"\",AO63,'Project Info'!M21),1)","v":1},1,null,null,null,10,15,12.143956043956047,12.005375000000004,12.351304347826099,11.821194029850757,12.194267515923578,12.445454545454554,12.173017077798811,12.356315789473685,12.556571428571436,12.761492537313442,12.160294117647062,null,10,15,10.505317162057358,9.8739277108221124,10.770065127982141,9.7730306912966292,10.233421429959368,9.9586243459007751,11.045844211117462,10.102206774998242,10.697639097550086,10.449555618632363,10.091281872943114,null,10,15,3.9643692940194,3.770730722817869,4.0477047813601414,3.737974162743583,3.8813716783045842,3.7989324861513278,4.1329550524179668,3.8426978337722635,4.0268452235516641,3.9502252149656845,3.8373009585317108]
["1976-01-03",1,3,2018,"2018-01-03",3,0,"11:00:00",11,10.039999999999999,8.0599999999999987,3.1999999999999993,8.5999999999999979,15.98,15.079999999999998,0.5,7.1599999999999966,6.620000000000001,12.920000000000002,5,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0,null,8,{"$f":"IF($AO$54=\"Yes\",IF('Project Info'!M22=\"\",AO64,'Project Info'!M22),1)","v":1},1,null,null,null,5,10,7.1231999999999971,7.3482758620689674,7.3266666666666662,7.4729545454545452,7.0285217391304364,7.1599999999999984,7.1635156249999969,7.2121739130434745,7.9126086956521791,7.4763636363636365,7.2270588235294095,null,5,10,5.8213126873197627,5.3994557003998711,5.9657836667020083,5.7925337842460998,5.6920614954373177,4.9613590938245942,6.2410717643107043,5.4320075551583722,6.4571279230983674,5.4848290474438945,5.5100779762314778,null,5,10,2.5340732271239945,2.4124401777155713,2.5778617634323422,2.5292877960108737,2.4963689721936477,2.283901023313557,2.6587456741458113,2.4209671595437721,2.726021073735684,2.4378279585803262,2.4438654360822536]
["1976-01-03",1,3,2018,"2018-01-03",3,0,"12:00:00",12,17.059999999999999,15.079999999999998,6.8000000000000007,14,19.04,17.96,-0.39999999999999858,9.14,9.14,16.52,8.0599999999999987,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0,null,9,{"$f":"IF($AO$54=\"Yes\",IF('Project Info'!M23=\"\",AO65,'Project Info'!M23),1)","v":1},1,null,null,null,0,5,2.5101935483870954,2.7525714285714264,2.4542857142857137,2.3744827586206894,2.6599999999999988,3.0199999999999991,2.2926779661016883,2.87230769230769,2.393033707865166,2.8664705882352934,2.5353846153846149,null,0,5,1.5011957900630817,1.2947474565917769,1.632595637333724,0.81073164717212665,1.5820257945671725,1.2490650573662765,1.4526956834484162,1.2972122185386956,1.1315452323249189,1.0401717114422091,0.97776083942616387,null,0,5,1.2684534669035181,1.2125890309189029,1.3046067057780639,1.0742852952782165,1.2923666220396746,1.2015862498272711,1.2536816550393302,1.2135746591585128,1.1651275557326455,1.1425767866934053,1.1222776601370716]
["1976-01-03",1,3,2018,"2018-01-03",3,0,"13:00:00",13,19.939999999999998,15.98,6.8000000000000007,17.600000000000001,21.92,21.02,-1.3000000000000043,10.039999999999999,11.3,19.579999999999998,8.9599999999999973,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0,null,10,{"$f":"IF($AO$54=\"Yes\",IF('Project Info'!M24=\"\",AO66,'Project Info'!M24),1)","v":1},1,null,null,null,-5,0,-1.7601612903225796,-1.7571999999999997,-1.721714285714286,-1.6730909090909092,-1.9209999999999989,-0.81399999999999939,-2.127862595419844,-1.6705882352941188,-2.3184210526315803,-0.78250000000000153,-1.8580000000000012,null,-5,0,-2.614664056490859,-2.8638564966159255,-2.5416473887382418,-2.7672698418309984,-2.9302904185522456,-2.3442909168057926,-2.9142840460295694,-2.6437520272058674,-3.2558844862560261,-2.2177803896129489,-2.6979305827751152,null,-5,0,0.10432208048436696,3.7125274396278857E-2,0.12473980820565492,6.3341550444547479E-2,1.7502428915022759E-2,0.18377533368217316,2.0917672675120503E-2,9.6652216659448426E-2,-7.2847704648359171E-2,0.21788381892575198,7.9897681234635337E-2]
["1976-01-03",1,3,2018,"2018-01-03",3,0,"14:00:00",14,24.98,15.98,8.5999999999999979,17.600000000000001,21.02,19.939999999999998,-2.2000000000000028,11.120000000000001,12.740000000000002,21.2,10.039999999999999,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0,null,11,{"$f":"IF($AO$54=\"Yes\",IF('Project Info'!M25=\"\",AO67,'Project Info'!M25),1)","v":1},1,null,null,null,-10,-5,-6.9832786885245905,-6.9250000000000034,-7.4823076923076943,-5.8000000000000043,-7.0103448275862092,{"$error":"#DIV/0!"},-7.3339473684210361,-5.8300000000000045,-6.7120000000000006,{"$error":"#DIV/0!"},-5.0800000000000054,null,-10,-5,-7.6036550438891606,-7.5039085724875187,-7.9685832867087072,-6.8086617265753633,-7.8080429475732451,{"$error":"#DIV/0!"},-7.9927476754286007,-6.3505620806960552,-7.4340394593162085,{"$error":"#DIV/0!"},-5.7491416057521336,null,-10,-5,-1.264641659568686,-1.2392557615113662,-1.3646811710723328,-1.0482979731728503,-1.318963063338942,{"$error":"#DIV/0!"},-1.369784934569809,-0.92768861091731891,-1.219551169809185,{"$error":"#DIV/0!"},-0.76294594383340797]
["1976-01-03",1,3,2018,"2018-01-03",3,0,"15:00:00",15,26.060000000000002,17.059999999999999,8.5999999999999979,17.600000000000001,19.939999999999998,19.939999999999998,-4,10.039999999999999,14.899999999999999,22.1,10.039999999999999,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0,null,12,{"$f":"IF($AO$54=\"Yes\",IF('Project Info'!M26=\"\",AO68,'Project Info'!M26),1)","v":1},1,null,null,null,-30,-10,-15.221363636363634,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},-18.010967741935485,{"$error":"#DIV/0!"},-15.934482758620671,{"$error":"#DIV/0!"},-12.136000000000003,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},null,-30,-10,-15.615870321812459,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},-18.346627853212443,{"$error":"#DIV/0!"},-16.373537438297813,{"$error":"#DIV/0!"},-12.495317231113276,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},null,-30,-10,-3.3820890518527036,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},-4.091252424436143,{"$error":"#DIV/0!"},-3.5748480574257919,{"$error":"#DIV/0!"},-2.5723377289499139,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["1976-01-03",1,3,2018,"2018-01-03",3,0,"16:00:00",16,26.96,17.059999999999999,8.5999999999999979,17.600000000000001,19.04,19.939999999999998,-5.8000000000000043,10.039999999999999,16.159999999999997,19.399999999999999,10.039999999999999,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-03",1,3,{"$f":"$AO$4","v":2018},"2018-01-03",3,{"$f":"COUNTIF($AM$34:$AM$43,E70)","v":0},"17:00:00",17,10.039999999999999,17.059999999999999,8.5999999999999979,17.600000000000001,10.039999999999999,17.059999999999999,-5.8000000000000043,8.0599999999999987,14.54,17.240000000000002,6.98,null,{"$f":"SUMPRODUCT($J$2:$T$2,J70:T70)","v":0},null,null,{"$f":"OR(B70<=$AO$14,B70>=$AN$14)*(F70<6)*(I70>$AN$15)*(I70<=$AO$15)*(G70<>1)","v":1},{"$f":"OR(B70<=$AO$14,B70>=$AN$14)*(Y70=0)","v":0},{"$f":"AND(B70>=$AN$24,B70<=$AO$24)*(F70<6)*(I70>$AN$25)*(I70<=$AO$25)*(G70<>1)","v":0},{"$f":"AND(B70>=$AN$24,B70<=$AO$24)*(AA70=0)","v":0},{"$f":"OR(B70<=$AO$19,B70>=$AN$19)*(F70<6)*(I70>$AN$20)*(I70<=$AO$20)","v":0},{"$f":"AND(B70>=$AN$29,B70<=$AO$29)*(F70<6)*(I70>$AN$30)*(I70<=$AO$30)","v":0},{"$f":"IF(OR(E70=$AM$34,E70=$AM$35,E70=$AM$36,E70=$AM$37,E70=$AM$38,E70=$AM$39,E70=$AM$40,E70=$AM$41,E70=$AM$42,E70=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E70>=$AM$47,E70<=$AN$47),AND(E70>=$AM$48,E70<=$AN$48),AND(E70>=$AM$49,E70<=$AN$49),AND(E70>=$AM$50,E70<=$AN$50),AND(E70>=$AM$51,E70<=$AN$51)),0,1)*AE70","v":1},{"$f":"(B70>=5)*(B70<=10)","v":0},{"$f":"1*OR(B70<=4,B70>=11)","v":1},{"$f":"LOOKUP(B70,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE70:AI70)*((F70<6)*(I70>$AO$7)*(I70<=$AP$7)+(F70=6)*(I70>$AO$8)*(I70<=$AP$8)+(F70>=7)*(I70>$AO$9)*(I70<=$AP$9))","v":0}]
["1976-01-03",1,3,2018,{"$f":"DATE(D71,B71,C71)","v":"2018-01-03"},{"$f":"WEEKDAY(E71,2)","v":3},0,"18:00:00",18,1.9400000000000013,10.940000000000001,6.8000000000000007,14,8.0599999999999987,14,-5.8000000000000043,7.1599999999999966,13.459999999999997,16.88,5,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-03",1,3,2018,"2018-01-03",3,0,"19:00:00",{"$f":"H72*24","v":19},-3.9999999999999147E-2,5,-0.39999999999999858,10.399999999999999,8.0599999999999987,14,-5.8000000000000043,6.0799999999999983,8.240000000000002,16.52,3.9200000000000017,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-03",1,3,2018,"2018-01-03",3,0,"20:00:00",20,-2.9200000000000017,5,-0.39999999999999858,10.399999999999999,5,12.920000000000002,4.0999999999999979,4.0999999999999979,10.399999999999999,16.52,1.9400000000000013,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-03",1,3,2018,"2018-01-03",3,0,"21:00:00",21,-7.0600000000000023,3.9200000000000017,-4,8.5999999999999979,1.9400000000000013,12.920000000000002,-5.8000000000000043,-1.8400000000000034,7.52,16.52,-0.94000000000000483,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-03",1,3,2018,"2018-01-03",3,0,"22:00:00",22,-2.9200000000000017,1.0399999999999991,-5.8000000000000043,6.8000000000000007,8.0599999999999987,12.920000000000002,-4,-0.94000000000000483,5.7199999999999989,14.54,-2.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-03",1,3,2018,"2018-01-03",3,0,"23:00:00",23,-4,1.0399999999999991,-7.6000000000000014,10.399999999999999,6.98,10.940000000000001,-2.2000000000000028,-5.980000000000004,1.5800000000000018,12.559999999999999,-2.9200000000000017,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-03",1,3,2018,"2018-01-03",3,0,1,24,-2.9200000000000017,-3.9999999999999147E-2,-9.3999999999999986,8.5999999999999979,1.0399999999999991,10.039999999999999,-0.39999999999999858,-5.980000000000004,-0.75999999999999801,12.2,-2.9200000000000017,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"01:00:00",1,-4,-2.019999999999996,-9.3999999999999986,8.5999999999999979,1.0399999999999991,8.0599999999999987,-0.39999999999999858,-5.980000000000004,-1.3000000000000043,9.5,-5.0800000000000054,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"02:00:00",2,-0.94000000000000483,-2.019999999999996,-9.3999999999999986,8.5999999999999979,3.019999999999996,6.98,-0.39999999999999858,-6.8800000000000026,-1.8400000000000034,8.7799999999999976,-5.0800000000000054,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"03:00:00",3,-0.5800000000000054,-3.9999999999999147E-2,-5.8000000000000043,10.399999999999999,1.9400000000000013,6.0799999999999983,1.3999999999999986,-0.94000000000000483,1.3999999999999986,11.120000000000001,-2.9200000000000017,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"04:00:00",4,-0.39999999999999858,-0.94000000000000483,-5.8000000000000043,8.5999999999999979,6.0799999999999983,6.0799999999999983,1.3999999999999986,-0.94000000000000483,0.68000000000000327,13.82,-0.94000000000000483,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"05:00:00",5,-3.9999999999999147E-2,-0.94000000000000483,-5.8000000000000043,10.399999999999999,6.98,5,1.3999999999999986,-1.8400000000000034,1.3999999999999986,13.64,-2.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"06:00:00",6,1.9400000000000013,-3.9999999999999147E-2,-5.8000000000000043,10.399999999999999,8.0599999999999987,5,1.3999999999999986,-1.8400000000000034,3.379999999999999,13.279999999999998,-0.94000000000000483,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"07:00:00",7,3.019999999999996,3.019999999999996,-4,12.2,8.9599999999999973,6.98,3.1999999999999993,3.019999999999996,5.3599999999999994,12.740000000000002,-2.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"08:00:00",8,6.8000000000000007,3.019999999999996,-5.8000000000000043,14,10.039999999999999,10.039999999999999,4.0999999999999979,3.019999999999996,5.7199999999999989,16.88,-0.94000000000000483,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"09:00:00",9,6.98,8.0599999999999987,-5.8000000000000043,15.8,10.039999999999999,19.939999999999998,5,10.039999999999999,5.3599999999999994,21.92,3.9200000000000017,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"10:00:00",10,6.98,12.920000000000002,-0.39999999999999858,21.2,12.02,26.96,5,13.099999999999998,7.52,27.14,8.9599999999999973,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"11:00:00",11,14,12.920000000000002,6.8000000000000007,24.8,12.920000000000002,30.02,6.8000000000000007,22.1,10.399999999999999,30.56,14,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"12:00:00",12,14,28.04,10.399999999999999,28.4,12.920000000000002,32.18,7.6999999999999993,26.060000000000002,14.719999999999999,32.36,19.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"13:00:00",13,14,33.08,10.399999999999999,32,15.079999999999998,33.08,8.5999999999999979,25.16,20.84,33.26,23,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"14:00:00",14,15.98,33.08,15.8,32.18,15.98,34.159999999999997,7.6999999999999993,25.16,33.08,34.159999999999997,23,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"15:00:00",15,17.96,34.340000000000003,17.600000000000001,32.72,19.04,35.06,6.8000000000000007,26.060000000000002,33.619999999999997,34.880000000000003,23,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"16:00:00",16,19.939999999999998,34.340000000000003,19.399999999999999,32.54,19.04,35.96,6.8000000000000007,26.060000000000002,33.799999999999997,35.24,24.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"17:00:00",17,30.02,33.979999999999997,15.8,33.799999999999997,21.02,35.06,6.8000000000000007,21.02,32.36,35.42,21.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"18:00:00",18,26.060000000000002,33.44,15.8,33.799999999999997,21.92,34.340000000000003,6.8000000000000007,24.08,32.36,35.42,21.02,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"19:00:00",19,26.96,32.72,17.600000000000001,33.799999999999997,19.04,33.26,8.5999999999999979,24.08,32.9,34.520000000000003,19.939999999999998,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"20:00:00",20,26.060000000000002,32.72,19.399999999999999,33.799999999999997,19.04,32.9,8.0599999999999987,20.12,33.619999999999997,34.159999999999997,21.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"21:00:00",21,24.98,32.54,19.399999999999999,33.799999999999997,19.04,32.54,7.34,24.08,33.08,33.799999999999997,19.939999999999998,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"22:00:00",22,26.060000000000002,32.18,19.399999999999999,33.799999999999997,19.939999999999998,32.18,6.8000000000000007,25.16,33.799999999999997,33.08,21.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,"23:00:00",23,26.060000000000002,33.979999999999997,19.399999999999999,33.799999999999997,19.939999999999998,35.06,6.8000000000000007,25.16,33.799999999999997,32.36,21.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-04",1,4,2018,"2018-01-04",4,0,1,24,28.04,32,17.600000000000001,33.799999999999997,19.939999999999998,35.06,6.8000000000000007,22.1,32.9,30.92,21.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"01:00:00",1,24.98,33.08,17.600000000000001,32,19.04,33.979999999999997,6.8000000000000007,21.02,32.72,32.72,21.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"02:00:00",2,24.08,33.08,15.8,30.2,17.96,33.979999999999997,5,20.12,32.36,33.799999999999997,21.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"03:00:00",3,24.08,30.02,15.8,32,14,33.979999999999997,6.8000000000000007,21.02,32.18,33.44,19.939999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"04:00:00",4,19.939999999999998,30.92,14,32,14,33.08,6.8000000000000007,19.04,33.08,31.64,19.939999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"05:00:00",5,17.96,30.92,12.2,32,12.02,33.979999999999997,6.8000000000000007,15.079999999999998,32.54,30.74,23,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"06:00:00",6,14,33.08,12.2,32,10.039999999999999,32,6.8000000000000007,18.14,31.82,30.74,21.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"07:00:00",7,12.02,32,10.399999999999999,32,8.0599999999999987,33.08,6.8000000000000007,19.04,32.9,30.38,19.939999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"08:00:00",8,12.02,32,10.399999999999999,32,6.98,33.08,1.3999999999999986,20.12,32,32.18,19.939999999999998,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"09:00:00",9,10.940000000000001,33.08,10.399999999999999,33.799999999999997,6.0799999999999983,35.96,1.3999999999999986,23,31.82,32.72,24.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"10:00:00",10,10.039999999999999,32.54,15.8,32,5,33.979999999999997,1.3999999999999986,29.12,31.1,34.340000000000003,26.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"11:00:00",11,10.039999999999999,32,19.399999999999999,32,3.9200000000000017,34.700000000000003,0.5,32.9,31.1,34.700000000000003,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"12:00:00",12,8.0599999999999987,33.979999999999997,24.8,32,5,34.700000000000003,-0.39999999999999858,36.86,30.02,34.520000000000003,33.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"13:00:00",13,8.0599999999999987,32.18,28.4,33.799999999999997,3.9200000000000017,35.06,-0.39999999999999858,33.619999999999997,29.3,34.520000000000003,33.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"14:00:00",14,6.0799999999999983,32.36,32.36,30.2,3.9200000000000017,35.24,-2.2000000000000028,34.700000000000003,30.74,34.700000000000003,32.18,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"15:00:00",15,6.0799999999999983,32.54,33.799999999999997,32,3.9200000000000017,35.96,-2.2000000000000028,35.78,30.2,35.24,32.54,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"16:00:00",16,3.9200000000000017,32,35.06,30.2,3.9200000000000017,34.159999999999997,-2.2000000000000028,35.78,29.3,33.619999999999997,32,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"17:00:00",17,1.9400000000000013,32,34.700000000000003,28.4,1.9400000000000013,33.08,-2.2000000000000028,35.6,27.5,32.9,30.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"18:00:00",18,5,26.060000000000002,33.08,26.6,-3.9999999999999147E-2,26.96,-0.39999999999999858,33.619999999999997,25.52,27.5,30.02,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"19:00:00",19,1.3999999999999986,21.92,33.26,23,-0.94000000000000483,24.08,1.3999999999999986,33.26,22.46,26.78,30.02,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"20:00:00",20,3.019999999999996,21.92,33.619999999999997,19.399999999999999,-2.019999999999996,24.08,3.1999999999999993,33.619999999999997,17.420000000000002,24.8,28.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"21:00:00",21,1.3999999999999986,14,33.08,17.600000000000001,-2.9200000000000017,21.02,5,33.44,14.54,22.28,28.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"22:00:00",22,1.9400000000000013,15.98,33.26,15.8,-2.9200000000000017,21.02,6.8000000000000007,33.979999999999997,12.2,21.2,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,"23:00:00",23,1.9400000000000013,15.98,33.26,15.8,-2.9200000000000017,17.059999999999999,6.8000000000000007,34.700000000000003,11.659999999999997,18.32,28.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-05",1,5,2018,"2018-01-05",5,0,1,24,1.0399999999999991,14,32.72,15.8,-2.019999999999996,17.059999999999999,10.399999999999999,34.880000000000003,11.3,17.600000000000001,30.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,2018,"2018-01-06",6,0,"01:00:00",1,-3.9999999999999147E-2,12.920000000000002,32.18,15.8,-2.019999999999996,19.04,10.399999999999999,34.880000000000003,10.399999999999999,19.04,32.36,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,2018,"2018-01-06",6,0,"02:00:00",2,1.9400000000000013,12.920000000000002,30.2,15.8,-2.019999999999996,19.939999999999998,11.3,34.880000000000003,9.14,19.939999999999998,28.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,2018,"2018-01-06",6,0,"03:00:00",3,-0.94000000000000483,17.059999999999999,32.36,17.600000000000001,-2.9200000000000017,21.02,12.2,35.06,11.3,20.84,28.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,2018,"2018-01-06",6,0,"04:00:00",4,-3.9999999999999147E-2,17.059999999999999,28.4,17.600000000000001,-2.9200000000000017,21.02,8.5999999999999979,34.880000000000003,12.920000000000002,21.92,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,2018,"2018-01-06",6,0,"05:00:00",5,-0.94000000000000483,17.059999999999999,26.6,19.399999999999999,-4,21.92,6.8000000000000007,33.619999999999997,14,22.64,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,2018,"2018-01-06",6,0,"06:00:00",6,-0.94000000000000483,19.04,26.6,19.399999999999999,-5.0800000000000054,21.2,6.8000000000000007,32.72,15.259999999999998,23,30.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,2018,"2018-01-06",6,0,"07:00:00",7,-0.94000000000000483,19.939999999999998,26.6,19.399999999999999,-5.980000000000004,21.92,8.5999999999999979,32.36,15.620000000000001,23,28.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,2018,"2018-01-06",6,0,"08:00:00",8,-2.2000000000000028,19.939999999999998,26.6,19.399999999999999,-7.0600000000000023,24.08,8.5999999999999979,32.72,15.8,23,30.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,{"$f":"$AO$4","v":2018},"2018-01-06",6,{"$f":"COUNTIF($AM$34:$AM$43,E134)","v":0},"09:00:00",9,-2.9200000000000017,21.2,28.4,19.399999999999999,-4,24.08,6.8000000000000007,33.799999999999997,16.7,23,32,null,{"$f":"SUMPRODUCT($J$2:$T$2,J134:T134)","v":0},null,null,{"$f":"OR(B134<=$AO$14,B134>=$AN$14)*(F134<6)*(I134>$AN$15)*(I134<=$AO$15)*(G134<>1)","v":0},{"$f":"OR(B134<=$AO$14,B134>=$AN$14)*(Y134=0)","v":1},{"$f":"AND(B134>=$AN$24,B134<=$AO$24)*(F134<6)*(I134>$AN$25)*(I134<=$AO$25)*(G134<>1)","v":0},{"$f":"AND(B134>=$AN$24,B134<=$AO$24)*(AA134=0)","v":0},{"$f":"OR(B134<=$AO$19,B134>=$AN$19)*(F134<6)*(I134>$AN$20)*(I134<=$AO$20)","v":0},{"$f":"AND(B134>=$AN$29,B134<=$AO$29)*(F134<6)*(I134>$AN$30)*(I134<=$AO$30)","v":0},{"$f":"IF(OR(E134=$AM$34,E134=$AM$35,E134=$AM$36,E134=$AM$37,E134=$AM$38,E134=$AM$39,E134=$AM$40,E134=$AM$41,E134=$AM$42,E134=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E134>=$AM$47,E134<=$AN$47),AND(E134>=$AM$48,E134<=$AN$48),AND(E134>=$AM$49,E134<=$AN$49),AND(E134>=$AM$50,E134<=$AN$50),AND(E134>=$AM$51,E134<=$AN$51)),0,1)*AE134","v":1},{"$f":"(B134>=5)*(B134<=10)","v":0},{"$f":"1*OR(B134<=4,B134>=11)","v":1},{"$f":"LOOKUP(B134,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE134:AI134)*((F134<6)*(I134>$AO$7)*(I134<=$AP$7)+(F134=6)*(I134>$AO$8)*(I134<=$AP$8)+(F134>=7)*(I134>$AO$9)*(I134<=$AP$9))","v":0}]
["1976-01-06",1,6,2018,{"$f":"DATE(D135,B135,C135)","v":"2018-01-06"},{"$f":"WEEKDAY(E135,2)","v":6},0,"10:00:00",10,-3.9999999999999147E-2,24.98,32.54,23,-2.019999999999996,28.04,8.5999999999999979,35.96,17.420000000000002,26.6,32.9,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,2018,"2018-01-06",6,0,"11:00:00",{"$f":"H136*24","v":11},1.0399999999999991,24.98,35.6,24.8,-2.019999999999996,32,8.5999999999999979,37.94,19.399999999999999,32.9,34.700000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,2018,"2018-01-06",6,0,"12:00:00",12,1.9400000000000013,32,35.78,26.6,1.0399999999999991,32.36,8.5999999999999979,38.840000000000003,22.46,35.96,35.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,2018,"2018-01-06",6,0,"13:00:00",13,1.0399999999999991,33.44,38.299999999999997,28.4,1.0399999999999991,35.6,8.5999999999999979,39.92,24.259999999999998,35.24,37.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,2018,"2018-01-06",6,0,"14:00:00",14,3.9200000000000017,35.42,39.74,32.36,1.9400000000000013,37.4,8.5999999999999979,39.92,25.7,36.68,39.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,2018,"2018-01-06",6,0,"15:00:00",15,1.9400000000000013,36.68,40.1,33.979999999999997,1.9400000000000013,39.019999999999996,9.5,40.1,27.5,38.840000000000003,39.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,2018,"2018-01-06",6,0,"16:00:00",16,1.0399999999999991,37.04,39.92,34.880000000000003,1.0399999999999991,37.94,10.399999999999999,38.840000000000003,32.9,38.480000000000004,38.840000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,2018,"2018-01-06",6,0,"17:00:00",17,-0.39999999999999858,37.04,39.74,34.880000000000003,-3.9999999999999147E-2,37.04,10.399999999999999,40.28,33.979999999999997,36.68,38.840000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,2018,"2018-01-06",6,0,"18:00:00",18,-3.9999999999999147E-2,33.44,38.840000000000003,30.2,-0.94000000000000483,34.159999999999997,10.399999999999999,39.74,27.5,34.880000000000003,37.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,2018,"2018-01-06",6,0,"19:00:00",19,1.3999999999999986,32.54,37.22,30.2,-2.019999999999996,32.9,12.2,37.58,26.96,34.700000000000003,35.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,2018,"2018-01-06",6,0,"20:00:00",20,-3.9999999999999147E-2,32.18,37.04,30.2,-4,32.36,12.2,37.4,26.96,34.159999999999997,36.86,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,2018,"2018-01-06",6,0,"21:00:00",21,-0.94000000000000483,32,36.32,30.2,-4,33.979999999999997,12.2,36.68,26.78,33.44,36.5,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,2018,"2018-01-06",6,0,"22:00:00",22,-3.9999999999999147E-2,28.04,36.14,28.4,-5.0800000000000054,32,12.2,36.14,26.060000000000002,32.9,35.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,2018,"2018-01-06",6,0,"23:00:00",23,-2.019999999999996,28.04,35.6,26.6,-5.0800000000000054,32,12.2,35.96,25.52,32.18,34.520000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-06",1,6,2018,"2018-01-06",6,0,1,24,-2.9200000000000017,28.94,35.06,26.6,-5.980000000000004,28.04,12.2,35.96,25.34,31.64,33.979999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"01:00:00",1,-2.019999999999996,24.98,34.159999999999997,26.6,-7.0600000000000023,28.94,12.2,36.14,25.34,30.2,34.159999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"02:00:00",2,-2.019999999999996,24.98,34.159999999999997,26.6,-7.9600000000000009,28.04,12.2,35.96,25.52,29.84,34.159999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"03:00:00",3,-5.0800000000000054,24.08,35.6,26.6,-7.0600000000000023,30.02,10.399999999999999,36.5,25.52,32,34.159999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"04:00:00",4,-4,24.98,35.78,30.2,-7.9600000000000009,26.96,10.399999999999999,36.5,26.24,29.12,33.979999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"05:00:00",5,-0.94000000000000483,24.98,35.24,28.4,-14.980000000000004,26.96,8.5999999999999979,36.14,32.72,29.12,33.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"06:00:00",6,-2.019999999999996,28.4,35.24,30.2,-18.04,26.060000000000002,5,36.32,32.18,30.74,33.26,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"07:00:00",7,-9.0399999999999991,32,35.42,32,-18.940000000000005,33.979999999999997,3.1999999999999993,36.14,30.2,25.88,33.44,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"08:00:00",8,-5.0800000000000054,32,35.78,30.2,-20.92,33.08,1.3999999999999986,35.78,26.96,28.58,33.44,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"09:00:00",9,-2.019999999999996,30.02,37.58,28.4,-16.96,33.08,3.1999999999999993,37.4,24.62,28.04,33.799999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"10:00:00",10,6.98,28.04,39.56,28.4,-9.9400000000000048,32,3.1999999999999993,40.46,23.36,29.12,37.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"11:00:00",11,15.079999999999998,28.04,41.9,28.4,-4,32,3.1999999999999993,41,24.8,31.28,39.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"12:00:00",12,12.920000000000002,28.94,44.06,28.4,1.0399999999999991,32,3.1999999999999993,44.78,24.62,31.64,42.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"13:00:00",13,10.940000000000001,28.94,46.58,26.6,3.019999999999996,32.18,5,48.74,25.16,32.54,44.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"14:00:00",14,15.98,28.94,45.68,28.4,5,32.18,5.8999999999999986,45.86,26.24,32,46.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"15:00:00",15,14,30.02,44.6,28.4,5,32.36,6.8000000000000007,48.92,26.96,32.36,46.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"16:00:00",16,10.039999999999999,30.02,46.22,28.4,5,32.18,7.6999999999999993,49.82,27.5,32.18,46.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"17:00:00",17,3.019999999999996,30.02,45.86,28.4,1.9400000000000013,28.04,8.5999999999999979,48.74,24.62,27.86,44.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"18:00:00",18,-4,21.02,43.16,23,3.019999999999996,24.08,8.5999999999999979,45.32,19.399999999999999,25.88,41.72,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"19:00:00",19,-2.9200000000000017,17.059999999999999,41.36,19.399999999999999,3.9200000000000017,24.08,8.5999999999999979,44.24,15.8,24.259999999999998,40.64,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"20:00:00",20,1.0399999999999991,17.059999999999999,40.28,17.600000000000001,6.0799999999999983,21.02,8.5999999999999979,43.34,13.64,21.92,41,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"21:00:00",21,-3.9999999999999147E-2,12.920000000000002,40.64,15.8,6.98,21.02,10.399999999999999,43.52,8.5999999999999979,20.299999999999997,39.200000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"22:00:00",22,1.9400000000000013,10.039999999999999,39.92,12.2,10.940000000000001,19.04,12.2,42.44,7.1599999999999966,24.08,41,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,"23:00:00",23,1.9400000000000013,10.039999999999999,39.019999999999996,10.399999999999999,12.920000000000002,15.079999999999998,10.399999999999999,41.9,4.4599999999999973,20.12,38.119999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-07",1,7,2018,"2018-01-07",7,0,1,24,3.9200000000000017,8.9599999999999973,38.299999999999997,10.399999999999999,12.02,15.98,8.5999999999999979,41.36,3.019999999999996,21.740000000000002,37.4,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"01:00:00",1,6.98,6.98,38.659999999999997,10.399999999999999,12.02,17.96,8.5999999999999979,41.54,1.5800000000000018,24.259999999999998,37.4,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"02:00:00",2,6.0799999999999983,6.98,38.840000000000003,8.5999999999999979,12.02,17.059999999999999,14,41.72,0.5,25.34,36.86,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"03:00:00",3,6.98,3.9200000000000017,39.74,8.5999999999999979,12.920000000000002,17.059999999999999,14,42.08,-0.5800000000000054,26.6,37.22,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"04:00:00",4,5,3.9200000000000017,41.72,12.2,12.920000000000002,12.920000000000002,14,43.52,-1.3000000000000043,25.16,39.200000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"05:00:00",5,6.98,3.9200000000000017,42.26,12.2,12.920000000000002,15.98,17.600000000000001,44.6,-2.2000000000000028,24.08,39.200000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"06:00:00",6,8.0599999999999987,1.9400000000000013,42.980000000000004,12.2,12.920000000000002,17.059999999999999,15.8,45.5,-2.3800000000000026,25.88,39.74,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"07:00:00",7,10.940000000000001,3.9200000000000017,41.72,12.2,14,15.079999999999998,14,45.14,-2.9200000000000017,25.52,39.200000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"08:00:00",8,10.940000000000001,3.9200000000000017,42.44,12.2,15.079999999999998,17.059999999999999,14,46.04,-2.5600000000000023,24.62,39.200000000000003,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"09:00:00",9,12.920000000000002,8.9599999999999973,43.16,17.600000000000001,17.059999999999999,24.98,15.8,46.58,-1.3000000000000043,28.94,41,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"10:00:00",10,17.059999999999999,17.96,45.86,24.8,19.939999999999998,32,14.899999999999999,48.74,1.0399999999999991,34.880000000000003,46.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"11:00:00",11,21.92,17.96,50.36,28.4,21.02,34.520000000000003,14,50,6.8000000000000007,34.340000000000003,51.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"12:00:00",12,19.04,36.32,53.96,32.54,21.92,37.94,15.8,56.120000000000005,11.659999999999997,37.76,57.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"13:00:00",13,24.08,39.92,58.1,35.6,24.98,40.28,15.8,66.92,33.44,39.92,59,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"14:00:00",14,24.98,39.92,59.18,37.58,28.04,42.980000000000004,15.8,64.94,35.24,43.52,60.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"15:00:00",15,30.02,42.08,59.72,38.659999999999997,28.04,42.980000000000004,32,62.96,36.32,44.06,59,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"16:00:00",16,23,41,59,39.019999999999996,26.96,42.08,14,62.06,36.32,42.44,50.18,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"17:00:00",17,30.02,41,56.480000000000004,39.200000000000003,24.98,39.92,14,58.82,35.42,39.74,53.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"18:00:00",18,24.08,33.799999999999997,51.980000000000004,32.72,24.98,35.06,14,53.78,24.259999999999998,37.22,53.06,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"19:00:00",19,26.96,33.26,51.08,32.36,26.060000000000002,33.979999999999997,14,53.96,21.02,36.5,51.980000000000004,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"20:00:00",20,28.04,32.36,49.46,28.4,26.96,32.72,15.8,50.900000000000006,19.939999999999998,34.880000000000003,47.66,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"21:00:00",21,26.96,23,48.379999999999995,28.4,26.96,30.02,17.600000000000001,50,17.96,33.26,48.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"22:00:00",22,30.92,21.02,46.76,28.4,28.04,26.96,17.600000000000001,47.84,16.88,33.619999999999997,46.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,"23:00:00",23,37.04,21.02,46.76,24.8,28.04,26.060000000000002,17.600000000000001,46.94,15.620000000000001,31.46,46.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-08",1,8,2018,"2018-01-08",1,0,1,24,33.799999999999997,21.92,46.22,24.8,28.04,24.98,19.399999999999999,48.74,16.159999999999997,30.02,46.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,{"$f":"$AO$4","v":2018},"2018-01-09",2,{"$f":"COUNTIF($AM$34:$AM$43,E198)","v":0},"01:00:00",1,33.979999999999997,19.939999999999998,46.58,26.6,28.04,21.92,19.399999999999999,48.92,14.719999999999999,28.58,44.6,null,{"$f":"SUMPRODUCT($J$2:$T$2,J198:T198)","v":0},null,null,{"$f":"OR(B198<=$AO$14,B198>=$AN$14)*(F198<6)*(I198>$AN$15)*(I198<=$AO$15)*(G198<>1)","v":0},{"$f":"OR(B198<=$AO$14,B198>=$AN$14)*(Y198=0)","v":1},{"$f":"AND(B198>=$AN$24,B198<=$AO$24)*(F198<6)*(I198>$AN$25)*(I198<=$AO$25)*(G198<>1)","v":0},{"$f":"AND(B198>=$AN$24,B198<=$AO$24)*(AA198=0)","v":0},{"$f":"OR(B198<=$AO$19,B198>=$AN$19)*(F198<6)*(I198>$AN$20)*(I198<=$AO$20)","v":0},{"$f":"AND(B198>=$AN$29,B198<=$AO$29)*(F198<6)*(I198>$AN$30)*(I198<=$AO$30)","v":0},{"$f":"IF(OR(E198=$AM$34,E198=$AM$35,E198=$AM$36,E198=$AM$37,E198=$AM$38,E198=$AM$39,E198=$AM$40,E198=$AM$41,E198=$AM$42,E198=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E198>=$AM$47,E198<=$AN$47),AND(E198>=$AM$48,E198<=$AN$48),AND(E198>=$AM$49,E198<=$AN$49),AND(E198>=$AM$50,E198<=$AN$50),AND(E198>=$AM$51,E198<=$AN$51)),0,1)*AE198","v":1},{"$f":"(B198>=5)*(B198<=10)","v":0},{"$f":"1*OR(B198<=4,B198>=11)","v":1},{"$f":"LOOKUP(B198,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE198:AI198)*((F198<6)*(I198>$AO$7)*(I198<=$AP$7)+(F198=6)*(I198>$AO$8)*(I198<=$AP$8)+(F198>=7)*(I198>$AO$9)*(I198<=$AP$9))","v":0}]
["1976-01-09",1,9,2018,{"$f":"DATE(D199,B199,C199)","v":"2018-01-09"},{"$f":"WEEKDAY(E199,2)","v":2},0,"02:00:00",2,33.979999999999997,19.939999999999998,46.58,24.8,28.04,24.98,19.399999999999999,49.1,15.8,27.32,42.8,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,2018,"2018-01-09",2,0,"03:00:00",{"$f":"H200*24","v":3},33.08,19.04,47.480000000000004,24.8,28.94,21.02,20.299999999999997,50,15.620000000000001,25.88,44.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,2018,"2018-01-09",2,0,"04:00:00",4,32,17.600000000000001,48.019999999999996,23,30.02,19.939999999999998,21.2,46.4,14.54,23.9,44.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,2018,"2018-01-09",2,0,"05:00:00",5,32,15.98,47.84,21.2,28.94,19.939999999999998,21.2,46.4,12.379999999999999,24.8,44.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,2018,"2018-01-09",2,0,"06:00:00",6,35.06,15.079999999999998,50.36,17.600000000000001,30.92,19.04,23,52.34,10.579999999999998,23.36,48.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,2018,"2018-01-09",2,0,"07:00:00",7,39.92,10.940000000000001,50.540000000000006,17.600000000000001,33.979999999999997,17.059999999999999,19.399999999999999,50.900000000000006,9.32,21.740000000000002,44.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,2018,"2018-01-09",2,0,"08:00:00",8,37.94,10.940000000000001,51.8,15.8,33.979999999999997,17.96,23,52.879999999999995,7.6999999999999993,25.34,46.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,2018,"2018-01-09",2,0,"09:00:00",9,37.04,12.920000000000002,53.6,17.600000000000001,30.02,21.02,23,55.94,7.6999999999999993,26.78,46.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,2018,"2018-01-09",2,0,"10:00:00",10,42.980000000000004,19.939999999999998,51.8,21.2,35.06,24.08,21.2,55.400000000000006,12.740000000000002,29.66,48.2,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,2018,"2018-01-09",2,0,"11:00:00",11,42.980000000000004,19.939999999999998,51.8,24.8,32,26.96,21.2,56.84,16.88,32.72,51.8,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,2018,"2018-01-09",2,0,"12:00:00",12,42.08,26.96,51.8,28.4,32.9,30.02,21.2,55.400000000000006,21.02,33.44,53.6,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,2018,"2018-01-09",2,0,"13:00:00",13,41,30.02,55.400000000000006,30.2,32.72,33.08,22.1,57.2,25.52,35.6,53.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,2018,"2018-01-09",2,0,"14:00:00",14,39.92,34.520000000000003,48.2,32.36,32.54,36.14,23,57.92,27.86,37.94,53.6,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,2018,"2018-01-09",2,0,"15:00:00",15,39.019999999999996,35.42,51.8,33.08,32.72,35.96,19.399999999999999,53.6,29.3,36.14,53.6,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,2018,"2018-01-09",2,0,"16:00:00",16,37.04,35.96,50,33.44,35.06,39.019999999999996,19.399999999999999,52.879999999999995,32,36.86,51.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,2018,"2018-01-09",2,0,"17:00:00",17,35.42,37.22,50,34.159999999999997,33.979999999999997,38.840000000000003,21.2,48.92,32.54,37.4,48.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,2018,"2018-01-09",2,0,"18:00:00",18,30.02,37.58,48.2,34.520000000000003,33.08,37.94,21.2,50.900000000000006,32.9,37.4,48.019999999999996,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,2018,"2018-01-09",2,0,"19:00:00",19,31.46,38.299999999999997,46.4,35.24,32,37.94,19.399999999999999,48.92,33.619999999999997,39.380000000000003,46.94,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,2018,"2018-01-09",2,0,"20:00:00",20,31.46,38.840000000000003,44.6,35.78,30.92,37.94,19.399999999999999,46.94,33.44,39.92,44.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,2018,"2018-01-09",2,0,"21:00:00",21,31.82,39.380000000000003,42.8,36.86,30.02,39.92,17.600000000000001,44.96,35.6,39.380000000000003,44.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,2018,"2018-01-09",2,0,"22:00:00",22,33.799999999999997,39.92,42.8,38.119999999999997,28.94,41,15.8,43.879999999999995,37.4,38.840000000000003,42.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,2018,"2018-01-09",2,0,"23:00:00",23,36.68,40.1,41,38.480000000000004,28.04,40.64,14,42.980000000000004,37.04,39.74,42.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-09",1,9,2018,"2018-01-09",2,0,1,24,35.06,41,41,38.119999999999997,28.04,42.980000000000004,14,41.9,36.32,40.82,42.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"01:00:00",1,35.06,41,39.200000000000003,38.299999999999997,24.08,42.08,15.8,39.92,36.5,40.64,42.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"02:00:00",2,35.78,41,37.4,39.200000000000003,24.98,42.08,14,39.92,36.14,40.46,41,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"03:00:00",3,35.06,39.019999999999996,37.4,37.4,19.04,42.08,14,41.18,36.32,41.36,39.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"04:00:00",4,34.520000000000003,37.94,37.94,39.200000000000003,14,41,14,41,35.96,40.28,39.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"05:00:00",5,33.799999999999997,37.94,37.04,37.4,12.920000000000002,39.92,12.2,40.28,35.42,39.56,39.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"06:00:00",6,35.42,37.04,34.340000000000003,35.96,10.039999999999999,39.019999999999996,12.2,37.94,34.520000000000003,38.480000000000004,37.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"07:00:00",7,37.76,37.04,34.159999999999997,36.14,8.0599999999999987,37.94,12.2,37.22,34.700000000000003,39.380000000000003,37.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"08:00:00",8,34.700000000000003,37.04,34.340000000000003,35.78,6.0799999999999983,39.019999999999996,12.2,37.94,34.159999999999997,39.56,36.68,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"09:00:00",9,35.6,36.86,34.340000000000003,35.78,8.0599999999999987,38.119999999999997,12.2,37.04,34.159999999999997,38.840000000000003,36.68,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"10:00:00",10,40.1,39.019999999999996,37.4,37.4,17.059999999999999,41,12.2,39.56,34.880000000000003,39.56,39.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"11:00:00",11,43.16,39.019999999999996,39.200000000000003,37.22,24.08,42.08,12.2,43.879999999999995,35.6,40.46,42.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"12:00:00",12,41.54,41,42.8,37.94,28.04,42.08,12.2,45.86,35.96,41,42.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"13:00:00",13,28.94,41,42.8,38.659999999999997,30.02,42.08,32.18,46.94,36.5,44.24,44.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"14:00:00",14,32,41,44.6,38.659999999999997,30.92,42.980000000000004,12.2,46.94,36.5,44.42,44.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"15:00:00",15,30.92,41,44.6,38.659999999999997,33.979999999999997,42.980000000000004,12.2,46.94,36.5,43.7,44.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"16:00:00",16,28.94,39.92,44.6,38.480000000000004,32.72,41,10.399999999999999,43.879999999999995,36.5,41.9,44.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"17:00:00",17,19.939999999999998,39.92,39.200000000000003,39.200000000000003,32.36,39.92,10.399999999999999,44.78,36.32,39.380000000000003,42.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"18:00:00",18,15.98,37.4,36.5,35.78,24.98,37.94,8.5999999999999979,40.46,33.979999999999997,38.119999999999997,38.659999999999997,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"19:00:00",19,17.059999999999999,36.5,36.5,34.880000000000003,26.96,37.04,10.399999999999999,39.200000000000003,33.08,36.86,39.019999999999996,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"20:00:00",20,17.059999999999999,36.14,36.86,34.700000000000003,30.02,37.4,12.2,37.04,33.44,37.76,36.86,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"21:00:00",21,19.939999999999998,35.06,34.520000000000003,33.799999999999997,32,36.32,19.399999999999999,35.24,33.08,36.86,35.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"22:00:00",22,21.02,32.9,33.799999999999997,33.799999999999997,32,33.979999999999997,23,33.979999999999997,33.08,35.06,33.619999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,"23:00:00",23,21.92,30.92,33.44,30.2,33.08,32.54,21.2,33.619999999999997,28.58,33.08,33.26,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-10",1,10,2018,"2018-01-10",3,0,1,24,23,23,28.4,28.4,33.08,30.02,24.8,32,31.82,32.72,30.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,2018,"2018-01-11",4,0,"01:00:00",1,24.08,24.08,33.44,28.4,33.08,26.96,24.8,34.700000000000003,30.74,29.84,30.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,2018,"2018-01-11",4,0,"02:00:00",2,26.6,24.08,32.54,24.8,33.979999999999997,26.060000000000002,26.6,33.44,30.02,26.24,33.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,2018,"2018-01-11",4,0,"03:00:00",3,26.96,21.02,32.9,24.8,33.979999999999997,24.08,26.6,33.619999999999997,26.78,24.98,33.979999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,2018,"2018-01-11",4,0,"04:00:00",4,28.04,19.04,34.700000000000003,21.2,33.979999999999997,24.08,32,34.520000000000003,23.36,26.6,33.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,2018,"2018-01-11",4,0,"05:00:00",5,28.04,19.04,34.700000000000003,21.2,33.08,23,30.2,35.06,21.2,24.259999999999998,33.619999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,2018,"2018-01-11",4,0,"06:00:00",6,28.94,17.96,33.26,21.2,34.700000000000003,21.92,30.2,35.6,20.12,23.9,35.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,2018,"2018-01-11",4,0,"07:00:00",7,30.02,19.04,33.26,19.399999999999999,34.159999999999997,21.92,29.3,35.96,18.86,24.259999999999998,36.14,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,2018,"2018-01-11",4,0,"08:00:00",8,26.96,19.04,33.08,19.399999999999999,33.44,21.92,28.4,36.32,17.240000000000002,24.439999999999998,35.6,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,2018,"2018-01-11",4,0,"09:00:00",9,30.92,23,33.08,21.2,33.619999999999997,26.060000000000002,28.4,36.5,18.68,27.86,37.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,2018,"2018-01-11",4,0,"10:00:00",10,33.44,28.94,32.72,24.8,37.04,30.92,30.2,35.6,22.1,33.08,37.4,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,2018,"2018-01-11",4,0,"11:00:00",11,34.700000000000003,32.36,32.9,30.2,39.019999999999996,34.159999999999997,30.2,35.96,27.5,32.18,37.4,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,2018,"2018-01-11",4,0,"12:00:00",12,35.6,33.08,32.18,30.2,39.92,35.96,32,35.6,30.92,33.44,36.14,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,2018,"2018-01-11",4,0,"13:00:00",13,38.119999999999997,33.979999999999997,33.979999999999997,32,41,37.04,32,37.4,33.26,34.880000000000003,37.4,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,2018,"2018-01-11",4,0,"14:00:00",14,38.119999999999997,34.340000000000003,35.6,32.36,42.8,35.96,28.4,37.4,35.6,35.42,37.4,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,2018,"2018-01-11",4,0,"15:00:00",15,38.659999999999997,35.06,37.76,32.9,41,37.04,29.3,42.980000000000004,35.78,36.86,37.4,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,2018,"2018-01-11",4,0,"16:00:00",16,39.56,35.06,41.18,33.08,43.16,37.04,30.2,46.58,35.78,36.5,39.74,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,{"$f":"$AO$4","v":2018},"2018-01-11",4,{"$f":"COUNTIF($AM$34:$AM$43,E262)","v":0},"17:00:00",17,39.019999999999996,35.06,45.5,33.26,43.16,35.96,26.6,50.72,32.18,36.32,42.620000000000005,null,{"$f":"SUMPRODUCT($J$2:$T$2,J262:T262)","v":0},null,null,{"$f":"OR(B262<=$AO$14,B262>=$AN$14)*(F262<6)*(I262>$AN$15)*(I262<=$AO$15)*(G262<>1)","v":1},{"$f":"OR(B262<=$AO$14,B262>=$AN$14)*(Y262=0)","v":0},{"$f":"AND(B262>=$AN$24,B262<=$AO$24)*(F262<6)*(I262>$AN$25)*(I262<=$AO$25)*(G262<>1)","v":0},{"$f":"AND(B262>=$AN$24,B262<=$AO$24)*(AA262=0)","v":0},{"$f":"OR(B262<=$AO$19,B262>=$AN$19)*(F262<6)*(I262>$AN$20)*(I262<=$AO$20)","v":0},{"$f":"AND(B262>=$AN$29,B262<=$AO$29)*(F262<6)*(I262>$AN$30)*(I262<=$AO$30)","v":0},{"$f":"IF(OR(E262=$AM$34,E262=$AM$35,E262=$AM$36,E262=$AM$37,E262=$AM$38,E262=$AM$39,E262=$AM$40,E262=$AM$41,E262=$AM$42,E262=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E262>=$AM$47,E262<=$AN$47),AND(E262>=$AM$48,E262<=$AN$48),AND(E262>=$AM$49,E262<=$AN$49),AND(E262>=$AM$50,E262<=$AN$50),AND(E262>=$AM$51,E262<=$AN$51)),0,1)*AE262","v":1},{"$f":"(B262>=5)*(B262<=10)","v":0},{"$f":"1*OR(B262<=4,B262>=11)","v":1},{"$f":"LOOKUP(B262,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE262:AI262)*((F262<6)*(I262>$AO$7)*(I262<=$AP$7)+(F262=6)*(I262>$AO$8)*(I262<=$AP$8)+(F262>=7)*(I262>$AO$9)*(I262<=$AP$9))","v":0}]
["1976-01-11",1,11,2018,{"$f":"DATE(D263,B263,C263)","v":"2018-01-11"},{"$f":"WEEKDAY(E263,2)","v":4},0,"18:00:00",18,38.840000000000003,33.44,36.5,32.36,42.980000000000004,34.340000000000003,24.8,47.120000000000005,34.700000000000003,36.5,42.620000000000005,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,2018,"2018-01-11",4,0,"19:00:00",{"$f":"H264*24","v":19},38.480000000000004,33.08,34.880000000000003,33.799999999999997,43.52,33.799999999999997,23,44.24,33.26,35.6,40.28,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,2018,"2018-01-11",4,0,"20:00:00",20,38.299999999999997,33.979999999999997,35.6,33.799999999999997,43.879999999999995,35.06,28.4,43.16,32.36,36.86,37.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,2018,"2018-01-11",4,0,"21:00:00",21,38.480000000000004,33.799999999999997,35.6,32,44.42,34.700000000000003,28.4,42.26,32,37.22,37.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,2018,"2018-01-11",4,0,"22:00:00",22,38.840000000000003,33.26,34.340000000000003,32,43.52,33.799999999999997,26.6,41,32,37.22,36.86,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,2018,"2018-01-11",4,0,"23:00:00",23,38.659999999999997,33.08,32.9,32.18,42.620000000000005,33.799999999999997,24.8,39.380000000000003,32,37.4,35.6,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-11",1,11,2018,"2018-01-11",4,0,1,24,38.299999999999997,33.26,33.26,32.18,42.08,33.799999999999997,24.8,38.299999999999997,32.54,37.4,35.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"01:00:00",1,38.480000000000004,33.08,34.159999999999997,32,42.980000000000004,33.979999999999997,26.6,37.76,32.54,37.4,35.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"02:00:00",2,38.480000000000004,33.08,35.6,32.18,42.980000000000004,33.799999999999997,26.6,37.94,32.54,37.4,35.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"03:00:00",3,39.92,33.44,34.880000000000003,32.18,42.980000000000004,33.799999999999997,26.6,37.4,32.36,37.4,35.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"04:00:00",4,39.92,33.619999999999997,34.520000000000003,32.36,46.04,33.979999999999997,26.6,37.4,32.36,39.200000000000003,35.78,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"05:00:00",5,39.56,33.619999999999997,35.42,32.36,44.06,34.520000000000003,26.6,37.76,32.36,39.200000000000003,35.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"06:00:00",6,44.06,33.799999999999997,34.159999999999997,32.9,42.980000000000004,34.700000000000003,28.4,35.6,32.18,37.76,35.42,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"07:00:00",7,42.620000000000005,33.799999999999997,34.340000000000003,32.9,48.019999999999996,33.979999999999997,30.2,35.6,32.36,37.4,35.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"08:00:00",8,42.620000000000005,33.979999999999997,33.979999999999997,33.08,46.04,35.06,32,35.42,32.18,37.4,35.24,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"09:00:00",9,41,33.799999999999997,33.799999999999997,33.26,45.86,35.6,32,35.6,32.18,37.4,35.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"10:00:00",10,44.06,35.06,34.700000000000003,33.799999999999997,46.04,35.96,33.799999999999997,37.94,32.9,37.4,35.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"11:00:00",11,44.06,36.86,35.6,35.6,48.92,37.58,33.08,39.92,35.06,38.840000000000003,39.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"12:00:00",12,44.06,37.4,39.200000000000003,35.6,51.08,37.4,34.700000000000003,41.36,35.42,39.200000000000003,39.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"13:00:00",13,48.92,37.4,41,37.4,53.06,39.380000000000003,35.6,45.86,37.04,42.8,44.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"14:00:00",14,46.04,39.380000000000003,41,38.299999999999997,53.96,39.200000000000003,37.4,45.86,36.5,41,44.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"15:00:00",15,46.4,39.200000000000003,42.8,38.299999999999997,53.06,39.200000000000003,36.5,45.86,37.22,41,44.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"16:00:00",16,48.019999999999996,39.200000000000003,42.8,38.119999999999997,51.08,39.019999999999996,37.22,43.879999999999995,37.76,40.64,42.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"17:00:00",17,50,37.94,39.200000000000003,37.58,50,39.019999999999996,35.6,41.9,37.22,39.92,41,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"18:00:00",18,44.06,37.4,34.880000000000003,37.04,53.96,39.019999999999996,35.6,39.200000000000003,35.78,39.200000000000003,37.58,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"19:00:00",19,48.2,37.4,33.799999999999997,36.86,50,37.94,35.6,37.76,36.5,39.200000000000003,37.04,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"20:00:00",20,48.019999999999996,37.04,32.9,36.86,53.06,39.74,34.700000000000003,36.32,36.5,39.019999999999996,35.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"21:00:00",21,51.980000000000004,37.4,32.36,36.86,53.96,37.94,34.700000000000003,34.700000000000003,36.5,39.200000000000003,33.979999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"22:00:00",22,46.94,37.4,28.4,36.32,55.040000000000006,39.56,34.159999999999997,32.9,35.78,39.200000000000003,32.18,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,"23:00:00",23,44.96,37.04,26.6,35.78,51.08,37.94,33.619999999999997,32,35.06,39.200000000000003,35.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-12",1,12,2018,"2018-01-12",5,0,1,24,42.980000000000004,37.76,24.8,35.6,49.64,37.4,34.340000000000003,27.14,35.06,39.74,33.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"01:00:00",1,37.94,37.4,24.8,35.6,43.16,39.200000000000003,34.159999999999997,26.060000000000002,35.06,39.200000000000003,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"02:00:00",2,33.979999999999997,37.94,23,35.6,36.5,39.74,34.700000000000003,25.16,34.700000000000003,41,35.06,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"03:00:00",3,35.06,37.58,23,35.6,32.36,39.380000000000003,35.24,24.08,34.340000000000003,40.82,33.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"04:00:00",4,35.06,37.4,21.2,35.6,35.96,39.380000000000003,35.06,24.08,33.979999999999997,41,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"05:00:00",5,33.979999999999997,36.5,21.2,34.340000000000003,35.06,38.659999999999997,34.520000000000003,22.1,33.26,41,30.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"06:00:00",6,30.02,37.04,21.2,35.6,33.08,38.840000000000003,35.24,22.1,34.700000000000003,41,24.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"07:00:00",7,30.02,36.86,19.399999999999999,35.6,32,38.840000000000003,35.24,22.1,34.520000000000003,39.200000000000003,26.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"08:00:00",8,24.08,36.5,19.399999999999999,34.700000000000003,26.96,38.299999999999997,35.6,21.02,34.520000000000003,39.200000000000003,28.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"09:00:00",9,24.98,35.6,19.399999999999999,35.6,23,37.04,35.96,27.14,34.159999999999997,41.18,32,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"10:00:00",10,24.08,37.04,24.8,35.6,21.92,39.380000000000003,37.04,32.9,36.5,41.54,35.06,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"11:00:00",11,19.939999999999998,38.840000000000003,33.799999999999997,37.4,21.2,39.019999999999996,39.200000000000003,36.5,37.58,42.44,35.42,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"12:00:00",12,17.96,39.019999999999996,35.78,37.4,21.02,42.08,39.019999999999996,37.94,38.480000000000004,42.8,37.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"13:00:00",13,17.96,39.92,38.840000000000003,39.56,19.939999999999998,43.879999999999995,41,38.840000000000003,40.46,44.6,39.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"14:00:00",14,17.059999999999999,43.7,39.200000000000003,41.18,21.92,42.08,41,41,42.26,44.6,39.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"15:00:00",15,15.98,44.24,41,41.72,21.92,44.06,41,41,42.8,44.42,39.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"16:00:00",16,14,44.6,39.200000000000003,42.08,19.04,44.6,41,39.92,42.8,44.78,37.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"17:00:00",17,12.920000000000002,44.96,37.04,42.44,17.059999999999999,44.6,38.659999999999997,37.94,42.08,45.32,35.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"18:00:00",18,12.02,45.86,33.799999999999997,42.44,15.079999999999998,46.4,36.5,36.86,41.36,46.22,34.880000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"19:00:00",19,8.0599999999999987,46.22,33.08,42.980000000000004,12.920000000000002,46.4,37.04,34.880000000000003,41.72,48.2,33.979999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"20:00:00",20,6.98,46.22,32.9,43.16,12.02,46.4,37.04,33.979999999999997,41.9,46.4,34.159999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"21:00:00",21,6.0799999999999983,42.8,32.54,43.34,10.940000000000001,46.4,37.4,34.159999999999997,42.08,48.2,33.799999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"22:00:00",22,6.0799999999999983,42.8,32.36,43.16,12.02,44.6,37.04,33.979999999999997,41.72,48.74,33.44,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,"23:00:00",23,6.0799999999999983,42.980000000000004,33.799999999999997,43.52,10.940000000000001,46.94,37.58,33.799999999999997,42.08,49.1,33.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-13",1,13,2018,"2018-01-13",6,0,1,24,6.0799999999999983,46.22,33.799999999999997,43.7,10.940000000000001,46.94,39.200000000000003,33.799999999999997,42.44,48.2,32.9,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,2018,"2018-01-14",7,0,"01:00:00",1,6.0799999999999983,46.4,33.799999999999997,43.52,10.039999999999999,46.94,39.200000000000003,33.979999999999997,42.08,49.1,32.9,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,2018,"2018-01-14",7,0,"02:00:00",2,5,46.04,33.799999999999997,43.52,8.9599999999999973,46.4,39.200000000000003,34.159999999999997,42.26,48.2,33.26,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,2018,"2018-01-14",7,0,"03:00:00",3,3.9200000000000017,45.68,33.799999999999997,42.8,8.0599999999999987,46.04,39.200000000000003,33.619999999999997,41.54,48.2,32.54,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,2018,"2018-01-14",7,0,"04:00:00",4,3.019999999999996,42.8,33.799999999999997,42.44,6.98,46.4,37.94,33.799999999999997,41.36,48.379999999999995,32.36,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,2018,"2018-01-14",7,0,"05:00:00",5,1.9400000000000013,44.42,30.2,41.72,6.0799999999999983,44.96,38.299999999999997,30.2,41,48.2,28.4,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,2018,"2018-01-14",7,0,"06:00:00",6,1.0399999999999991,42.8,28.4,43.34,5,44.6,41,28.4,42.26,48.2,26.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,2018,"2018-01-14",7,0,"07:00:00",7,1.0399999999999991,42.8,28.4,43.16,3.9200000000000017,46.04,41,28.4,41.72,48.2,24.8,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,2018,"2018-01-14",7,0,"08:00:00",8,-2.9200000000000017,45.86,28.4,42.620000000000005,3.9200000000000017,47.66,39.200000000000003,29.12,41.18,47.66,24.8,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,{"$f":"$AO$4","v":2018},"2018-01-14",7,{"$f":"COUNTIF($AM$34:$AM$43,E326)","v":0},"09:00:00",9,1.0399999999999991,46.22,28.4,41,6.0799999999999983,48.2,40.28,28.4,41.18,48.2,24.8,null,{"$f":"SUMPRODUCT($J$2:$T$2,J326:T326)","v":0},null,null,{"$f":"OR(B326<=$AO$14,B326>=$AN$14)*(F326<6)*(I326>$AN$15)*(I326<=$AO$15)*(G326<>1)","v":0},{"$f":"OR(B326<=$AO$14,B326>=$AN$14)*(Y326=0)","v":1},{"$f":"AND(B326>=$AN$24,B326<=$AO$24)*(F326<6)*(I326>$AN$25)*(I326<=$AO$25)*(G326<>1)","v":0},{"$f":"AND(B326>=$AN$24,B326<=$AO$24)*(AA326=0)","v":0},{"$f":"OR(B326<=$AO$19,B326>=$AN$19)*(F326<6)*(I326>$AN$20)*(I326<=$AO$20)","v":0},{"$f":"AND(B326>=$AN$29,B326<=$AO$29)*(F326<6)*(I326>$AN$30)*(I326<=$AO$30)","v":0},{"$f":"IF(OR(E326=$AM$34,E326=$AM$35,E326=$AM$36,E326=$AM$37,E326=$AM$38,E326=$AM$39,E326=$AM$40,E326=$AM$41,E326=$AM$42,E326=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E326>=$AM$47,E326<=$AN$47),AND(E326>=$AM$48,E326<=$AN$48),AND(E326>=$AM$49,E326<=$AN$49),AND(E326>=$AM$50,E326<=$AN$50),AND(E326>=$AM$51,E326<=$AN$51)),0,1)*AE326","v":1},{"$f":"(B326>=5)*(B326<=10)","v":0},{"$f":"1*OR(B326<=4,B326>=11)","v":1},{"$f":"LOOKUP(B326,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE326:AI326)*((F326<6)*(I326>$AO$7)*(I326<=$AP$7)+(F326=6)*(I326>$AO$8)*(I326<=$AP$8)+(F326>=7)*(I326>$AO$9)*(I326<=$AP$9))","v":0}]
["1976-01-14",1,14,2018,{"$f":"DATE(D327,B327,C327)","v":"2018-01-14"},{"$f":"WEEKDAY(E327,2)","v":7},0,"10:00:00",10,3.9200000000000017,47.480000000000004,28.4,44.06,8.0599999999999987,49.46,42.44,28.4,42.980000000000004,48.2,24.8,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,2018,"2018-01-14",7,0,"11:00:00",{"$f":"H328*24","v":11},3.9200000000000017,49.1,28.4,46.4,10.039999999999999,46.4,42.8,26.6,45.32,50.900000000000006,24.8,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,2018,"2018-01-14",7,0,"12:00:00",12,6.98,50.72,28.4,50,10.940000000000001,53.06,44.06,26.6,45.14,50.540000000000006,24.8,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,2018,"2018-01-14",7,0,"13:00:00",13,8.0599999999999987,55.94,28.4,55.400000000000006,14,57.92,43.34,28.4,49.28,59.18,24.8,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,2018,"2018-01-14",7,0,"14:00:00",14,10.039999999999999,55.94,28.4,55.400000000000006,15.079999999999998,57.019999999999996,40.64,28.4,47.120000000000005,60.26,26.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,2018,"2018-01-14",7,0,"15:00:00",15,10.039999999999999,53.06,30.2,51.8,15.98,55.040000000000006,38.840000000000003,29.12,48.92,57.379999999999995,26.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,2018,"2018-01-14",7,0,"16:00:00",16,10.399999999999999,48.92,30.2,50,15.079999999999998,51.980000000000004,37.04,29.12,46.94,54.32,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,2018,"2018-01-14",7,0,"17:00:00",17,6.98,48.92,30.2,46.4,12.920000000000002,48.92,35.24,29.12,44.6,47.480000000000004,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,2018,"2018-01-14",7,0,"18:00:00",18,5,42.08,28.4,40.28,10.940000000000001,46.04,12.2,28.4,37.76,43.7,24.8,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,2018,"2018-01-14",7,0,"19:00:00",19,-2.019999999999996,39.92,28.4,39.200000000000003,10.039999999999999,42.980000000000004,12.2,29.12,36.86,43.52,24.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,2018,"2018-01-14",7,0,"20:00:00",20,-5.980000000000004,39.92,28.4,39.200000000000003,8.9599999999999973,42.980000000000004,12.2,28.04,36.32,43.34,24.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,2018,"2018-01-14",7,0,"21:00:00",21,-7.0600000000000023,40.1,28.4,37.4,5,41,12.2,28.4,35.96,42.44,24.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,2018,"2018-01-14",7,0,"22:00:00",22,-9.0399999999999991,38.840000000000003,28.4,35.6,3.9200000000000017,39.92,10.399999999999999,28.4,35.78,40.46,24.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,2018,"2018-01-14",7,0,"23:00:00",23,-9.9400000000000048,37.4,26.6,35.06,3.019999999999996,39.019999999999996,10.399999999999999,25.16,33.799999999999997,39.380000000000003,23,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-14",1,14,2018,"2018-01-14",7,0,1,24,-14.080000000000005,36.86,26.6,34.520000000000003,1.9400000000000013,37.94,10.399999999999999,24.8,33.44,38.119999999999997,19.939999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"01:00:00",1,-13,36.32,26.6,33.979999999999997,1.0399999999999991,37.94,8.5999999999999979,21.2,33.08,37.94,21.02,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"02:00:00",2,-14.980000000000004,36.14,24.8,33.799999999999997,3.9200000000000017,37.04,10.399999999999999,21.2,33.26,37.04,21.2,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"03:00:00",3,-14.980000000000004,35.78,24.8,33.979999999999997,3.019999999999996,37.04,12.2,21.2,33.08,36.32,23,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"04:00:00",4,-13,34.700000000000003,24.8,32.54,3.019999999999996,37.04,15.8,22.1,33.26,36.86,23,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"05:00:00",5,-13,33.26,24.8,32,3.019999999999996,35.96,8.5999999999999979,21.02,31.28,36.5,21.92,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"06:00:00",6,-11.019999999999996,24.08,26.6,30.2,3.019999999999996,33.08,6.8000000000000007,22.1,32.9,34.700000000000003,21.2,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"07:00:00",7,-11.019999999999996,23,26.6,28.4,3.019999999999996,33.08,11.3,21.2,33.08,33.799999999999997,19.04,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"08:00:00",8,-9.0399999999999991,23,26.6,26.6,3.019999999999996,30.92,15.8,23,32.9,32.72,19.04,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"09:00:00",9,-5.0800000000000054,30.92,26.6,28.4,6.0799999999999983,35.06,12.2,25.16,32.9,32.72,19.939999999999998,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"10:00:00",10,-0.94000000000000483,34.159999999999997,26.6,32.18,8.9599999999999973,35.42,14,29.12,33.979999999999997,35.96,24.08,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"11:00:00",11,3.019999999999996,35.96,26.6,33.26,10.039999999999999,37.04,14,31.1,34.880000000000003,38.659999999999997,26.96,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"12:00:00",12,6.98,36.14,26.6,33.619999999999997,12.920000000000002,39.019999999999996,10.399999999999999,31.1,35.24,37.94,28.94,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"13:00:00",13,12.02,37.04,28.4,34.520000000000003,15.98,39.019999999999996,12.2,32.54,32.36,38.840000000000003,30.92,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"14:00:00",14,15.079999999999998,37.04,28.4,34.700000000000003,17.059999999999999,37.94,12.2,32.9,32.54,39.56,32,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"15:00:00",15,15.98,37.04,30.2,34.159999999999997,19.939999999999998,39.019999999999996,10.399999999999999,33.44,32.18,39.74,32,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"16:00:00",16,15.079999999999998,36.68,30.2,33.799999999999997,19.939999999999998,37.94,11.3,33.26,34.880000000000003,38.480000000000004,30.92,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"17:00:00",17,6.0799999999999983,35.06,28.4,32.54,15.98,37.04,12.2,29.12,34.520000000000003,37.94,28.94,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"18:00:00",18,1.9400000000000013,32.54,26.6,30.2,17.059999999999999,34.880000000000003,8.5999999999999979,23,33.44,37.94,26.96,null,0,null,null,0,1,0,0,1,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"19:00:00",19,3.019999999999996,32.18,24.8,28.4,17.059999999999999,34.159999999999997,8.5999999999999979,21.02,30.56,35.06,24.98,null,0,null,null,0,1,0,0,1,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"20:00:00",20,3.9200000000000017,32,24.8,28.4,15.98,33.08,6.8000000000000007,22.64,28.58,34.520000000000003,23,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"21:00:00",21,6.0799999999999983,26.96,23,28.4,15.98,32.72,6.8000000000000007,24.08,28.4,34.880000000000003,21.02,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"22:00:00",22,8.0599999999999987,28.04,21.2,28.4,15.98,32,7.6999999999999993,25.16,28.4,33.979999999999997,19.939999999999998,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,"23:00:00",23,8.0599999999999987,28.04,21.2,28.4,15.8,32,8.5999999999999979,24.08,28.4,33.619999999999997,19.939999999999998,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1976-01-15",1,15,2018,"2018-01-15",1,1,1,24,8.9599999999999973,26.96,19.399999999999999,28.4,15.98,30.92,11.3,23,28.4,32.9,19.939999999999998,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"01:00:00",1,6.0799999999999983,26.96,15.8,28.4,15.98,30.92,14,23,28.22,32.54,21.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"02:00:00",2,5,26.96,12.2,28.4,15.98,30.92,14,23,28.22,32.9,19.939999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"03:00:00",3,1.9400000000000013,28.04,12.2,28.4,15.079999999999998,30.92,14,22.1,28.4,33.08,17.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"04:00:00",4,3.019999999999996,28.04,8.5999999999999979,28.4,15.079999999999998,30.92,14,22.1,28.4,33.619999999999997,17.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"05:00:00",5,3.9200000000000017,28.04,8.5999999999999979,28.4,15.079999999999998,30.92,14,18.14,28.759999999999998,33.26,17.059999999999999,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"06:00:00",6,5,28.4,8.5999999999999979,28.4,15.98,30.2,10.399999999999999,19.04,29.12,32,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"07:00:00",7,5,28.4,6.8000000000000007,28.4,15.98,28.94,10.399999999999999,21.02,27.86,28.94,17.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"08:00:00",8,3.9200000000000017,28.04,6.8000000000000007,26.6,15.98,28.4,8.5999999999999979,21.02,27.5,28.4,19.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"09:00:00",9,6.98,28.4,6.8000000000000007,26.6,17.600000000000001,28.4,10.399999999999999,24.08,27.5,29.48,21.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"10:00:00",10,8.0599999999999987,28.4,12.2,26.6,21.02,30.02,12.2,27.14,28.04,30.2,24.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"11:00:00",11,10.940000000000001,30.02,24.8,28.4,21.92,30.2,12.2,30.02,28.22,31.1,26.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"12:00:00",12,15.98,30.2,26.6,28.4,24.98,30.2,14,32,28.759999999999998,30.2,26.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"13:00:00",13,21.02,30.2,28.4,28.4,26.96,30.2,14,32.9,29.3,30.92,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"14:00:00",14,21.92,30.92,28.4,28.4,28.04,30.2,14,32.9,29.84,32,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"15:00:00",15,21.92,30.2,30.2,28.4,28.94,32,15.8,32,29.84,32,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"16:00:00",16,21.92,30.2,30.2,28.4,28.94,32,15.8,31.1,30.02,32.36,28.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"17:00:00",17,21.92,30.02,28.4,28.4,28.04,32,15.8,30.02,29.84,32.54,28.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"18:00:00",18,21.02,30.2,28.4,28.4,26.96,32,15.8,28.04,29.3,30.2,26.060000000000002,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"19:00:00",19,19.939999999999998,26.6,21.2,28.4,26.96,30.92,15.8,26.060000000000002,28.4,30.2,24.98,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"20:00:00",20,19.04,26.96,19.399999999999999,28.4,26.96,30.2,17.600000000000001,24.08,28.4,30.2,23,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"21:00:00",21,17.96,28.4,15.8,28.4,26.96,30.2,15.8,23,28.4,30.2,21.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"22:00:00",22,17.96,28.94,12.2,28.4,26.96,30.92,14,24.08,28.759999999999998,30.2,21.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,"23:00:00",23,19.399999999999999,28.94,10.399999999999999,28.4,26.96,30.2,12.2,18.14,28.58,28.759999999999998,19.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-16",1,16,2018,"2018-01-16",2,0,1,24,19.04,24.8,8.5999999999999979,28.4,26.96,30.2,12.2,16.159999999999997,28.4,29.3,17.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,{"$f":"$AO$4","v":2018},"2018-01-17",3,{"$f":"COUNTIF($AM$34:$AM$43,E390)","v":0},"01:00:00",1,19.939999999999998,21.2,8.5999999999999979,26.6,26.060000000000002,30.2,12.2,14,28.04,28.4,15.079999999999998,null,{"$f":"SUMPRODUCT($J$2:$T$2,J390:T390)","v":0},null,null,{"$f":"OR(B390<=$AO$14,B390>=$AN$14)*(F390<6)*(I390>$AN$15)*(I390<=$AO$15)*(G390<>1)","v":0},{"$f":"OR(B390<=$AO$14,B390>=$AN$14)*(Y390=0)","v":1},{"$f":"AND(B390>=$AN$24,B390<=$AO$24)*(F390<6)*(I390>$AN$25)*(I390<=$AO$25)*(G390<>1)","v":0},{"$f":"AND(B390>=$AN$24,B390<=$AO$24)*(AA390=0)","v":0},{"$f":"OR(B390<=$AO$19,B390>=$AN$19)*(F390<6)*(I390>$AN$20)*(I390<=$AO$20)","v":0},{"$f":"AND(B390>=$AN$29,B390<=$AO$29)*(F390<6)*(I390>$AN$30)*(I390<=$AO$30)","v":0},{"$f":"IF(OR(E390=$AM$34,E390=$AM$35,E390=$AM$36,E390=$AM$37,E390=$AM$38,E390=$AM$39,E390=$AM$40,E390=$AM$41,E390=$AM$42,E390=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E390>=$AM$47,E390<=$AN$47),AND(E390>=$AM$48,E390<=$AN$48),AND(E390>=$AM$49,E390<=$AN$49),AND(E390>=$AM$50,E390<=$AN$50),AND(E390>=$AM$51,E390<=$AN$51)),0,1)*AE390","v":1},{"$f":"(B390>=5)*(B390<=10)","v":0},{"$f":"1*OR(B390<=4,B390>=11)","v":1},{"$f":"LOOKUP(B390,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE390:AI390)*((F390<6)*(I390>$AO$7)*(I390<=$AP$7)+(F390=6)*(I390>$AO$8)*(I390<=$AP$8)+(F390>=7)*(I390>$AO$9)*(I390<=$AP$9))","v":0}]
["1976-01-17",1,17,2018,{"$f":"DATE(D391,B391,C391)","v":"2018-01-17"},{"$f":"WEEKDAY(E391,2)","v":3},0,"02:00:00",2,19.04,19.939999999999998,6.8000000000000007,26.6,26.060000000000002,26.6,10.399999999999999,10.039999999999999,26.060000000000002,27.68,14,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,2018,"2018-01-17",3,0,"03:00:00",{"$f":"H392*24","v":3},19.939999999999998,21.2,6.8000000000000007,28.4,26.060000000000002,24.8,8.5999999999999979,9.14,23,27.68,10.940000000000001,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,2018,"2018-01-17",3,0,"04:00:00",4,19.04,17.600000000000001,3.1999999999999993,28.4,26.060000000000002,26.6,8.5999999999999979,8.0599999999999987,21.2,26.6,10.039999999999999,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,2018,"2018-01-17",3,0,"05:00:00",5,19.939999999999998,15.079999999999998,3.1999999999999993,26.6,26.060000000000002,26.060000000000002,8.5999999999999979,5,20.84,27.68,6.0799999999999983,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,2018,"2018-01-17",3,0,"06:00:00",6,19.399999999999999,19.939999999999998,3.1999999999999993,28.4,26.060000000000002,28.94,8.5999999999999979,7.1599999999999966,22.46,27.5,8.0599999999999987,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,2018,"2018-01-17",3,0,"07:00:00",7,19.939999999999998,21.92,3.1999999999999993,30.2,26.060000000000002,28.04,10.399999999999999,7.1599999999999966,23,26.78,6.0799999999999983,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,2018,"2018-01-17",3,0,"08:00:00",8,19.04,21.92,3.1999999999999993,32,26.060000000000002,26.96,8.5999999999999979,10.039999999999999,23.54,27.14,6.0799999999999983,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,2018,"2018-01-17",3,0,"09:00:00",9,19.939999999999998,33.08,3.1999999999999993,30.2,26.060000000000002,30.02,10.399999999999999,13.099999999999998,23.9,30.38,10.039999999999999,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,2018,"2018-01-17",3,0,"10:00:00",10,19.939999999999998,32.36,8.5999999999999979,33.799999999999997,26.96,33.619999999999997,10.399999999999999,17.600000000000001,27.5,33.799999999999997,19.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,2018,"2018-01-17",3,0,"11:00:00",11,21.02,32.54,12.2,35.6,26.96,34.880000000000003,8.5999999999999979,22.1,31.82,34.700000000000003,24.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,2018,"2018-01-17",3,0,"12:00:00",12,24.08,34.520000000000003,17.600000000000001,32.36,28.04,36.68,3.1999999999999993,26.6,37.04,36.14,26.6,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,2018,"2018-01-17",3,0,"13:00:00",13,24.98,35.42,21.2,32.9,28.04,39.019999999999996,1.3999999999999986,28.4,31.46,38.480000000000004,28.4,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,2018,"2018-01-17",3,0,"14:00:00",14,26.060000000000002,36.14,26.6,33.08,28.94,39.019999999999996,-4,30.02,30.02,39.74,30.2,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,2018,"2018-01-17",3,0,"15:00:00",15,26.060000000000002,35.96,28.4,30.2,28.94,38.840000000000003,-5.8000000000000043,31.1,28.4,39.200000000000003,30.2,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,2018,"2018-01-17",3,0,"16:00:00",16,26.060000000000002,33.799999999999997,28.4,28.4,28.4,37.22,-9.3999999999999986,31.1,27.14,37.76,30.2,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,2018,"2018-01-17",3,0,"17:00:00",17,26.060000000000002,32.18,28.4,26.6,28.94,35.6,-9.3999999999999986,30.02,24.08,36.32,28.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,2018,"2018-01-17",3,0,"18:00:00",18,24.98,28.04,28.4,24.8,28.04,30.92,-9.3999999999999986,30.02,21.92,32.72,28.04,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,2018,"2018-01-17",3,0,"19:00:00",19,19.939999999999998,26.96,26.6,21.2,23,30.02,-9.3999999999999986,30.02,20.479999999999997,30.02,28.04,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,2018,"2018-01-17",3,0,"20:00:00",20,21.02,26.96,26.6,21.2,28.04,28.94,-9.3999999999999986,30.02,18.5,28.94,28.4,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,2018,"2018-01-17",3,0,"21:00:00",21,19.939999999999998,24.98,28.4,21.2,26.96,28.94,-9.3999999999999986,29.12,17.059999999999999,28.04,26.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,2018,"2018-01-17",3,0,"22:00:00",22,21.92,24.08,26.6,19.399999999999999,23,28.04,-10.300000000000004,29.12,16.340000000000003,26.24,28.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,2018,"2018-01-17",3,0,"23:00:00",23,23,24.08,26.6,19.399999999999999,15.98,26.96,-11.200000000000003,28.4,16.159999999999997,25.7,28.4,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-17",1,17,2018,"2018-01-17",3,0,1,24,24.08,19.939999999999998,26.6,17.600000000000001,12.920000000000002,26.060000000000002,-12.100000000000001,28.04,15.259999999999998,24.62,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"01:00:00",1,23,19.04,26.6,17.600000000000001,15.079999999999998,24.08,-13,28.4,14.36,23.54,26.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"02:00:00",2,19.04,19.04,26.6,15.8,8.9599999999999973,21.02,-14.800000000000004,26.6,13.82,21.740000000000002,26.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"03:00:00",3,12.920000000000002,15.079999999999998,26.6,15.8,1.9400000000000013,19.939999999999998,-16.600000000000001,26.6,12.559999999999999,20.299999999999997,26.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"04:00:00",4,8.0599999999999987,14,26.6,12.2,3.9200000000000017,17.96,-16.600000000000001,26.6,10.579999999999998,19.22,32.72,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"05:00:00",5,3.9200000000000017,14,28.4,10.399999999999999,8.0599999999999987,15.98,-18.399999999999999,26.6,8.5999999999999979,17.059999999999999,32.54,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"06:00:00",6,-3.9999999999999147E-2,10.039999999999999,28.4,10.399999999999999,5,14,-20.200000000000003,33.08,6.8000000000000007,14.54,34.700000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"07:00:00",7,10.940000000000001,8.0599999999999987,30.2,6.8000000000000007,3.019999999999996,12.920000000000002,-20.200000000000003,33.619999999999997,5.3599999999999994,12.920000000000002,34.520000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"08:00:00",8,6.98,8.0599999999999987,30.2,6.8000000000000007,-5.980000000000004,12.02,-22,33.979999999999997,4.6400000000000006,12.379999999999999,34.520000000000003,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"09:00:00",9,10.940000000000001,8.9599999999999973,32,6.8000000000000007,1.0399999999999991,12.02,-22,34.520000000000003,4.6400000000000006,13.279999999999998,35.6,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"10:00:00",10,14,12.02,33.799999999999997,8.5999999999999979,10.940000000000001,14,-22,35.06,6.4400000000000013,14.36,36.14,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"11:00:00",11,23,12.02,33.799999999999997,10.399999999999999,15.98,17.059999999999999,-22,35.6,9.5,15.440000000000001,37.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"12:00:00",12,23,17.059999999999999,35.24,12.2,23,19.04,-19.300000000000004,36.14,11.3,17.96,35.6,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"13:00:00",13,24.08,17.96,39.74,14,24.98,19.939999999999998,-16.600000000000001,41.54,13.64,19.399999999999999,38.119999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"14:00:00",14,23,17.96,39.200000000000003,15.8,28.04,21.92,-16.600000000000001,45.86,16.7,19.939999999999998,42.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"15:00:00",15,23,19.939999999999998,39.74,17.600000000000001,26.96,21.92,-14.800000000000004,43.879999999999995,18.14,21.02,42.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"16:00:00",16,23,19.939999999999998,38.840000000000003,19.399999999999999,26.96,21.92,-13,42.980000000000004,19.04,21.02,42.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"17:00:00",17,23,19.939999999999998,39.200000000000003,17.600000000000001,26.96,21.02,-13,39.92,17.600000000000001,19.399999999999999,39.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"18:00:00",18,23,15.98,34.520000000000003,17.600000000000001,26.060000000000002,19.939999999999998,-14.800000000000004,37.94,15.620000000000001,18.68,37.94,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"19:00:00",19,23,15.079999999999998,32.9,12.2,24.98,19.04,-13,36.86,9.68,14.18,37.04,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"20:00:00",20,23,15.079999999999998,30.2,10.399999999999999,21.02,17.96,-12.100000000000001,35.42,5.8999999999999986,15.079999999999998,35.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"21:00:00",21,23,12.02,30.2,10.399999999999999,21.02,17.059999999999999,-11.200000000000003,34.340000000000003,3.1999999999999993,15.079999999999998,34.159999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"22:00:00",22,23,10.940000000000001,26.6,12.2,23,17.059999999999999,-10.300000000000004,32.54,1.9400000000000013,15.079999999999998,32.18,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,"23:00:00",23,23,10.940000000000001,28.4,12.2,23,15.98,-9.3999999999999986,30.02,1.0399999999999991,15.259999999999998,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-18",1,18,2018,"2018-01-18",4,0,1,24,21.2,15.079999999999998,28.4,12.2,23,19.04,-7.6000000000000014,29.12,2.84,17.420000000000002,28.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,2018,"2018-01-19",5,0,"01:00:00",1,19.939999999999998,17.059999999999999,26.6,17.600000000000001,24.08,19.04,-5.8000000000000043,25.16,5.7199999999999989,19.939999999999998,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,2018,"2018-01-19",5,0,"02:00:00",2,19.04,17.059999999999999,24.8,17.600000000000001,24.98,21.02,-2.2000000000000028,24.08,7.34,21.740000000000002,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,2018,"2018-01-19",5,0,"03:00:00",3,19.399999999999999,19.04,21.2,17.600000000000001,24.08,21.92,1.3999999999999986,22.1,8.9599999999999973,22.82,24.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,2018,"2018-01-19",5,0,"04:00:00",4,19.939999999999998,19.939999999999998,19.399999999999999,17.600000000000001,24.8,24.08,3.1999999999999993,22.1,9.86,24.439999999999998,24.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,2018,"2018-01-19",5,0,"05:00:00",5,19.939999999999998,19.939999999999998,17.600000000000001,19.399999999999999,24.08,24.98,5,24.08,10.399999999999999,25.34,24.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,2018,"2018-01-19",5,0,"06:00:00",6,21.02,21.92,15.8,19.399999999999999,23,26.060000000000002,8.5999999999999979,21.02,10.579999999999998,26.060000000000002,24.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,2018,"2018-01-19",5,0,"07:00:00",7,19.04,21.92,15.8,17.600000000000001,21.92,26.96,6.8000000000000007,24.08,11.3,27.5,21.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,2018,"2018-01-19",5,0,"08:00:00",8,19.939999999999998,21.92,14,17.600000000000001,19.939999999999998,28.04,6.8000000000000007,24.08,12.2,30.02,21.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,2018,"2018-01-19",5,0,"09:00:00",9,21.02,26.060000000000002,14,17.600000000000001,21.92,32,8.5999999999999979,25.16,13.099999999999998,31.82,23,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,2018,"2018-01-19",5,0,"10:00:00",10,21.92,30.02,19.399999999999999,19.399999999999999,24.98,35.06,10.399999999999999,29.12,14.899999999999999,33.979999999999997,28.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,2018,"2018-01-19",5,0,"11:00:00",11,23,30.02,24.8,21.2,26.060000000000002,34.159999999999997,10.399999999999999,31.1,19.04,34.159999999999997,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,2018,"2018-01-19",5,0,"12:00:00",12,26.060000000000002,33.44,28.4,24.8,26.96,35.96,12.2,32,21.92,35.6,32,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,2018,"2018-01-19",5,0,"13:00:00",13,26.060000000000002,36.86,30.2,34.340000000000003,28.04,39.56,12.2,32.9,32.54,38.480000000000004,32,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,2018,"2018-01-19",5,0,"14:00:00",14,26.060000000000002,39.019999999999996,32,36.14,28.04,42.980000000000004,12.2,33.979999999999997,34.700000000000003,39.56,32,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,2018,"2018-01-19",5,0,"15:00:00",15,26.060000000000002,41,33.799999999999997,37.58,30.2,42.980000000000004,12.2,32.54,35.6,42.8,32,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,2018,"2018-01-19",5,0,"16:00:00",16,26.060000000000002,41,33.799999999999997,38.119999999999997,30.02,42.980000000000004,14,32.9,36.32,42.26,30.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,{"$f":"$AO$4","v":2018},"2018-01-19",5,{"$f":"COUNTIF($AM$34:$AM$43,E454)","v":0},"17:00:00",17,26.060000000000002,41,32,38.840000000000003,28.4,42.980000000000004,14,32.9,37.22,41.18,30.02,null,{"$f":"SUMPRODUCT($J$2:$T$2,J454:T454)","v":0},null,null,{"$f":"OR(B454<=$AO$14,B454>=$AN$14)*(F454<6)*(I454>$AN$15)*(I454<=$AO$15)*(G454<>1)","v":1},{"$f":"OR(B454<=$AO$14,B454>=$AN$14)*(Y454=0)","v":0},{"$f":"AND(B454>=$AN$24,B454<=$AO$24)*(F454<6)*(I454>$AN$25)*(I454<=$AO$25)*(G454<>1)","v":0},{"$f":"AND(B454>=$AN$24,B454<=$AO$24)*(AA454=0)","v":0},{"$f":"OR(B454<=$AO$19,B454>=$AN$19)*(F454<6)*(I454>$AN$20)*(I454<=$AO$20)","v":0},{"$f":"AND(B454>=$AN$29,B454<=$AO$29)*(F454<6)*(I454>$AN$30)*(I454<=$AO$30)","v":0},{"$f":"IF(OR(E454=$AM$34,E454=$AM$35,E454=$AM$36,E454=$AM$37,E454=$AM$38,E454=$AM$39,E454=$AM$40,E454=$AM$41,E454=$AM$42,E454=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E454>=$AM$47,E454<=$AN$47),AND(E454>=$AM$48,E454<=$AN$48),AND(E454>=$AM$49,E454<=$AN$49),AND(E454>=$AM$50,E454<=$AN$50),AND(E454>=$AM$51,E454<=$AN$51)),0,1)*AE454","v":1},{"$f":"(B454>=5)*(B454<=10)","v":0},{"$f":"1*OR(B454<=4,B454>=11)","v":1},{"$f":"LOOKUP(B454,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE454:AI454)*((F454<6)*(I454>$AO$7)*(I454<=$AP$7)+(F454=6)*(I454>$AO$8)*(I454<=$AP$8)+(F454>=7)*(I454>$AO$9)*(I454<=$AP$9))","v":0}]
["1976-01-19",1,19,2018,{"$f":"DATE(D455,B455,C455)","v":"2018-01-19"},{"$f":"WEEKDAY(E455,2)","v":5},0,"18:00:00",18,24.98,38.480000000000004,30.2,36.5,28.94,41,14.899999999999999,32,35.06,41,30.02,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,2018,"2018-01-19",5,0,"19:00:00",{"$f":"H456*24","v":19},24.08,37.04,30.2,35.6,28.04,39.92,15.8,32,34.340000000000003,40.28,30.02,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,2018,"2018-01-19",5,0,"20:00:00",20,24.98,37.04,28.4,34.880000000000003,28.04,37.94,15.8,30.02,33.619999999999997,39.380000000000003,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,2018,"2018-01-19",5,0,"21:00:00",21,24.08,35.96,28.4,34.159999999999997,28.04,37.94,15.8,30.02,32.9,38.840000000000003,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,2018,"2018-01-19",5,0,"22:00:00",22,24.98,35.24,28.4,33.26,24.08,36.86,15.8,29.12,32.36,37.22,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,2018,"2018-01-19",5,0,"23:00:00",23,24.08,35.6,26.6,33.44,26.96,37.04,19.399999999999999,29.12,32.72,37.04,28.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-19",1,19,2018,"2018-01-19",5,0,1,24,24.08,35.06,28.4,33.26,28.04,37.04,21.2,29.12,32.72,36.68,28.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"01:00:00",1,21.92,36.14,26.6,33.799999999999997,26.96,37.04,17.600000000000001,29.12,33.08,37.04,28.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"02:00:00",2,19.04,36.68,26.6,34.159999999999997,26.96,37.04,17.600000000000001,28.04,33.44,39.200000000000003,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"03:00:00",3,21.92,37.04,24.8,34.520000000000003,26.060000000000002,39.019999999999996,19.399999999999999,28.04,33.08,37.76,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"04:00:00",4,23,36.68,24.8,33.979999999999997,24.98,37.94,18.5,27.14,32.36,38.299999999999997,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"05:00:00",5,19.939999999999998,36.5,23,33.799999999999997,28.94,37.04,17.600000000000001,26.060000000000002,32.18,37.94,24.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"06:00:00",6,23,36.5,21.2,33.799999999999997,28.94,37.04,19.399999999999999,24.08,32,38.299999999999997,24.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"07:00:00",7,23,36.5,21.2,33.26,28.94,37.04,19.399999999999999,23,15.98,37.4,21.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"08:00:00",8,17.96,36.5,19.399999999999999,33.44,26.060000000000002,37.94,19.399999999999999,22.1,15.079999999999998,38.659999999999997,21.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"09:00:00",9,33.979999999999997,37.94,17.600000000000001,33.979999999999997,32.18,38.840000000000003,18.5,22.1,32,38.840000000000003,17.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"10:00:00",10,37.04,40.82,17.600000000000001,37.4,33.979999999999997,42.26,17.600000000000001,21.02,35.42,41.18,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"11:00:00",11,37.94,44.06,19.399999999999999,40.64,34.880000000000003,48.019999999999996,17.600000000000001,22.1,39.019999999999996,43.34,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"12:00:00",12,33.26,44.96,19.399999999999999,44.6,36.86,48.019999999999996,35.06,24.08,40.1,45.5,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"13:00:00",13,35.96,47.3,21.2,43.52,39.92,49.82,35.96,22.1,39.200000000000003,48.019999999999996,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"14:00:00",14,36.5,42.08,19.399999999999999,39.200000000000003,41.18,46.76,34.159999999999997,21.02,37.22,44.42,17.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"15:00:00",15,36.86,42.08,19.399999999999999,37.94,42.08,44.96,32.72,21.02,35.96,44.6,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"16:00:00",16,37.4,39.019999999999996,17.600000000000001,37.22,42.44,42.08,6.8000000000000007,20.12,35.06,43.7,17.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"17:00:00",17,39.019999999999996,39.019999999999996,17.600000000000001,35.06,42.980000000000004,40.82,5,19.04,32.54,40.1,15.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"18:00:00",18,35.96,32.36,15.8,32,40.28,35.06,3.1999999999999993,17.059999999999999,32,36.68,15.079999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"19:00:00",19,35.6,30.92,15.8,30.2,39.380000000000003,33.619999999999997,1.3999999999999986,16.159999999999997,30.92,35.24,15.079999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"20:00:00",20,36.5,30.92,14,28.4,39.019999999999996,32.54,-2.2000000000000028,15.079999999999998,29.3,34.159999999999997,12.920000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"21:00:00",21,35.96,28.94,14,28.4,37.58,30.02,-4,15.079999999999998,28.04,32.54,12.920000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"22:00:00",22,35.24,26.060000000000002,15.8,26.6,36.14,28.4,-5.8000000000000043,15.079999999999998,25.52,29.84,14,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,"23:00:00",23,35.78,26.060000000000002,14,24.8,35.24,26.6,-9.3999999999999986,13.099999999999998,23.9,28.04,12.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-20",1,20,2018,"2018-01-20",6,0,1,24,35.96,23,14,23,34.700000000000003,26.6,-11.200000000000003,14,22.1,26.6,14,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"01:00:00",1,32.36,21.92,12.2,21.2,33.799999999999997,24.8,-13,13.099999999999998,20.84,24.98,14,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"02:00:00",2,33.44,21.92,12.2,19.399999999999999,35.06,24.8,-13,13.099999999999998,18.86,23.72,14,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"03:00:00",3,33.44,19.04,12.2,17.600000000000001,35.06,23,-13.899999999999999,12.02,17.420000000000002,22.82,12.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"04:00:00",4,35.6,17.96,12.2,17.600000000000001,35.06,21.2,-14.800000000000004,12.02,16.159999999999997,21.560000000000002,12.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"05:00:00",5,35.96,17.96,12.2,15.8,35.96,19.399999999999999,-14.800000000000004,11.120000000000001,14.719999999999999,20.12,10.940000000000001,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"06:00:00",6,35.06,15.98,12.2,15.8,33.979999999999997,19.399999999999999,-16.600000000000001,12.02,13.64,19.759999999999998,8.9599999999999973,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"07:00:00",7,33.979999999999997,15.079999999999998,10.399999999999999,15.8,34.520000000000003,19.399999999999999,-16.600000000000001,11.120000000000001,10.039999999999999,18.86,8.9599999999999973,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"08:00:00",8,33.979999999999997,15.079999999999998,10.399999999999999,14,35.24,19.399999999999999,-16.600000000000001,12.02,5,20.12,8.9599999999999973,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"09:00:00",9,33.979999999999997,19.939999999999998,10.399999999999999,15.8,35.06,21.2,-15.700000000000003,14,5.8999999999999986,22.46,12.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"10:00:00",10,35.06,21.92,12.2,17.600000000000001,35.96,21.2,-14.800000000000004,17.059999999999999,14,24.8,14,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"11:00:00",11,35.06,21.92,15.8,19.399999999999999,36.68,23,-13,18.14,15.98,24.8,15.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"12:00:00",12,35.06,24.08,17.600000000000001,21.2,37.4,23,-12.100000000000001,20.12,19.579999999999998,25.88,17.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"13:00:00",13,37.04,24.98,17.600000000000001,23,38.659999999999997,24.8,-11.200000000000003,21.02,21.2,25.88,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"14:00:00",14,35.96,24.98,17.600000000000001,23,38.840000000000003,24.8,-9.3999999999999986,22.1,22.64,25.88,19.939999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"15:00:00",15,35.96,24.98,19.399999999999999,24.8,38.840000000000003,24.8,-9.3999999999999986,22.1,22.46,25.7,19.939999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"16:00:00",16,35.96,24.08,19.399999999999999,23,37.94,24.8,-9.3999999999999986,21.02,23,25.52,19.939999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"17:00:00",17,33.979999999999997,24.08,19.399999999999999,23,38.299999999999997,24.8,-9.3999999999999986,20.12,23.18,24.98,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"18:00:00",18,33.979999999999997,21.92,17.600000000000001,23,35.6,24.8,-7.6000000000000014,19.04,22.46,24.98,17.059999999999999,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"19:00:00",19,32,21.02,12.2,21.2,34.880000000000003,23,-7.6000000000000014,15.079999999999998,21.92,24.8,14,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"20:00:00",20,32,21.02,10.399999999999999,19.399999999999999,34.340000000000003,21.2,-7.6000000000000014,12.02,21.02,22.64,14,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"21:00:00",21,30.92,19.939999999999998,8.5999999999999979,19.399999999999999,33.619999999999997,21.2,-7.6000000000000014,10.039999999999999,19.939999999999998,22.1,14,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"22:00:00",22,32,19.04,6.8000000000000007,19.399999999999999,30.02,21.2,-5.8000000000000043,8.0599999999999987,19.399999999999999,21.2,12.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,"23:00:00",23,32,19.04,3.1999999999999993,17.600000000000001,30.92,19.399999999999999,-5.8000000000000043,5,18.14,21.560000000000002,12.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-21",1,21,2018,"2018-01-21",7,0,1,24,32,19.939999999999998,3.1999999999999993,17.600000000000001,28.94,19.399999999999999,-5.8000000000000043,5,17.600000000000001,22.1,10.039999999999999,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,2018,"2018-01-22",1,0,"01:00:00",1,30.92,19.399999999999999,1.3999999999999986,19.399999999999999,28.94,19.399999999999999,-5.8000000000000043,3.1999999999999993,18.14,21.92,8.9599999999999973,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,2018,"2018-01-22",1,0,"02:00:00",2,30.92,19.04,1.3999999999999986,19.399999999999999,30.92,19.399999999999999,-5.8000000000000043,6.8000000000000007,17.420000000000002,21.2,6.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,2018,"2018-01-22",1,0,"03:00:00",3,30.92,19.399999999999999,5,17.600000000000001,30.92,17.600000000000001,-5.8000000000000043,8.5999999999999979,17.600000000000001,21.560000000000002,6.0799999999999983,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,2018,"2018-01-22",1,0,"04:00:00",4,30.92,19.399999999999999,6.8000000000000007,15.8,30.92,17.600000000000001,-5.8000000000000043,10.399999999999999,17.059999999999999,21.2,6.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,2018,"2018-01-22",1,0,"05:00:00",5,30.92,17.96,5,15.8,30.92,19.399999999999999,-7.6000000000000014,12.2,16.88,20.12,8.0599999999999987,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,2018,"2018-01-22",1,0,"06:00:00",6,30.92,17.600000000000001,3.1999999999999993,12.2,30.92,19.399999999999999,-7.6000000000000014,6.8000000000000007,15.620000000000001,19.399999999999999,8.0599999999999987,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,2018,"2018-01-22",1,0,"07:00:00",7,30.02,17.600000000000001,1.3999999999999986,12.2,32,17.600000000000001,-7.6000000000000014,12.2,15.8,15.8,8.0599999999999987,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,2018,"2018-01-22",1,0,"08:00:00",8,30.02,17.059999999999999,1.3999999999999986,12.2,32,19.399999999999999,-9.3999999999999986,10.399999999999999,14.18,16.159999999999997,10.039999999999999,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,{"$f":"$AO$4","v":2018},"2018-01-22",1,{"$f":"COUNTIF($AM$34:$AM$43,E518)","v":0},"09:00:00",9,30.92,15.8,3.1999999999999993,12.2,33.08,19.399999999999999,-9.3999999999999986,15.8,13.82,15.8,12.02,null,{"$f":"SUMPRODUCT($J$2:$T$2,J518:T518)","v":0},null,null,{"$f":"OR(B518<=$AO$14,B518>=$AN$14)*(F518<6)*(I518>$AN$15)*(I518<=$AO$15)*(G518<>1)","v":1},{"$f":"OR(B518<=$AO$14,B518>=$AN$14)*(Y518=0)","v":0},{"$f":"AND(B518>=$AN$24,B518<=$AO$24)*(F518<6)*(I518>$AN$25)*(I518<=$AO$25)*(G518<>1)","v":0},{"$f":"AND(B518>=$AN$24,B518<=$AO$24)*(AA518=0)","v":0},{"$f":"OR(B518<=$AO$19,B518>=$AN$19)*(F518<6)*(I518>$AN$20)*(I518<=$AO$20)","v":0},{"$f":"AND(B518>=$AN$29,B518<=$AO$29)*(F518<6)*(I518>$AN$30)*(I518<=$AO$30)","v":0},{"$f":"IF(OR(E518=$AM$34,E518=$AM$35,E518=$AM$36,E518=$AM$37,E518=$AM$38,E518=$AM$39,E518=$AM$40,E518=$AM$41,E518=$AM$42,E518=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E518>=$AM$47,E518<=$AN$47),AND(E518>=$AM$48,E518<=$AN$48),AND(E518>=$AM$49,E518<=$AN$49),AND(E518>=$AM$50,E518<=$AN$50),AND(E518>=$AM$51,E518<=$AN$51)),0,1)*AE518","v":1},{"$f":"(B518>=5)*(B518<=10)","v":0},{"$f":"1*OR(B518<=4,B518>=11)","v":1},{"$f":"LOOKUP(B518,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE518:AI518)*((F518<6)*(I518>$AO$7)*(I518<=$AP$7)+(F518=6)*(I518>$AO$8)*(I518<=$AP$8)+(F518>=7)*(I518>$AO$9)*(I518<=$AP$9))","v":0}]
["1976-01-22",1,22,2018,{"$f":"DATE(D519,B519,C519)","v":"2018-01-22"},{"$f":"WEEKDAY(E519,2)","v":1},0,"10:00:00",10,32,19.04,8.5999999999999979,15.8,33.799999999999997,21.2,-7.6000000000000014,21.2,14.899999999999999,20.84,17.059999999999999,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,2018,"2018-01-22",1,0,"11:00:00",{"$f":"H520*24","v":11},32,19.04,21.2,17.600000000000001,33.979999999999997,21.2,-9.3999999999999986,27.14,16.88,24.98,21.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,2018,"2018-01-22",1,0,"12:00:00",12,30.92,21.02,28.4,19.399999999999999,35.06,21.2,-10.300000000000004,31.1,19.04,23.54,28.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,2018,"2018-01-22",1,0,"13:00:00",13,30.92,19.04,30.2,19.399999999999999,35.06,21.2,-11.200000000000003,33.979999999999997,18.5,26.060000000000002,32,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,2018,"2018-01-22",1,0,"14:00:00",14,30.92,19.04,32,19.399999999999999,35.06,21.92,-11.200000000000003,36.68,18.14,25.34,33.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,2018,"2018-01-22",1,0,"15:00:00",15,30.92,21.02,33.799999999999997,19.399999999999999,33.979999999999997,23,-13,36.5,17.78,24.98,35.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,2018,"2018-01-22",1,0,"16:00:00",16,30.02,17.96,30.2,17.600000000000001,33.08,19.939999999999998,-14.800000000000004,37.4,17.059999999999999,21.560000000000002,35.6,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,2018,"2018-01-22",1,0,"17:00:00",17,30.02,17.96,30.2,15.8,32,19.04,-16.600000000000001,34.880000000000003,15.620000000000001,19.22,33.799999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,2018,"2018-01-22",1,0,"18:00:00",18,28.94,15.079999999999998,30.2,15.8,30.92,17.059999999999999,-18.399999999999999,33.08,12.920000000000002,17.420000000000002,32.36,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,2018,"2018-01-22",1,0,"19:00:00",19,28.04,15.8,30.2,12.2,30.92,15.079999999999998,-20.200000000000003,33.619999999999997,11.659999999999997,17.059999999999999,30.92,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,2018,"2018-01-22",1,0,"20:00:00",20,26.96,14,30.2,10.399999999999999,30.02,15.079999999999998,-20.200000000000003,33.26,8.9599999999999973,15.259999999999998,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,2018,"2018-01-22",1,0,"21:00:00",21,26.060000000000002,10.940000000000001,30.2,10.399999999999999,30.02,14,-23.800000000000004,32.9,8.5999999999999979,13.64,28.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,2018,"2018-01-22",1,0,"22:00:00",22,24.98,10.039999999999999,28.4,8.5999999999999979,30.2,12.920000000000002,-25.6,33.26,7.6999999999999993,12.379999999999999,28.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,2018,"2018-01-22",1,0,"23:00:00",23,26.060000000000002,10.039999999999999,24.8,6.8000000000000007,28.94,12.02,-25.6,32,5.8999999999999986,11.84,26.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-22",1,22,2018,"2018-01-22",1,0,1,24,26.96,3.019999999999996,23,5,28.4,10.940000000000001,-25.6,32.36,5,10.039999999999999,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"01:00:00",1,28.04,1.9400000000000013,23,5,28.4,10.039999999999999,-27.4,31.1,3.9200000000000017,7.52,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"02:00:00",2,28.94,1.9400000000000013,24.8,3.1999999999999993,28.94,8.9599999999999973,-29.200000000000003,32,0.85999999999999943,6.98,26.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"03:00:00",3,30.2,6.98,28.4,1.3999999999999986,28.94,8.9599999999999973,-30.1,32,2.3000000000000007,6.8000000000000007,26.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"04:00:00",4,30.92,6.98,28.4,1.3999999999999986,30.02,8.9599999999999973,-31,30.02,0.5,7.34,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"05:00:00",5,32,6.98,28.4,-0.39999999999999858,30.02,8.0599999999999987,-32.799999999999997,29.12,-2.740000000000002,7.1599999999999966,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"06:00:00",6,30.92,1.0399999999999991,26.6,-0.39999999999999858,30.92,6.98,-32.799999999999997,28.04,-2.9200000000000017,4.4599999999999973,26.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"07:00:00",7,30.92,-0.94000000000000483,26.6,-2.2000000000000028,30.02,6.98,-32.799999999999997,24.08,-4.1800000000000068,2.84,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"08:00:00",8,28.94,-0.94000000000000483,19.399999999999999,-2.2000000000000028,30.92,3.019999999999996,-34.600000000000009,21.02,-5.259999999999998,2.84,24.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"09:00:00",9,28.4,1.0399999999999991,21.2,-2.2000000000000028,30.92,5,-34.600000000000009,29.12,-4.8999999999999986,5,26.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"10:00:00",10,30.02,3.019999999999996,24.8,-2.2000000000000028,32,8.0599999999999987,-32.799999999999997,30.02,-3.1000000000000014,6.4400000000000013,28.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"11:00:00",11,30.02,3.019999999999996,26.6,-0.39999999999999858,33.08,8.9599999999999973,-31,31.1,-1.6599999999999966,7.34,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"12:00:00",12,33.08,6.98,28.4,1.3999999999999986,33.08,10.039999999999999,-29.200000000000003,32,-0.39999999999999858,8.9599999999999973,30.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"13:00:00",13,33.979999999999997,8.0599999999999987,28.4,1.3999999999999986,33.979999999999997,10.940000000000001,-29.200000000000003,32.9,0.5,10.399999999999999,32,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"14:00:00",14,33.979999999999997,8.0599999999999987,30.2,3.1999999999999993,32.9,10.940000000000001,-29.200000000000003,32,1.759999999999998,10.579999999999998,30.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"15:00:00",15,35.06,8.9599999999999973,30.2,5,33.619999999999997,12.02,-27.4,32.36,2.84,10.399999999999999,32,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"16:00:00",16,35.06,8.0599999999999987,30.2,5,35.06,10.940000000000001,-27.4,32.9,3.1999999999999993,9.5,30.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"17:00:00",17,33.979999999999997,8.0599999999999987,30.2,3.1999999999999993,33.799999999999997,8.9599999999999973,-27.4,32.54,2.3000000000000007,7.52,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"18:00:00",18,33.979999999999997,3.9200000000000017,28.4,1.3999999999999986,33.979999999999997,8.0599999999999987,-29.200000000000003,30.02,0.5,6.259999999999998,28.04,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"19:00:00",19,33.979999999999997,3.019999999999996,26.6,-0.39999999999999858,33.979999999999997,6.98,-29.200000000000003,30.02,-0.75999999999999801,5.5399999999999991,28.04,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"20:00:00",20,33.979999999999997,3.019999999999996,26.6,-0.39999999999999858,33.979999999999997,6.0799999999999983,-31,29.12,-1.6599999999999966,4.0999999999999979,26.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"21:00:00",21,33.979999999999997,-3.9999999999999147E-2,26.6,-0.39999999999999858,32,5,-27.4,28.04,-1.1199999999999974,4.0999999999999979,26.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"22:00:00",22,33.979999999999997,-0.94000000000000483,24.8,-0.39999999999999858,34.700000000000003,3.9200000000000017,-26.5,27.14,-2.740000000000002,2.3000000000000007,24.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,"23:00:00",23,35.96,-0.94000000000000483,24.8,-0.39999999999999858,33.979999999999997,3.019999999999996,-25.6,27.14,-3.8200000000000003,1.9400000000000013,24.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-23",1,23,2018,"2018-01-23",2,0,1,24,37.04,-4,24.8,-2.2000000000000028,33.44,1.9400000000000013,-25.6,25.16,-3.6400000000000006,1.3999999999999986,24.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"01:00:00",1,37.94,-2.9200000000000017,23,-2.2000000000000028,33.44,1.9400000000000013,-29.200000000000003,24.08,-4.7199999999999989,1.3999999999999986,23,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"02:00:00",2,37.94,-2.9200000000000017,21.2,-2.2000000000000028,33.979999999999997,-3.9999999999999147E-2,-27.4,23,-4.8999999999999986,0.5,21.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"03:00:00",3,35.96,-2.9200000000000017,17.600000000000001,-4,34.700000000000003,-3.9999999999999147E-2,-26.5,22.1,-5.8000000000000043,-0.39999999999999858,19.939999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"04:00:00",4,35.96,-4,17.600000000000001,-4,32.72,-0.94000000000000483,-25.6,22.1,-6.519999999999996,-0.5800000000000054,17.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"05:00:00",5,35.06,-4,17.600000000000001,-5.8000000000000043,32.72,-2.019999999999996,-25.6,22.1,-6.7000000000000028,-0.94000000000000483,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"06:00:00",6,33.979999999999997,-4,12.2,-5.8000000000000043,35.96,-2.019999999999996,-23.800000000000004,19.04,-6.1599999999999966,-1.3000000000000043,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"07:00:00",7,33.08,-4,12.2,-5.8000000000000043,33.979999999999997,-2.019999999999996,-23.800000000000004,16.159999999999997,-6.1599999999999966,-2.019999999999996,17.059999999999999,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"08:00:00",8,28.04,-4,10.399999999999999,-5.8000000000000043,32,-0.94000000000000483,-23.800000000000004,14,-5.8000000000000043,-0.39999999999999858,17.059999999999999,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"09:00:00",9,26.060000000000002,1.0399999999999991,10.399999999999999,-2.2000000000000028,32,1.9400000000000013,-22,19.04,-4.1800000000000068,2.3000000000000007,21.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"10:00:00",10,21.92,3.019999999999996,15.8,1.3999999999999986,30.02,6.0799999999999983,-20.200000000000003,25.16,-1.6599999999999966,6.259999999999998,23,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"11:00:00",11,19.939999999999998,3.019999999999996,19.399999999999999,3.1999999999999993,28.94,8.9599999999999973,-20.200000000000003,26.060000000000002,-0.5800000000000054,9.86,24.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"12:00:00",12,19.04,8.0599999999999987,23,5,28.94,10.940000000000001,-20.200000000000003,28.04,2.4800000000000004,12.379999999999999,26.060000000000002,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"13:00:00",13,19.04,10.039999999999999,24.8,6.8000000000000007,28.94,12.920000000000002,-20.200000000000003,28.04,4.0999999999999979,14.36,26.060000000000002,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"14:00:00",14,19.939999999999998,10.039999999999999,24.8,8.5999999999999979,28.94,15.079999999999998,-20.200000000000003,29.12,7.52,14.719999999999999,26.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"15:00:00",15,19.04,12.920000000000002,24.8,10.399999999999999,28.04,17.059999999999999,-20.200000000000003,28.04,7.6999999999999993,14.36,26.060000000000002,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"16:00:00",16,15.98,12.920000000000002,24.8,10.399999999999999,26.96,15.98,-21.1,28.04,10.399999999999999,14.18,24.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"17:00:00",17,15.079999999999998,12.920000000000002,24.8,10.399999999999999,24.98,14,-22,27.14,10.399999999999999,13.279999999999998,23,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"18:00:00",18,14,10.940000000000001,21.2,10.399999999999999,24.08,14,-23.800000000000004,25.16,9.5,12.740000000000002,21.92,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"19:00:00",19,12.920000000000002,10.039999999999999,21.2,8.5999999999999979,21.92,12.920000000000002,-25.6,25.16,7.6999999999999993,12.02,19.939999999999998,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"20:00:00",20,12.920000000000002,10.039999999999999,19.399999999999999,6.8000000000000007,21.02,12.920000000000002,-27.4,23,5.3599999999999994,11.3,19.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"21:00:00",21,12.920000000000002,8.0599999999999987,17.600000000000001,5,19.939999999999998,12.02,-27.4,22.1,4.82,9.68,15.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"22:00:00",22,12.920000000000002,6.98,12.2,5,19.04,10.940000000000001,-27.4,19.04,4.82,8.4200000000000017,15.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,"23:00:00",23,12.920000000000002,6.98,10.399999999999999,3.1999999999999993,19.04,10.039999999999999,-27.4,14,3.5599999999999987,7.879999999999999,14,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-24",1,24,2018,"2018-01-24",3,0,1,24,12.02,6.0799999999999983,8.5999999999999979,3.1999999999999993,17.96,8.9599999999999973,-16.600000000000001,11.120000000000001,3.1999999999999993,7.34,14,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,{"$f":"$AO$4","v":2018},"2018-01-25",4,{"$f":"COUNTIF($AM$34:$AM$43,E582)","v":0},"01:00:00",1,10.940000000000001,5,6.8000000000000007,3.1999999999999993,17.96,8.0599999999999987,-14.800000000000004,16.159999999999997,2.84,6.620000000000001,12.920000000000002,null,{"$f":"SUMPRODUCT($J$2:$T$2,J582:T582)","v":0},null,null,{"$f":"OR(B582<=$AO$14,B582>=$AN$14)*(F582<6)*(I582>$AN$15)*(I582<=$AO$15)*(G582<>1)","v":0},{"$f":"OR(B582<=$AO$14,B582>=$AN$14)*(Y582=0)","v":1},{"$f":"AND(B582>=$AN$24,B582<=$AO$24)*(F582<6)*(I582>$AN$25)*(I582<=$AO$25)*(G582<>1)","v":0},{"$f":"AND(B582>=$AN$24,B582<=$AO$24)*(AA582=0)","v":0},{"$f":"OR(B582<=$AO$19,B582>=$AN$19)*(F582<6)*(I582>$AN$20)*(I582<=$AO$20)","v":0},{"$f":"AND(B582>=$AN$29,B582<=$AO$29)*(F582<6)*(I582>$AN$30)*(I582<=$AO$30)","v":0},{"$f":"IF(OR(E582=$AM$34,E582=$AM$35,E582=$AM$36,E582=$AM$37,E582=$AM$38,E582=$AM$39,E582=$AM$40,E582=$AM$41,E582=$AM$42,E582=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E582>=$AM$47,E582<=$AN$47),AND(E582>=$AM$48,E582<=$AN$48),AND(E582>=$AM$49,E582<=$AN$49),AND(E582>=$AM$50,E582<=$AN$50),AND(E582>=$AM$51,E582<=$AN$51)),0,1)*AE582","v":1},{"$f":"(B582>=5)*(B582<=10)","v":0},{"$f":"1*OR(B582<=4,B582>=11)","v":1},{"$f":"LOOKUP(B582,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE582:AI582)*((F582<6)*(I582>$AO$7)*(I582<=$AP$7)+(F582=6)*(I582>$AO$8)*(I582<=$AP$8)+(F582>=7)*(I582>$AO$9)*(I582<=$AP$9))","v":0}]
["1976-01-25",1,25,2018,{"$f":"DATE(D583,B583,C583)","v":"2018-01-25"},{"$f":"WEEKDAY(E583,2)","v":4},0,"02:00:00",2,10.039999999999999,5,5,3.1999999999999993,17.059999999999999,8.0599999999999987,-16.600000000000001,15.079999999999998,2.6599999999999966,6.8000000000000007,12.920000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,2018,"2018-01-25",4,0,"03:00:00",{"$f":"H584*24","v":3},8.9599999999999973,3.9200000000000017,3.1999999999999993,3.1999999999999993,17.059999999999999,8.0599999999999987,-16.600000000000001,13.099999999999998,2.3000000000000007,6.620000000000001,12.920000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,2018,"2018-01-25",4,0,"04:00:00",4,8.9599999999999973,3.9200000000000017,1.3999999999999986,1.3999999999999986,15.98,6.98,-16.600000000000001,10.039999999999999,1.759999999999998,6.0799999999999983,10.940000000000001,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,2018,"2018-01-25",4,0,"05:00:00",5,8.0599999999999987,3.9200000000000017,1.3999999999999986,1.3999999999999986,15.98,6.0799999999999983,-11.200000000000003,8.0599999999999987,1.5800000000000018,6.0799999999999983,12.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,2018,"2018-01-25",4,0,"06:00:00",6,6.98,3.9200000000000017,-0.39999999999999858,1.3999999999999986,15.079999999999998,6.0799999999999983,-11.200000000000003,3.019999999999996,1.9400000000000013,5.8999999999999986,10.039999999999999,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,2018,"2018-01-25",4,0,"07:00:00",7,6.0799999999999983,3.019999999999996,-2.2000000000000028,1.3999999999999986,14,6.0799999999999983,-7.6000000000000014,10.039999999999999,2.1199999999999974,6.0799999999999983,10.039999999999999,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,2018,"2018-01-25",4,0,"08:00:00",8,5,3.019999999999996,-2.2000000000000028,1.3999999999999986,12.920000000000002,6.0799999999999983,-9.3999999999999986,7.1599999999999966,1.5800000000000018,7.879999999999999,10.039999999999999,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,2018,"2018-01-25",4,0,"09:00:00",9,6.0799999999999983,6.0799999999999983,-2.2000000000000028,3.1999999999999993,14,8.9599999999999973,-7.6000000000000014,16.159999999999997,2.1199999999999974,9.5,12.920000000000002,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,2018,"2018-01-25",4,0,"10:00:00",10,6.98,8.9599999999999973,3.1999999999999993,5,17.059999999999999,10.039999999999999,-5.8000000000000043,19.04,3.1999999999999993,12.02,15.079999999999998,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,2018,"2018-01-25",4,0,"11:00:00",11,8.0599999999999987,8.9599999999999973,10.399999999999999,8.5999999999999979,17.96,14,-5.8000000000000043,22.1,5,13.82,17.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,2018,"2018-01-25",4,0,"12:00:00",12,10.940000000000001,12.920000000000002,19.399999999999999,10.399999999999999,19.04,15.98,-5.8000000000000043,26.060000000000002,7.52,17.600000000000001,19.939999999999998,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,2018,"2018-01-25",4,0,"13:00:00",13,12.02,15.079999999999998,23,10.399999999999999,21.92,19.04,-2.2000000000000028,27.14,9.5,18.86,21.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,2018,"2018-01-25",4,0,"14:00:00",14,12.920000000000002,15.079999999999998,26.6,14,21.92,19.939999999999998,1.3999999999999986,28.04,13.099999999999998,20.12,24.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,2018,"2018-01-25",4,0,"15:00:00",15,14,17.96,24.8,17.600000000000001,21.92,19.939999999999998,1.3999999999999986,28.04,14.719999999999999,20.84,24.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,2018,"2018-01-25",4,0,"16:00:00",16,12.920000000000002,17.96,26.6,17.600000000000001,21.92,21.02,1.3999999999999986,27.14,15.440000000000001,19.22,24.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,2018,"2018-01-25",4,0,"17:00:00",17,10.039999999999999,17.96,26.6,15.8,21.02,19.939999999999998,3.1999999999999993,24.08,14.54,18.32,24.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,2018,"2018-01-25",4,0,"18:00:00",18,8.0599999999999987,15.98,24.8,15.8,19.939999999999998,19.04,1.3999999999999986,26.060000000000002,14,17.78,23,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,2018,"2018-01-25",4,0,"19:00:00",19,8.0599999999999987,15.98,24.8,15.8,19.04,19.04,1.3999999999999986,25.16,13.82,17.96,21.92,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,2018,"2018-01-25",4,0,"20:00:00",20,6.98,15.98,24.8,14,17.96,19.04,1.3999999999999986,24.08,13.82,17.600000000000001,21.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,2018,"2018-01-25",4,0,"21:00:00",21,6.98,15.98,21.2,14,17.059999999999999,17.96,1.3999999999999986,23,13.64,17.78,19.939999999999998,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,2018,"2018-01-25",4,0,"22:00:00",22,8.0599999999999987,15.98,23,14,14,17.96,-0.39999999999999858,20.12,13.64,17.78,17.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,2018,"2018-01-25",4,0,"23:00:00",23,8.0599999999999987,15.98,15.8,15.8,10.039999999999999,17.96,-2.2000000000000028,21.02,13.099999999999998,17.600000000000001,19.939999999999998,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-25",1,25,2018,"2018-01-25",4,0,1,24,8.0599999999999987,14,17.600000000000001,14,10.039999999999999,15.98,-2.2000000000000028,17.059999999999999,12.559999999999999,17.600000000000001,17.059999999999999,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"01:00:00",1,1.9400000000000013,12.2,17.600000000000001,14,8.9599999999999973,15.079999999999998,-2.2000000000000028,20.12,12.740000000000002,15.8,15.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"02:00:00",2,6.98,12.02,21.2,14,8.0599999999999987,14,-2.2000000000000028,20.12,12.02,14.36,15.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"03:00:00",3,1.9400000000000013,10.940000000000001,14,12.2,6.98,14,-5.8000000000000043,20.12,11.3,14.18,15.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"04:00:00",4,-2.019999999999996,10.039999999999999,19.399999999999999,12.2,6.98,12.920000000000002,-4,20.12,11.120000000000001,14,14,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"05:00:00",5,-0.94000000000000483,10.039999999999999,19.399999999999999,10.399999999999999,6.0799999999999983,10.940000000000001,-5.8000000000000043,17.059999999999999,10.039999999999999,11.84,15.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"06:00:00",6,-5.980000000000004,6.98,17.600000000000001,6.8000000000000007,6.98,10.940000000000001,-6.7000000000000028,11.120000000000001,9.14,10.039999999999999,17.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"07:00:00",7,-4,6.0799999999999983,12.2,6.8000000000000007,5,10.940000000000001,-7.6000000000000014,12.02,8.5999999999999979,10.399999999999999,12.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"08:00:00",8,-7.0600000000000023,6.0799999999999983,12.2,6.8000000000000007,5,10.940000000000001,-7.6000000000000014,14,7.6999999999999993,12.379999999999999,14,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"09:00:00",9,3.9200000000000017,10.940000000000001,12.2,10.399999999999999,10.039999999999999,12.920000000000002,-7.6000000000000014,18.14,8.0599999999999987,12.2,19.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"10:00:00",10,12.02,14,15.8,12.2,15.079999999999998,15.079999999999998,-9.3999999999999986,24.08,9.5,17.420000000000002,23,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"11:00:00",11,15.079999999999998,14,21.2,15.8,19.939999999999998,17.059999999999999,-9.3999999999999986,27.14,11.3,19.939999999999998,26.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"12:00:00",12,17.059999999999999,17.96,26.6,15.8,21.92,19.04,-10.300000000000004,30.02,13.099999999999998,22.28,26.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"13:00:00",13,19.939999999999998,19.04,26.6,17.600000000000001,24.98,19.939999999999998,-11.200000000000003,30.02,14,24.439999999999998,28.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"14:00:00",14,21.92,19.04,28.4,17.600000000000001,28.04,19.939999999999998,-13,30.02,15.8,24.439999999999998,28.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"15:00:00",15,23,19.04,28.4,17.600000000000001,28.94,21.02,-14.800000000000004,32,15.8,23.18,28.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"16:00:00",16,23,17.96,28.4,17.600000000000001,28.94,19.939999999999998,-16.600000000000001,31.1,16.159999999999997,21.02,26.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"17:00:00",17,17.96,17.96,28.4,15.8,26.060000000000002,19.04,-18.399999999999999,30.02,14.899999999999999,18.86,26.060000000000002,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"18:00:00",18,10.940000000000001,15.079999999999998,26.6,15.8,21.92,17.96,-18.399999999999999,26.060000000000002,13.82,17.78,24.08,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"19:00:00",19,6.98,12.920000000000002,23,12.2,19.04,15.98,-18.399999999999999,23,11.84,16.7,23,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"20:00:00",20,5,12.920000000000002,21.2,12.2,17.96,15.079999999999998,-18.399999999999999,22.1,10.940000000000001,15.259999999999998,21.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"21:00:00",21,3.019999999999996,12.02,19.399999999999999,10.399999999999999,17.059999999999999,14,-18.399999999999999,22.1,10.039999999999999,13.64,19.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"22:00:00",22,3.019999999999996,10.940000000000001,21.2,10.399999999999999,15.98,14,-16.600000000000001,22.1,9.68,12.559999999999999,15.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,"23:00:00",23,1.9400000000000013,10.940000000000001,19.399999999999999,10.399999999999999,15.079999999999998,14,-16.600000000000001,19.04,9.5,12.740000000000002,15.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-26",1,26,2018,"2018-01-26",5,0,1,24,1.0399999999999991,10.940000000000001,19.399999999999999,10.399999999999999,15.079999999999998,14,-16.600000000000001,21.02,10.579999999999998,12.920000000000002,17.059999999999999,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,2018,"2018-01-27",6,0,"01:00:00",1,1.0399999999999991,10.940000000000001,21.2,10.399999999999999,14,14,-16.600000000000001,20.12,12.02,12.2,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,2018,"2018-01-27",6,0,"02:00:00",2,-3.9999999999999147E-2,10.940000000000001,21.2,10.399999999999999,14,14,-16.600000000000001,21.2,11.3,12.740000000000002,21.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,2018,"2018-01-27",6,0,"03:00:00",3,1.0399999999999991,10.940000000000001,19.399999999999999,10.399999999999999,14,14,-14.800000000000004,20.12,11.3,12.740000000000002,21.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,2018,"2018-01-27",6,0,"04:00:00",4,1.9400000000000013,12.02,21.2,10.399999999999999,14,14,-13,22.1,10.579999999999998,12.740000000000002,21.2,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,2018,"2018-01-27",6,0,"05:00:00",5,1.0399999999999991,12.02,21.2,10.399999999999999,14,14,-14.800000000000004,21.2,9.5,12.920000000000002,21.2,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,2018,"2018-01-27",6,0,"06:00:00",6,-2.019999999999996,10.940000000000001,21.2,10.399999999999999,17.059999999999999,12.920000000000002,-13.899999999999999,21.2,9.86,12.559999999999999,21.2,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,2018,"2018-01-27",6,0,"07:00:00",7,-0.94000000000000483,10.039999999999999,21.2,10.399999999999999,15.079999999999998,12.920000000000002,-13,21.2,9.5,12.2,21.2,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,2018,"2018-01-27",6,0,"08:00:00",8,1.9400000000000013,10.039999999999999,21.2,10.399999999999999,19.04,14,-9.3999999999999986,21.2,8.5999999999999979,13.64,21.2,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,2018,"2018-01-27",6,0,"09:00:00",9,5,14,21.2,10.399999999999999,23,17.059999999999999,-7.6000000000000014,24.08,9.5,16.52,21.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,2018,"2018-01-27",6,0,"10:00:00",10,8.0599999999999987,17.059999999999999,23,12.2,28.94,17.96,-5.8000000000000043,24.8,10.940000000000001,20.12,21.2,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,2018,"2018-01-27",6,0,"11:00:00",11,15.079999999999998,17.059999999999999,24.8,14,33.979999999999997,21.02,-4,24.8,11.84,22.64,24.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,2018,"2018-01-27",6,0,"12:00:00",12,21.92,21.02,26.6,17.600000000000001,35.06,23,-4,24.8,14,24.98,24.8,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,2018,"2018-01-27",6,0,"13:00:00",13,28.94,24.08,26.6,19.399999999999999,39.019999999999996,24.98,-4,26.6,17.059999999999999,27.68,24.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,2018,"2018-01-27",6,0,"14:00:00",14,32.72,24.08,26.6,21.2,42.08,26.96,-4,26.6,19.579999999999998,28.22,24.8,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,2018,"2018-01-27",6,0,"15:00:00",15,33.979999999999997,26.060000000000002,28.4,21.2,42.980000000000004,28.04,-4,28.4,21.02,28.22,26.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,2018,"2018-01-27",6,0,"16:00:00",16,35.78,24.98,28.4,21.2,44.06,28.04,-0.39999999999999858,29.12,21.02,26.96,26.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,{"$f":"$AO$4","v":2018},"2018-01-27",6,{"$f":"COUNTIF($AM$34:$AM$43,E646)","v":0},"17:00:00",17,35.06,24.98,28.4,21.2,44.96,26.96,-4,28.04,19.939999999999998,24.8,24.98,null,{"$f":"SUMPRODUCT($J$2:$T$2,J646:T646)","v":0},null,null,{"$f":"OR(B646<=$AO$14,B646>=$AN$14)*(F646<6)*(I646>$AN$15)*(I646<=$AO$15)*(G646<>1)","v":0},{"$f":"OR(B646<=$AO$14,B646>=$AN$14)*(Y646=0)","v":1},{"$f":"AND(B646>=$AN$24,B646<=$AO$24)*(F646<6)*(I646>$AN$25)*(I646<=$AO$25)*(G646<>1)","v":0},{"$f":"AND(B646>=$AN$24,B646<=$AO$24)*(AA646=0)","v":0},{"$f":"OR(B646<=$AO$19,B646>=$AN$19)*(F646<6)*(I646>$AN$20)*(I646<=$AO$20)","v":0},{"$f":"AND(B646>=$AN$29,B646<=$AO$29)*(F646<6)*(I646>$AN$30)*(I646<=$AO$30)","v":0},{"$f":"IF(OR(E646=$AM$34,E646=$AM$35,E646=$AM$36,E646=$AM$37,E646=$AM$38,E646=$AM$39,E646=$AM$40,E646=$AM$41,E646=$AM$42,E646=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E646>=$AM$47,E646<=$AN$47),AND(E646>=$AM$48,E646<=$AN$48),AND(E646>=$AM$49,E646<=$AN$49),AND(E646>=$AM$50,E646<=$AN$50),AND(E646>=$AM$51,E646<=$AN$51)),0,1)*AE646","v":1},{"$f":"(B646>=5)*(B646<=10)","v":0},{"$f":"1*OR(B646<=4,B646>=11)","v":1},{"$f":"LOOKUP(B646,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE646:AI646)*((F646<6)*(I646>$AO$7)*(I646<=$AP$7)+(F646=6)*(I646>$AO$8)*(I646<=$AP$8)+(F646>=7)*(I646>$AO$9)*(I646<=$AP$9))","v":0}]
["1976-01-27",1,27,2018,{"$f":"DATE(D647,B647,C647)","v":"2018-01-27"},{"$f":"WEEKDAY(E647,2)","v":6},0,"18:00:00",18,35.24,19.939999999999998,26.6,19.399999999999999,42.980000000000004,24.98,-4,27.14,17.96,22.82,24.8,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,2018,"2018-01-27",6,0,"19:00:00",{"$f":"H648*24","v":19},35.42,19.04,26.6,17.600000000000001,41.36,23,-4.8999999999999986,26.6,16.7,21.38,21.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,2018,"2018-01-27",6,0,"20:00:00",20,37.04,19.04,26.6,15.8,42.980000000000004,19.939999999999998,-5.8000000000000043,24.08,15.620000000000001,20.12,21.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,2018,"2018-01-27",6,0,"21:00:00",21,36.68,14,24.8,15.8,41.36,19.04,-0.39999999999999858,24.08,12.379999999999999,18.68,21.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,2018,"2018-01-27",6,0,"22:00:00",22,36.86,12.920000000000002,24.8,14,42.980000000000004,17.96,1.3999999999999986,23,13.459999999999997,17.96,21.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,2018,"2018-01-27",6,0,"23:00:00",23,36.86,12.920000000000002,21.2,14,42.08,17.059999999999999,2.3000000000000007,22.1,14.899999999999999,16.159999999999997,19.939999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-27",1,27,2018,"2018-01-27",6,0,1,24,37.04,8.9599999999999973,19.399999999999999,12.2,39.92,17.96,3.1999999999999993,21.02,14.36,17.600000000000001,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"01:00:00",1,38.119999999999997,8.9599999999999973,15.8,14,42.26,17.96,3.1999999999999993,20.12,12.920000000000002,17.240000000000002,17.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"02:00:00",2,38.299999999999997,8.9599999999999973,15.8,10.399999999999999,42.980000000000004,17.059999999999999,1.3999999999999986,19.04,13.64,16.340000000000003,17.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"03:00:00",3,38.299999999999997,6.98,12.2,14,41,17.059999999999999,1.3999999999999986,15.079999999999998,11.84,16.88,17.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"04:00:00",4,38.480000000000004,6.0799999999999983,10.399999999999999,12.2,44.06,15.98,3.1999999999999993,16.159999999999997,11.3,15.8,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"05:00:00",5,39.200000000000003,6.0799999999999983,12.2,12.2,42.980000000000004,17.059999999999999,5,13.099999999999998,9.86,15.079999999999998,17.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"06:00:00",6,37.58,8.0599999999999987,12.2,12.2,40.46,17.059999999999999,6.8000000000000007,12.02,6.0799999999999983,12.559999999999999,15.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"07:00:00",7,37.94,10.039999999999999,21.2,10.399999999999999,41,17.059999999999999,8.5999999999999979,15.079999999999998,6.8000000000000007,11.48,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"08:00:00",8,38.119999999999997,10.039999999999999,19.399999999999999,12.2,40.64,17.96,9.5,14,7.1599999999999966,16.159999999999997,19.939999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"09:00:00",9,36.86,15.079999999999998,21.2,15.8,39.92,19.939999999999998,10.399999999999999,23,8.4200000000000017,20.12,24.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"10:00:00",10,37.4,17.96,26.6,17.600000000000001,39.92,21.92,14,29.12,10.219999999999999,22.46,28.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"11:00:00",11,37.04,17.96,26.6,19.399999999999999,40.46,24.08,14,32.9,12.2,24.439999999999998,33.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"12:00:00",12,37.4,24.08,30.2,19.399999999999999,42.08,24.98,15.8,35.96,15.8,26.42,35.06,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"13:00:00",13,38.840000000000003,23,32,21.2,43.879999999999995,24.08,17.600000000000001,35.24,17.96,26.96,33.44,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"14:00:00",14,39.56,21.92,33.799999999999997,21.2,44.78,24.8,15.8,36.86,17.240000000000002,26.6,35.42,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"15:00:00",15,39.380000000000003,21.2,32.18,17.600000000000001,46.94,26.060000000000002,14,37.94,17.600000000000001,24.439999999999998,36.32,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"16:00:00",16,36.68,21.2,32.9,17.600000000000001,46.04,26.6,15.8,36.86,18.14,24.8,37.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"17:00:00",17,36.86,21.92,32.54,17.600000000000001,42.08,23,15.8,36.68,18.5,23,36.68,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"18:00:00",18,32.54,21.2,32,17.600000000000001,37.58,24.8,15.8,32.9,18.5,23,32.36,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"19:00:00",19,37.04,21.2,28.4,19.399999999999999,35.6,24.8,19.399999999999999,30.02,18.68,23,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"20:00:00",20,35.06,21.92,28.4,19.399999999999999,35.78,23,19.399999999999999,28.04,18.5,23,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"21:00:00",21,32.36,21.2,28.4,19.399999999999999,35.6,23,19.399999999999999,23,18.86,23,28.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"22:00:00",22,26.060000000000002,21.2,26.6,19.399999999999999,33.08,23,21.2,23,19.04,23,26.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,"23:00:00",23,24.98,21.02,26.6,19.399999999999999,28.94,23,23,23,19.04,22.64,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-28",1,28,2018,"2018-01-28",7,0,1,24,24.98,21.2,24.8,19.399999999999999,28.04,24.8,21.2,22.1,19.22,22.82,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"01:00:00",1,26.96,21.2,21.2,19.399999999999999,26.96,23,19.399999999999999,20.12,19.399999999999999,23.36,23,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"02:00:00",2,30.02,21.02,17.600000000000001,19.399999999999999,26.96,23,21.2,17.059999999999999,19.399999999999999,23,23,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"03:00:00",3,30.02,19.399999999999999,15.8,19.399999999999999,26.96,23,21.2,17.059999999999999,19.759999999999998,23,23,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"04:00:00",4,28.94,21.02,15.8,19.399999999999999,24.98,23,21.2,16.159999999999997,19.399999999999999,23,21.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"05:00:00",5,24.98,21.02,14,19.399999999999999,24.08,24.8,21.2,14,16.52,23.54,21.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"06:00:00",6,24.98,15.8,12.2,14,21.92,21.92,21.2,14,11.84,23,21.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"07:00:00",7,24.08,12.2,12.2,10.399999999999999,21.92,21.2,23.9,13.099999999999998,9.86,23.9,19.939999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"08:00:00",8,26.060000000000002,10.940000000000001,10.399999999999999,8.5999999999999979,21.92,21.92,26.6,14,7.879999999999999,24.08,21.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"09:00:00",9,24.98,17.96,12.2,10.399999999999999,23,24.08,26.6,22.1,8.9599999999999973,24.98,24.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"10:00:00",10,26.060000000000002,19.399999999999999,19.399999999999999,17.600000000000001,26.96,24.8,26.6,27.14,14.899999999999999,26.060000000000002,28.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"11:00:00",11,30.02,23,24.8,24.8,32,28.04,26.6,32,21.02,28.4,35.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"12:00:00",12,30.92,28.04,26.6,26.6,35.06,30.02,28.4,36.14,26.060000000000002,30.2,32.54,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"13:00:00",13,32,28.4,33.26,30.2,35.06,30.2,26.6,38.840000000000003,29.12,32,34.700000000000003,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"14:00:00",14,32,30.92,34.880000000000003,26.6,32,32.36,30.2,39.92,31.46,32.54,34.340000000000003,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"15:00:00",15,30.02,32,35.6,30.2,32,33.44,28.4,39.92,32.72,32.18,34.880000000000003,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"16:00:00",16,28.94,32,35.6,30.2,33.08,33.799999999999997,28.4,39.92,32.9,32.36,35.42,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"17:00:00",17,28.04,32.18,35.6,28.4,33.979999999999997,33.44,28.4,39.380000000000003,32,32.9,35.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"18:00:00",18,26.060000000000002,30.2,37.22,28.4,32,33.08,23,37.94,31.1,33.26,35.06,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"19:00:00",19,26.060000000000002,30.92,36.5,28.4,32,33.08,26.6,36.86,30.92,33.799999999999997,33.979999999999997,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"20:00:00",20,24.08,30.92,35.78,28.4,32,32,26.6,36.86,30.2,33.799999999999997,33.979999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"21:00:00",21,24.08,30.02,35.06,28.4,30.92,32,28.4,35.96,30.2,33.799999999999997,33.979999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"22:00:00",22,23,30.2,34.520000000000003,30.2,30.02,30.2,30.2,34.880000000000003,30.74,34.340000000000003,34.880000000000003,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,"23:00:00",23,21.02,30.92,33.799999999999997,28.4,28.94,32,28.4,34.159999999999997,30.74,34.880000000000003,33.979999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-29",1,29,2018,"2018-01-29",1,0,1,24,21.02,30.2,33.619999999999997,30.2,28.04,32.18,28.4,34.880000000000003,31.46,35.24,33.799999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,2018,"2018-01-30",2,0,"01:00:00",1,19.939999999999998,30.2,33.26,30.2,28.4,32.36,28.4,35.06,32,35.06,35.06,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,2018,"2018-01-30",2,0,"02:00:00",2,19.939999999999998,32,32.72,30.2,26.96,32,32,33.979999999999997,32,34.700000000000003,34.700000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,2018,"2018-01-30",2,0,"03:00:00",3,19.04,32,32.72,32,26.96,33.799999999999997,32,33.799999999999997,32,34.880000000000003,34.159999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,2018,"2018-01-30",2,0,"04:00:00",4,17.96,32,33.799999999999997,32,26.6,32.18,33.799999999999997,34.520000000000003,32.36,35.24,35.06,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,2018,"2018-01-30",2,0,"05:00:00",5,17.059999999999999,32.36,35.6,33.799999999999997,26.060000000000002,32.72,35.6,35.78,32.36,35.6,35.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,2018,"2018-01-30",2,0,"06:00:00",6,17.059999999999999,33.26,37.4,32.36,26.060000000000002,33.799999999999997,37.4,36.86,32.54,36.86,37.58,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,2018,"2018-01-30",2,0,"07:00:00",7,15.98,33.26,37.4,32.18,26.060000000000002,33.799999999999997,37.4,37.22,32.36,37.4,37.4,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,2018,"2018-01-30",2,0,"08:00:00",8,15.98,32.9,37.22,32,26.060000000000002,33.979999999999997,37.4,38.119999999999997,32.54,37.4,37.4,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,{"$f":"$AO$4","v":2018},"2018-01-30",2,{"$f":"COUNTIF($AM$34:$AM$43,E710)","v":0},"09:00:00",9,15.98,33.08,37.76,33.799999999999997,26.96,34.520000000000003,35.6,39.56,32.36,36.32,39.200000000000003,null,{"$f":"SUMPRODUCT($J$2:$T$2,J710:T710)","v":0},null,null,{"$f":"OR(B710<=$AO$14,B710>=$AN$14)*(F710<6)*(I710>$AN$15)*(I710<=$AO$15)*(G710<>1)","v":1},{"$f":"OR(B710<=$AO$14,B710>=$AN$14)*(Y710=0)","v":0},{"$f":"AND(B710>=$AN$24,B710<=$AO$24)*(F710<6)*(I710>$AN$25)*(I710<=$AO$25)*(G710<>1)","v":0},{"$f":"AND(B710>=$AN$24,B710<=$AO$24)*(AA710=0)","v":0},{"$f":"OR(B710<=$AO$19,B710>=$AN$19)*(F710<6)*(I710>$AN$20)*(I710<=$AO$20)","v":0},{"$f":"AND(B710>=$AN$29,B710<=$AO$29)*(F710<6)*(I710>$AN$30)*(I710<=$AO$30)","v":0},{"$f":"IF(OR(E710=$AM$34,E710=$AM$35,E710=$AM$36,E710=$AM$37,E710=$AM$38,E710=$AM$39,E710=$AM$40,E710=$AM$41,E710=$AM$42,E710=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E710>=$AM$47,E710<=$AN$47),AND(E710>=$AM$48,E710<=$AN$48),AND(E710>=$AM$49,E710<=$AN$49),AND(E710>=$AM$50,E710<=$AN$50),AND(E710>=$AM$51,E710<=$AN$51)),0,1)*AE710","v":1},{"$f":"(B710>=5)*(B710<=10)","v":0},{"$f":"1*OR(B710<=4,B710>=11)","v":1},{"$f":"LOOKUP(B710,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE710:AI710)*((F710<6)*(I710>$AO$7)*(I710<=$AP$7)+(F710=6)*(I710>$AO$8)*(I710<=$AP$8)+(F710>=7)*(I710>$AO$9)*(I710<=$AP$9))","v":0}]
["1976-01-30",1,30,2018,{"$f":"DATE(D711,B711,C711)","v":"2018-01-30"},{"$f":"WEEKDAY(E711,2)","v":2},0,"10:00:00",10,17.059999999999999,35.42,38.659999999999997,32.9,26.96,37.94,37.4,41.54,32.36,39.200000000000003,39.200000000000003,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,2018,"2018-01-30",2,0,"11:00:00",{"$f":"H712*24","v":11},17.96,41.18,39.200000000000003,37.22,28.04,43.879999999999995,34.880000000000003,44.24,36.86,42.8,39.200000000000003,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,2018,"2018-01-30",2,0,"12:00:00",12,19.04,44.42,38.299999999999997,38.840000000000003,28.94,46.94,35.6,43.879999999999995,37.58,45.14,41,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,2018,"2018-01-30",2,0,"13:00:00",13,21.02,47.120000000000005,41,41.36,28.94,49.1,36.86,44.96,39.380000000000003,47.3,41,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,2018,"2018-01-30",2,0,"14:00:00",14,21.92,48.2,40.1,43.16,30.02,49.64,37.94,44.6,40.64,48.2,42.8,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,2018,"2018-01-30",2,0,"15:00:00",15,21.02,50.540000000000006,35.6,46.04,28.94,51.8,41,44.24,43.7,50,44.6,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,2018,"2018-01-30",2,0,"16:00:00",16,19.04,52.519999999999996,32.18,47.66,28.04,53.78,41,40.28,45.14,51.8,41.54,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,2018,"2018-01-30",2,0,"17:00:00",17,15.98,52.879999999999995,33.799999999999997,48.74,24.98,54.14,41,37.58,46.58,49.82,36.68,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,2018,"2018-01-30",2,0,"18:00:00",18,15.98,54.32,30.2,51.26,23,51.8,41,33.799999999999997,48.74,50,32,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,2018,"2018-01-30",2,0,"19:00:00",19,15.079999999999998,55.22,30.2,51.980000000000004,21.92,55.400000000000006,41,33.08,49.64,53.6,30.02,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,2018,"2018-01-30",2,0,"20:00:00",20,14,54.86,28.4,51.8,19.939999999999998,55.400000000000006,42.980000000000004,32.72,49.1,57.2,28.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,2018,"2018-01-30",2,0,"21:00:00",21,12.2,54.68,26.6,51.44,19.04,55.400000000000006,43.34,32.36,48.92,59,28.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,2018,"2018-01-30",2,0,"22:00:00",22,12.02,50,26.6,51.44,17.059999999999999,55.400000000000006,43.52,29.12,49.28,57.74,28.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,2018,"2018-01-30",2,0,"23:00:00",23,12.920000000000002,55.040000000000006,26.6,51.620000000000005,17.059999999999999,55.400000000000006,43.879999999999995,27.14,49.28,53.6,26.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-30",1,30,2018,"2018-01-30",2,0,1,24,12.02,55.040000000000006,26.6,51.8,15.98,55.400000000000006,44.42,27.14,49.28,59,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"01:00:00",1,10.039999999999999,51.8,24.8,52.34,12.920000000000002,55.400000000000006,44.42,27.14,49.46,57.2,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"02:00:00",2,10.039999999999999,53.06,23,48.2,15.079999999999998,57.2,44.24,26.060000000000002,50.540000000000006,53.6,24.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"03:00:00",3,8.9599999999999973,55.040000000000006,23,55.400000000000006,15.079999999999998,57.2,46.58,24.08,52.519999999999996,55.400000000000006,24.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"04:00:00",4,8.9599999999999973,55.400000000000006,21.2,55.400000000000006,15.079999999999998,60.08,48.74,23,53.42,57.2,23,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"05:00:00",5,8.9599999999999973,55.94,19.399999999999999,55.400000000000006,12.02,60.980000000000004,48.92,20.12,53.06,59,21.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"06:00:00",6,8.0599999999999987,57.92,19.399999999999999,57.2,10.039999999999999,60.8,48.2,18.14,53.78,60.8,19.939999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"07:00:00",7,6.98,57.2,15.8,59,8.0599999999999987,60.8,49.46,20.12,49.64,60.8,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"08:00:00",8,8.0599999999999987,57.019999999999996,15.8,55.400000000000006,8.9599999999999973,60.8,49.64,22.1,51.980000000000004,59.540000000000006,19.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"09:00:00",9,10.039999999999999,55.040000000000006,15.8,55.400000000000006,14,57.019999999999996,49.28,25.16,52.7,59,23,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"10:00:00",10,10.940000000000001,54.68,23,53.6,17.96,53.6,46.94,27.14,46.58,59,24.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"11:00:00",11,14,44.96,24.8,42.8,21.02,44.96,40.64,29.12,38.299999999999997,50.540000000000006,26.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"12:00:00",12,17.059999999999999,41.9,26.6,39.380000000000003,23,44.96,36.14,30.02,36.5,47.84,28.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"13:00:00",13,17.96,42.08,28.4,40.28,23,44.06,33.619999999999997,32.9,37.22,45.5,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"14:00:00",14,19.939999999999998,42.08,30.2,39.200000000000003,24.98,42.08,33.619999999999997,32.54,36.5,44.78,30.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"15:00:00",15,21.02,41.18,30.2,39.200000000000003,26.060000000000002,43.52,32.18,33.26,35.42,42.620000000000005,30.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"16:00:00",16,19.939999999999998,38.840000000000003,32,37.4,26.060000000000002,41.36,6.8000000000000007,33.44,33.619999999999997,42.44,30.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"17:00:00",17,19.939999999999998,37.04,30.2,33.799999999999997,26.060000000000002,39.200000000000003,5.8999999999999986,33.44,34.880000000000003,40.28,28.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"18:00:00",18,19.939999999999998,32.54,28.4,33.799999999999997,26.96,35.96,5,28.04,33.799999999999997,36.5,28.04,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"19:00:00",19,19.04,31.1,25.16,31.64,27.86,33.619999999999997,1.2199999999999953,24.439999999999998,31.1,35.24,25.16,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"20:00:00",20,18.5,30.56,23.9,30.2,28.04,32.72,-0.21999999999999886,22.82,29.66,34.159999999999997,24.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"21:00:00",21,17.78,29.48,23.9,29.3,28.04,31.82,-1.8400000000000034,22.1,28.4,33.26,24.8,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"22:00:00",22,14.18,22.1,16.7,22.46,27.14,24.8,-1.8400000000000034,16.340000000000003,21.92,26.42,19.22,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,"23:00:00",23,11.120000000000001,14.54,9.32,15.079999999999998,26.060000000000002,17.96,-0.75999999999999801,11.48,14.719999999999999,19.399999999999999,13.459999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1976-01-31",1,31,2018,"2018-01-31",3,0,1,24,7.6999999999999993,5.5399999999999991,3.019999999999996,8.240000000000002,24.62,11.84,-0.39999999999999858,6.8000000000000007,6.4400000000000013,12.740000000000002,7.6999999999999993,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"01:00:00",1,4.4599999999999973,-2.2000000000000028,-4.1800000000000068,1.5800000000000018,23.36,5.8999999999999986,1.0399999999999991,2.1199999999999974,-2.3800000000000026,5.8999999999999986,2.1199999999999974,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"02:00:00",2,3.9200000000000017,-2.9200000000000017,-4.1800000000000068,1.3999999999999986,23,5.5399999999999991,1.0399999999999991,3.019999999999996,-6.1599999999999966,5.18,1.759999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"03:00:00",3,3.379999999999999,-2.2000000000000028,-3.8200000000000003,1.759999999999998,23,5.5399999999999991,0.5,2.4800000000000004,-8.6800000000000068,4.82,1.3999999999999986,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"04:00:00",4,3.1999999999999993,-3.9999999999999147E-2,-3.4600000000000009,1.9400000000000013,22.64,4.82,0.5,2.4800000000000004,-7.9600000000000009,4.4599999999999973,1.2199999999999953,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"05:00:00",5,3.019999999999996,1.5800000000000018,-2.9200000000000017,2.4800000000000004,22.46,4.2799999999999976,-3.9999999999999147E-2,2.4800000000000004,-7.0600000000000023,4.4599999999999973,1.5800000000000018,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"06:00:00",6,3.5599999999999987,3.9200000000000017,-0.39999999999999858,3.9200000000000017,22.46,5,1.0399999999999991,4.4599999999999973,-3.6400000000000006,5.5399999999999991,3.379999999999999,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"07:00:00",7,3.019999999999996,3.019999999999996,-2.9200000000000017,1.9400000000000013,21.92,3.019999999999996,-0.39999999999999858,1.9400000000000013,-3.1000000000000014,4.0999999999999979,1.0399999999999991,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"08:00:00",8,3.1999999999999993,3.019999999999996,-2.019999999999996,3.9200000000000017,21.92,3.9200000000000017,-0.39999999999999858,3.9200000000000017,-4.5399999999999991,5,3.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"09:00:00",9,5,6.98,6.0799999999999983,8.0599999999999987,23,8.0599999999999987,5,10.940000000000001,3.740000000000002,8.5999999999999979,8.0599999999999987,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"10:00:00",10,6.98,12.02,10.940000000000001,10.940000000000001,23,10.940000000000001,6.8000000000000007,12.02,6.8000000000000007,11.659999999999997,10.940000000000001,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"11:00:00",11,8.9599999999999973,12.02,12.920000000000002,12.2,24.08,14,5,15.079999999999998,10.940000000000001,13.82,14,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"12:00:00",12,10.940000000000001,15.98,15.98,17.059999999999999,26.060000000000002,17.059999999999999,5,19.04,13.459999999999997,16.159999999999997,15.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"13:00:00",13,12.02,17.059999999999999,17.96,19.04,26.96,17.059999999999999,8.5999999999999979,19.939999999999998,15.259999999999998,19.399999999999999,17.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"14:00:00",14,12.920000000000002,17.059999999999999,21.02,19.04,24.98,19.04,6.8000000000000007,21.02,17.059999999999999,20.12,19.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"15:00:00",15,14,19.04,21.92,17.96,24.98,21.02,6.8000000000000007,19.939999999999998,18.14,20.299999999999997,19.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"16:00:00",16,12.920000000000002,17.96,19.04,17.96,24.08,19.939999999999998,8.5999999999999979,19.939999999999998,17.059999999999999,19.939999999999998,19.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"17:00:00",17,10.940000000000001,17.96,15.079999999999998,15.079999999999998,21.02,19.04,6.8000000000000007,17.059999999999999,15.98,18.14,17.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"18:00:00",18,6.98,14,12.02,12.920000000000002,19.939999999999998,17.059999999999999,6.8000000000000007,15.079999999999998,14.54,16.52,15.079999999999998,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"19:00:00",19,1.9400000000000013,12.02,6.0799999999999983,10.039999999999999,19.939999999999998,15.98,8.5999999999999979,8.0599999999999987,8.0599999999999987,14.719999999999999,14,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"20:00:00",20,-5.980000000000004,12.02,1.9400000000000013,10.039999999999999,19.939999999999998,15.079999999999998,8.5999999999999979,6.0799999999999983,3.5599999999999987,13.64,10.940000000000001,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"21:00:00",21,-0.94000000000000483,5,-0.94000000000000483,8.0599999999999987,19.939999999999998,10.039999999999999,8.5999999999999979,3.9200000000000017,1.0399999999999991,12.2,12.920000000000002,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"22:00:00",22,-9.0399999999999991,3.9200000000000017,-2.9200000000000017,6.98,19.399999999999999,12.02,8.5999999999999979,3.019999999999996,-0.39999999999999858,11.48,12.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,"23:00:00",23,-11.920000000000002,3.9200000000000017,-4,5,17.600000000000001,8.0599999999999987,8.5999999999999979,-3.9999999999999147E-2,-2.740000000000002,10.399999999999999,10.940000000000001,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-01",2,1,2018,"2018-02-01",4,0,1,24,-14.080000000000005,-3.9999999999999147E-2,-5.980000000000004,6.98,17.059999999999999,8.9599999999999973,8.5999999999999979,-0.94000000000000483,2.6599999999999966,8.4200000000000017,8.9599999999999973,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,{"$f":"$AO$4","v":2018},"2018-02-02",5,{"$f":"COUNTIF($AM$34:$AM$43,E774)","v":0},"01:00:00",1,-14.980000000000004,-2.9200000000000017,-5.980000000000004,1.9400000000000013,15.98,10.039999999999999,8.5999999999999979,-4,-5.980000000000004,9.14,6.0799999999999983,null,{"$f":"SUMPRODUCT($J$2:$T$2,J774:T774)","v":0},null,null,{"$f":"OR(B774<=$AO$14,B774>=$AN$14)*(F774<6)*(I774>$AN$15)*(I774<=$AO$15)*(G774<>1)","v":0},{"$f":"OR(B774<=$AO$14,B774>=$AN$14)*(Y774=0)","v":1},{"$f":"AND(B774>=$AN$24,B774<=$AO$24)*(F774<6)*(I774>$AN$25)*(I774<=$AO$25)*(G774<>1)","v":0},{"$f":"AND(B774>=$AN$24,B774<=$AO$24)*(AA774=0)","v":0},{"$f":"OR(B774<=$AO$19,B774>=$AN$19)*(F774<6)*(I774>$AN$20)*(I774<=$AO$20)","v":0},{"$f":"AND(B774>=$AN$29,B774<=$AO$29)*(F774<6)*(I774>$AN$30)*(I774<=$AO$30)","v":0},{"$f":"IF(OR(E774=$AM$34,E774=$AM$35,E774=$AM$36,E774=$AM$37,E774=$AM$38,E774=$AM$39,E774=$AM$40,E774=$AM$41,E774=$AM$42,E774=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E774>=$AM$47,E774<=$AN$47),AND(E774>=$AM$48,E774<=$AN$48),AND(E774>=$AM$49,E774<=$AN$49),AND(E774>=$AM$50,E774<=$AN$50),AND(E774>=$AM$51,E774<=$AN$51)),0,1)*AE774","v":1},{"$f":"(B774>=5)*(B774<=10)","v":0},{"$f":"1*OR(B774<=4,B774>=11)","v":1},{"$f":"LOOKUP(B774,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE774:AI774)*((F774<6)*(I774>$AO$7)*(I774<=$AP$7)+(F774=6)*(I774>$AO$8)*(I774<=$AP$8)+(F774>=7)*(I774>$AO$9)*(I774<=$AP$9))","v":0}]
["1977-02-02",2,2,2018,{"$f":"DATE(D775,B775,C775)","v":"2018-02-02"},{"$f":"WEEKDAY(E775,2)","v":5},0,"02:00:00",2,-16.96,-2.9200000000000017,-7.9600000000000009,-3.9999999999999147E-2,15.98,10.039999999999999,10.399999999999999,-2.019999999999996,-8.6800000000000068,7.34,6.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,2018,"2018-02-02",5,0,"03:00:00",{"$f":"H776*24","v":3},-16.060000000000002,-5.0800000000000054,-9.0399999999999991,-2.9200000000000017,15.8,8.9599999999999973,14,-4,-6.1599999999999966,7.879999999999999,5,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,2018,"2018-02-02",5,0,"04:00:00",4,-14.980000000000004,-7.0600000000000023,-9.9400000000000048,-2.019999999999996,15.8,5,12.2,-2.9200000000000017,-7.6000000000000014,7.34,3.9200000000000017,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,2018,"2018-02-02",5,0,"05:00:00",5,-13,-7.0600000000000023,-9.0399999999999991,-2.9200000000000017,14,-3.9999999999999147E-2,8.5999999999999979,-5.0800000000000054,-10.300000000000004,6.98,3.9200000000000017,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,2018,"2018-02-02",5,0,"06:00:00",6,-9.0399999999999991,-9.9400000000000048,-9.0399999999999991,-0.94000000000000483,12.2,3.019999999999996,8.5999999999999979,-4,-13,6.259999999999998,6.0799999999999983,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,2018,"2018-02-02",5,0,"07:00:00",7,-9.0399999999999991,-7.9600000000000009,-9.0399999999999991,-2.019999999999996,12.2,1.0399999999999991,8.5999999999999979,-5.0800000000000054,-13.719999999999999,3.379999999999999,5,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,2018,"2018-02-02",5,0,"08:00:00",8,-13,-7.9600000000000009,-7.9600000000000009,3.9200000000000017,8.9599999999999973,3.019999999999996,5,-2.019999999999996,-13.180000000000007,6.259999999999998,6.0799999999999983,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,2018,"2018-02-02",5,0,"09:00:00",9,-2.9200000000000017,1.0399999999999991,1.0399999999999991,8.9599999999999973,15.079999999999998,6.0799999999999983,5,8.0599999999999987,-10.480000000000004,10.039999999999999,8.9599999999999973,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,2018,"2018-02-02",5,0,"10:00:00",10,1.0399999999999991,8.0599999999999987,10.940000000000001,12.920000000000002,17.059999999999999,12.02,3.1999999999999993,17.96,-3.2800000000000011,13.82,14,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,2018,"2018-02-02",5,0,"11:00:00",11,3.9200000000000017,8.0599999999999987,19.939999999999998,15.98,19.04,17.96,3.1999999999999993,22.46,2.3000000000000007,17.420000000000002,17.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,2018,"2018-02-02",5,0,"12:00:00",12,14,19.939999999999998,19.04,19.939999999999998,21.02,21.92,3.1999999999999993,26.96,10.759999999999998,21.38,19.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,2018,"2018-02-02",5,0,"13:00:00",13,15.079999999999998,23,23,21.92,21.92,24.98,5,26.060000000000002,19.22,23.18,23,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,2018,"2018-02-02",5,0,"14:00:00",14,17.059999999999999,23,26.96,26.060000000000002,23,26.060000000000002,5,30.02,23.36,25.34,24.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,2018,"2018-02-02",5,0,"15:00:00",15,15.98,26.060000000000002,30.92,26.96,23,30.02,6.8000000000000007,33.08,26.6,26.24,26.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,2018,"2018-02-02",5,0,"16:00:00",16,15.079999999999998,28.04,30.02,26.96,23,30.92,14,32,28.22,27.14,26.060000000000002,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,2018,"2018-02-02",5,0,"17:00:00",17,15.079999999999998,28.04,28.94,26.060000000000002,21.92,30.92,17.600000000000001,30.02,28.04,29.12,26.060000000000002,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,2018,"2018-02-02",5,0,"18:00:00",18,15.079999999999998,28.94,28.04,25.7,21.2,30.92,17.600000000000001,30.02,27.5,30.02,24.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,2018,"2018-02-02",5,0,"19:00:00",19,15.079999999999998,30.02,28.94,25.34,21.02,30.92,15.8,30.92,25.88,30.2,23,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,2018,"2018-02-02",5,0,"20:00:00",20,19.04,30.02,28.94,24.98,21.2,30.92,14,30.92,24.62,30.38,28.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,2018,"2018-02-02",5,0,"21:00:00",21,19.939999999999998,28.04,30.2,24.08,19.939999999999998,30.92,12.2,32,22.64,29.12,26.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,2018,"2018-02-02",5,0,"22:00:00",22,19.939999999999998,28.04,30.92,24.98,19.939999999999998,33.08,6.8000000000000007,32,23.9,24.62,28.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,2018,"2018-02-02",5,0,"23:00:00",23,19.939999999999998,28.04,33.08,24.98,19.939999999999998,30.92,5,30.02,24.8,26.6,26.060000000000002,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-02",2,2,2018,"2018-02-02",5,0,1,24,17.96,26.96,30.92,24.98,19.04,28.94,3.1999999999999993,32,24.62,26.060000000000002,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"01:00:00",1,17.96,26.060000000000002,30.2,24.08,17.96,26.060000000000002,3.1999999999999993,29.48,24.259999999999998,26.060000000000002,26.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"02:00:00",2,14,26.060000000000002,26.060000000000002,24.08,17.96,26.96,-0.39999999999999858,26.96,23.36,26.24,24.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"03:00:00",3,15.079999999999998,21.92,24.08,23,17.059999999999999,24.08,0.5,24.08,22.1,23.72,21.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"04:00:00",4,5,19.04,21.92,17.96,15.98,21.02,1.3999999999999986,19.939999999999998,21.2,23.54,21.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"05:00:00",5,1.9400000000000013,19.04,23,15.98,14,19.04,5,17.96,20.84,21.740000000000002,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"06:00:00",6,-4,12.02,24.8,15.079999999999998,15.8,19.04,3.1999999999999993,21.02,18.86,17.78,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"07:00:00",7,-3.9999999999999147E-2,15.079999999999998,24.8,15.8,15.98,21.02,3.1999999999999993,23,18.32,16.340000000000003,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"08:00:00",8,5,15.079999999999998,24.8,19.04,15.079999999999998,21.92,3.1999999999999993,24.08,18.5,18.5,19.939999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"09:00:00",9,6.98,21.2,26.96,23,15.8,23,3.1999999999999993,26.96,19.939999999999998,22.1,21.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"10:00:00",10,10.940000000000001,21.92,28.94,26.96,17.059999999999999,24.08,3.1999999999999993,30.92,22.28,25.34,24.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"11:00:00",11,19.939999999999998,23,33.08,28.4,17.600000000000001,28.04,4.6400000000000006,32,24.8,26.96,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"12:00:00",12,26.96,26.96,33.799999999999997,30.92,23,30.02,5.3599999999999994,33.08,27.32,28.759999999999998,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"13:00:00",13,26.96,30.02,33.799999999999997,30.2,24.98,32,7.52,32.72,28.94,31.1,32,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"14:00:00",14,28.04,30.02,33.619999999999997,30.2,26.060000000000002,33.44,7.6999999999999993,34.880000000000003,29.84,31.82,32,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"15:00:00",15,28.04,32,35.96,32,26.96,34.880000000000003,9.14,36.5,30.2,31.28,32,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"16:00:00",16,26.96,34.159999999999997,37.94,28.94,26.96,37.04,14.18,38.659999999999997,30.74,32.9,30.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"17:00:00",17,26.96,35.24,38.299999999999997,28.94,26.96,37.04,17.96,38.299999999999997,30.56,33.979999999999997,32.9,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"18:00:00",18,26.060000000000002,35.24,38.840000000000003,28.4,21.92,35.96,17.420000000000002,36.86,30.2,33.979999999999997,32.72,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"19:00:00",19,24.98,33.799999999999997,37.4,28.94,19.939999999999998,34.159999999999997,16.52,34.700000000000003,30.02,33.619999999999997,30.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"20:00:00",20,26.060000000000002,32.54,36.14,28.94,17.96,33.08,13.82,33.44,29.66,33.44,30.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"21:00:00",21,26.6,32.36,35.42,28.94,19.939999999999998,32.54,11.120000000000001,32.72,29.66,33.44,30.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"22:00:00",22,26.060000000000002,32.18,35.06,28.94,19.939999999999998,32.18,8.5999999999999979,32.54,29.48,33.08,30.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,"23:00:00",23,26.060000000000002,32.18,33.619999999999997,28.04,19.939999999999998,32.36,5.8999999999999986,32.72,29.3,32.9,30.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-03",2,3,2018,"2018-02-03",6,0,1,24,26.060000000000002,32.54,33.44,28.94,19.04,32.36,3.1999999999999993,32.72,28.759999999999998,33.08,32,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,2018,"2018-02-04",7,0,"01:00:00",1,28.04,33.799999999999997,34.159999999999997,28.94,17.059999999999999,33.619999999999997,1.3999999999999986,33.799999999999997,28.759999999999998,33.799999999999997,32.9,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,2018,"2018-02-04",7,0,"02:00:00",2,26.96,34.700000000000003,34.880000000000003,28.04,19.04,34.340000000000003,3.1999999999999993,34.700000000000003,28.4,33.799999999999997,33.44,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,2018,"2018-02-04",7,0,"03:00:00",3,28.04,34.880000000000003,35.42,28.04,19.04,34.700000000000003,3.1999999999999993,35.06,28.4,33.799999999999997,32.9,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,2018,"2018-02-04",7,0,"04:00:00",4,28.04,36.86,36.32,33.44,17.059999999999999,36.32,3.1999999999999993,36.32,32.72,35.42,34.880000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,2018,"2018-02-04",7,0,"05:00:00",5,28.04,35.96,34.700000000000003,33.26,15.98,35.06,1.3999999999999986,35.24,32.72,34.880000000000003,34.159999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,2018,"2018-02-04",7,0,"06:00:00",6,28.94,34.700000000000003,33.08,32.72,19.04,33.26,1.3999999999999986,33.08,32.9,33.44,33.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,2018,"2018-02-04",7,0,"07:00:00",7,28.94,34.700000000000003,33.26,32.72,19.04,33.799999999999997,1.3999999999999986,33.979999999999997,32.9,33.799999999999997,33.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,2018,"2018-02-04",7,0,"08:00:00",8,30.02,34.700000000000003,32.72,33.08,19.04,34.159999999999997,1.3999999999999986,34.340000000000003,33.08,34.159999999999997,33.619999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,2018,"2018-02-04",7,0,"09:00:00",9,30.92,36.14,33.619999999999997,34.340000000000003,21.02,35.78,1.3999999999999986,35.78,33.979999999999997,35.24,35.06,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,2018,"2018-02-04",7,0,"10:00:00",10,33.08,37.94,36.86,37.4,21.92,39.92,1.3999999999999986,39.92,35.78,37.76,37.76,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,2018,"2018-02-04",7,0,"11:00:00",11,33.44,43.34,44.06,39.92,24.08,46.04,5,46.22,39.56,41,41.72,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,2018,"2018-02-04",7,0,"12:00:00",12,33.619999999999997,46.4,44.6,43.7,26.6,46.94,3.1999999999999993,55.040000000000006,42.44,43.52,44.06,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,2018,"2018-02-04",7,0,"13:00:00",13,37.04,55.040000000000006,48.56,46.22,24.98,57.92,3.1999999999999993,59,42.620000000000005,46.22,47.3,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,2018,"2018-02-04",7,0,"14:00:00",14,36.68,55.040000000000006,51.26,48.2,24.98,60.08,1.3999999999999986,60.980000000000004,45.14,48.019999999999996,49.28,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,2018,"2018-02-04",7,0,"15:00:00",15,37.4,59,59,55.040000000000006,26.060000000000002,60.980000000000004,-0.39999999999999858,60.980000000000004,48.56,48.019999999999996,50.36,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,2018,"2018-02-04",7,0,"16:00:00",16,38.299999999999997,57.92,57.92,50,24.98,62.06,-0.39999999999999858,59,46.4,48.019999999999996,49.82,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,{"$f":"$AO$4","v":2018},"2018-02-04",7,{"$f":"COUNTIF($AM$34:$AM$43,E838)","v":0},"17:00:00",17,39.200000000000003,57.92,53.78,49.64,23,57.019999999999996,-0.39999999999999858,57.379999999999995,48.019999999999996,46.22,48.56,null,{"$f":"SUMPRODUCT($J$2:$T$2,J838:T838)","v":0},null,null,{"$f":"OR(B838<=$AO$14,B838>=$AN$14)*(F838<6)*(I838>$AN$15)*(I838<=$AO$15)*(G838<>1)","v":0},{"$f":"OR(B838<=$AO$14,B838>=$AN$14)*(Y838=0)","v":1},{"$f":"AND(B838>=$AN$24,B838<=$AO$24)*(F838<6)*(I838>$AN$25)*(I838<=$AO$25)*(G838<>1)","v":0},{"$f":"AND(B838>=$AN$24,B838<=$AO$24)*(AA838=0)","v":0},{"$f":"OR(B838<=$AO$19,B838>=$AN$19)*(F838<6)*(I838>$AN$20)*(I838<=$AO$20)","v":0},{"$f":"AND(B838>=$AN$29,B838<=$AO$29)*(F838<6)*(I838>$AN$30)*(I838<=$AO$30)","v":0},{"$f":"IF(OR(E838=$AM$34,E838=$AM$35,E838=$AM$36,E838=$AM$37,E838=$AM$38,E838=$AM$39,E838=$AM$40,E838=$AM$41,E838=$AM$42,E838=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E838>=$AM$47,E838<=$AN$47),AND(E838>=$AM$48,E838<=$AN$48),AND(E838>=$AM$49,E838<=$AN$49),AND(E838>=$AM$50,E838<=$AN$50),AND(E838>=$AM$51,E838<=$AN$51)),0,1)*AE838","v":1},{"$f":"(B838>=5)*(B838<=10)","v":0},{"$f":"1*OR(B838<=4,B838>=11)","v":1},{"$f":"LOOKUP(B838,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE838:AI838)*((F838<6)*(I838>$AO$7)*(I838<=$AP$7)+(F838=6)*(I838>$AO$8)*(I838<=$AP$8)+(F838>=7)*(I838>$AO$9)*(I838<=$AP$9))","v":0}]
["1977-02-04",2,4,2018,{"$f":"DATE(D839,B839,C839)","v":"2018-02-04"},{"$f":"WEEKDAY(E839,2)","v":7},0,"18:00:00",18,38.119999999999997,48.379999999999995,48.379999999999995,44.96,21.02,50,-0.39999999999999858,51.08,45.86,42.44,44.24,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,2018,"2018-02-04",7,0,"19:00:00",{"$f":"H840*24","v":19},38.840000000000003,46.04,45.86,43.7,19.939999999999998,46.94,-0.39999999999999858,48.379999999999995,44.96,45.32,46.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,2018,"2018-02-04",7,0,"20:00:00",20,37.58,42.620000000000005,42.620000000000005,41.36,19.04,44.42,-0.39999999999999858,44.78,43.16,41.9,43.16,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,2018,"2018-02-04",7,0,"21:00:00",21,36.68,41.36,41.72,41,17.96,44.96,0.5,43.34,43.16,44.78,44.06,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,2018,"2018-02-04",7,0,"22:00:00",22,35.96,39.56,39.74,39.380000000000003,17.059999999999999,42.08,1.3999999999999986,41.36,41.72,40.64,41,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,2018,"2018-02-04",7,0,"23:00:00",23,34.880000000000003,38.659999999999997,39.019999999999996,37.4,15.98,37.94,5,40.1,39.200000000000003,38.299999999999997,38.659999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-04",2,4,2018,"2018-02-04",7,0,1,24,33.619999999999997,36.86,37.4,35.42,15.079999999999998,37.76,8.5999999999999979,38.299999999999997,37.58,39.200000000000003,36.5,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"01:00:00",1,33.26,35.96,36.32,33.26,10.940000000000001,36.68,12.2,37.22,33.979999999999997,36.68,35.42,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"02:00:00",2,33.08,35.42,36.32,28.4,8.0599999999999987,37.04,14,36.86,28.22,35.96,34.520000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"03:00:00",3,32.72,34.880000000000003,35.42,32.18,8.0599999999999987,35.6,10.399999999999999,36.14,32.36,35.42,33.979999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"04:00:00",4,34.880000000000003,36.68,36.32,34.159999999999997,6.0799999999999983,37.22,12.2,37.76,33.799999999999997,36.68,35.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"05:00:00",5,35.06,37.76,37.22,35.06,5,38.840000000000003,12.2,39.56,34.159999999999997,37.22,35.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"06:00:00",6,36.86,37.76,36.86,35.24,3.9200000000000017,38.480000000000004,12.2,38.840000000000003,34.520000000000003,38.119999999999997,37.58,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"07:00:00",7,37.04,37.94,37.76,37.04,3.019999999999996,38.659999999999997,10.399999999999999,39.019999999999996,36.5,40.1,37.58,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"08:00:00",8,37.94,37.94,39.200000000000003,37.76,6.0799999999999983,39.74,10.399999999999999,39.019999999999996,37.94,39.380000000000003,39.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"09:00:00",9,37.94,39.92,39.92,39.200000000000003,8.9599999999999973,41.18,10.399999999999999,41.54,38.480000000000004,40.64,41,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"10:00:00",10,40.1,43.16,42.08,41.54,12.02,43.7,12.2,44.24,40.46,42.8,42.8,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"11:00:00",11,41,46.94,48.019999999999996,48.019999999999996,15.98,48.379999999999995,15.8,49.1,43.52,45.32,45.68,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"12:00:00",12,41.9,57.019999999999996,51.980000000000004,51.980000000000004,21.02,53.24,17.600000000000001,53.6,46.58,48.92,50,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"13:00:00",13,44.42,57.019999999999996,57.019999999999996,53.96,21.92,60.08,19.399999999999999,60.980000000000004,50.900000000000006,57.92,60.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"14:00:00",14,45.68,57.019999999999996,55.94,53.96,26.060000000000002,60.980000000000004,19.399999999999999,60.980000000000004,50,59.36,60.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"15:00:00",15,45.86,57.92,55.94,55.94,26.96,60.08,19.399999999999999,60.980000000000004,50.18,59.18,60.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"16:00:00",16,43.16,57.019999999999996,55.040000000000006,53.06,26.96,59,19.399999999999999,59,47.84,58.82,59,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"17:00:00",17,42.26,57.019999999999996,51.08,53.06,24.98,55.94,23,55.94,47.66,54.14,55.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"18:00:00",18,34.520000000000003,50,48.019999999999996,48.92,21.92,53.06,21.2,53.06,42.44,52.34,53.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"19:00:00",19,33.08,48.92,44.96,42.980000000000004,21.02,51.08,21.2,48.92,40.64,50.72,50,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"20:00:00",20,33.979999999999997,48.92,44.06,42.620000000000005,17.96,48.92,23,46.94,40.1,48.379999999999995,44.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"21:00:00",21,32,44.24,39.92,40.46,19.939999999999998,44.96,23,44.06,36.68,43.16,42.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"22:00:00",22,28.94,40.64,37.94,35.96,21.02,42.08,23,41,32.9,40.46,41.72,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,"23:00:00",23,28.94,37.94,37.4,34.880000000000003,17.96,39.019999999999996,19.399999999999999,40.46,33.979999999999997,38.659999999999997,37.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-05",2,5,2018,"2018-02-05",1,0,1,24,24.98,37.04,35.96,34.159999999999997,19.939999999999998,38.659999999999997,17.600000000000001,37.94,32,39.380000000000003,38.299999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"01:00:00",1,24.08,34.159999999999997,35.06,30.92,19.939999999999998,35.96,23,37.22,29.3,36.86,35.78,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"02:00:00",2,21.2,32.72,32.9,28.94,21.02,33.979999999999997,23,35.42,27.32,35.42,34.520000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"03:00:00",3,21.02,30.02,28.04,28.04,21.02,33.08,12.2,34.159999999999997,25.7,34.520000000000003,33.619999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"04:00:00",4,17.96,28.04,26.96,26.96,19.939999999999998,30.92,12.2,32.18,24.98,32.36,30.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"05:00:00",5,17.059999999999999,28.04,28.94,26.060000000000002,19.939999999999998,30.02,10.399999999999999,30.92,23.9,30.02,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"06:00:00",6,15.079999999999998,26.060000000000002,26.96,24.98,21.02,28.94,8.5999999999999979,28.94,23.72,28.759999999999998,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"07:00:00",7,12.920000000000002,26.060000000000002,24.98,24.98,19.939999999999998,28.94,6.8000000000000007,26.96,23.18,26.96,26.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"08:00:00",8,15.079999999999998,26.060000000000002,26.060000000000002,24.98,21.92,30.02,6.8000000000000007,28.94,22.64,30.2,28.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"09:00:00",9,17.96,30.02,28.04,26.96,26.060000000000002,33.08,6.8000000000000007,32,23.9,31.64,30.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"10:00:00",10,21.92,30.92,30.02,28.94,30.02,32,6.8000000000000007,32.36,25.7,32.18,33.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"11:00:00",11,26.060000000000002,33.08,32.36,32,32,34.700000000000003,6.8000000000000007,34.880000000000003,28.94,33.44,33.26,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"12:00:00",12,28.94,34.700000000000003,34.520000000000003,33.979999999999997,33.08,36.14,7.6999999999999993,36.68,33.08,33.799999999999997,34.159999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"13:00:00",13,32,37.04,37.04,33.08,33.979999999999997,37.94,8.5999999999999979,39.200000000000003,37.04,35.06,35.78,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"14:00:00",14,35.06,39.019999999999996,38.840000000000003,34.520000000000003,33.799999999999997,39.92,8.5999999999999979,41,38.299999999999997,35.24,35.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"15:00:00",15,35.96,37.94,38.480000000000004,34.700000000000003,35.06,37.94,8.5999999999999979,39.019999999999996,32,34.520000000000003,35.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"16:00:00",16,35.06,37.4,38.480000000000004,34.880000000000003,32,37.4,8.5999999999999979,37.94,32.72,33.44,34.159999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"17:00:00",17,33.979999999999997,35.96,37.22,33.799999999999997,30.92,35.78,8.5999999999999979,36.32,32.18,32.54,32.72,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"18:00:00",18,33.08,32.54,34.700000000000003,33.979999999999997,26.96,32.72,6.8000000000000007,33.08,35.96,30.74,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"19:00:00",19,32,30.02,34.159999999999997,33.08,24.98,32.18,8.5999999999999979,32.54,35.6,32,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"20:00:00",20,32,30.02,32,30.02,23,32,8.5999999999999979,32.18,32.9,32.18,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"21:00:00",21,30.2,30.02,33.799999999999997,28.4,21.02,32,8.5999999999999979,30.2,30.56,32.36,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"22:00:00",22,30.02,30.02,33.08,30.2,19.04,32,8.5999999999999979,30.2,29.84,32.54,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,"23:00:00",23,30.02,30.92,32,28.4,17.059999999999999,33.08,8.5999999999999979,32,29.66,32.18,30.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-06",2,6,2018,"2018-02-06",2,0,1,24,30.02,30.92,33.08,28.4,14,33.08,8.5999999999999979,32.18,29.66,32.54,32,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,2018,"2018-02-07",3,0,"01:00:00",1,28.94,32,32,30.2,12.920000000000002,32.18,8.5999999999999979,32.54,29.84,33.08,30.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,2018,"2018-02-07",3,0,"02:00:00",2,28.94,32,33.08,30.2,12.02,32,8.5999999999999979,32.54,30.02,33.26,32,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,2018,"2018-02-07",3,0,"03:00:00",3,30.02,32,33.799999999999997,30.2,10.039999999999999,32.18,8.5999999999999979,32.54,30.02,33.619999999999997,32,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,2018,"2018-02-07",3,0,"04:00:00",4,30.02,32,32,30.2,10.940000000000001,32.36,8.5999999999999979,32.72,30.2,33.979999999999997,32,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,2018,"2018-02-07",3,0,"05:00:00",5,28.94,32,32,30.2,10.039999999999999,32.72,9.5,33.26,30.56,34.520000000000003,32.54,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,2018,"2018-02-07",3,0,"06:00:00",6,28.94,32,33.08,30.92,8.0599999999999987,32.9,10.399999999999999,33.26,30.74,34.520000000000003,32.36,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,2018,"2018-02-07",3,0,"07:00:00",7,28.94,32,33.08,30.2,8.9599999999999973,33.08,10.399999999999999,33.08,30.92,34.700000000000003,32.54,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,2018,"2018-02-07",3,0,"08:00:00",8,30.2,32,33.799999999999997,30.2,8.9599999999999973,32.9,10.399999999999999,33.08,31.1,34.700000000000003,32.54,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,{"$f":"$AO$4","v":2018},"2018-02-07",3,{"$f":"COUNTIF($AM$34:$AM$43,E902)","v":0},"09:00:00",9,30.02,32,33.799999999999997,30.2,10.940000000000001,33.26,11.3,33.619999999999997,31.64,35.24,33.08,null,{"$f":"SUMPRODUCT($J$2:$T$2,J902:T902)","v":0},null,null,{"$f":"OR(B902<=$AO$14,B902>=$AN$14)*(F902<6)*(I902>$AN$15)*(I902<=$AO$15)*(G902<>1)","v":1},{"$f":"OR(B902<=$AO$14,B902>=$AN$14)*(Y902=0)","v":0},{"$f":"AND(B902>=$AN$24,B902<=$AO$24)*(F902<6)*(I902>$AN$25)*(I902<=$AO$25)*(G902<>1)","v":0},{"$f":"AND(B902>=$AN$24,B902<=$AO$24)*(AA902=0)","v":0},{"$f":"OR(B902<=$AO$19,B902>=$AN$19)*(F902<6)*(I902>$AN$20)*(I902<=$AO$20)","v":0},{"$f":"AND(B902>=$AN$29,B902<=$AO$29)*(F902<6)*(I902>$AN$30)*(I902<=$AO$30)","v":0},{"$f":"IF(OR(E902=$AM$34,E902=$AM$35,E902=$AM$36,E902=$AM$37,E902=$AM$38,E902=$AM$39,E902=$AM$40,E902=$AM$41,E902=$AM$42,E902=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E902>=$AM$47,E902<=$AN$47),AND(E902>=$AM$48,E902<=$AN$48),AND(E902>=$AM$49,E902<=$AN$49),AND(E902>=$AM$50,E902<=$AN$50),AND(E902>=$AM$51,E902<=$AN$51)),0,1)*AE902","v":1},{"$f":"(B902>=5)*(B902<=10)","v":0},{"$f":"1*OR(B902<=4,B902>=11)","v":1},{"$f":"LOOKUP(B902,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE902:AI902)*((F902<6)*(I902>$AO$7)*(I902<=$AP$7)+(F902=6)*(I902>$AO$8)*(I902<=$AP$8)+(F902>=7)*(I902>$AO$9)*(I902<=$AP$9))","v":0}]
["1977-02-07",2,7,2018,{"$f":"DATE(D903,B903,C903)","v":"2018-02-07"},{"$f":"WEEKDAY(E903,2)","v":3},0,"10:00:00",10,30.2,32.18,32.36,32,14,33.979999999999997,12.2,34.159999999999997,32,35.96,33.799999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,2018,"2018-02-07",3,0,"11:00:00",{"$f":"H904*24","v":11},33.08,32.54,32.54,33.08,15.98,33.979999999999997,13.099999999999998,34.880000000000003,32.9,36.5,34.520000000000003,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,2018,"2018-02-07",3,0,"12:00:00",12,33.08,33.44,33.44,33.799999999999997,19.04,35.06,14,35.96,33.44,37.04,35.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,2018,"2018-02-07",3,0,"13:00:00",13,33.979999999999997,34.159999999999997,34.159999999999997,33.799999999999997,21.02,36.14,15.8,35.6,34.159999999999997,36.68,35.6,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,2018,"2018-02-07",3,0,"14:00:00",14,35.06,35.06,34.700000000000003,32.36,23,35.96,15.8,36.86,34.700000000000003,37.4,35.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,2018,"2018-02-07",3,0,"15:00:00",15,35.06,35.06,35.24,32.9,23,35.96,15.8,37.4,35.06,38.299999999999997,35.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,2018,"2018-02-07",3,0,"16:00:00",16,35.06,35.06,36.14,33.44,23,37.4,15.8,37.76,34.880000000000003,37.76,35.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,2018,"2018-02-07",3,0,"17:00:00",17,35.06,35.06,36.14,33.26,21.92,35.6,17.600000000000001,37.22,32,37.22,35.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,2018,"2018-02-07",3,0,"18:00:00",18,33.979999999999997,33.979999999999997,34.520000000000003,32.72,21.92,35.6,14,35.6,34.159999999999997,36.32,35.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,2018,"2018-02-07",3,0,"19:00:00",19,33.979999999999997,33.979999999999997,34.340000000000003,32.72,19.939999999999998,35.96,14,35.96,33.979999999999997,36.86,35.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,2018,"2018-02-07",3,0,"20:00:00",20,33.979999999999997,33.979999999999997,33.799999999999997,32.36,19.04,35.96,15.8,35.96,33.799999999999997,36.86,35.24,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,2018,"2018-02-07",3,0,"21:00:00",21,35.96,33.979999999999997,33.799999999999997,32.36,19.04,35.96,17.600000000000001,35.06,33.44,35.96,35.42,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,2018,"2018-02-07",3,0,"22:00:00",22,35.6,33.979999999999997,33.799999999999997,32.72,19.04,35.96,17.600000000000001,35.6,33.26,37.22,35.6,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,2018,"2018-02-07",3,0,"23:00:00",23,35.06,33.979999999999997,33.619999999999997,32.54,19.04,35.06,17.600000000000001,35.6,33.08,37.22,35.78,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-07",2,7,2018,"2018-02-07",3,0,1,24,35.06,33.619999999999997,33.44,32.18,19.04,35.06,17.600000000000001,35.6,33.08,37.04,35.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"01:00:00",1,35.06,33.799999999999997,33.979999999999997,32.54,19.04,35.06,17.600000000000001,35.06,33.08,37.4,35.78,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"02:00:00",2,35.06,33.979999999999997,33.799999999999997,32.54,21.02,35.06,17.600000000000001,35.42,33.08,37.22,35.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"03:00:00",3,35.96,33.979999999999997,33.799999999999997,32.72,21.92,35.06,17.600000000000001,35.42,33.26,37.04,35.42,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"04:00:00",4,35.96,34.159999999999997,34.520000000000003,33.44,21.02,35.24,15.8,35.6,32.9,36.86,35.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"05:00:00",5,35.96,34.340000000000003,35.6,33.44,21.02,35.24,15.8,35.78,32.9,36.32,35.06,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"06:00:00",6,35.96,33.979999999999997,34.880000000000003,32.72,19.399999999999999,35.06,14.899999999999999,35.42,32.36,35.6,33.979999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"07:00:00",7,35.06,33.979999999999997,35.6,32.54,19.399999999999999,35.06,14,35.6,32.36,35.06,33.979999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"08:00:00",8,35.96,34.340000000000003,35.6,32.36,19.399999999999999,35.6,14,36.32,32,35.06,33.979999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"09:00:00",9,35.96,35.24,37.22,32.54,19.399999999999999,35.6,14,37.4,32,35.6,34.159999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"10:00:00",10,35.06,37.04,37.4,33.44,19.399999999999999,37.4,15.8,37.4,32.9,35.6,35.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"11:00:00",11,32.9,40.46,41.18,35.6,19.399999999999999,41.36,14,41.72,35.42,38.299999999999997,37.4,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"12:00:00",12,33.799999999999997,42.44,42.620000000000005,39.200000000000003,21.02,43.16,12.2,42.8,37.58,39.74,40.64,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"13:00:00",13,36.5,45.68,41,42.8,21.02,46.58,8.5999999999999979,50,40.64,42.8,44.78,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"14:00:00",14,38.659999999999997,46.94,41.72,42.8,21.92,48.92,3.1999999999999993,50,40.46,44.6,46.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"15:00:00",15,39.56,46.04,44.06,42.8,23,48.92,1.3999999999999986,48.92,40.82,50,48.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"16:00:00",16,35.78,44.06,42.08,42.980000000000004,23,46.94,-2.2000000000000028,46.04,38.119999999999997,48.2,46.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"17:00:00",17,32.72,44.06,38.840000000000003,39.019999999999996,21.2,42.980000000000004,-5.8000000000000043,42.980000000000004,35.6,44.42,42.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"18:00:00",18,30.92,35.96,33.979999999999997,33.26,21.2,39.019999999999996,-9.3999999999999986,40.1,35.42,41,39.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"19:00:00",19,28.94,33.619999999999997,30.02,32,21.2,36.32,-11.200000000000003,37.04,32,36.86,35.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"20:00:00",20,26.060000000000002,32.18,28.94,30.02,21.2,33.979999999999997,-14.800000000000004,34.340000000000003,30.74,35.42,34.159999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"21:00:00",21,24.98,30.02,28.04,28.04,21.2,32.72,-18.399999999999999,32.9,29.12,33.799999999999997,32.9,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"22:00:00",22,24.08,28.04,26.060000000000002,26.96,21.2,28.94,-18.399999999999999,28.94,27.32,30.74,28.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,"23:00:00",23,23,28.04,26.060000000000002,24.98,19.939999999999998,28.94,-20.200000000000003,28.04,26.24,29.48,28.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-08",2,8,2018,"2018-02-08",4,0,1,24,19.939999999999998,26.060000000000002,24.98,24.98,19.939999999999998,28.04,-22,26.96,25.52,28.4,26.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"01:00:00",1,19.939999999999998,24.08,24.08,24.8,19.04,26.96,-22,26.060000000000002,23.9,27.68,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"02:00:00",2,17.059999999999999,24.08,23,21.02,17.96,26.060000000000002,-21.1,24.98,22.1,26.42,24.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"03:00:00",3,15.98,21.92,21.92,19.939999999999998,17.600000000000001,24.08,-20.200000000000003,24.08,20.479999999999997,24.98,23,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"04:00:00",4,15.98,21.02,21.02,19.04,17.600000000000001,24.08,-16.600000000000001,24.08,19.04,23.36,21.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"05:00:00",5,15.079999999999998,21.02,21.02,19.04,17.600000000000001,23,-15.700000000000003,23,18.5,22.64,21.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"06:00:00",6,14,19.939999999999998,21.02,17.96,15.8,21.92,-14.800000000000004,21.92,18.32,22.1,19.939999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"07:00:00",7,12.920000000000002,19.939999999999998,21.02,17.96,15.8,21.92,-13,21.92,18.5,21.560000000000002,19.939999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"08:00:00",8,12.2,19.939999999999998,21.02,18.5,12.920000000000002,23,-11.200000000000003,23,18.32,22.64,21.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"09:00:00",9,12.02,21.92,21.02,19.04,12.2,24.08,-11.200000000000003,24.08,18.14,24.08,21.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"10:00:00",10,14,23,21.92,21.02,12.2,24.98,-9.3999999999999986,24.98,19.22,25.34,24.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"11:00:00",11,15.079999999999998,23,24.98,21.92,15.98,26.96,-7.6000000000000014,26.96,20.299999999999997,26.42,24.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"12:00:00",12,15.98,26.060000000000002,26.96,23,17.96,28.94,-5.8000000000000043,28.94,21.560000000000002,28.4,26.060000000000002,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"13:00:00",13,17.059999999999999,28.04,28.04,24.08,19.04,30.02,-5.8000000000000043,30.92,22.64,29.48,28.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"14:00:00",14,19.04,28.04,28.94,24.08,19.939999999999998,30.92,-4,30.92,23.9,30.56,28.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"15:00:00",15,17.96,28.94,28.94,24.98,19.939999999999998,30.92,-2.2000000000000028,32,24.8,31.28,28.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"16:00:00",16,17.96,28.04,28.04,24.439999999999998,19.939999999999998,30.92,-4,30.92,25.34,30.02,28.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"17:00:00",17,15.98,28.04,26.96,24.08,17.96,30.02,-4,28.94,24.62,28.22,26.060000000000002,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"18:00:00",18,14,24.98,26.060000000000002,21.92,15.98,28.04,-4,28.04,22.46,26.6,24.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"19:00:00",19,12.920000000000002,24.08,24.98,21.02,14,26.96,-4,26.96,20.66,25.52,24.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"20:00:00",20,12.920000000000002,24.08,24.08,19.939999999999998,12.02,26.96,-5.8000000000000043,26.060000000000002,19.399999999999999,24.439999999999998,21.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"21:00:00",21,12.02,17.96,23,19.04,12.02,26.060000000000002,-5.8000000000000043,24.98,18.32,23.54,21.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"22:00:00",22,6.0799999999999983,21.02,19.939999999999998,17.059999999999999,10.039999999999999,24.98,-5.8000000000000043,24.08,17.600000000000001,23,21.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,"23:00:00",23,1.9400000000000013,21.02,17.059999999999999,17.96,8.0599999999999987,24.08,-5.8000000000000043,24.08,17.420000000000002,22.46,19.939999999999998,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-09",2,9,2018,"2018-02-09",5,0,1,24,-0.94000000000000483,19.939999999999998,15.98,17.059999999999999,5,23,-5.8000000000000043,23,16.52,21.38,19.939999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,{"$f":"$AO$4","v":2018},"2018-02-10",6,{"$f":"COUNTIF($AM$34:$AM$43,E966)","v":0},"01:00:00",1,-2.019999999999996,19.04,14,17.96,-2.9200000000000017,23,-5.8000000000000043,21.92,16.159999999999997,20.66,19.939999999999998,null,{"$f":"SUMPRODUCT($J$2:$T$2,J966:T966)","v":0},null,null,{"$f":"OR(B966<=$AO$14,B966>=$AN$14)*(F966<6)*(I966>$AN$15)*(I966<=$AO$15)*(G966<>1)","v":0},{"$f":"OR(B966<=$AO$14,B966>=$AN$14)*(Y966=0)","v":1},{"$f":"AND(B966>=$AN$24,B966<=$AO$24)*(F966<6)*(I966>$AN$25)*(I966<=$AO$25)*(G966<>1)","v":0},{"$f":"AND(B966>=$AN$24,B966<=$AO$24)*(AA966=0)","v":0},{"$f":"OR(B966<=$AO$19,B966>=$AN$19)*(F966<6)*(I966>$AN$20)*(I966<=$AO$20)","v":0},{"$f":"AND(B966>=$AN$29,B966<=$AO$29)*(F966<6)*(I966>$AN$30)*(I966<=$AO$30)","v":0},{"$f":"IF(OR(E966=$AM$34,E966=$AM$35,E966=$AM$36,E966=$AM$37,E966=$AM$38,E966=$AM$39,E966=$AM$40,E966=$AM$41,E966=$AM$42,E966=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E966>=$AM$47,E966<=$AN$47),AND(E966>=$AM$48,E966<=$AN$48),AND(E966>=$AM$49,E966<=$AN$49),AND(E966>=$AM$50,E966<=$AN$50),AND(E966>=$AM$51,E966<=$AN$51)),0,1)*AE966","v":1},{"$f":"(B966>=5)*(B966<=10)","v":0},{"$f":"1*OR(B966<=4,B966>=11)","v":1},{"$f":"LOOKUP(B966,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE966:AI966)*((F966<6)*(I966>$AO$7)*(I966<=$AP$7)+(F966=6)*(I966>$AO$8)*(I966<=$AP$8)+(F966>=7)*(I966>$AO$9)*(I966<=$AP$9))","v":0}]
["1977-02-10",2,10,2018,{"$f":"DATE(D967,B967,C967)","v":"2018-02-10"},{"$f":"WEEKDAY(E967,2)","v":6},0,"02:00:00",2,12.920000000000002,19.04,15.98,17.059999999999999,-2.9200000000000017,21.92,-5.8000000000000043,21.02,15.620000000000001,21.2,17.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,2018,"2018-02-10",6,0,"03:00:00",{"$f":"H968*24","v":3},10.940000000000001,17.96,15.98,17.96,-7.9600000000000009,21.92,-6.7000000000000028,21.02,15.440000000000001,20.479999999999997,15.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,2018,"2018-02-10",6,0,"04:00:00",4,12.920000000000002,17.96,17.96,17.96,-9.9400000000000048,21.02,-7.6000000000000014,21.02,15.440000000000001,20.66,17.059999999999999,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,2018,"2018-02-10",6,0,"05:00:00",5,10.940000000000001,17.96,17.059999999999999,17.420000000000002,-7.0600000000000023,19.939999999999998,-9.3999999999999986,21.02,15.620000000000001,19.759999999999998,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,2018,"2018-02-10",6,0,"06:00:00",6,10.940000000000001,17.059999999999999,17.059999999999999,17.059999999999999,-9.9400000000000048,19.939999999999998,-9.3999999999999986,20.479999999999997,15.440000000000001,19.399999999999999,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,2018,"2018-02-10",6,0,"07:00:00",7,10.039999999999999,17.96,19.04,15.98,-11.200000000000003,19.939999999999998,-9.3999999999999986,19.939999999999998,15.8,19.22,17.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,2018,"2018-02-10",6,0,"08:00:00",8,10.940000000000001,17.96,19.04,17.059999999999999,-9.0399999999999991,21.02,-9.3999999999999986,21.02,14.719999999999999,20.12,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,2018,"2018-02-10",6,0,"09:00:00",9,14,21.02,21.92,18.5,-0.94000000000000483,23,-9.3999999999999986,23,16.7,22.82,19.939999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,2018,"2018-02-10",6,0,"10:00:00",10,15.079999999999998,23,23,19.939999999999998,6.0799999999999983,24.98,-9.3999999999999986,26.060000000000002,18.68,25.52,24.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,2018,"2018-02-10",6,0,"11:00:00",11,17.059999999999999,23,24.98,23,14,28.04,-9.3999999999999986,28.04,20.299999999999997,27.32,24.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,2018,"2018-02-10",6,0,"12:00:00",12,19.939999999999998,26.96,28.04,24.08,17.96,30.02,-9.3999999999999986,30.02,21.92,29.12,26.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,2018,"2018-02-10",6,0,"13:00:00",13,21.02,28.04,28.94,24.98,24.98,30.92,-9.3999999999999986,30.92,24.08,31.28,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,2018,"2018-02-10",6,0,"14:00:00",14,21.92,28.04,30.02,26.060000000000002,26.060000000000002,32,-9.3999999999999986,33.08,26.060000000000002,31.46,28.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,2018,"2018-02-10",6,0,"15:00:00",15,23,30.92,30.92,28.04,30.02,33.08,-11.200000000000003,32.54,27.32,31.82,30.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,2018,"2018-02-10",6,0,"16:00:00",16,23,30.02,30.02,28.04,21.92,32.18,-11.200000000000003,33.08,27.5,30.74,28.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,2018,"2018-02-10",6,0,"17:00:00",17,21.02,30.02,28.04,26.060000000000002,24.08,30.92,-11.200000000000003,32.54,26.42,29.66,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,2018,"2018-02-10",6,0,"18:00:00",18,19.04,26.96,26.96,24.08,10.940000000000001,30.02,-12.100000000000001,30.02,24.8,27.86,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,2018,"2018-02-10",6,0,"19:00:00",19,17.96,26.060000000000002,26.060000000000002,21.92,10.940000000000001,28.94,-13,28.04,23.72,27.86,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,2018,"2018-02-10",6,0,"20:00:00",20,17.059999999999999,26.060000000000002,24.08,21.92,6.0799999999999983,28.04,-13,28.04,18.32,27.14,24.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,2018,"2018-02-10",6,0,"21:00:00",21,17.059999999999999,21.92,24.08,21.92,6.98,28.94,-11.200000000000003,26.96,22.1,26.42,24.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,2018,"2018-02-10",6,0,"22:00:00",22,15.079999999999998,24.08,24.08,21.92,3.9200000000000017,28.04,-11.200000000000003,26.96,20.84,25.88,24.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,2018,"2018-02-10",6,0,"23:00:00",23,12.920000000000002,24.08,23,21.92,3.019999999999996,28.04,-11.200000000000003,26.96,21.2,26.6,24.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-10",2,10,2018,"2018-02-10",6,0,1,24,15.079999999999998,24.08,24.08,19.939999999999998,6.0799999999999983,26.96,-11.200000000000003,26.96,20.12,26.6,24.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-11",2,11,2018,"2018-02-11",7,0,"01:00:00",1,15.079999999999998,23,24.08,19.939999999999998,6.0799999999999983,26.96,-11.200000000000003,26.96,19.22,25.88,24.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-11",2,11,2018,"2018-02-11",7,0,"02:00:00",2,14,23,24.08,19.04,6.0799999999999983,26.060000000000002,-11.200000000000003,26.96,17.059999999999999,25.34,23,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-11",2,11,2018,"2018-02-11",7,0,"03:00:00",3,12.920000000000002,21.92,23,17.96,6.98,26.060000000000002,-11.200000000000003,26.060000000000002,15.079999999999998,24.62,21.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-11",2,11,2018,"2018-02-11",7,0,"04:00:00",4,12.02,21.92,23,17.059999999999999,10.940000000000001,24.98,-12.100000000000001,26.060000000000002,16.88,23.9,21.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-11",2,11,2018,"2018-02-11",7,0,"05:00:00",5,6.0799999999999983,21.92,23,17.059999999999999,12.02,24.98,-13,24.98,17.240000000000002,23.36,21.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-11",2,11,2018,"2018-02-11",7,0,"06:00:00",6,3.019999999999996,21.02,23,15.98,12.920000000000002,24.08,-13,24.08,15.440000000000001,23.18,19.939999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-11",2,11,2018,"2018-02-11",7,0,"07:00:00",7,3.019999999999996,19.939999999999998,23,15.98,14,24.08,-11.200000000000003,24.08,16.7,22.64,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-11",2,11,2018,"2018-02-11",7,0,"08:00:00",8,6.98,19.939999999999998,23,17.059999999999999,15.98,24.08,-11.200000000000003,24.08,16.159999999999997,22.82,21.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-11",2,11,2018,"2018-02-11",7,0,"09:00:00",9,12.02,21.02,23,19.04,17.600000000000001,24.08,-11.200000000000003,24.98,17.600000000000001,23.54,23,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-11",2,11,2018,"2018-02-11",7,0,"10:00:00",10,14,24.08,24.08,20.479999999999997,19.399999999999999,26.060000000000002,-9.3999999999999986,26.060000000000002,19.939999999999998,26.42,24.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-11",2,11,2018,"2018-02-11",7,0,"11:00:00",11,15.98,24.08,24.98,21.92,19.399999999999999,28.94,-9.3999999999999986,28.04,21.740000000000002,28.58,26.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-11",2,11,2018,"2018-02-11",7,0,"16:00:00",16,17.96,30.02,30.92,26.060000000000002,30.02,32.36,-5.8000000000000043,33.08,26.42,30.92,30.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-11",2,11,2018,"2018-02-11",7,0,"21:00:00",21,6.98,21.02,23,17.059999999999999,30.2,24.98,-2.2000000000000028,24.98,16.7,23,21.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-12",2,12,2018,"2018-02-12",1,0,"06:00:00",6,-11.920000000000002,10.039999999999999,10.940000000000001,6.0799999999999983,32,14,1.3999999999999986,12.920000000000002,7.1599999999999966,13.459999999999997,10.039999999999999,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-12",2,12,2018,"2018-02-12",1,0,"14:00:00",14,19.04,19.939999999999998,19.939999999999998,19.04,37.22,21.92,5,21.2,19.939999999999998,21.38,19.939999999999998,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-12",2,12,2018,"2018-02-12",1,0,"20:00:00",20,17.96,17.96,19.399999999999999,15.8,35.06,21.02,1.3999999999999986,19.399999999999999,17.420000000000002,21.2,17.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-13",2,13,2018,"2018-02-13",2,0,"07:00:00",7,24.08,26.96,28.04,26.6,21.92,32,-7.6000000000000014,32.18,28.04,33.799999999999997,30.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-13",2,13,2018,"2018-02-13",2,0,"10:00:00",10,24.98,28.94,28.4,28.4,33.979999999999997,30.92,-2.2000000000000028,30.92,31.1,32.54,28.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-13",2,13,2018,"2018-02-13",2,0,"16:00:00",16,30.02,35.6,33.979999999999997,33.979999999999997,34.340000000000003,37.94,8.5999999999999979,38.840000000000003,32,38.480000000000004,37.22,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-13",2,13,2018,"2018-02-13",2,0,1,24,24.98,28.04,28.04,26.96,24.98,30.02,15.8,28.94,27.14,30.56,28.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-14",2,14,2018,"2018-02-14",3,0,"09:00:00",9,21.02,26.96,26.96,26.060000000000002,28.04,30.02,23,28.4,24.439999999999998,29.12,28.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-14",2,14,2018,"2018-02-14",3,0,"17:00:00",17,26.060000000000002,33.979999999999997,34.159999999999997,32,35.06,35.96,39.92,37.04,32.9,34.520000000000003,33.619999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-15",2,15,2018,"2018-02-15",4,0,"02:00:00",2,1.9400000000000013,21.02,21.92,17.96,21.92,26.060000000000002,-9.3999999999999986,24.08,16.159999999999997,26.24,21.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-15",2,15,2018,"2018-02-15",4,0,"07:00:00",7,17.059999999999999,24.08,32,24.98,24.98,28.04,-14.800000000000004,24.98,18.86,32.18,23,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-15",2,15,2018,"2018-02-15",4,0,"19:00:00",19,33.979999999999997,42.26,40.82,37.94,38.659999999999997,44.6,1.3999999999999986,45.14,35.42,42.8,42.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-15",2,15,2018,"2018-02-15",4,0,"21:00:00",21,33.979999999999997,40.82,40.28,38.659999999999997,36.14,42.620000000000005,5,43.16,37.04,42.08,42.26,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-16",2,16,2018,"2018-02-16",5,0,"04:00:00",4,28.94,32.18,30.92,26.96,30.02,33.979999999999997,6.8000000000000007,34.880000000000003,30.02,35.6,34.159999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-16",2,16,2018,"2018-02-16",5,0,"18:00:00",18,21.92,32.72,32,29.48,28.94,35.06,14.54,35.06,31.1,35.06,33.979999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-16",2,16,2018,"2018-02-16",5,0,"21:00:00",21,19.04,26.060000000000002,28.04,23,24.98,30.02,15.8,30.92,23.18,30.2,28.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-17",2,17,2018,"2018-02-17",6,0,"04:00:00",4,12.02,17.059999999999999,17.96,17.059999999999999,19.04,21.02,26.6,19.04,16.52,21.02,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-17",2,17,2018,"2018-02-17",6,0,"14:00:00",14,24.08,30.02,30.92,28.04,17.96,33.08,42.980000000000004,35.06,27.5,30.02,30.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-17",2,17,2018,"2018-02-17",6,0,"18:00:00",18,19.04,26.96,28.04,26.96,15.98,32,42.980000000000004,28.04,26.060000000000002,27.32,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-18",2,18,2018,"2018-02-18",7,0,"07:00:00",7,10.039999999999999,24.98,26.6,19.399999999999999,10.940000000000001,26.96,34.700000000000003,26.060000000000002,17.600000000000001,26.6,23,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-18",2,18,2018,"2018-02-18",7,0,"15:00:00",15,21.92,23,28.4,21.2,28.04,26.060000000000002,43.7,28.4,25.34,23,23,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-18",2,18,2018,"2018-02-18",7,0,"16:00:00",16,21.92,24.08,28.94,26.6,26.96,26.060000000000002,46.22,28.4,25.7,23,23,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-19",2,19,2018,"2018-02-19",1,1,"05:00:00",5,5,12.02,1.9400000000000013,8.9599999999999973,12.920000000000002,12.920000000000002,6.8000000000000007,14,10.399999999999999,14.18,12.920000000000002,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1977-02-19",2,19,2018,"2018-02-19",1,1,"09:00:00",9,8.0599999999999987,12.920000000000002,15.98,15.079999999999998,17.059999999999999,17.059999999999999,-2.2000000000000028,17.96,10.399999999999999,16.7,15.98,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1977-02-19",2,19,2018,"2018-02-19",1,1,"15:00:00",15,15.98,26.060000000000002,30.02,24.08,37.94,28.94,-4,28.94,21.92,27.32,26.060000000000002,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1977-02-20",2,20,2018,"2018-02-20",2,0,"02:00:00",2,10.940000000000001,8.0599999999999987,3.9200000000000017,6.98,33.799999999999997,15.079999999999998,-4,6.98,11.84,15.98,12.920000000000002,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["1977-02-20",2,20,2018,"2018-02-20",2,0,"12:00:00",12,21.02,23,24.98,26.060000000000002,30.02,26.96,5,30.92,22.64,24.98,24.98,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1977-02-20",2,20,2018,"2018-02-20",2,0,"19:00:00",{"$f":"H1224*24","v":19},14,26.060000000000002,24.08,23,26.060000000000002,28.04,8.5999999999999979,28.04,26.060000000000002,27.14,26.060000000000002,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1977-02-21",2,21,2018,"2018-02-21",3,0,"02:00:00",2,15.98,21.92,21.2,19.399999999999999,23,23,3.1999999999999993,23,20.84,23,21.92,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["1977-02-21",2,21,2018,"2018-02-21",3,0,"04:00:00",4,19.939999999999998,21.92,23,19.399999999999999,21.02,24.08,-0.39999999999999858,24.8,20.66,24.8,21.92,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["1977-02-21",2,21,2018,"2018-02-21",3,0,"16:00:00",16,35.06,42.08,42.08,39.92,24.08,46.04,-11.200000000000003,44.06,37.22,43.34,42.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1977-02-21",2,21,2018,"2018-02-21",3,0,"21:00:00",21,32.72,37.94,39.019999999999996,37.94,21.2,41,-16.600000000000001,39.92,37.94,39.92,39.92,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1977-02-22",2,22,2018,"2018-02-22",4,0,"06:00:00",6,24.8,33.979999999999997,33.44,32.18,26.060000000000002,33.26,-0.39999999999999858,33.979999999999997,32,34.159999999999997,33.619999999999997,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["1977-02-22",2,22,2018,"2018-02-22",4,0,"15:00:00",15,30.92,37.22,37.94,34.700000000000003,34.880000000000003,39.56,6.8000000000000007,42.08,32,40.82,39.92,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1977-02-22",2,22,2018,"2018-02-22",4,0,"23:00:00",23,12.02,26.060000000000002,21.92,24.08,30.92,32,5,26.96,27.68,30.2,28.94,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1977-02-23",2,23,2018,"2018-02-23",5,0,"05:00:00",5,-0.94000000000000483,19.939999999999998,15.98,17.059999999999999,32,24.98,4.0999999999999979,21.02,14.719999999999999,23,21.92,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["1977-02-23",2,23,2018,"2018-02-23",5,0,"16:00:00",16,35.06,36.32,37.04,34.880000000000003,32.18,37.58,10.399999999999999,37.94,33.08,36.14,36.5,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1977-02-23",2,23,2018,"2018-02-23",5,0,"22:00:00",22,17.96,24.08,28.04,21.92,32,28.04,11.3,28.04,21.740000000000002,29.48,28.04,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1977-02-24",2,24,2018,"2018-02-24",6,0,"01:00:00",1,15.079999999999998,26.96,28.04,21.92,32,30.02,14,28.94,21.2,30.2,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-24",2,24,2018,"2018-02-24",6,0,"12:00:00",12,33.08,33.979999999999997,33.44,32.9,35.6,35.96,15.8,37.04,32.18,37.4,35.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-24",2,24,2018,"2018-02-24",6,0,"18:00:00",18,30.92,35.96,35.6,34.340000000000003,33.799999999999997,39.019999999999996,15.8,37.94,32.9,41,40.28,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-25",2,25,2018,"2018-02-25",7,0,"02:00:00",2,33.08,35.96,34.700000000000003,34.700000000000003,32,37.94,10.399999999999999,37.04,33.44,36.14,35.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-25",2,25,2018,"2018-02-25",7,0,"11:00:00",11,28.4,32,30.02,30.2,33.26,33.08,14,33.44,31.82,33.619999999999997,32.72,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-25",2,25,2018,"2018-02-25",7,0,"16:00:00",16,21.02,30.02,28.94,28.94,34.340000000000003,32.36,10.399999999999999,32.72,28.4,32.72,30.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-26",2,26,2018,"2018-02-26",1,0,"04:00:00",4,8.0599999999999987,17.96,19.939999999999998,14,30.2,21.92,-5.8000000000000043,21.92,15.620000000000001,20.66,17.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-26",2,26,2018,"2018-02-26",1,0,"09:00:00",9,6.0799999999999983,15.079999999999998,17.059999999999999,14,30.2,19.04,-9.3999999999999986,19.939999999999998,10.940000000000001,18.14,15.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-26",2,26,2018,"2018-02-26",1,0,"13:00:00",13,10.039999999999999,19.939999999999998,21.02,17.96,37.04,24.08,-5.8000000000000043,24.98,15.440000000000001,23.18,19.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-26",2,26,2018,"2018-02-26",1,0,"23:00:00",23,1.9400000000000013,10.940000000000001,14,5,35.06,14,1.3999999999999986,15.079999999999998,6.8000000000000007,12.379999999999999,10.039999999999999,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-27",2,27,2018,"2018-02-27",2,0,"06:00:00",6,-7.9600000000000009,3.019999999999996,5,-3.9999999999999147E-2,33.799999999999997,6.98,5,8.0599999999999987,0.5,6.259999999999998,3.9200000000000017,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-27",2,27,2018,"2018-02-27",2,0,"13:00:00",13,8.9599999999999973,12.920000000000002,14,14,33.26,17.059999999999999,8.5999999999999979,17.059999999999999,9.5,15.98,15.079999999999998,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-27",2,27,2018,"2018-02-27",2,0,"23:00:00",23,-3.9999999999999147E-2,12.02,14,10.399999999999999,32,15.079999999999998,6.8000000000000007,15.8,9.5,15.8,12.920000000000002,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-28",2,28,2018,"2018-02-28",3,0,"03:00:00",3,-5.980000000000004,12.2,12.2,10.399999999999999,32,14,15.8,14,8.9599999999999973,13.82,12.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-28",2,28,2018,"2018-02-28",3,0,"16:00:00",16,21.02,26.96,26.060000000000002,28.94,37.94,30.02,24.8,32,26.42,29.3,28.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1977-02-28",2,28,{"$f":"$AO$4","v":2018},"2018-02-28",3,{"$f":"COUNTIF($AM$34:$AM$43,E1414)","v":0},"17:00:00",17,19.939999999999998,26.96,26.060000000000002,26.060000000000002,39.019999999999996,28.04,23,28.94,25.88,29.12,28.04,null,{"$f":"SUMPRODUCT($J$2:$T$2,J1414:T1414)","v":0},null,null,{"$f":"OR(B1414<=$AO$14,B1414>=$AN$14)*(F1414<6)*(I1414>$AN$15)*(I1414<=$AO$15)*(G1414<>1)","v":1},{"$f":"OR(B1414<=$AO$14,B1414>=$AN$14)*(Y1414=0)","v":0},{"$f":"AND(B1414>=$AN$24,B1414<=$AO$24)*(F1414<6)*(I1414>$AN$25)*(I1414<=$AO$25)*(G1414<>1)","v":0},{"$f":"AND(B1414>=$AN$24,B1414<=$AO$24)*(AA1414=0)","v":0},{"$f":"OR(B1414<=$AO$19,B1414>=$AN$19)*(F1414<6)*(I1414>$AN$20)*(I1414<=$AO$20)","v":0},{"$f":"AND(B1414>=$AN$29,B1414<=$AO$29)*(F1414<6)*(I1414>$AN$30)*(I1414<=$AO$30)","v":0},{"$f":"IF(OR(E1414=$AM$34,E1414=$AM$35,E1414=$AM$36,E1414=$AM$37,E1414=$AM$38,E1414=$AM$39,E1414=$AM$40,E1414=$AM$41,E1414=$AM$42,E1414=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E1414>=$AM$47,E1414<=$AN$47),AND(E1414>=$AM$48,E1414<=$AN$48),AND(E1414>=$AM$49,E1414<=$AN$49),AND(E1414>=$AM$50,E1414<=$AN$50),AND(E1414>=$AM$51,E1414<=$AN$51)),0,1)*AE1414","v":1},{"$f":"(B1414>=5)*(B1414<=10)","v":0},{"$f":"1*OR(B1414<=4,B1414>=11)","v":1},{"$f":"LOOKUP(B1414,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE1414:AI1414)*((F1414<6)*(I1414>$AO$7)*(I1414<=$AP$7)+(F1414=6)*(I1414>$AO$8)*(I1414<=$AP$8)+(F1414>=7)*(I1414>$AO$9)*(I1414<=$AP$9))","v":0}]
["1981-03-01",3,1,2018,"2018-03-01",4,0,"01:00:00",1,-2.2000000000000028,32.18,34.700000000000003,31.64,14.18,33.44,21.02,22.82,33.619999999999997,33.619999999999997,32.36,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-01",3,1,2018,"2018-03-01",4,0,"10:00:00",10,10.940000000000001,34.880000000000003,33.26,33.799999999999997,17.96,35.42,20.299999999999997,21.02,36.5,35.96,35.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-01",3,1,2018,"2018-03-01",4,0,"18:00:00",18,24.98,35.06,33.44,34.340000000000003,28.04,35.96,19.399999999999999,25.16,32.18,35.96,35.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-01",3,1,2018,"2018-03-01",4,0,1,24,19.04,32.36,33.799999999999997,32.18,26.96,33.26,17.600000000000001,24.8,32.36,35.24,34.520000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-02",3,2,2018,"2018-03-02",5,0,"11:00:00",11,15.8,34.159999999999997,32.18,32.9,19.399999999999999,35.6,10.399999999999999,21.2,34.880000000000003,35.6,35.42,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-02",3,2,2018,"2018-03-02",5,0,"14:00:00",14,17.600000000000001,36.32,33.44,35.06,21.2,38.480000000000004,5,23,32.18,39.200000000000003,38.659999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-03",3,3,2018,"2018-03-03",6,0,"04:00:00",4,6.98,28.04,28.4,28.4,12.920000000000002,30.02,-4,15.079999999999998,28.04,30.2,30.2,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-03",3,3,2018,"2018-03-03",6,0,"11:00:00",{"$f":"H1480*24","v":11},10.940000000000001,28.94,28.4,30.2,17.059999999999999,30.2,-4,19.04,30.2,33.799999999999997,33.26,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-03",3,3,2018,"2018-03-03",6,0,"13:00:00",13,15.079999999999998,33.799999999999997,32,33.44,21.92,35.6,-4,22.1,34.340000000000003,36.14,35.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-03",3,3,2018,"2018-03-03",6,0,"21:00:00",21,6.98,32,32,32,12.920000000000002,33.26,-11.200000000000003,16.159999999999997,31.1,35.42,33.979999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-04",3,4,2018,"2018-03-04",7,0,"06:00:00",6,-13,26.96,26.6,26.6,-3.9999999999999147E-2,30.2,-15.700000000000003,2.1199999999999974,26.6,29.3,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-04",3,4,2018,"2018-03-04",7,0,"15:00:00",15,19.939999999999998,32.18,32.54,32,30.92,35.96,-5.8000000000000043,30.02,30.74,34.340000000000003,32.36,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-04",3,4,2018,"2018-03-04",7,0,"20:00:00",20,14,30.02,32,28.4,19.04,32,-7.6000000000000014,22.1,26.42,31.28,30.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-05",3,5,2018,"2018-03-05",1,0,"08:00:00",8,-5.0800000000000054,28.04,28.4,28.4,10.039999999999999,32,-5.8000000000000043,12.02,28.94,34.159999999999997,32,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-05",3,5,2018,"2018-03-05",1,0,"10:00:00",10,17.96,33.979999999999997,32,33.799999999999997,21.02,33.619999999999997,-4,31.1,30.92,35.24,34.340000000000003,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-05",3,5,2018,"2018-03-05",1,0,"17:00:00",17,28.94,42.08,39.380000000000003,39.200000000000003,33.26,42.08,10.399999999999999,37.4,40.1,39.380000000000003,41,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-06",3,6,2018,"2018-03-06",2,0,"07:00:00",7,24.8,33.799999999999997,33.26,32.9,35.06,34.880000000000003,23,36.86,32,35.6,35.24,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-06",3,6,2018,"2018-03-06",2,0,"10:00:00",10,26.6,34.340000000000003,34.159999999999997,32.36,33.799999999999997,35.6,28.4,41,34.700000000000003,36.68,35.42,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-06",3,6,2018,"2018-03-06",2,0,"21:00:00",21,37.04,32.9,32.54,32,42.980000000000004,33.979999999999997,36.32,45.86,33.44,35.42,33.799999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-07",3,7,2018,"2018-03-07",3,0,"03:00:00",3,39.92,30.02,32,30.2,41,33.26,39.74,42.620000000000005,32.54,34.700000000000003,33.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-07",3,7,2018,"2018-03-07",3,0,"11:00:00",11,41,32,33.799999999999997,32,44.6,32.36,39.74,53.96,34.159999999999997,33.08,33.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-07",3,7,2018,"2018-03-07",3,0,"20:00:00",20,37.76,30.02,33.799999999999997,32,42.980000000000004,30.2,37.4,43.879999999999995,31.82,33.44,32.18,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-08",3,8,2018,"2018-03-08",4,0,"04:00:00",4,33.799999999999997,30.2,30.2,32,35.78,30.2,33.08,39.92,31.46,30.2,30.2,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-08",3,8,2018,"2018-03-08",4,0,"05:00:00",5,32.54,30.02,30.2,28.4,35.42,30.2,32.18,42.980000000000004,32,29.48,28.4,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-08",3,8,2018,{"$f":"DATE(D1607,B1607,C1607)","v":"2018-03-08"},{"$f":"WEEKDAY(E1607,2)","v":4},0,"18:00:00",18,33.979999999999997,39.92,39.200000000000003,39.74,40.28,41,33.799999999999997,50,38.299999999999997,41.18,41,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-08",3,8,2018,"2018-03-08",4,0,"22:00:00",22,26.96,36.5,35.06,35.6,36.32,37.76,24.8,42.980000000000004,33.26,40.46,38.840000000000003,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-09",3,9,2018,"2018-03-09",5,0,"08:00:00",8,26.96,17.059999999999999,19.399999999999999,21.2,33.799999999999997,32,23,32,31.1,36.14,35.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-09",3,9,2018,"2018-03-09",5,0,"15:00:00",15,28.4,46.04,47.120000000000005,44.24,33.799999999999997,45.86,24.8,30.2,44.24,41.54,43.52,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-09",3,9,2018,"2018-03-09",5,0,"22:00:00",22,24.8,32.18,30.2,28.4,33.08,30.92,21.2,30.02,29.12,28.4,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-10",3,10,2018,"2018-03-10",6,0,"08:00:00",8,17.059999999999999,19.04,19.399999999999999,21.2,30.2,28.94,28.4,26.060000000000002,20.66,28.759999999999998,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-10",3,10,2018,"2018-03-10",6,0,"15:00:00",15,37.4,42.08,42.620000000000005,40.46,37.4,41.36,35.96,39.56,40.64,37.22,41,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-10",3,10,2018,"2018-03-10",6,0,"17:00:00",17,36.86,42.08,43.16,40.46,37.94,40.82,35.06,39.74,40.82,38.119999999999997,37.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-11",3,11,2018,"2018-03-11",7,0,"05:00:00",5,33.08,32.18,33.619999999999997,30.2,32.54,33.08,19.399999999999999,34.880000000000003,31.82,33.979999999999997,32.72,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-11",3,11,2018,{"$f":"DATE(D1671,B1671,C1671)","v":"2018-03-11"},{"$f":"WEEKDAY(E1671,2)","v":7},0,"10:00:00",10,35.06,37.94,37.4,35.6,34.880000000000003,37.58,21.2,37.4,36.32,36.86,36.5,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-11",3,11,2018,"2018-03-11",7,0,"19:00:00",19,42.08,44.96,41,41.36,43.16,45.14,39.56,44.96,40.1,41.9,42.980000000000004,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-12",3,12,2018,"2018-03-12",1,0,"03:00:00",3,19.04,41,44.6,38.480000000000004,28.94,44.06,-4,34.159999999999997,37.58,40.64,39.200000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-12",3,12,2018,"2018-03-12",1,0,"09:00:00",9,17.059999999999999,41,42.8,39.200000000000003,26.060000000000002,44.6,-11.200000000000003,29.12,38.840000000000003,45.14,42.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-12",3,12,2018,"2018-03-12",1,0,"20:00:00",20,14,48.2,48.2,46.04,24.08,53.6,-10.300000000000004,29.12,42.8,45.68,46.4,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-13",3,13,2018,"2018-03-13",2,0,"02:00:00",2,1.0399999999999991,41,36.5,39.200000000000003,15.98,42.08,-12.100000000000001,22.1,38.659999999999997,44.6,44.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-13",3,13,2018,"2018-03-13",2,0,"05:00:00",5,-4,37.04,33.619999999999997,37.4,10.940000000000001,38.119999999999997,-13,19.04,35.06,39.56,37.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-13",3,13,2018,"2018-03-13",2,0,"16:00:00",16,28.04,42.980000000000004,44.6,41.72,35.96,48.019999999999996,1.3999999999999986,35.96,39.56,49.46,46.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-13",3,13,2018,"2018-03-13",2,0,"22:00:00",22,17.96,34.700000000000003,33.619999999999997,28.4,26.96,37.04,3.1999999999999993,27.14,32,38.299999999999997,35.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-14",3,14,2018,"2018-03-14",3,0,"06:00:00",6,3.019999999999996,28.94,28.4,30.2,15.98,32,1.3999999999999986,22.1,31.1,29.48,32,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-14",3,14,2018,"2018-03-14",3,0,"15:00:00",15,34.520000000000003,33.08,28.4,32,42.620000000000005,32.18,34.520000000000003,50.900000000000006,31.1,34.520000000000003,33.26,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-14",3,14,2018,"2018-03-14",3,0,1,24,17.96,19.04,21.2,17.600000000000001,26.060000000000002,21.02,14,35.42,17.96,20.299999999999997,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-15",3,15,2018,"2018-03-15",4,0,"05:00:00",5,17.96,15.98,17.600000000000001,15.8,21.92,19.04,15.8,25.16,16.159999999999997,17.78,17.059999999999999,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-15",3,15,2018,"2018-03-15",4,0,"17:00:00",17,39.380000000000003,35.96,34.159999999999997,32.9,47.66,37.04,39.200000000000003,57.92,31.46,36.86,36.5,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-15",3,15,2018,"2018-03-15",4,0,"19:00:00",19,33.619999999999997,32.9,32.36,30.2,39.74,34.520000000000003,33.799999999999997,47.84,31.46,35.78,33.979999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-16",3,16,2018,"2018-03-16",5,0,"02:00:00",2,21.02,26.96,28.4,26.6,26.060000000000002,30.02,17.600000000000001,32.18,26.96,27.5,26.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-16",3,16,2018,"2018-03-16",5,0,"09:00:00",9,30.92,28.04,24.8,24.8,35.96,28.94,17.600000000000001,32.54,23.54,30.38,28.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-16",3,16,2018,"2018-03-16",5,0,"19:00:00",{"$f":"H1800*24","v":19},33.26,30.02,33.799999999999997,30.2,36.5,32.36,19.399999999999999,35.06,29.3,33.26,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-17",3,17,2018,"2018-03-17",6,0,"02:00:00",2,23,21.02,21.2,17.600000000000001,30.02,24.98,20.299999999999997,28.04,19.22,22.64,24.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-17",3,17,2018,"2018-03-17",6,0,"12:00:00",12,39.019999999999996,33.08,32,28.4,44.42,33.44,38.480000000000004,42.620000000000005,25.88,32.54,30.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-17",3,17,2018,"2018-03-17",6,0,"16:00:00",16,42.08,30.92,32,28.4,49.64,33.08,41,51.980000000000004,27.5,32.36,30.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-18",3,18,2018,"2018-03-18",7,0,"05:00:00",5,21.92,14,12.2,12.2,32,17.059999999999999,26.6,28.04,10.399999999999999,15.98,10.940000000000001,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-18",3,18,2018,"2018-03-18",7,0,"06:00:00",6,23,8.0599999999999987,10.399999999999999,10.399999999999999,33.619999999999997,17.059999999999999,26.6,33.44,9.14,14.719999999999999,10.940000000000001,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-18",3,18,2018,"2018-03-18",7,0,"14:00:00",14,42.980000000000004,33.979999999999997,33.08,32,51.44,35.06,46.22,62.96,33.799999999999997,32.9,33.26,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-19",3,19,2018,"2018-03-19",1,0,"03:00:00",3,42.08,26.6,26.6,26.6,41,28.04,41.18,48.92,27.14,30.02,28.4,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-19",3,19,2018,"2018-03-19",1,0,"07:00:00",7,39.92,28.4,28.4,26.6,37.04,30.2,37.58,43.879999999999995,27.68,31.82,30.2,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-19",3,19,2018,"2018-03-19",1,0,"13:00:00",13,38.480000000000004,32,33.799999999999997,30.2,45.14,32.9,38.119999999999997,43.879999999999995,31.1,33.619999999999997,32.54,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-19",3,19,2018,"2018-03-19",1,0,1,24,24.08,24.8,26.6,24.8,30.02,24.8,5,36.86,25.7,24.8,24.8,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-20",3,20,2018,"2018-03-20",2,0,"03:00:00",3,19.04,23,23,21.2,28.04,24.98,12.2,34.159999999999997,24.439999999999998,24.08,24.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-20",3,20,2018,"2018-03-20",2,0,"17:00:00",17,32,34.159999999999997,32.72,33.08,35.06,35.96,6.8000000000000007,41,34.340000000000003,35.6,34.880000000000003,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-20",3,20,2018,"2018-03-20",2,0,1,24,14,24.98,23,28.4,24.08,28.04,8.5999999999999979,24.08,28.94,29.48,26.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-21",3,21,2018,"2018-03-21",3,0,"02:00:00",2,10.039999999999999,24.08,17.600000000000001,24.8,19.04,24.98,8.5999999999999979,23,19.759999999999998,25.34,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-21",3,21,2018,"2018-03-21",3,0,"14:00:00",14,32,35.06,32.72,33.08,40.1,35.42,32.18,42.980000000000004,35.96,34.700000000000003,34.880000000000003,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-21",3,21,2018,"2018-03-21",3,0,"19:00:00",19,28.94,36.5,33.799999999999997,34.700000000000003,35.96,35.96,12.2,37.94,33.979999999999997,33.08,33.44,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-21",3,21,2018,"2018-03-21",3,0,1,24,23,21.02,24.8,23,26.96,28.04,10.399999999999999,28.04,28.04,28.4,28.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-22",3,22,2018,"2018-03-22",4,0,"12:00:00",12,33.08,32.9,33.799999999999997,33.799999999999997,38.299999999999997,34.340000000000003,8.5999999999999979,45.86,33.08,35.06,34.700000000000003,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-22",3,22,2018,"2018-03-22",4,0,"21:00:00",21,21.92,32,30.2,30.2,28.94,33.08,-2.2000000000000028,33.799999999999997,31.1,34.159999999999997,32.36,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-23",3,23,2018,"2018-03-23",5,0,"05:00:00",5,10.940000000000001,24.08,24.8,24.8,19.939999999999998,28.04,-11.200000000000003,23,27.68,27.14,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-23",3,23,2018,"2018-03-23",5,0,"11:00:00",11,17.059999999999999,34.700000000000003,33.44,33.26,26.060000000000002,35.96,-9.3999999999999986,28.04,32.18,36.86,35.6,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-23",3,23,2018,"2018-03-23",5,0,"14:00:00",14,19.04,37.04,36.32,37.4,30.02,39.92,-7.6000000000000014,32,34.340000000000003,39.56,39.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-24",3,24,2018,"2018-03-24",6,0,"01:00:00",1,15.079999999999998,32.54,33.799999999999997,32,15.98,32.72,-2.2000000000000028,22.1,32.9,34.340000000000003,33.979999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-24",3,24,2018,"2018-03-24",6,0,"07:00:00",7,21.92,33.08,32,32,24.08,35.06,1.3999999999999986,27.14,32,32.54,32.18,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-24",3,24,2018,"2018-03-24",6,0,"15:00:00",15,33.44,39.92,39.200000000000003,39.019999999999996,40.82,41.18,32.9,44.96,36.5,43.879999999999995,44.06,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-24",3,24,2018,"2018-03-24",6,0,1,24,21.02,24.98,26.6,26.6,21.02,33.979999999999997,15.8,32.36,26.24,32.54,30.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-25",3,25,2018,"2018-03-25",7,0,"09:00:00",9,30.92,35.96,28.4,28.4,33.979999999999997,32.18,19.399999999999999,34.700000000000003,25.7,33.26,32.18,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-25",3,25,2018,"2018-03-25",7,0,"14:00:00",14,41.9,42.08,41,39.200000000000003,51.980000000000004,41.36,43.16,51.980000000000004,40.1,38.480000000000004,41,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-25",3,25,2018,"2018-03-25",7,0,"18:00:00",18,40.64,37.94,37.76,37.58,42.980000000000004,38.299999999999997,40.28,45.86,37.4,37.58,37.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-26",3,26,2018,"2018-03-26",1,0,"07:00:00",7,21.92,32.36,33.44,30.2,28.04,33.799999999999997,31.1,29.12,31.46,33.619999999999997,32.54,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-26",3,26,2018,"2018-03-26",1,0,"11:00:00",11,40.46,39.92,39.200000000000003,39.200000000000003,48.019999999999996,42.980000000000004,40.1,51.980000000000004,38.299999999999997,40.82,41.18,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-26",3,26,2018,"2018-03-26",1,0,"21:00:00",21,35.96,38.299999999999997,34.340000000000003,37.94,39.200000000000003,41,35.6,42.8,35.96,40.82,40.1,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-27",3,27,2018,"2018-03-27",2,0,"04:00:00",4,32.72,24.08,23,28.4,35.96,32.54,32.36,38.299999999999997,31.64,33.26,33.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-27",3,27,2018,"2018-03-27",2,0,"11:00:00",{"$f":"H2056*24","v":11},39.200000000000003,48.019999999999996,44.6,43.34,42.8,50,39.380000000000003,46.4,42.980000000000004,45.32,48.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-27",3,27,2018,"2018-03-27",2,0,"21:00:00",21,35.24,39.019999999999996,39.200000000000003,39.200000000000003,42.980000000000004,42.08,32,45.86,37.76,39.200000000000003,39.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-28",3,28,2018,"2018-03-28",3,0,"01:00:00",1,26.060000000000002,37.76,35.6,35.6,35.96,37.94,32.18,39.200000000000003,36.5,37.22,37.4,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-28",3,28,2018,"2018-03-28",3,0,"06:00:00",6,26.060000000000002,36.14,35.6,34.700000000000003,36.68,37.04,33.08,39.92,33.979999999999997,36.86,35.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-28",3,28,2018,"2018-03-28",3,0,"15:00:00",15,46.76,44.96,48.2,42.8,56.66,46.94,44.78,59,42.8,47.120000000000005,45.5,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-28",3,28,2018,"2018-03-28",3,0,"23:00:00",23,36.32,39.56,39.380000000000003,38.299999999999997,42.08,39.56,36.32,41.9,35.24,38.659999999999997,39.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-29",3,29,2018,"2018-03-29",4,0,"08:00:00",8,33.799999999999997,41,39.019999999999996,39.200000000000003,36.14,42.980000000000004,33.979999999999997,37.4,38.480000000000004,41,41,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-29",3,29,2018,"2018-03-29",4,0,"16:00:00",16,35.24,50,50,44.6,37.76,51.980000000000004,34.700000000000003,41,44.06,53.6,50,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-29",3,29,2018,"2018-03-29",4,0,"22:00:00",22,36.14,41.54,41,39.200000000000003,37.94,44.06,35.6,41,38.659999999999997,42.8,42.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-30",3,30,2018,"2018-03-30",5,0,"09:00:00",9,35.42,41.18,40.1,38.840000000000003,38.299999999999997,42.8,35.24,42.8,37.22,42.08,42.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-30",3,30,2018,"2018-03-30",5,0,"12:00:00",12,37.94,51.980000000000004,48.2,48.2,36.86,53.06,37.04,41,48.2,53.06,53.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-30",3,30,2018,"2018-03-30",5,0,"18:00:00",18,35.06,48.019999999999996,47.480000000000004,44.24,39.74,51.980000000000004,34.700000000000003,44.6,42.8,50,48.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-31",3,31,2018,"2018-03-31",6,0,"02:00:00",2,32.9,26.060000000000002,33.799999999999997,28.4,35.96,30.92,32.54,39.92,24.62,34.880000000000003,32.9,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-31",3,31,2018,"2018-03-31",6,0,"11:00:00",11,34.520000000000003,48.92,48.2,44.6,39.380000000000003,53.06,34.520000000000003,50.900000000000006,46.4,51.08,51.980000000000004,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1981-03-31",3,31,2018,"2018-03-31",6,0,"19:00:00",19,31.28,48.56,43.879999999999995,46.76,37.94,48.2,32.54,42.26,45.5,49.28,48.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-01",4,1,2018,"2018-04-01",7,0,"04:00:00",4,26.060000000000002,27.5,21.2,26.24,35.6,29.3,0.5,28.759999999999998,26.24,26.42,25.7,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-01",4,1,2018,"2018-04-01",7,0,"09:00:00",9,33.979999999999997,35.06,32,32,37.22,32.72,-0.39999999999999858,33.26,30.02,35.6,35.06,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-01",4,1,2018,"2018-04-01",7,0,"21:00:00",21,34.520000000000003,34.520000000000003,32.36,30.2,32,35.96,1.3999999999999986,36.5,29.3,34.880000000000003,33.26,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-01",4,1,2018,"2018-04-01",7,0,"23:00:00",23,24.98,24.98,26.6,28.4,30.02,28.94,2.6599999999999966,27.14,25.7,29.12,26.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-02",4,2,2018,"2018-04-02",1,0,"06:00:00",6,19.04,19.939999999999998,19.399999999999999,21.2,26.060000000000002,24.08,8.5999999999999979,23,18.32,26.78,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-02",4,2,2018,"2018-04-02",1,0,"20:00:00",20,35.96,53.06,51.8,46.22,30.92,53.96,36.68,52.879999999999995,44.96,47.3,44.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-02",4,2,2018,"2018-04-02",1,0,"23:00:00",23,26.96,50,46.4,45.68,30.02,51.08,38.840000000000003,51.980000000000004,43.879999999999995,47.480000000000004,48.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-03",4,3,2018,"2018-04-03",2,0,"06:00:00",6,32,46.94,47.480000000000004,46.4,26.060000000000002,51.08,40.1,46.94,43.7,48.019999999999996,42.980000000000004,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-03",4,3,2018,"2018-04-03",2,0,"16:00:00",16,34.520000000000003,62.96,60.8,62.6,39.74,64.039999999999992,50.540000000000006,63.86,53.24,62.6,60.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-03",4,3,2018,"2018-04-03",2,0,"20:00:00",20,30.02,55.040000000000006,48.379999999999995,48.2,33.799999999999997,55.94,41.54,48.92,51.44,45.32,46.76,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-04",4,4,{"$f":"$AO$4","v":2018},"2018-04-04",3,{"$f":"COUNTIF($AM$34:$AM$43,E2246)","v":0},"09:00:00",9,33.979999999999997,44.06,42.8,39.200000000000003,37.04,46.04,35.96,44.6,38.480000000000004,42.44,44.6,null,{"$f":"SUMPRODUCT($J$2:$T$2,J2246:T2246)","v":0},null,null,{"$f":"OR(B2246<=$AO$14,B2246>=$AN$14)*(F2246<6)*(I2246>$AN$15)*(I2246<=$AO$15)*(G2246<>1)","v":1},{"$f":"OR(B2246<=$AO$14,B2246>=$AN$14)*(Y2246=0)","v":0},{"$f":"AND(B2246>=$AN$24,B2246<=$AO$24)*(F2246<6)*(I2246>$AN$25)*(I2246<=$AO$25)*(G2246<>1)","v":0},{"$f":"AND(B2246>=$AN$24,B2246<=$AO$24)*(AA2246=0)","v":0},{"$f":"OR(B2246<=$AO$19,B2246>=$AN$19)*(F2246<6)*(I2246>$AN$20)*(I2246<=$AO$20)","v":0},{"$f":"AND(B2246>=$AN$29,B2246<=$AO$29)*(F2246<6)*(I2246>$AN$30)*(I2246<=$AO$30)","v":0},{"$f":"IF(OR(E2246=$AM$34,E2246=$AM$35,E2246=$AM$36,E2246=$AM$37,E2246=$AM$38,E2246=$AM$39,E2246=$AM$40,E2246=$AM$41,E2246=$AM$42,E2246=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E2246>=$AM$47,E2246<=$AN$47),AND(E2246>=$AM$48,E2246<=$AN$48),AND(E2246>=$AM$49,E2246<=$AN$49),AND(E2246>=$AM$50,E2246<=$AN$50),AND(E2246>=$AM$51,E2246<=$AN$51)),0,1)*AE2246","v":1},{"$f":"(B2246>=5)*(B2246<=10)","v":0},{"$f":"1*OR(B2246<=4,B2246>=11)","v":1},{"$f":"LOOKUP(B2246,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE2246:AI2246)*((F2246<6)*(I2246>$AO$7)*(I2246<=$AP$7)+(F2246=6)*(I2246>$AO$8)*(I2246<=$AP$8)+(F2246>=7)*(I2246>$AO$9)*(I2246<=$AP$9))","v":0}]
["1990-04-04",4,4,2018,"2018-04-04",3,0,"18:00:00",18,35.78,37.04,39.200000000000003,33.799999999999997,46.4,39.92,3.1999999999999993,39.92,33.979999999999997,37.4,36.5,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-04",4,4,2018,"2018-04-04",3,0,"19:00:00",19,34.159999999999997,35.06,36.14,32.36,44.78,37.94,1.3999999999999986,37.94,32.9,35.42,34.880000000000003,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-05",4,5,2018,"2018-04-05",4,0,"03:00:00",3,35.06,26.060000000000002,26.6,21.2,35.6,30.02,3.1999999999999993,29.12,24.259999999999998,29.66,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-05",4,5,2018,"2018-04-05",4,0,"16:00:00",16,39.019999999999996,42.08,39.200000000000003,40.1,50,42.08,10.399999999999999,41,37.22,44.24,44.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-05",4,5,2018,"2018-04-05",4,0,"20:00:00",20,33.979999999999997,35.96,35.24,35.6,37.94,37.94,6.8000000000000007,37.94,32.9,37.76,37.22,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-06",4,6,2018,"2018-04-06",5,0,"06:00:00",6,30.02,26.060000000000002,33.08,24.8,24.98,32,5,32.9,24.439999999999998,29.3,26.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-06",4,6,2018,"2018-04-06",5,0,"13:00:00",13,35.96,42.08,46.4,35.6,34.520000000000003,44.96,14,46.94,34.520000000000003,36.5,36.68,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-06",4,6,2018,"2018-04-06",5,0,"20:00:00",20,35.24,37.94,46.4,35.42,33.979999999999997,37.94,21.2,38.840000000000003,34.520000000000003,36.5,35.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-07",4,7,2018,"2018-04-07",6,0,"06:00:00",6,23,34.700000000000003,35.6,33.26,28.04,35.78,19.399999999999999,35.96,32.54,35.6,35.06,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-07",4,7,2018,"2018-04-07",6,0,"13:00:00",13,53.06,41.54,41,42.8,47.84,42.08,38.659999999999997,41.9,41.9,41.36,41,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-07",4,7,2018,"2018-04-07",6,0,"15:00:00",15,51.980000000000004,43.879999999999995,41.72,42.8,55.94,44.06,39.74,42.980000000000004,42.44,40.46,42.980000000000004,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-08",4,8,2018,"2018-04-08",7,0,"03:00:00",3,36.5,33.619999999999997,32.36,30.2,44.06,33.799999999999997,15.8,33.979999999999997,24.439999999999998,34.340000000000003,33.619999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-08",4,8,2018,"2018-04-08",7,0,"08:00:00",8,38.119999999999997,33.619999999999997,33.799999999999997,33.799999999999997,39.74,34.340000000000003,18.86,34.340000000000003,26.96,33.619999999999997,32.72,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-08",4,8,2018,"2018-04-08",7,0,"17:00:00",17,42.980000000000004,33.44,33.26,34.159999999999997,59,33.799999999999997,33.08,33.799999999999997,33.799999999999997,34.340000000000003,33.799999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-09",4,9,2018,"2018-04-09",1,0,"01:00:00",1,37.04,30.02,32,28.4,42.980000000000004,30.92,14,32.9,28.4,32.72,28.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-09",4,9,2018,"2018-04-09",1,0,"07:00:00",7,34.520000000000003,30.02,30.2,28.4,42.8,30.92,24.8,32,29.12,32.9,30.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-09",4,9,2018,{"$f":"DATE(D2375,B2375,C2375)","v":"2018-04-09"},{"$f":"WEEKDAY(E2375,2)","v":1},0,"18:00:00",18,33.26,33.26,33.619999999999997,32.18,53.06,35.06,24.8,35.6,34.700000000000003,34.880000000000003,33.979999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-09",4,9,2018,"2018-04-09",1,0,1,24,26.060000000000002,33.08,32.9,32,42.980000000000004,33.979999999999997,21.2,34.880000000000003,32,35.6,34.520000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-10",4,10,2018,"2018-04-10",2,0,"03:00:00",3,21.02,33.26,32.9,32.18,42.8,34.340000000000003,24.8,34.520000000000003,32.54,35.96,34.700000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-10",4,10,2018,"2018-04-10",2,0,"14:00:00",14,48.379999999999995,39.92,42.8,37.4,51.8,44.06,36.68,45.86,37.94,42.8,40.28,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-10",4,10,2018,"2018-04-10",2,0,"20:00:00",20,43.16,48.2,46.4,42.44,43.16,46.04,37.76,46.4,40.1,47.120000000000005,46.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-11",4,11,2018,"2018-04-11",3,0,"04:00:00",4,41.54,44.06,44.24,44.6,39.56,46.04,37.04,45.5,42.08,44.42,42.980000000000004,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-11",4,11,2018,"2018-04-11",3,0,"13:00:00",13,53.78,48.92,50,44.6,38.299999999999997,51.980000000000004,35.78,54.86,42.980000000000004,53.6,48.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-11",4,11,2018,"2018-04-11",3,0,"18:00:00",18,45.14,48.019999999999996,46.4,42.980000000000004,35.24,50,35.06,50,40.28,49.28,48.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-12",4,12,2018,"2018-04-12",4,0,"06:00:00",6,26.060000000000002,37.22,35.78,35.78,32,35.96,17.059999999999999,37.22,34.520000000000003,38.480000000000004,39.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-12",4,12,2018,"2018-04-12",4,0,"11:00:00",{"$f":"H2440*24","v":11},49.28,55.94,53.6,53.6,32,59,47.3,59.900000000000006,52.7,58.64,59,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-12",4,12,2018,"2018-04-12",4,0,"15:00:00",15,52.34,66.92,64.400000000000006,62.6,33.799999999999997,68,51.26,66.92,54.68,68,66.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-13",4,13,2018,"2018-04-13",5,0,"01:00:00",1,35.96,41.18,41.54,37.58,33.979999999999997,41,33.979999999999997,43.34,37.22,42.8,42.44,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-13",4,13,2018,"2018-04-13",5,0,"08:00:00",8,35.96,44.24,43.16,41.9,32.54,46.94,38.840000000000003,46.94,42.44,43.879999999999995,44.78,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-13",4,13,2018,"2018-04-13",5,0,"15:00:00",15,35.42,71.960000000000008,71.599999999999994,71.599999999999994,44.6,73.039999999999992,59.18,73.94,71.960000000000008,69.44,73.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-14",4,14,2018,"2018-04-14",6,0,"01:00:00",1,32,59,57.2,57.2,36.86,57.92,39.200000000000003,57.92,52.7,57.379999999999995,57.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-14",4,14,2018,"2018-04-14",6,0,"05:00:00",5,30.92,57.92,55.400000000000006,55.400000000000006,38.299999999999997,60.08,44.06,59.900000000000006,54.86,58.1,57.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-14",4,14,2018,"2018-04-14",6,0,"18:00:00",18,56.84,60.980000000000004,62.6,60.8,44.96,62.96,46.4,61.88,60.08,60.8,60.980000000000004,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-14",4,14,2018,"2018-04-14",6,0,"19:00:00",19,53.6,60.08,57.2,57.2,42.08,60.08,44.78,56.84,57.2,58.46,57.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-15",4,15,2018,"2018-04-15",7,0,"04:00:00",4,50,41.36,40.82,37.4,26.060000000000002,42.8,31.64,43.879999999999995,35.96,42.980000000000004,41,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-15",4,15,2018,"2018-04-15",7,0,"12:00:00",12,54.86,62.96,59,57.2,51.08,62.96,48.019999999999996,64.94,56.84,65.300000000000011,62.06,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-15",4,15,2018,"2018-04-15",7,0,"18:00:00",18,53.96,57.019999999999996,60.8,57.2,57.92,60.08,42.44,60.980000000000004,54.86,58.46,55.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-16",4,16,2018,"2018-04-16",1,0,"05:00:00",5,21.02,32.54,26.6,30.2,37.94,33.979999999999997,24.8,35.42,26.6,36.5,33.799999999999997,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["1990-04-16",4,16,2018,"2018-04-16",1,0,"11:00:00",11,26.060000000000002,55.040000000000006,55.400000000000006,51.8,59,57.019999999999996,46.04,59,54.5,54.14,57.92,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1990-04-16",4,16,2018,"2018-04-16",1,0,"22:00:00",22,15.079999999999998,53.06,51.8,46.4,53.6,53.96,46.04,52.879999999999995,50.900000000000006,50.72,50.540000000000006,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1990-04-17",4,17,2018,"2018-04-17",2,0,"01:00:00",1,14,47.84,50,45.32,51.08,51.08,41.72,50.900000000000006,44.6,49.64,46.04,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["1990-04-17",4,17,2018,"2018-04-17",2,0,"07:00:00",7,19.939999999999998,51.980000000000004,46.4,48.2,42.980000000000004,51.980000000000004,39.019999999999996,53.96,44.06,48.2,46.04,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["1990-04-17",4,17,2018,"2018-04-17",2,0,"15:00:00",15,37.4,62.96,60.8,59,60.08,62.06,49.64,62.96,61.7,63.319999999999993,60.08,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1990-04-17",4,17,2018,"2018-04-17",2,0,1,24,28.04,50.72,49.82,44.6,37.94,48.92,42.980000000000004,46.94,45.68,51.620000000000005,51.08,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["1990-04-18",4,18,2018,"2018-04-18",3,0,"12:00:00",12,41.36,64.94,66.2,57.2,50.36,64.94,50,68.900000000000006,64.039999999999992,51.8,57.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1990-04-18",4,18,2018,"2018-04-18",3,0,"17:00:00",17,42.26,55.040000000000006,64.400000000000006,53.6,60.980000000000004,63.319999999999993,43.879999999999995,66.2,56.3,46.4,46.94,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1990-04-18",4,18,2018,"2018-04-18",3,0,"22:00:00",22,28.04,48.019999999999996,51.8,46.4,50.540000000000006,51.08,35.42,50,42.26,42.44,42.26,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1990-04-19",4,19,2018,"2018-04-19",4,0,"10:00:00",10,41,48.379999999999995,48.2,45.32,57.74,51.980000000000004,35.78,52.879999999999995,43.7,50.72,48.92,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1990-04-19",4,19,2018,"2018-04-19",4,0,"12:00:00",12,44.06,57.019999999999996,53.6,53.6,71.960000000000008,57.019999999999996,42.980000000000004,55.94,53.06,51.08,55.94,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1990-04-19",4,19,2018,"2018-04-19",4,0,"19:00:00",19,41,50,55.400000000000006,53.6,69.800000000000011,51.08,39.56,48.92,51.620000000000005,42.26,46.94,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1990-04-20",4,20,{"$f":"$AO$4","v":2018},"2018-04-20",5,{"$f":"COUNTIF($AM$34:$AM$43,E2630)","v":0},"09:00:00",9,36.32,42.980000000000004,41,39.200000000000003,41.72,42.08,36.14,42.8,39.380000000000003,41.9,42.08,null,{"$f":"SUMPRODUCT($J$2:$T$2,J2630:T2630)","v":0},null,null,{"$f":"OR(B2630<=$AO$14,B2630>=$AN$14)*(F2630<6)*(I2630>$AN$15)*(I2630<=$AO$15)*(G2630<>1)","v":1},{"$f":"OR(B2630<=$AO$14,B2630>=$AN$14)*(Y2630=0)","v":0},{"$f":"AND(B2630>=$AN$24,B2630<=$AO$24)*(F2630<6)*(I2630>$AN$25)*(I2630<=$AO$25)*(G2630<>1)","v":0},{"$f":"AND(B2630>=$AN$24,B2630<=$AO$24)*(AA2630=0)","v":0},{"$f":"OR(B2630<=$AO$19,B2630>=$AN$19)*(F2630<6)*(I2630>$AN$20)*(I2630<=$AO$20)","v":0},{"$f":"AND(B2630>=$AN$29,B2630<=$AO$29)*(F2630<6)*(I2630>$AN$30)*(I2630<=$AO$30)","v":0},{"$f":"IF(OR(E2630=$AM$34,E2630=$AM$35,E2630=$AM$36,E2630=$AM$37,E2630=$AM$38,E2630=$AM$39,E2630=$AM$40,E2630=$AM$41,E2630=$AM$42,E2630=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E2630>=$AM$47,E2630<=$AN$47),AND(E2630>=$AM$48,E2630<=$AN$48),AND(E2630>=$AM$49,E2630<=$AN$49),AND(E2630>=$AM$50,E2630<=$AN$50),AND(E2630>=$AM$51,E2630<=$AN$51)),0,1)*AE2630","v":0},{"$f":"(B2630>=5)*(B2630<=10)","v":0},{"$f":"1*OR(B2630<=4,B2630>=11)","v":1},{"$f":"LOOKUP(B2630,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE2630:AI2630)*((F2630<6)*(I2630>$AO$7)*(I2630<=$AP$7)+(F2630=6)*(I2630>$AO$8)*(I2630<=$AP$8)+(F2630>=7)*(I2630>$AO$9)*(I2630<=$AP$9))","v":0}]
["1990-04-20",4,20,2018,"2018-04-20",5,0,"12:00:00",12,53.06,42.08,44.6,40.28,51.8,44.06,36.32,44.6,38.119999999999997,42.8,42.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1990-04-20",4,20,2018,"2018-04-20",5,0,"23:00:00",23,35.96,46.94,46.4,44.6,34.520000000000003,46.94,39.380000000000003,48.2,44.42,46.4,44.96,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1990-04-21",4,21,2018,"2018-04-21",6,0,"05:00:00",5,33.979999999999997,46.94,46.4,44.6,33.979999999999997,48.019999999999996,38.299999999999997,48.92,44.96,46.4,46.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-21",4,21,2018,"2018-04-21",6,0,"13:00:00",13,64.039999999999992,53.6,55.400000000000006,53.6,41.36,59,41.54,60.8,47.120000000000005,61.34,55.76,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-21",4,21,2018,"2018-04-21",6,0,"22:00:00",22,48.92,46.04,50.18,43.879999999999995,33.979999999999997,44.96,35.78,49.82,42.08,47.66,44.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-22",4,22,2018,"2018-04-22",7,0,"06:00:00",6,44.06,39.200000000000003,38.480000000000004,38.119999999999997,33.08,40.28,33.44,40.64,38.480000000000004,40.28,39.200000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-22",4,22,2018,"2018-04-22",7,0,"07:00:00",7,46.94,39.92,39.380000000000003,38.659999999999997,32.72,42.08,35.42,41.72,39.380000000000003,42.980000000000004,41.54,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-22",4,22,2018,"2018-04-22",7,0,"20:00:00",20,51.08,55.94,48.2,53.6,42.980000000000004,55.94,42.08,55.94,50.36,59,57.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-22",4,22,2018,"2018-04-22",7,0,1,24,48.92,44.96,41,44.6,33.799999999999997,44.96,39.74,46.4,42.980000000000004,49.28,48.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-23",4,23,2018,"2018-04-23",1,0,"10:00:00",10,42.980000000000004,43.34,42.8,42.8,35.06,44.96,35.42,46.94,41.18,46.76,46.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-23",4,23,2018,"2018-04-23",1,0,"17:00:00",17,39.380000000000003,46.04,41,44.6,41,46.04,35.42,45.86,41,48.379999999999995,44.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-23",4,23,2018,"2018-04-23",1,0,1,24,36.32,34.520000000000003,33.799999999999997,33.26,37.4,35.96,13.099999999999998,36.32,32,38.299999999999997,36.32,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-24",4,24,2018,"2018-04-24",2,0,"10:00:00",10,33.979999999999997,41,37.4,39.200000000000003,53.96,42.08,14,43.879999999999995,37.4,42.980000000000004,42.620000000000005,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-24",4,24,2018,"2018-04-24",2,0,"17:00:00",17,44.96,44.06,42.8,41,73.94,44.96,32.54,45.86,38.480000000000004,46.4,42.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-24",4,24,2018,"2018-04-24",2,0,"19:00:00",19,41.18,39.92,39.200000000000003,37.76,69.080000000000013,42.980000000000004,10.399999999999999,43.879999999999995,35.24,40.64,41.54,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-25",4,25,2018,"2018-04-25",3,0,"07:00:00",7,33.619999999999997,34.880000000000003,33.799999999999997,34.159999999999997,42.26,35.78,10.399999999999999,35.96,32.72,36.86,36.14,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-25",4,25,2018,"2018-04-25",3,0,"12:00:00",12,48.379999999999995,50,48.2,46.4,55.040000000000006,51.980000000000004,36.86,50.900000000000006,45.32,51.44,51.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-25",4,25,2018,"2018-04-25",3,0,"21:00:00",21,41,41,46.4,41,45.32,44.96,35.24,45.86,41.18,46.22,45.14,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-26",4,26,2018,"2018-04-26",4,0,"06:00:00",6,37.04,40.82,39.56,41,37.04,40.46,34.700000000000003,41.9,40.28,40.46,41,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-26",4,26,2018,"2018-04-26",4,0,"14:00:00",14,37.22,53.96,53.6,53.6,57.019999999999996,55.94,43.879999999999995,53.96,52.7,50.900000000000006,53.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-26",4,26,2018,"2018-04-26",4,0,"20:00:00",20,35.24,51.08,51.8,48.2,46.94,53.06,41,52.879999999999995,48.019999999999996,46.4,48.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-27",4,27,2018,"2018-04-27",5,0,"07:00:00",7,34.520000000000003,48.019999999999996,44.6,44.6,36.5,48.019999999999996,37.58,47.84,44.24,49.64,48.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-27",4,27,2018,"2018-04-27",5,0,"10:00:00",10,37.58,53.06,50,50,48.56,53.06,39.200000000000003,54.86,46.58,54.32,51.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-27",4,27,2018,"2018-04-27",5,0,"16:00:00",16,44.96,53.96,51.8,51.8,64.039999999999992,53.96,43.52,54.86,51.08,51.8,51.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-27",4,27,2018,"2018-04-27",5,0,1,24,34.700000000000003,46.94,46.4,46.4,42.980000000000004,48.019999999999996,39.200000000000003,47.84,44.24,44.78,44.06,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-28",4,28,{"$f":"$AO$4","v":2018},"2018-04-28",6,{"$f":"COUNTIF($AM$34:$AM$43,E2822)","v":0},"09:00:00",9,38.480000000000004,46.4,48.2,48.2,51.980000000000004,47.120000000000005,37.22,50,44.06,48.74,46.94,null,{"$f":"SUMPRODUCT($J$2:$T$2,J2822:T2822)","v":0},null,null,{"$f":"OR(B2822<=$AO$14,B2822>=$AN$14)*(F2822<6)*(I2822>$AN$15)*(I2822<=$AO$15)*(G2822<>1)","v":0},{"$f":"OR(B2822<=$AO$14,B2822>=$AN$14)*(Y2822=0)","v":1},{"$f":"AND(B2822>=$AN$24,B2822<=$AO$24)*(F2822<6)*(I2822>$AN$25)*(I2822<=$AO$25)*(G2822<>1)","v":0},{"$f":"AND(B2822>=$AN$24,B2822<=$AO$24)*(AA2822=0)","v":0},{"$f":"OR(B2822<=$AO$19,B2822>=$AN$19)*(F2822<6)*(I2822>$AN$20)*(I2822<=$AO$20)","v":0},{"$f":"AND(B2822>=$AN$29,B2822<=$AO$29)*(F2822<6)*(I2822>$AN$30)*(I2822<=$AO$30)","v":0},{"$f":"IF(OR(E2822=$AM$34,E2822=$AM$35,E2822=$AM$36,E2822=$AM$37,E2822=$AM$38,E2822=$AM$39,E2822=$AM$40,E2822=$AM$41,E2822=$AM$42,E2822=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E2822>=$AM$47,E2822<=$AN$47),AND(E2822>=$AM$48,E2822<=$AN$48),AND(E2822>=$AM$49,E2822<=$AN$49),AND(E2822>=$AM$50,E2822<=$AN$50),AND(E2822>=$AM$51,E2822<=$AN$51)),0,1)*AE2822","v":1},{"$f":"(B2822>=5)*(B2822<=10)","v":0},{"$f":"1*OR(B2822<=4,B2822>=11)","v":1},{"$f":"LOOKUP(B2822,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE2822:AI2822)*((F2822<6)*(I2822>$AO$7)*(I2822<=$AP$7)+(F2822=6)*(I2822>$AO$8)*(I2822<=$AP$8)+(F2822>=7)*(I2822>$AO$9)*(I2822<=$AP$9))","v":0}]
["1990-04-28",4,28,2018,"2018-04-28",6,0,"17:00:00",17,48.92,60.08,59,55.400000000000006,71.06,60.08,51.620000000000005,59.900000000000006,55.040000000000006,60.980000000000004,59,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-29",4,29,2018,"2018-04-29",7,0,"02:00:00",2,37.94,51.08,48.019999999999996,51.8,44.96,51.980000000000004,42.620000000000005,50.900000000000006,46.94,48.019999999999996,51.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-29",4,29,2018,"2018-04-29",7,0,"07:00:00",7,34.880000000000003,48.019999999999996,47.120000000000005,46.22,46.22,51.980000000000004,39.74,51.980000000000004,44.78,49.46,51.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-29",4,29,2018,"2018-04-29",7,0,"19:00:00",19,48.019999999999996,55.040000000000006,62.6,55.400000000000006,60.980000000000004,55.94,45.5,56.84,54.68,48.2,48.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-29",4,29,2018,"2018-04-29",7,0,"21:00:00",21,41,51.980000000000004,55.400000000000006,51.8,57.92,53.06,43.879999999999995,52.879999999999995,52.519999999999996,48.379999999999995,48.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-30",4,30,2018,"2018-04-30",1,0,"04:00:00",4,34.340000000000003,48.019999999999996,46.4,46.4,48.2,48.92,38.659999999999997,47.84,44.6,46.04,46.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-30",4,30,2018,"2018-04-30",1,0,"11:00:00",11,39.56,55.94,50,55.400000000000006,66.92,57.019999999999996,52.7,56.84,59.36,57.019999999999996,59,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1990-04-30",4,30,2018,"2018-04-30",1,0,"21:00:00",21,34.340000000000003,47.480000000000004,51.44,48.2,54.68,48.2,43.879999999999995,48.2,50,45.14,45.68,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-05-01",5,1,2018,"2018-05-01",2,0,"04:00:00",4,40.28,43.34,43.7,43.16,38.119999999999997,42.620000000000005,30.74,41.36,35.96,44.6,42.8,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-01",5,1,2018,"2018-05-01",2,0,"14:00:00",14,78.98,71.960000000000008,71.599999999999994,73.400000000000006,55.94,71.960000000000008,57.92,70.88,63.86,62.96,69.080000000000013,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-01",5,1,2018,"2018-05-01",2,0,"18:00:00",18,62.78,68,73.400000000000006,71.599999999999994,64.039999999999992,68,55.22,66.92,65.84,58.82,62.06,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-02",5,2,2018,"2018-05-02",3,0,"07:00:00",7,44.96,48.92,48.379999999999995,48.2,42.26,51.980000000000004,39.56,50.900000000000006,40.46,53.24,53.96,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-02",5,2,2018,"2018-05-02",3,0,"08:00:00",8,55.94,55.58,54.86,55.400000000000006,47.480000000000004,57.92,40.64,57.92,43.52,53.06,54.32,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-02",5,2,2018,"2018-05-02",3,0,"16:00:00",16,66.92,64.039999999999992,78.800000000000011,57.2,60.08,55.94,45.32,59,48.2,49.46,51.08,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-03",5,3,2018,"2018-05-03",4,0,"05:00:00",5,33.979999999999997,37.94,41,37.4,42.08,40.46,33.979999999999997,42.980000000000004,39.56,42.44,40.28,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-03",5,3,2018,"2018-05-03",4,0,"09:00:00",9,45.68,49.64,50,51.8,50.540000000000006,53.96,35.78,52.879999999999995,39.92,48.2,48.56,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-03",5,3,2018,"2018-05-03",4,0,"15:00:00",15,69.080000000000013,66.02,66.2,64.400000000000006,57.019999999999996,62.96,38.299999999999997,62.96,41.18,54.32,60.08,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-04",5,4,2018,"2018-05-04",5,0,"02:00:00",2,44.24,45.86,47.120000000000005,46.4,48.019999999999996,44.96,36.86,42.980000000000004,43.34,41.18,42.08,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-04",5,4,2018,"2018-05-04",5,0,"05:00:00",5,37.22,37.04,41.9,37.58,46.04,41,36.68,39.92,41.54,39.92,39.380000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-04",5,4,2018,"2018-05-04",5,0,"19:00:00",19,62.06,56.120000000000005,62.6,60.8,48.92,51.08,44.06,52.879999999999995,50.900000000000006,48.56,46.94,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-05",5,5,2018,"2018-05-05",6,0,"02:00:00",2,37.58,40.1,39.92,39.74,48.92,39.92,39.56,38.840000000000003,43.7,42.8,40.82,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-05",5,5,2018,"2018-05-05",6,0,"04:00:00",4,35.6,38.299999999999997,39.019999999999996,38.299999999999997,46.04,37.94,39.92,34.880000000000003,42.8,38.659999999999997,36.14,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-05",5,5,2018,"2018-05-05",6,0,"16:00:00",16,73.94,68,71.599999999999994,69.800000000000011,51.620000000000005,64.94,43.879999999999995,63.86,46.4,53.96,57.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-05",5,5,2018,"2018-05-05",6,0,"21:00:00",21,55.76,48.019999999999996,55.400000000000006,53.6,46.04,48.92,41.36,47.84,45.86,48.74,49.28,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-06",5,6,2018,"2018-05-06",7,0,"06:00:00",6,43.7,40.46,42.26,41,37.76,41.72,40.46,42.26,42.8,41.9,42.26,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-06",5,6,2018,"2018-05-06",7,0,"15:00:00",15,77,73.039999999999992,73.400000000000006,71.599999999999994,54.68,73.039999999999992,46.04,72.86,55.040000000000006,54.68,62.96,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-06",5,6,2018,"2018-05-06",7,0,"23:00:00",23,48.74,48.92,55.22,50,40.28,53.06,43.7,50,47.66,46.04,46.04,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-07",5,7,2018,"2018-05-07",1,0,"05:00:00",5,42.620000000000005,44.96,45.32,42.08,28.94,44.6,41.9,47.120000000000005,42.980000000000004,45.5,42.980000000000004,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-07",5,7,2018,"2018-05-07",1,0,"08:00:00",8,59,54.68,51.8,55.400000000000006,43.879999999999995,57.92,45.32,59.900000000000006,51.26,48.2,53.06,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-07",5,7,2018,"2018-05-07",1,0,"22:00:00",22,60.44,62.06,60.8,66.2,44.96,66.02,49.64,64.94,51.08,59.72,57.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-08",5,8,2018,"2018-05-08",2,0,"01:00:00",1,50.18,55.94,55.400000000000006,57.2,35.96,60.980000000000004,47.120000000000005,55.94,48.379999999999995,55.22,53.96,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-08",5,8,2018,"2018-05-08",2,0,"12:00:00",12,75.92,71.960000000000008,73.400000000000006,71.599999999999994,64.94,75.02,55.22,73.94,52.879999999999995,64.400000000000006,69.800000000000011,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-08",5,8,2018,"2018-05-08",2,0,"18:00:00",18,66.92,62.6,64.400000000000006,66.2,69.98,66.2,50.72,65.84,57.019999999999996,59,64.400000000000006,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-09",5,9,2018,{"$f":"DATE(D3079,B3079,C3079)","v":"2018-05-09"},{"$f":"WEEKDAY(E3079,2)","v":3},0,"02:00:00",2,54.14,57.92,60.8,57.2,51.980000000000004,57.2,46.76,59,50.900000000000006,54.32,55.040000000000006,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-09",5,9,2018,"2018-05-09",3,0,"11:00:00",11,58.46,60.08,66.2,60.8,53.96,60.08,48.2,60.8,51.8,59,60.8,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-09",5,9,2018,"2018-05-09",3,0,"16:00:00",16,60.8,60.8,66.2,62.6,53.96,66.2,38.119999999999997,68,45.32,57.2,59,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-09",5,9,2018,"2018-05-09",3,0,"20:00:00",20,57.92,60.980000000000004,60.8,57.2,51.980000000000004,60.08,36.5,60.8,44.06,54.5,57.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-10",5,10,2018,"2018-05-10",4,0,"09:00:00",9,60.8,59.36,55.400000000000006,57.74,55.94,64.94,32.36,60.8,38.659999999999997,59,64.400000000000006,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-10",5,10,2018,"2018-05-10",4,0,"13:00:00",13,69.080000000000013,75.92,73.400000000000006,73.400000000000006,78.080000000000013,78.98,41.9,77.900000000000006,50.540000000000006,71.599999999999994,75.02,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-10",5,10,2018,"2018-05-10",4,0,"23:00:00",23,53.6,62.06,60.8,59,68,64.039999999999992,37.94,63.86,39.74,54.68,55.040000000000006,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-11",5,11,2018,"2018-05-11",5,0,"06:00:00",6,53.06,57.92,57.2,57.2,55.94,59,39.019999999999996,59,43.7,57.2,53.96,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-11",5,11,2018,"2018-05-11",5,0,"13:00:00",13,64.94,64.039999999999992,62.6,66.2,71.960000000000008,69.080000000000013,58.64,69.800000000000011,64.400000000000006,68,64.94,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-11",5,11,2018,"2018-05-11",5,0,"23:00:00",23,55.94,60.08,60.8,60.8,53.96,62.06,45.14,62.6,45.86,60.8,62.6,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-12",5,12,2018,"2018-05-12",6,0,"03:00:00",3,51.8,59,59,59,44.06,60.8,39.380000000000003,60.980000000000004,41.72,59,60.8,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-12",5,12,2018,"2018-05-12",6,0,"08:00:00",8,53.6,59,55.400000000000006,57.2,62.06,60.8,48.379999999999995,59.900000000000006,54.5,60.8,60.8,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-12",5,12,2018,"2018-05-12",6,0,"17:00:00",17,51.980000000000004,60.08,55.400000000000006,57.2,82.94,60.980000000000004,60.980000000000004,60.980000000000004,71.599999999999994,65.84,62.06,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-13",5,13,2018,"2018-05-13",7,0,"01:00:00",1,37.04,44.96,44.6,44.6,62.06,46.94,41,46.94,44.78,45.68,46.04,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-13",5,13,2018,"2018-05-13",7,0,"10:00:00",10,38.659999999999997,48.019999999999996,44.6,46.4,55.040000000000006,50,63.319999999999993,52.879999999999995,65.48,53.6,50,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-13",5,13,2018,"2018-05-13",7,0,"18:00:00",18,46.94,50,48.2,50,55.040000000000006,51.980000000000004,70.16,50.900000000000006,80.78,51.8,51.08,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-13",5,13,2018,"2018-05-13",7,0,1,24,33.979999999999997,42.26,41,42.8,51.980000000000004,44.06,55.94,43.52,58.1,43.34,45.14,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-14",5,14,2018,"2018-05-14",1,0,"11:00:00",{"$f":"H3208*24","v":11},45.32,51.980000000000004,51.8,51.8,66.92,55.94,67.28,53.96,70.16,56.480000000000004,53.06,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-14",5,14,2018,"2018-05-14",1,0,"14:00:00",14,51.980000000000004,55.040000000000006,53.6,55.400000000000006,77,59,62.06,56.84,68.539999999999992,59.72,59,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-14",5,14,2018,"2018-05-14",1,0,"20:00:00",20,42.980000000000004,53.06,46.4,51.8,64.94,51.08,56.480000000000004,48.92,59.36,50.72,50,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-15",5,15,2018,"2018-05-15",2,0,"04:00:00",4,24.08,35.96,36.32,34.700000000000003,57.92,35.6,50.900000000000006,35.96,49.1,40.82,37.04,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-15",5,15,2018,"2018-05-15",2,0,"13:00:00",13,62.96,64.94,60.8,62.6,66.92,64.94,67.64,64.94,69.98,58.64,60.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-15",5,15,2018,"2018-05-15",2,0,"21:00:00",21,46.22,53.96,53.6,51.8,71.06,57.019999999999996,60.620000000000005,55.94,59.18,53.24,53.06,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-16",5,16,2018,"2018-05-16",3,0,"06:00:00",6,42.8,51.44,50.36,50,66.02,51.08,42.08,52.879999999999995,46.04,51.44,51.980000000000004,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-16",5,16,2018,"2018-05-16",3,0,"15:00:00",15,68,77,75.2,75.2,69.080000000000013,80.06,47.3,80.960000000000008,47.66,79.16,78.080000000000013,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-16",5,16,2018,"2018-05-16",3,0,"20:00:00",20,53.96,73.039999999999992,71.599999999999994,66.2,68,73.039999999999992,35.96,72.86,41.36,69.259999999999991,66.02,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-17",5,17,2018,"2018-05-17",4,0,"08:00:00",8,44.24,53.06,51.8,51.8,55.94,57.019999999999996,12.2,56.84,38.299999999999997,53.78,57.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-17",5,17,2018,"2018-05-17",4,0,"10:00:00",10,44.78,57.92,55.400000000000006,55.400000000000006,53.06,60.08,34.340000000000003,60.980000000000004,39.92,63.319999999999993,60.08,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-17",5,17,2018,"2018-05-17",4,0,"17:00:00",17,57.92,68,58.46,62.6,64.039999999999992,69.080000000000013,37.94,68.900000000000006,46.4,62.06,64.039999999999992,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-17",5,17,2018,"2018-05-17",4,0,1,24,41.54,48.92,46.04,46.04,42.980000000000004,50,35.96,46.94,42.44,50.36,48.92,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-18",5,18,2018,"2018-05-18",5,0,"10:00:00",10,51.620000000000005,66.02,62.24,62.6,60.08,68,48.379999999999995,68.900000000000006,54.68,62.96,66.92,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-18",5,18,2018,"2018-05-18",5,0,"21:00:00",21,52.34,51.980000000000004,61.519999999999996,51.8,51.08,53.96,47.120000000000005,59.900000000000006,58.1,51.26,51.08,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-19",5,19,2018,"2018-05-19",6,0,"03:00:00",3,40.46,48.2,48.2,44.24,42.26,46.94,37.4,50,45.14,50.36,50,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-19",5,19,2018,"2018-05-19",6,0,"11:00:00",11,60.8,59,64.22,55.400000000000006,62.06,66.92,52.16,68.900000000000006,58.1,55.400000000000006,55.040000000000006,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-19",5,19,2018,"2018-05-19",6,0,"20:00:00",20,55.040000000000006,53.06,54.32,55.400000000000006,50,55.400000000000006,54.14,55.94,60.26,50,51.8,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-19",5,19,2018,"2018-05-19",6,0,"21:00:00",21,53.06,51.8,53.96,55.400000000000006,50,55.94,53.42,55.94,55.22,50.72,51.08,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-20",5,20,2018,"2018-05-20",7,0,"05:00:00",5,48.019999999999996,53.96,53.96,53.6,41.9,57.019999999999996,42.620000000000005,56.84,46.58,55.400000000000006,53.6,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-20",5,20,2018,"2018-05-20",7,0,"18:00:00",18,69.080000000000013,71.06,75.92,69.800000000000011,69.98,75.92,49.82,79.88,56.3,73.400000000000006,71.960000000000008,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-20",5,20,2018,"2018-05-20",7,0,"22:00:00",22,55.040000000000006,60.08,70.7,59,48.019999999999996,64.94,46.58,66.92,49.46,57.379999999999995,60.08,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-21",5,21,2018,"2018-05-21",1,0,"08:00:00",8,55.400000000000006,57.019999999999996,64.400000000000006,57.2,53.06,60.08,46.76,60.980000000000004,50,56.66,55.400000000000006,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-21",5,21,2018,"2018-05-21",1,0,"15:00:00",15,48.56,66.92,80.599999999999994,57.2,75.92,66.02,64.94,68.900000000000006,72.86,51.620000000000005,51.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-21",5,21,2018,"2018-05-21",1,0,"22:00:00",22,50,50,53.06,50,62.96,50,51.8,51.8,50,50,48.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-22",5,22,2018,"2018-05-22",2,0,"08:00:00",8,46.4,51.08,52.34,51.8,57.92,55.040000000000006,58.82,53.96,58.28,53.6,51.8,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-22",5,22,2018,"2018-05-22",2,0,"15:00:00",15,55.76,60.08,71.78,59,59,60.08,69.800000000000011,64.400000000000006,75.740000000000009,55.400000000000006,55.040000000000006,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-22",5,22,2018,"2018-05-22",2,0,"17:00:00",17,62.06,57.92,70.7,57.2,59,57.019999999999996,68.539999999999992,57.92,73.759999999999991,54.68,55.400000000000006,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-23",5,23,2018,"2018-05-23",3,0,"05:00:00",5,46.94,51.08,61.519999999999996,51.8,55.94,53.6,51.980000000000004,53.6,52.16,50,50,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-23",5,23,2018,"2018-05-23",3,0,"10:00:00",10,58.82,55.400000000000006,62.6,55.400000000000006,57.92,57.2,61.16,63.680000000000007,65.84,56.66,55.400000000000006,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-23",5,23,2018,"2018-05-23",3,0,"19:00:00",19,62.24,68,65.300000000000011,69.800000000000011,55.94,68,60.44,66.92,65.12,69.800000000000011,68,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-24",5,24,2018,"2018-05-24",4,0,"03:00:00",3,60.08,64.039999999999992,61.7,64.400000000000006,53.06,64.400000000000006,47.66,64.400000000000006,46.4,62.24,64.94,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-24",5,24,2018,"2018-05-24",4,0,"09:00:00",9,62.6,66.2,63.319999999999993,66.2,57.92,66.2,57.56,66.2,57.2,66.2,64.400000000000006,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-24",5,24,2018,"2018-05-24",4,0,"20:00:00",20,46.94,51.08,46.04,51.8,53.06,51.8,65.84,51.8,66.92,54.5,53.96,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-25",5,25,2018,{"$f":"DATE(D3463,B3463,C3463)","v":"2018-05-25"},{"$f":"WEEKDAY(E3463,2)","v":5},0,"02:00:00",2,44.6,46.04,44.06,46.4,51.08,48.2,52.519999999999996,48.2,53.96,48.92,48.2,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-25",5,25,2018,"2018-05-25",5,0,"05:00:00",5,41.54,46.04,42.620000000000005,46.4,46.76,48.2,53.06,46.4,52.34,48.2,48.2,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-25",5,25,2018,"2018-05-25",5,0,"16:00:00",16,39.200000000000003,44.6,41.54,46.4,80.06,44.96,61.88,44.96,64.580000000000013,50.900000000000006,50,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-25",5,25,2018,"2018-05-25",5,0,"22:00:00",22,34.880000000000003,40.28,38.299999999999997,39.380000000000003,55.94,42.8,54.68,42.8,60.26,42.8,44.78,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-26",5,26,2018,"2018-05-26",6,0,"06:00:00",6,35.42,39.019999999999996,40.82,39.200000000000003,55.94,39.92,54.68,41.9,53.42,41,42.08,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-26",5,26,2018,"2018-05-26",6,0,"15:00:00",15,43.52,53.06,51.980000000000004,51.8,75.92,55.040000000000006,73.580000000000013,59,81.86,57.379999999999995,55.94,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-26",5,26,2018,"2018-05-26",6,0,1,24,35.06,42.980000000000004,39.56,42.08,55.94,44.96,57.379999999999995,42.980000000000004,56.84,44.78,44.96,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-27",5,27,2018,"2018-05-27",7,0,"05:00:00",5,30.2,38.480000000000004,37.4,37.76,51.980000000000004,39.92,50.540000000000006,40.1,51.08,42.44,39.92,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-27",5,27,2018,"2018-05-27",7,0,"09:00:00",9,44.24,53.96,52.7,53.6,66.92,55.400000000000006,59,55.76,68.900000000000006,54.68,59,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-27",5,27,2018,"2018-05-27",7,0,"19:00:00",{"$f":"H3528*24","v":19},57.019999999999996,62.96,64.94,64.400000000000006,53.06,68,69.800000000000011,66.92,78.62,62.42,62.06,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-28",5,28,2018,"2018-05-28",1,1,"02:00:00",2,36.5,41,46.58,41,44.6,46.94,56.84,43.879999999999995,60.26,49.1,46.22,null,0,null,null,0,1,0,0,0,0,0,1,0,1,0,1,0]
["1978-05-28",5,28,2018,"2018-05-28",1,1,"09:00:00",9,51.44,62.06,56.84,57.2,46.22,66.02,51.8,63.86,63.14,57.74,58.28,null,0,null,null,0,1,0,0,0,0,0,1,0,1,0,1,0]
["1978-05-28",5,28,2018,"2018-05-28",1,1,"19:00:00",19,64.94,60.980000000000004,65.84,66.2,49.64,64.94,69.44,64.94,78.259999999999991,55.040000000000006,60.08,null,0,null,null,0,1,0,0,0,0,0,1,0,1,0,1,0]
["1978-05-29",5,29,2018,"2018-05-29",2,0,"02:00:00",2,44.06,51.08,55.58,50,39.92,57.92,61.88,57.2,60.980000000000004,51.8,50,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-29",5,29,2018,"2018-05-29",2,0,"12:00:00",12,51.44,60.08,58.1,53.6,64.039999999999992,60.8,78.800000000000011,62.6,86.9,59,57.2,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-29",5,29,2018,"2018-05-29",2,0,"16:00:00",16,53.6,62.06,67.28,55.400000000000006,71.06,66.2,81.319999999999993,66.92,90.5,63.14,60.08,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-29",5,29,2018,"2018-05-29",2,0,"21:00:00",21,55.94,57.2,67.64,55.400000000000006,55.94,62.6,72.14,64.400000000000006,70.88,55.400000000000006,59,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-30",5,30,2018,"2018-05-30",3,0,"06:00:00",6,57.2,57.2,64.22,57.2,45.68,64.94,55.400000000000006,66.92,66.38,62.6,64.039999999999992,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-30",5,30,2018,"2018-05-30",3,0,"14:00:00",14,80.960000000000008,87.080000000000013,84.2,82.4,66.02,87.080000000000013,60.8,86.9,69.62,86.36,87.080000000000013,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-30",5,30,2018,"2018-05-30",3,0,"20:00:00",20,64.94,82.039999999999992,75.2,73.400000000000006,57.92,80.960000000000008,53.6,75.92,61.7,76.819999999999993,78.98,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-31",5,31,2018,"2018-05-31",4,0,"07:00:00",7,64.94,71.06,60.8,66.2,50,73.039999999999992,54.5,73.94,55.76,74.300000000000011,75.92,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-31",5,31,2018,"2018-05-31",4,0,"13:00:00",13,84.2,91.94,89.6,87.800000000000011,59.900000000000006,93.02,73.580000000000013,92.84,75.02,91.76,91.039999999999992,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-05-31",5,31,2018,"2018-05-31",4,0,1,24,46.4,55.94,55.22,68.900000000000006,51.44,60.26,51.08,58.46,55.22,57.74,66.02,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["2002-06-01",6,1,2018,"2018-06-01",5,0,"03:00:00",3,39.56,51.44,51.44,67.28,49.64,51.26,44.96,51.8,50.72,50.18,61.519999999999996,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-01",6,1,2018,"2018-06-01",5,0,"09:00:00",9,56.480000000000004,66.02,59,73.94,56.66,68,53.42,61.88,54.5,61.88,73.94,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-01",6,1,2018,"2018-06-01",5,0,"17:00:00",17,75.92,75.02,71.06,82.94,69.98,73.94,60.980000000000004,75.02,69.080000000000013,74.66,77,null,0,null,null,0,0,1,0,0,1,1,1,1,1,0,1,0]
["2002-06-02",6,2,2018,{"$f":"DATE(D3655,B3655,C3655)","v":"2018-06-02"},{"$f":"WEEKDAY(E3655,2)","v":6},0,"02:00:00",2,48.379999999999995,55.94,52.16,55.040000000000006,50.36,57.92,46.04,51.980000000000004,52.16,56.3,55.040000000000006,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-02",6,2,2018,"2018-06-02",6,0,"14:00:00",14,84.02,64.039999999999992,64.039999999999992,77,60.980000000000004,68,58.28,71.06,62.96,69.44,71.960000000000008,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-02",6,2,2018,"2018-06-02",6,0,"19:00:00",19,77,57.92,60.08,66.02,55.94,62.06,48.92,64.039999999999992,53.24,59,59,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-02",6,2,2018,"2018-06-02",6,0,1,24,57.56,48.92,46.04,55.040000000000006,48.92,53.06,44.96,48.92,46.4,51.620000000000005,51.980000000000004,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-03",6,3,2018,"2018-06-03",7,0,"12:00:00",12,80.06,60.980000000000004,60.08,69.800000000000011,53.6,62.96,46.76,62.06,51.8,62.96,53.6,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-03",6,3,2018,"2018-06-03",7,0,"14:00:00",14,80.06,62.96,64.94,71.06,56.66,66.02,49.46,66.02,56.66,66.2,55.94,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-03",6,3,2018,"2018-06-03",7,0,"21:00:00",21,62.96,57.019999999999996,57.019999999999996,55.400000000000006,55.040000000000006,60.08,49.64,59,53.78,55.58,55.400000000000006,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-04",6,4,2018,"2018-06-04",1,0,"11:00:00",11,60.08,69.98,68,60.980000000000004,69.080000000000013,69.98,61.519999999999996,69.98,68,70.7,53.6,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-04",6,4,2018,"2018-06-04",1,0,"14:00:00",14,56.66,71.960000000000008,68,71.06,69.98,71.960000000000008,64.759999999999991,69.98,71.06,67.64,55.040000000000006,null,0,null,null,0,0,1,0,0,1,1,1,1,1,0,1,0]
["2002-06-05",6,5,2018,"2018-06-05",2,0,"01:00:00",1,51.620000000000005,55.94,53.96,57.92,55.040000000000006,55.94,50.36,55.400000000000006,53.96,56.3,50,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-05",6,5,2018,"2018-06-05",2,0,"07:00:00",7,53.96,55.040000000000006,55.400000000000006,64.039999999999992,55.94,55.400000000000006,51.620000000000005,55.94,54.14,54.32,50,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-05",6,5,2018,"2018-06-05",2,0,"15:00:00",15,66.02,57.019999999999996,57.92,80.06,53.24,55.94,49.82,55.94,56.3,53.6,51.8,null,0,null,null,0,0,1,0,0,1,1,1,1,1,0,1,0]
["2002-06-05",6,5,2018,"2018-06-05",2,0,1,24,57.92,51.08,53.06,59,53.6,51.980000000000004,45.32,51.08,50.900000000000006,49.64,50,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-06",6,6,2018,"2018-06-06",3,0,"09:00:00",9,57.92,48.92,48.2,62.6,47.120000000000005,48.92,42.8,48.92,49.46,48.2,51.08,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-06",6,6,2018,"2018-06-06",3,0,"14:00:00",14,62.96,48.019999999999996,50,62.6,50,48.92,45.32,48.92,48.56,48.2,57.2,null,0,null,null,0,0,1,0,0,1,1,1,1,1,0,1,0]
["2002-06-06",6,6,2018,"2018-06-06",3,0,"18:00:00",18,66.92,50,48.2,60.8,51.08,50,47.480000000000004,50,48.379999999999995,50.540000000000006,57.92,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-07",6,7,2018,"2018-06-07",4,0,"07:00:00",7,57.2,51.980000000000004,51.08,59,48.92,53.06,47.480000000000004,53.06,50.900000000000006,53.78,51.980000000000004,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-07",6,7,2018,"2018-06-07",4,0,"11:00:00",{"$f":"H3784*24","v":11},75.02,64.039999999999992,66.02,75.02,64.94,69.080000000000013,60.620000000000005,66.02,67.28,66.2,59,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-07",6,7,2018,"2018-06-07",4,0,"21:00:00",21,57.92,60.980000000000004,63.319999999999993,66.02,55.94,62.96,61.88,60.08,58.1,55.400000000000006,51.08,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-08",6,8,2018,"2018-06-08",5,0,"04:00:00",4,48.019999999999996,48.019999999999996,46.4,53.96,46.94,51.08,44.6,48.92,48.92,51.26,48.92,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-08",6,8,2018,"2018-06-08",5,0,"11:00:00",11,82.039999999999992,75.02,75.92,69.080000000000013,77,78.080000000000013,72.319999999999993,78.98,77.72,74.48,60.8,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-08",6,8,2018,"2018-06-08",5,0,"21:00:00",21,64.039999999999992,62.06,60.08,60.980000000000004,62.96,62.96,64.759999999999991,62.96,63.319999999999993,55.76,53.06,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-09",6,9,2018,"2018-06-09",6,0,"01:00:00",1,55.040000000000006,55.94,53.06,57.92,53.96,57.019999999999996,55.76,57.019999999999996,55.22,53.24,53.06,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-09",6,9,2018,"2018-06-09",6,0,"06:00:00",6,57.92,55.040000000000006,53.06,57.92,55.94,55.94,53.96,55.040000000000006,53.06,54.5,53.6,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-09",6,9,2018,"2018-06-09",6,0,"15:00:00",15,80.960000000000008,73.94,75.2,62.96,73.039999999999992,75.02,66.2,75.02,73.580000000000013,69.800000000000011,75.92,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-09",6,9,2018,"2018-06-09",6,0,"23:00:00",23,62.06,66.02,55.94,53.06,62.06,66.02,58.64,64.94,58.28,63.680000000000007,59,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-10",6,10,2018,"2018-06-10",7,0,"08:00:00",8,68,64.94,68,50,64.039999999999992,71.06,58.1,71.960000000000008,59.540000000000006,71.240000000000009,66.02,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-10",6,10,2018,"2018-06-10",7,0,"16:00:00",16,64.94,84.92,82.039999999999992,53.96,82.039999999999992,84.92,69.259999999999991,82.039999999999992,80.960000000000008,74.66,75.92,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-10",6,10,2018,"2018-06-10",7,0,"22:00:00",22,50,66.02,64.039999999999992,53.06,62.06,73.94,63.5,73.94,63.86,72.14,60.980000000000004,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-11",6,11,2018,"2018-06-11",1,0,"09:00:00",9,55.94,80.06,78.080000000000013,55.94,77,82.94,71.78,80.960000000000008,71.960000000000008,81.319999999999993,73.94,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-11",6,11,2018,"2018-06-11",1,0,"12:00:00",12,73.039999999999992,87.080000000000013,84.92,60.980000000000004,84.02,86,79.34,84.92,82.580000000000013,87.800000000000011,78.080000000000013,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-11",6,11,2018,"2018-06-11",1,0,"18:00:00",18,66.92,89.960000000000008,87.98,64.039999999999992,89.06,91.039999999999992,82.4,89.960000000000008,89.6,89.6,66.92,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-12",6,12,2018,"2018-06-12",2,0,"02:00:00",2,53.96,66.92,62.06,48.019999999999996,62.06,71.960000000000008,65.12,69.080000000000013,62.24,68.539999999999992,53.06,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-12",6,12,2018,"2018-06-12",2,0,"11:00:00",11,55.94,89.06,87.98,60.08,89.06,89.960000000000008,83.48,89.960000000000008,86.18,90.68,66.02,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-12",6,12,2018,"2018-06-12",2,0,"19:00:00",{"$f":"H3912*24","v":19},55.94,87.080000000000013,80.960000000000008,55.94,80.960000000000008,89.06,80.960000000000008,87.98,88.16,87.080000000000013,64.94,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-13",6,13,2018,"2018-06-13",3,0,"04:00:00",4,57.019999999999996,64.039999999999992,62.06,55.400000000000006,64.039999999999992,71.960000000000008,64.580000000000013,73.94,67.64,71.599999999999994,57.92,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-13",6,13,2018,"2018-06-13",3,0,"09:00:00",9,60.08,84.92,82.94,64.94,82.94,87.080000000000013,71.78,84.92,81.680000000000007,85.82,69.98,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-13",6,13,2018,"2018-06-13",3,0,"21:00:00",21,57.019999999999996,75.02,73.400000000000006,50,71.06,78.98,67.099999999999994,78.98,70.88,77.900000000000006,64.94,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-13",6,13,2018,"2018-06-13",3,0,"23:00:00",23,55.94,73.039999999999992,69.98,50,66.02,75.92,60.8,75.92,66.740000000000009,74.66,64.039999999999992,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-14",6,14,2018,"2018-06-14",4,0,"06:00:00",6,55.94,62.06,57.019999999999996,55.400000000000006,55.040000000000006,66.02,51.08,64.94,58.28,66.56,62.6,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-14",6,14,2018,"2018-06-14",4,0,"13:00:00",13,64.94,77,77,64.039999999999992,75.02,78.98,64.039999999999992,78.080000000000013,71.240000000000009,70.16,64.400000000000006,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-14",6,14,2018,"2018-06-14",4,0,"23:00:00",23,55.94,57.92,58.28,55.040000000000006,50,59,49.28,55.94,51.8,54.32,62.6,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-15",6,15,2018,"2018-06-15",5,0,"06:00:00",6,55.040000000000006,53.06,48.92,53.96,48.019999999999996,55.040000000000006,47.84,53.96,51.08,56.3,57.92,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-15",6,15,2018,"2018-06-15",5,0,"16:00:00",16,69.080000000000013,77,77,71.960000000000008,78.98,78.98,71.42,77,77.72,66.38,75.92,null,0,null,null,0,0,1,0,0,1,1,1,1,1,0,1,0]
["2002-06-15",6,15,2018,"2018-06-15",5,0,"20:00:00",20,62.24,66.92,68,62.06,73.039999999999992,68,62.42,66.92,66.740000000000009,60.44,62.96,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-16",6,16,2018,"2018-06-16",6,0,"09:00:00",9,58.1,62.06,64.039999999999992,71.06,60.980000000000004,64.94,51.44,64.94,55.76,62.78,68,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-16",6,16,2018,"2018-06-16",6,0,"10:00:00",10,61.34,64.039999999999992,66.02,73.039999999999992,60.08,66.02,51.980000000000004,66.92,57.2,63.86,69.98,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-16",6,16,2018,"2018-06-16",6,0,"19:00:00",19,66.02,57.92,60.980000000000004,73.039999999999992,62.96,57.92,52.879999999999995,57.92,57.56,55.400000000000006,66.92,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-17",6,17,2018,"2018-06-17",7,0,"03:00:00",3,57.019999999999996,57.019999999999996,59,51.980000000000004,59,57.2,50.36,57.2,55.76,57.2,51.980000000000004,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-17",6,17,2018,"2018-06-17",7,0,"09:00:00",9,65.48,60.980000000000004,62.96,71.06,64.94,62.06,55.400000000000006,60.980000000000004,60.980000000000004,61.34,62.6,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-17",6,17,2018,"2018-06-17",7,0,"20:00:00",20,71.06,69.080000000000013,69.98,71.06,71.960000000000008,69.98,67.28,69.800000000000011,68.900000000000006,62.6,55.040000000000006,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-18",6,18,2018,"2018-06-18",1,0,"06:00:00",6,66.92,68,68,57.019999999999996,71.960000000000008,71.06,65.300000000000011,69.800000000000011,66.2,64.400000000000006,51.980000000000004,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-18",6,18,2018,"2018-06-18",1,0,"13:00:00",13,71.06,84.92,80.599999999999994,75.92,84.92,86,77.539999999999992,86,82.039999999999992,84.02,66.02,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-18",6,18,2018,"2018-06-18",1,0,"20:00:00",20,68,80.06,77,72.86,78.98,80.06,75.56,78.98,79.7,74.12,55.040000000000006,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-18",6,18,2018,"2018-06-18",1,0,"22:00:00",22,66.02,75.02,75.92,57.92,78.080000000000013,77,69.800000000000011,75.92,76.64,71.42,51.08,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-19",6,19,2018,"2018-06-19",2,0,"06:00:00",6,57.92,73.400000000000006,75.02,57.019999999999996,73.94,75.02,69.62,75.2,69.800000000000011,76.28,53.96,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-19",6,19,2018,"2018-06-19",2,0,"15:00:00",15,71.960000000000008,84.92,71.599999999999994,78.98,75.92,86,73.039999999999992,84.02,74.84,81.86,66.92,null,0,null,null,0,0,1,0,0,1,1,1,1,1,0,1,0]
["2002-06-20",6,20,2018,"2018-06-20",3,0,"03:00:00",3,46.04,69.080000000000013,68,51.08,69.800000000000011,71.06,63.5,69.98,66.2,70.88,55.400000000000006,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-20",6,20,2018,"2018-06-20",3,0,"08:00:00",8,51.44,71.06,73.94,66.02,73.94,75.02,64.039999999999992,73.94,71.599999999999994,71.599999999999994,57.2,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-20",6,20,{"$f":"$AO$4","v":2018},"2018-06-20",3,{"$f":"COUNTIF($AM$34:$AM$43,E4102)","v":0},"17:00:00",17,59,82.94,78.98,86,77,82.039999999999992,69.44,82.039999999999992,73.759999999999991,82.759999999999991,75.02,null,{"$f":"SUMPRODUCT($J$2:$T$2,J4102:T4102)","v":0},null,null,{"$f":"OR(B4102<=$AO$14,B4102>=$AN$14)*(F4102<6)*(I4102>$AN$15)*(I4102<=$AO$15)*(G4102<>1)","v":0},{"$f":"OR(B4102<=$AO$14,B4102>=$AN$14)*(Y4102=0)","v":0},{"$f":"AND(B4102>=$AN$24,B4102<=$AO$24)*(F4102<6)*(I4102>$AN$25)*(I4102<=$AO$25)*(G4102<>1)","v":1},{"$f":"AND(B4102>=$AN$24,B4102<=$AO$24)*(AA4102=0)","v":0},{"$f":"OR(B4102<=$AO$19,B4102>=$AN$19)*(F4102<6)*(I4102>$AN$20)*(I4102<=$AO$20)","v":0},{"$f":"AND(B4102>=$AN$29,B4102<=$AO$29)*(F4102<6)*(I4102>$AN$30)*(I4102<=$AO$30)","v":1},{"$f":"IF(OR(E4102=$AM$34,E4102=$AM$35,E4102=$AM$36,E4102=$AM$37,E4102=$AM$38,E4102=$AM$39,E4102=$AM$40,E4102=$AM$41,E4102=$AM$42,E4102=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E4102>=$AM$47,E4102<=$AN$47),AND(E4102>=$AM$48,E4102<=$AN$48),AND(E4102>=$AM$49,E4102<=$AN$49),AND(E4102>=$AM$50,E4102<=$AN$50),AND(E4102>=$AM$51,E4102<=$AN$51)),0,1)*AE4102","v":1},{"$f":"(B4102>=5)*(B4102<=10)","v":1},{"$f":"1*OR(B4102<=4,B4102>=11)","v":0},{"$f":"LOOKUP(B4102,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE4102:AI4102)*((F4102<6)*(I4102>$AO$7)*(I4102<=$AP$7)+(F4102=6)*(I4102>$AO$8)*(I4102<=$AP$8)+(F4102>=7)*(I4102>$AO$9)*(I4102<=$AP$9))","v":0}]
["2002-06-21",6,21,2018,"2018-06-21",4,0,"01:00:00",1,42.26,62.96,59,66.02,60.980000000000004,64.94,57.2,62.06,60.44,64.759999999999991,64.94,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-21",6,21,2018,"2018-06-21",4,0,"07:00:00",7,46.76,66.02,64.039999999999992,68,64.94,66.02,58.64,69.080000000000013,58.1,68.36,73.94,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-21",6,21,2018,"2018-06-21",4,0,"10:00:00",10,62.06,77,71.78,80.960000000000008,66.02,78.080000000000013,60.620000000000005,77,70.16,79.16,87.080000000000013,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-21",6,21,2018,"2018-06-21",4,0,1,24,44.24,59,55.040000000000006,73.039999999999992,55.94,68,55.58,64.039999999999992,63.680000000000007,64.039999999999992,80.06,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-22",6,22,2018,"2018-06-22",5,0,"03:00:00",3,40.28,53.96,57.379999999999995,68,53.06,60.980000000000004,50.72,57.019999999999996,54.68,59.540000000000006,80.06,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-22",6,22,2018,"2018-06-22",5,0,"14:00:00",14,75.02,80.960000000000008,78.080000000000013,78.98,78.98,82.039999999999992,69.080000000000013,80.960000000000008,75.56,81.86,91.039999999999992,null,0,null,null,0,0,1,0,0,1,1,1,1,1,0,1,0]
["2002-06-22",6,22,2018,"2018-06-22",5,0,"20:00:00",20,55.040000000000006,75.92,69.98,64.94,66.02,75.92,66.02,71.06,70.7,67.28,84.02,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["2002-06-23",6,23,2018,"2018-06-23",6,0,"04:00:00",4,45.86,62.96,62.06,51.980000000000004,62.06,69.080000000000013,56.120000000000005,68,61.16,67.64,66.92,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-23",6,23,2018,"2018-06-23",6,0,"13:00:00",13,80.06,82.94,87.98,66.02,87.080000000000013,87.98,72.680000000000007,89.06,76.28,79.16,91.94,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-23",6,23,2018,"2018-06-23",6,0,"18:00:00",18,73.94,82.94,78.98,68,82.039999999999992,86,70.16,82.94,75.2,75.02,75.92,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-23",6,23,2018,"2018-06-23",6,0,"22:00:00",22,57.92,75.02,75.92,55.040000000000006,75.92,78.080000000000013,66.2,75.92,70.7,75.740000000000009,71.06,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-24",6,24,2018,"2018-06-24",7,0,"11:00:00",11,71.960000000000008,75.02,73.94,71.960000000000008,73.94,77,67.28,78.080000000000013,75.56,82.580000000000013,80.06,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-24",6,24,2018,"2018-06-24",7,0,"15:00:00",15,73.94,84.92,82.94,75.02,82.94,87.080000000000013,73.400000000000006,86,80.599999999999994,85.460000000000008,80.06,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["2002-06-25",6,25,2018,"2018-06-25",1,0,"01:00:00",1,66.02,69.080000000000013,60.08,53.96,64.039999999999992,71.06,57.56,71.06,56.66,67.28,60.980000000000004,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["2002-06-25",6,25,2018,"2018-06-25",1,0,"08:00:00",8,69.080000000000013,68,69.080000000000013,64.94,69.98,73.039999999999992,60.44,71.960000000000008,66.02,72.5,71.960000000000008,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["2002-06-25",6,25,2018,"2018-06-25",1,0,"15:00:00",15,69.98,82.94,80.06,78.98,80.06,82.039999999999992,71.599999999999994,78.080000000000013,74.12,79.88,82.039999999999992,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["2002-06-26",6,26,{"$f":"$AO$4","v":2018},"2018-06-26",2,{"$f":"COUNTIF($AM$34:$AM$43,E4230)","v":0},"01:00:00",1,64.039999999999992,66.02,60.08,55.94,57.92,62.96,51.8,60.08,55.400000000000006,63.14,64.94,null,{"$f":"SUMPRODUCT($J$2:$T$2,J4230:T4230)","v":0},null,null,{"$f":"OR(B4230<=$AO$14,B4230>=$AN$14)*(F4230<6)*(I4230>$AN$15)*(I4230<=$AO$15)*(G4230<>1)","v":0},{"$f":"OR(B4230<=$AO$14,B4230>=$AN$14)*(Y4230=0)","v":0},{"$f":"AND(B4230>=$AN$24,B4230<=$AO$24)*(F4230<6)*(I4230>$AN$25)*(I4230<=$AO$25)*(G4230<>1)","v":0},{"$f":"AND(B4230>=$AN$24,B4230<=$AO$24)*(AA4230=0)","v":1},{"$f":"OR(B4230<=$AO$19,B4230>=$AN$19)*(F4230<6)*(I4230>$AN$20)*(I4230<=$AO$20)","v":0},{"$f":"AND(B4230>=$AN$29,B4230<=$AO$29)*(F4230<6)*(I4230>$AN$30)*(I4230<=$AO$30)","v":0},{"$f":"IF(OR(E4230=$AM$34,E4230=$AM$35,E4230=$AM$36,E4230=$AM$37,E4230=$AM$38,E4230=$AM$39,E4230=$AM$40,E4230=$AM$41,E4230=$AM$42,E4230=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E4230>=$AM$47,E4230<=$AN$47),AND(E4230>=$AM$48,E4230<=$AN$48),AND(E4230>=$AM$49,E4230<=$AN$49),AND(E4230>=$AM$50,E4230<=$AN$50),AND(E4230>=$AM$51,E4230<=$AN$51)),0,1)*AE4230","v":0},{"$f":"(B4230>=5)*(B4230<=10)","v":1},{"$f":"1*OR(B4230<=4,B4230>=11)","v":0},{"$f":"LOOKUP(B4230,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE4230:AI4230)*((F4230<6)*(I4230>$AO$7)*(I4230<=$AP$7)+(F4230=6)*(I4230>$AO$8)*(I4230<=$AP$8)+(F4230>=7)*(I4230>$AO$9)*(I4230<=$AP$9))","v":0}]
["2002-06-26",6,26,2018,"2018-06-26",2,0,"05:00:00",5,62.96,60.08,53.96,55.040000000000006,53.06,60.08,49.82,57.019999999999996,49.28,60.620000000000005,62.96,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["2002-06-26",6,26,2018,"2018-06-26",2,0,"10:00:00",10,64.94,71.960000000000008,69.98,73.039999999999992,69.98,71.960000000000008,58.46,71.960000000000008,66.02,72.5,71.599999999999994,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["2002-06-26",6,26,2018,"2018-06-26",2,0,"19:00:00",19,66.02,69.080000000000013,66.92,75.02,60.08,69.080000000000013,59.36,62.96,65.300000000000011,68.72,64.400000000000006,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["2002-06-27",6,27,2018,"2018-06-27",3,0,"03:00:00",3,48.019999999999996,55.94,55.400000000000006,55.040000000000006,55.94,57.019999999999996,47.480000000000004,55.040000000000006,50.900000000000006,57.74,60.8,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["2002-06-27",6,27,2018,"2018-06-27",3,0,"12:00:00",12,80.06,69.080000000000013,64.94,84.02,69.080000000000013,71.960000000000008,63.319999999999993,71.960000000000008,66.92,71.240000000000009,68,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["2002-06-27",6,27,2018,"2018-06-27",3,0,"18:00:00",18,80.960000000000008,64.039999999999992,62.6,82.039999999999992,60.26,69.080000000000013,54.32,66.92,58.46,60.8,62.96,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["2002-06-28",6,28,2018,"2018-06-28",4,0,"05:00:00",5,46.04,50.540000000000006,46.4,66.92,48.92,53.06,44.06,53.06,48.2,53.78,60.08,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["2002-06-28",6,28,2018,"2018-06-28",4,0,"11:00:00",11,82.039999999999992,68,69.98,82.94,68,71.06,58.82,71.960000000000008,65.66,70.88,68,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["2002-06-28",6,28,2018,"2018-06-28",4,0,"22:00:00",22,55.94,57.92,55.040000000000006,73.039999999999992,53.96,64.039999999999992,52.34,60.08,55.400000000000006,60.620000000000005,64.039999999999992,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["2002-06-29",6,29,2018,"2018-06-29",5,0,"01:00:00",1,48.92,51.980000000000004,51.980000000000004,71.06,51.08,59,48.74,55.94,50,56.66,62.96,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["2002-06-29",6,29,2018,"2018-06-29",5,0,"07:00:00",7,60.980000000000004,57.019999999999996,57.019999999999996,69.98,55.040000000000006,62.06,53.78,64.039999999999992,51.26,61.88,66.92,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["2002-06-29",6,29,2018,"2018-06-29",5,0,"15:00:00",15,84.02,71.06,73.039999999999992,80.599999999999994,68,73.94,61.519999999999996,75.92,64.94,73.22,78.98,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["2002-06-29",6,29,2018,"2018-06-29",5,0,1,24,57.019999999999996,62.96,66.02,69.98,60.980000000000004,69.98,50,69.080000000000013,58.28,68,60.980000000000004,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["2002-06-30",6,30,2018,"2018-06-30",6,0,"05:00:00",5,55.040000000000006,60.980000000000004,60.08,62.6,62.06,66.92,50,64.94,58.46,65.84,60.08,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["2002-06-30",6,30,2018,"2018-06-30",6,0,"17:00:00",17,84.92,84.02,75.2,77,73.94,82.94,69.62,82.039999999999992,80.240000000000009,78.800000000000011,84.92,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["2002-06-30",6,30,2018,"2018-06-30",6,0,"22:00:00",22,62.78,69.080000000000013,68.180000000000007,66.56,67.460000000000008,70.7,61.88,68.539999999999992,66.02,68.180000000000007,72.680000000000007,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-01",7,1,2018,{"$f":"DATE(D4359,B4359,C4359)","v":"2018-07-01"},{"$f":"WEEKDAY(E4359,2)","v":7},0,"10:00:00",10,71.960000000000008,64.039999999999992,73.400000000000006,80.599999999999994,66.02,64.94,67.28,78.080000000000013,73.580000000000013,64.400000000000006,82.039999999999992,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-01",7,1,2018,"2018-07-01",7,0,"12:00:00",12,77,64.94,78.800000000000011,82.4,68,66.92,69.080000000000013,80.960000000000008,77.72,64.039999999999992,84.92,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-01",7,1,2018,"2018-07-01",7,0,"19:00:00",19,73.94,68,80.599999999999994,84.2,71.06,69.98,69.080000000000013,78.080000000000013,78.98,69.800000000000011,84.02,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-02",7,2,2018,"2018-07-02",1,0,"02:00:00",2,48.92,62.06,57.2,75.2,60.980000000000004,62.06,55.76,62.06,55.400000000000006,61.88,73.94,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-02",7,2,2018,"2018-07-02",1,0,"12:00:00",12,80.960000000000008,75.92,80.599999999999994,87.800000000000011,73.039999999999992,75.92,74.300000000000011,84.92,79.16,76.099999999999994,89.960000000000008,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-02",7,2,2018,"2018-07-02",1,0,"23:00:00",23,62.96,60.08,64.400000000000006,69.800000000000011,53.96,64.94,61.34,69.800000000000011,62.96,64.400000000000006,69.98,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-03",7,3,2018,"2018-07-03",2,0,"05:00:00",5,59,51.08,57.2,68,46.04,57.92,57.74,64.94,59.900000000000006,56.120000000000005,68,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-03",7,3,2018,"2018-07-03",2,0,"13:00:00",13,68,78.080000000000013,71.599999999999994,78.800000000000011,78.080000000000013,77,62.24,77,69.080000000000013,77.72,78.080000000000013,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-03",7,3,2018,"2018-07-03",2,0,"22:00:00",22,48.019999999999996,65.48,55.400000000000006,68,64.400000000000006,66.02,52.519999999999996,60.08,52.879999999999995,62.06,68,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-03",7,3,2018,"2018-07-03",2,0,"23:00:00",23,51.8,64.22,53.6,66.2,53.06,64.039999999999992,51.26,57.019999999999996,50.36,61.34,66.92,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-04",7,4,2018,"2018-07-04",3,1,"07:00:00",7,60.08,57.92,53.6,68,55.040000000000006,60.08,54.5,66.92,53.42,62.78,69.080000000000013,null,0,null,null,0,0,0,1,0,0,0,1,0,1,0,1,0]
["1981-07-04",7,4,2018,"2018-07-04",3,1,"20:00:00",20,59,66.92,73.400000000000006,66.2,62.96,64.94,66.38,73.039999999999992,66.92,63.319999999999993,66.02,null,0,null,null,0,0,0,1,0,0,0,1,0,1,0,1,0]
["1981-07-04",7,4,2018,"2018-07-04",3,1,1,24,57.379999999999995,53.96,63.319999999999993,60.8,59,57.92,56.84,64.94,54.5,57.56,64.039999999999992,null,0,null,null,0,0,0,1,0,0,0,1,0,1,0,1,0]
["1981-07-05",7,5,2018,"2018-07-05",4,0,"10:00:00",10,75.92,75.92,73.400000000000006,66.2,73.94,75.92,69.800000000000011,82.039999999999992,73.94,76.099999999999994,69.080000000000013,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-05",7,5,2018,"2018-07-05",4,0,"17:00:00",17,80.960000000000008,82.94,84.2,77,82.039999999999992,82.94,76.099999999999994,84.92,84.2,82.580000000000013,78.080000000000013,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["1981-07-05",7,5,2018,"2018-07-05",4,0,1,24,60.08,62.96,64.400000000000006,69.800000000000011,64.039999999999992,68,60.980000000000004,71.06,67.099999999999994,65.300000000000011,69.98,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-06",7,6,2018,"2018-07-06",5,0,"10:00:00",10,78.080000000000013,78.080000000000013,73.400000000000006,73.400000000000006,75.92,80.960000000000008,72.86,73.039999999999992,71.06,78.800000000000011,75.02,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-06",7,6,{"$f":"$AO$4","v":2018},"2018-07-06",5,{"$f":"COUNTIF($AM$34:$AM$43,E4486)","v":0},"17:00:00",17,84.02,84.02,86,82.4,82.94,84.92,77.900000000000006,87.080000000000013,86,76.460000000000008,82.039999999999992,null,{"$f":"SUMPRODUCT($J$2:$T$2,J4486:T4486)","v":0},null,null,{"$f":"OR(B4486<=$AO$14,B4486>=$AN$14)*(F4486<6)*(I4486>$AN$15)*(I4486<=$AO$15)*(G4486<>1)","v":0},{"$f":"OR(B4486<=$AO$14,B4486>=$AN$14)*(Y4486=0)","v":0},{"$f":"AND(B4486>=$AN$24,B4486<=$AO$24)*(F4486<6)*(I4486>$AN$25)*(I4486<=$AO$25)*(G4486<>1)","v":1},{"$f":"AND(B4486>=$AN$24,B4486<=$AO$24)*(AA4486=0)","v":0},{"$f":"OR(B4486<=$AO$19,B4486>=$AN$19)*(F4486<6)*(I4486>$AN$20)*(I4486<=$AO$20)","v":0},{"$f":"AND(B4486>=$AN$29,B4486<=$AO$29)*(F4486<6)*(I4486>$AN$30)*(I4486<=$AO$30)","v":1},{"$f":"IF(OR(E4486=$AM$34,E4486=$AM$35,E4486=$AM$36,E4486=$AM$37,E4486=$AM$38,E4486=$AM$39,E4486=$AM$40,E4486=$AM$41,E4486=$AM$42,E4486=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E4486>=$AM$47,E4486<=$AN$47),AND(E4486>=$AM$48,E4486<=$AN$48),AND(E4486>=$AM$49,E4486<=$AN$49),AND(E4486>=$AM$50,E4486<=$AN$50),AND(E4486>=$AM$51,E4486<=$AN$51)),0,1)*AE4486","v":0},{"$f":"(B4486>=5)*(B4486<=10)","v":1},{"$f":"1*OR(B4486<=4,B4486>=11)","v":0},{"$f":"LOOKUP(B4486,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE4486:AI4486)*((F4486<6)*(I4486>$AO$7)*(I4486<=$AP$7)+(F4486=6)*(I4486>$AO$8)*(I4486<=$AP$8)+(F4486>=7)*(I4486>$AO$9)*(I4486<=$AP$9))","v":0}]
["1981-07-06",7,6,2018,"2018-07-06",5,0,"19:00:00",{"$f":"H4488*24","v":19},78.080000000000013,75.92,84.2,78.800000000000011,73.039999999999992,80.960000000000008,73.580000000000013,80.960000000000008,82.759999999999991,71.960000000000008,77,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-07",7,7,2018,"2018-07-07",6,0,"07:00:00",7,66.92,69.98,64.400000000000006,68,66.02,71.960000000000008,65.12,77,60.08,68,69.080000000000013,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-07",7,7,2018,"2018-07-07",6,0,"12:00:00",12,86,82.039999999999992,84.2,80.599999999999994,80.06,84.02,77.539999999999992,91.039999999999992,85.460000000000008,81.680000000000007,82.039999999999992,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-07",7,7,2018,"2018-07-07",6,0,"21:00:00",21,69.98,73.039999999999992,71.599999999999994,71.599999999999994,75.92,75.92,70.88,77,71.599999999999994,77,73.400000000000006,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-08",7,8,2018,"2018-07-08",7,0,"06:00:00",6,64.039999999999992,69.98,62.6,66.2,71.960000000000008,71.960000000000008,55.400000000000006,66.92,64.94,73.400000000000006,71.06,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-08",7,8,2018,"2018-07-08",7,0,"14:00:00",14,75.92,80.06,89.6,84.2,78.080000000000013,82.039999999999992,72.5,84.02,77.72,84.2,87.080000000000013,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-08",7,8,2018,"2018-07-08",7,0,"20:00:00",20,66.92,73.039999999999992,78.800000000000011,80.599999999999994,66.92,75.02,66.02,78.080000000000013,73.400000000000006,70.7,80.960000000000008,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-08",7,8,2018,"2018-07-08",7,0,"23:00:00",23,64.039999999999992,66.02,71.599999999999994,78.800000000000011,57.92,66.92,62.78,66.2,69.44,68,75.92,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-09",7,9,2018,{"$f":"DATE(D4551,B4551,C4551)","v":"2018-07-09"},{"$f":"WEEKDAY(E4551,2)","v":1},0,"10:00:00",10,64.039999999999992,69.98,69.800000000000011,78.800000000000011,68,69.98,53.6,66.2,63.86,68.36,80.06,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-09",7,9,2018,"2018-07-09",1,0,"16:00:00",16,63.86,73.039999999999992,78.800000000000011,82.4,73.039999999999992,75.92,62.96,69.98,67.819999999999993,69.800000000000011,84.92,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["1981-07-09",7,9,2018,"2018-07-09",1,0,1,24,60.08,60.8,62.6,64.400000000000006,66.92,60.980000000000004,58.1,62.06,60.8,60.8,66.02,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-10",7,10,2018,"2018-07-10",2,0,"09:00:00",9,59,73.039999999999992,60.8,68,69.98,73.94,52.519999999999996,60.980000000000004,58.1,66.2,73.039999999999992,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-10",7,10,2018,"2018-07-10",2,0,"17:00:00",17,60.08,82.94,62.6,78.800000000000011,82.039999999999992,84.02,50,62.6,60.44,82.94,78.98,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["1981-07-11",7,11,2018,"2018-07-11",3,0,"02:00:00",2,51.26,60.08,57.2,55.400000000000006,53.96,66.02,46.4,59,56.3,63.14,57.019999999999996,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-11",7,11,2018,"2018-07-11",3,0,"07:00:00",7,51.8,66.92,59,60.8,60.980000000000004,69.98,48.2,59,56.3,69.800000000000011,62.96,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-11",7,11,2018,"2018-07-11",3,0,"11:00:00",11,54.5,80.960000000000008,64.400000000000006,71.599999999999994,82.039999999999992,82.039999999999992,54.14,62.6,60.26,83.12,75.02,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-11",7,11,2018,"2018-07-11",3,0,"21:00:00",21,60.08,71.06,62.6,68,68,75.92,55.76,60.8,62.78,73.759999999999991,64.039999999999992,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-12",7,12,2018,"2018-07-12",4,0,"04:00:00",4,55.94,60.08,59,57.2,57.92,66.02,52.879999999999995,57.92,60.26,66.92,57.92,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-12",7,12,2018,"2018-07-12",4,0,"11:00:00",11,68,82.94,69.800000000000011,77,84.02,86,64.039999999999992,68,72.319999999999993,84.92,78.98,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-12",7,12,2018,"2018-07-12",4,0,"21:00:00",21,59,73.94,62.6,75.2,69.98,78.98,65.12,66.02,63.319999999999993,77.180000000000007,69.080000000000013,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-13",7,13,2018,"2018-07-13",5,0,"04:00:00",4,48.019999999999996,66.02,53.6,66.2,64.039999999999992,71.960000000000008,48.2,55.94,50.36,68,64.039999999999992,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-13",7,13,2018,"2018-07-13",5,0,"14:00:00",14,84.02,80.06,82.4,80.599999999999994,86,80.960000000000008,78.44,86,82.759999999999991,75.56,82.94,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["1981-07-13",7,13,2018,"2018-07-13",5,0,"18:00:00",18,78.98,78.080000000000013,82.4,77,80.960000000000008,78.080000000000013,73.759999999999991,84.92,83.48,70.16,80.06,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-13",7,13,2018,"2018-07-13",5,0,"23:00:00",23,62.06,66.92,64.400000000000006,69.800000000000011,64.94,66.92,66.38,71.960000000000008,60.980000000000004,64.759999999999991,71.06,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-14",7,14,2018,"2018-07-14",6,0,"08:00:00",8,69.98,62.96,69.800000000000011,73.400000000000006,64.580000000000013,69.080000000000013,68.36,75.92,64.759999999999991,66.2,78.080000000000013,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-14",7,14,2018,"2018-07-14",6,0,"16:00:00",16,87.98,77,89.6,84.2,75.02,80.599999999999994,83.300000000000011,89.960000000000008,89.78,69.800000000000011,82.94,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-14",7,14,2018,"2018-07-14",6,0,"22:00:00",22,69.080000000000013,69.98,77,75.2,66.92,75.02,71.960000000000008,77,72.5,68.900000000000006,75.02,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-15",7,15,2018,"2018-07-15",7,0,"09:00:00",9,82.94,75.02,73.400000000000006,73.400000000000006,66.02,78.800000000000011,72.14,75.92,73.94,75.2,75.02,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-15",7,15,2018,"2018-07-15",7,0,"15:00:00",15,84.92,77,86,75.2,71.06,80.960000000000008,78.800000000000011,86,84.740000000000009,76.099999999999994,78.98,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-16",7,16,2018,"2018-07-16",1,0,"02:00:00",2,62.06,53.96,66.2,68,48.019999999999996,60.980000000000004,64.759999999999991,71.599999999999994,67.28,58.82,71.06,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-16",7,16,2018,"2018-07-16",1,0,"05:00:00",5,60.08,48.92,69.800000000000011,68,46.04,55.94,62.24,71.06,66.2,55.94,71.06,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-16",7,16,2018,"2018-07-16",1,0,"11:00:00",11,80.06,66.92,84.2,69.800000000000011,68,71.06,74.66,87.98,80.78,69.62,71.06,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-16",7,16,2018,"2018-07-16",1,0,"19:00:00",19,73.94,73.039999999999992,73.400000000000006,73.400000000000006,68,75.02,74.66,82.94,83.84,63.319999999999993,73.039999999999992,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-17",7,17,2018,"2018-07-17",2,0,"04:00:00",4,55.94,48.92,64.400000000000006,62.6,46.94,57.019999999999996,59.540000000000006,66.02,60.8,54.68,62.06,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-17",7,17,2018,"2018-07-17",2,0,"16:00:00",16,75.02,78.98,82.4,78.800000000000011,78.080000000000013,80.06,73.22,87.98,80.240000000000009,71.06,80.06,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["1981-07-17",7,17,2018,"2018-07-17",2,0,"21:00:00",21,62.96,69.080000000000013,69.800000000000011,68,64.94,73.039999999999992,66.2,75.92,68,66.56,68,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-18",7,18,2018,"2018-07-18",3,0,"06:00:00",6,60.980000000000004,64.039999999999992,66.2,55.400000000000006,64.94,66.02,61.34,71.06,63.86,64.759999999999991,60.08,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-18",7,18,2018,"2018-07-18",3,0,"15:00:00",15,80.06,75.92,82.4,78.800000000000011,73.94,75.92,70.52,84.92,79.16,74.84,78.98,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["1981-07-18",7,18,2018,"2018-07-18",3,0,"23:00:00",23,64.039999999999992,71.960000000000008,66.2,60.8,69.98,71.960000000000008,60.620000000000005,71.06,63.680000000000007,70.88,60.980000000000004,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-19",7,19,2018,"2018-07-19",4,0,"05:00:00",5,60.980000000000004,68,60.8,55.400000000000006,71.06,69.98,57.74,66.02,60.8,68,55.94,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-19",7,19,2018,"2018-07-19",4,0,"08:00:00",8,62.78,69.98,69.800000000000011,64.400000000000006,73.039999999999992,75.92,62.96,80.960000000000008,63.14,78.080000000000013,71.06,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-19",7,19,2018,"2018-07-19",4,0,"15:00:00",15,78.98,91.039999999999992,73.400000000000006,75.2,89.960000000000008,89.960000000000008,71.78,93.56,78.44,86.539999999999992,75.92,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["1981-07-20",7,20,{"$f":"$AO$4","v":2018},"2018-07-20",5,{"$f":"COUNTIF($AM$34:$AM$43,E4806)","v":0},"01:00:00",1,57.92,69.98,66.2,62.6,69.080000000000013,73.039999999999992,60.08,73.94,63.14,68.72,62.06,null,{"$f":"SUMPRODUCT($J$2:$T$2,J4806:T4806)","v":0},null,null,{"$f":"OR(B4806<=$AO$14,B4806>=$AN$14)*(F4806<6)*(I4806>$AN$15)*(I4806<=$AO$15)*(G4806<>1)","v":0},{"$f":"OR(B4806<=$AO$14,B4806>=$AN$14)*(Y4806=0)","v":0},{"$f":"AND(B4806>=$AN$24,B4806<=$AO$24)*(F4806<6)*(I4806>$AN$25)*(I4806<=$AO$25)*(G4806<>1)","v":0},{"$f":"AND(B4806>=$AN$24,B4806<=$AO$24)*(AA4806=0)","v":1},{"$f":"OR(B4806<=$AO$19,B4806>=$AN$19)*(F4806<6)*(I4806>$AN$20)*(I4806<=$AO$20)","v":0},{"$f":"AND(B4806>=$AN$29,B4806<=$AO$29)*(F4806<6)*(I4806>$AN$30)*(I4806<=$AO$30)","v":0},{"$f":"IF(OR(E4806=$AM$34,E4806=$AM$35,E4806=$AM$36,E4806=$AM$37,E4806=$AM$38,E4806=$AM$39,E4806=$AM$40,E4806=$AM$41,E4806=$AM$42,E4806=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E4806>=$AM$47,E4806<=$AN$47),AND(E4806>=$AM$48,E4806<=$AN$48),AND(E4806>=$AM$49,E4806<=$AN$49),AND(E4806>=$AM$50,E4806<=$AN$50),AND(E4806>=$AM$51,E4806<=$AN$51)),0,1)*AE4806","v":0},{"$f":"(B4806>=5)*(B4806<=10)","v":1},{"$f":"1*OR(B4806<=4,B4806>=11)","v":0},{"$f":"LOOKUP(B4806,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE4806:AI4806)*((F4806<6)*(I4806>$AO$7)*(I4806<=$AP$7)+(F4806=6)*(I4806>$AO$8)*(I4806<=$AP$8)+(F4806>=7)*(I4806>$AO$9)*(I4806<=$AP$9))","v":0}]
["1981-07-20",7,20,2018,"2018-07-20",5,0,"12:00:00",12,66.92,89.960000000000008,71.599999999999994,71.599999999999994,87.080000000000013,89.06,62.6,77,67.819999999999993,88.34,73.94,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-20",7,20,2018,"2018-07-20",5,0,"18:00:00",18,62.96,87.080000000000013,71.599999999999994,73.400000000000006,84.92,89.06,61.16,73.94,70.88,87.080000000000013,71.06,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-21",7,21,2018,"2018-07-21",6,0,"02:00:00",2,50,66.02,51.8,57.2,64.039999999999992,71.06,48.74,57.92,53.96,66.92,55.040000000000006,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-21",7,21,2018,"2018-07-21",6,0,"11:00:00",11,73.039999999999992,78.080000000000013,73.94,71.599999999999994,70.34,84.02,65.300000000000011,77,72.5,72.319999999999993,75.92,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-21",7,21,2018,"2018-07-21",6,0,"16:00:00",16,73.94,84.92,79.52,78.800000000000011,78.98,87.98,67.28,80.06,77.180000000000007,68.900000000000006,75.92,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-21",7,21,2018,"2018-07-21",6,0,"20:00:00",20,59,75.92,73.580000000000013,73.400000000000006,68,80.960000000000008,64.94,71.960000000000008,65.48,66.2,66.02,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-22",7,22,2018,"2018-07-22",7,0,"09:00:00",9,63.14,73.039999999999992,69.800000000000011,73.400000000000006,71.06,73.94,62.96,78.98,65.84,75.740000000000009,77,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-22",7,22,2018,"2018-07-22",7,0,"13:00:00",13,80.960000000000008,78.98,82.4,84.2,66.02,82.039999999999992,74.66,86,80.599999999999994,81.14,87.080000000000013,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-22",7,22,2018,"2018-07-22",7,0,"23:00:00",23,64.94,68,64.400000000000006,75.2,62.06,66.92,67.819999999999993,73.94,62.78,65.66,71.960000000000008,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-23",7,23,2018,"2018-07-23",1,0,"06:00:00",6,64.94,60.980000000000004,68.900000000000006,71.599999999999994,59,64.039999999999992,63.86,73.039999999999992,67.819999999999993,65.300000000000011,71.960000000000008,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-23",7,23,2018,"2018-07-23",1,0,"13:00:00",13,86,78.080000000000013,91.4,87.800000000000011,75.02,78.98,79.7,91.94,88.16,76.28,89.960000000000008,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-23",7,23,2018,"2018-07-23",1,0,"23:00:00",23,66.92,64.039999999999992,73.400000000000006,69.800000000000011,62.96,69.080000000000013,64.039999999999992,80.06,68.36,64.400000000000006,69.98,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-24",7,24,2018,"2018-07-24",2,0,"03:00:00",3,60.8,57.019999999999996,66.2,68,55.94,64.94,62.96,75.02,66.2,63.5,69.98,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-24",7,24,2018,"2018-07-24",2,0,"08:00:00",8,68,64.94,75.2,66.2,64.039999999999992,69.98,64.94,82.94,69.62,71.240000000000009,68,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-24",7,24,2018,"2018-07-24",2,0,"17:00:00",17,64.039999999999992,77,86,77,68.36,71.960000000000008,68.72,89.960000000000008,73.22,71.599999999999994,71.960000000000008,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["1981-07-25",7,25,2018,"2018-07-25",3,0,"01:00:00",1,60.980000000000004,57.019999999999996,62.6,55.400000000000006,55.040000000000006,60.980000000000004,56.84,64.94,64.400000000000006,60.8,57.019999999999996,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-25",7,25,2018,{"$f":"DATE(D4935,B4935,C4935)","v":"2018-07-25"},{"$f":"WEEKDAY(E4935,2)","v":3},0,"10:00:00",10,68,68,71.599999999999994,69.800000000000011,63.14,64.039999999999992,62.96,78.98,69.98,64.400000000000006,75.02,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-25",7,25,2018,"2018-07-25",3,0,"18:00:00",18,73.94,66.92,84.2,77,73.039999999999992,68,66.56,84.02,78.44,62.6,75.92,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-25",7,25,2018,"2018-07-25",3,0,1,24,57.019999999999996,60.08,60.8,66.2,68,62.06,53.24,66.02,57.2,60.8,68,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-26",7,26,2018,"2018-07-26",4,0,"11:00:00",11,78.98,66.02,86,75.2,69.98,69.98,72.14,87.080000000000013,77.72,68,78.080000000000013,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-26",7,26,2018,"2018-07-26",4,0,"14:00:00",14,84.92,71.06,89.960000000000008,78.800000000000011,75.92,75.2,78.800000000000011,95,84.2,71.599999999999994,80.960000000000008,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["1981-07-26",7,26,2018,"2018-07-26",4,0,"20:00:00",20,69.98,73.039999999999992,78.98,71.599999999999994,73.039999999999992,75.02,68.900000000000006,80.960000000000008,75.2,68.180000000000007,71.06,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-27",7,27,2018,"2018-07-27",5,0,"04:00:00",4,62.06,66.02,66.92,62.6,68,64.039999999999992,63.5,73.039999999999992,63.5,64.400000000000006,60.980000000000004,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-27",7,27,2018,"2018-07-27",5,0,"13:00:00",13,82.039999999999992,80.06,86,68,84.02,82.039999999999992,74.48,89.06,81.319999999999993,77,69.080000000000013,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-27",7,27,2018,"2018-07-27",5,0,"21:00:00",21,68,69.98,79.16,69.800000000000011,71.960000000000008,73.039999999999992,68.900000000000006,78.98,71.06,67.099999999999994,68,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-28",7,28,2018,"2018-07-28",6,0,"06:00:00",6,55.040000000000006,69.080000000000013,57.2,64.400000000000006,68,69.080000000000013,60.980000000000004,69.080000000000013,57.2,67.64,68,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-28",7,28,2018,"2018-07-28",6,0,"15:00:00",15,84.92,91.94,89.960000000000008,69.800000000000011,89.960000000000008,91.039999999999992,78.259999999999991,91.94,88.34,83.12,80.06,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-28",7,28,2018,"2018-07-28",6,0,"20:00:00",20,68,84.02,73.94,64.400000000000006,71.06,80.06,72.14,78.080000000000013,73.759999999999991,71.240000000000009,66.2,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-28",7,28,2018,"2018-07-28",6,0,1,24,60.980000000000004,68,62.96,64.400000000000006,64.94,73.039999999999992,68,69.98,74.300000000000011,68.180000000000007,62.96,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-29",7,29,2018,"2018-07-29",7,0,"10:00:00",10,82.039999999999992,87.080000000000013,82.94,66.2,82.039999999999992,87.080000000000013,76.099999999999994,87.98,77.900000000000006,87.080000000000013,69.98,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-29",7,29,2018,"2018-07-29",7,0,"17:00:00",17,78.080000000000013,93.02,87.080000000000013,71.599999999999994,91.94,93.92,71.599999999999994,87.080000000000013,82.039999999999992,86,73.94,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-29",7,29,2018,"2018-07-29",7,0,1,24,62.06,69.98,71.960000000000008,57.2,68,77,64.039999999999992,77,67.099999999999994,76.28,57.92,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-30",7,30,2018,"2018-07-30",1,0,"10:00:00",10,71.960000000000008,87.98,73.400000000000006,66.2,82.039999999999992,87.080000000000013,68.539999999999992,71.599999999999994,70.34,86.72,68,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-30",7,30,2018,"2018-07-30",1,0,"14:00:00",14,82.94,91.039999999999992,77,71.599999999999994,82.94,89.06,75.38,84.02,83.300000000000011,87.98,75.02,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["1981-07-31",7,31,2018,"2018-07-31",2,0,"03:00:00",3,55.400000000000006,64.94,62.6,53.6,60.980000000000004,69.080000000000013,54.5,66.92,61.16,68.72,55.94,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1981-07-31",7,31,2018,"2018-07-31",2,0,"11:00:00",11,77,82.039999999999992,77,73.400000000000006,80.06,84.02,67.460000000000008,82.039999999999992,75.56,83.84,77,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-31",7,31,2018,"2018-07-31",2,0,"12:00:00",12,78.080000000000013,84.92,78.080000000000013,73.400000000000006,82.039999999999992,84.92,68.539999999999992,82.94,76.28,86,77,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1981-07-31",7,31,2018,"2018-07-31",2,0,"21:00:00",21,55.400000000000006,62.96,69.259999999999991,63.5,62.6,70.52,58.28,74.48,62.96,69.080000000000013,64.759999999999991,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-01",8,1,2018,"2018-08-01",3,0,"05:00:00",5,52.879999999999995,54.68,60.44,64.039999999999992,53.96,60.44,51.08,56.84,60.08,64.22,58.28,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-01",8,1,2018,"2018-08-01",3,0,"11:00:00",11,69.080000000000013,71.960000000000008,75.2,75.2,75.02,75.2,69.62,75.92,65.300000000000011,76.099999999999994,75.02,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-01",8,1,2018,"2018-08-01",3,0,"22:00:00",22,59,66.92,66.2,64.400000000000006,68,69.080000000000013,60.980000000000004,69.98,62.96,68,62.96,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-02",8,2,2018,"2018-08-02",4,0,"08:00:00",8,66.92,62.96,60.8,66.2,68,69.080000000000013,60.620000000000005,71.960000000000008,64.22,69.800000000000011,68,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-02",8,2,2018,"2018-08-02",4,0,"15:00:00",15,66.92,71.960000000000008,82.4,80.599999999999994,77,84.02,70.34,86,66.2,73.22,78.080000000000013,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["1989-08-02",8,2,2018,"2018-08-02",4,0,"22:00:00",22,59,64.94,64.400000000000006,71.599999999999994,69.800000000000011,66.92,62.24,73.94,61.7,68.36,64.94,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-02",8,2,2018,"2018-08-02",4,0,1,24,59,64.039999999999992,60.8,66.2,66.92,69.98,60.44,70.88,61.16,68.539999999999992,62.06,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-03",8,3,2018,"2018-08-03",5,0,"08:00:00",8,62.96,68,69.800000000000011,71.599999999999994,71.06,73.039999999999992,64.400000000000006,77.900000000000006,62.78,71.599999999999994,71.06,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-03",8,3,2018,"2018-08-03",5,0,"17:00:00",17,80.06,84.92,84.2,87.800000000000011,82.94,84.92,68.180000000000007,86,71.78,77.539999999999992,82.94,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["1989-08-04",8,4,2018,"2018-08-04",6,0,"05:00:00",5,50,69.080000000000013,64.400000000000006,64.400000000000006,71.599999999999994,71.06,64.400000000000006,71.960000000000008,57.379999999999995,68.539999999999992,69.800000000000011,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-04",8,4,2018,"2018-08-04",6,0,"10:00:00",10,75.92,84.02,75.2,75.2,84.02,82.4,68.539999999999992,82.94,66.740000000000009,86.18,82.039999999999992,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-04",8,4,2018,"2018-08-04",6,0,"19:00:00",19,71.960000000000008,84.92,78.800000000000011,66.2,78.98,87.080000000000013,75.02,86.9,74.300000000000011,83.300000000000011,84.92,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-05",8,5,2018,"2018-08-05",7,0,"03:00:00",{"$f":"H5192*24","v":3},58.64,73.039999999999992,57.2,59,71.06,75.02,67.460000000000008,74.84,63.319999999999993,70.7,73.039999999999992,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-05",8,5,2018,"2018-08-05",7,0,"09:00:00",9,75.02,78.080000000000013,69.800000000000011,69.800000000000011,78.800000000000011,78.98,72.86,81.86,60.980000000000004,82.94,77,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-05",8,5,2018,"2018-08-05",7,0,"12:00:00",12,84.02,78.800000000000011,78.800000000000011,75.2,82.4,82.94,73.22,86.9,80.960000000000008,82.580000000000013,80.599999999999994,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-06",8,6,2018,"2018-08-06",1,0,"02:00:00",2,55.040000000000006,66.02,53.6,62.6,73.039999999999992,69.080000000000013,62.24,68,55.94,66.2,68,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-06",8,6,2018,"2018-08-06",1,0,"05:00:00",5,59.18,64.039999999999992,56.66,55.400000000000006,66.92,69.080000000000013,59.36,70.88,60.08,68,66.02,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-06",8,6,2018,"2018-08-06",1,0,"16:00:00",16,87.080000000000013,78.98,75.2,75.2,75.02,82.94,63.5,84.92,88.16,85.1,82.039999999999992,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["1989-08-06",8,6,2018,"2018-08-06",1,0,"22:00:00",22,69.98,59,59,60.8,53.06,66.02,52.519999999999996,64.94,67.28,74.12,60.08,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-07",8,7,2018,"2018-08-07",2,0,"06:00:00",6,66.02,56.66,55.400000000000006,55.400000000000006,51.08,55.040000000000006,43.16,54.86,63.5,72.86,51.980000000000004,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-07",8,7,2018,"2018-08-07",2,0,"15:00:00",15,71.06,75.92,77,73.400000000000006,75.02,77,62.96,78.98,87.080000000000013,81.5,75.92,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["1989-08-07",8,7,2018,"2018-08-07",2,0,1,24,55.040000000000006,59.36,55.400000000000006,59,51.08,60.08,45.32,55.94,61.519999999999996,62.78,55.040000000000006,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-08",8,8,2018,"2018-08-08",3,0,"05:00:00",5,54.68,50,51.8,55.400000000000006,50,53.96,45.32,52.879999999999995,55.94,58.1,51.980000000000004,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-08",8,8,2018,"2018-08-08",3,0,"09:00:00",9,62.78,71.06,64.400000000000006,68,69.98,69.080000000000013,59.18,73.94,71.599999999999994,74.48,73.039999999999992,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-08",8,8,2018,"2018-08-08",3,0,"19:00:00",19,64.94,78.98,75.2,73.400000000000006,69.98,78.080000000000013,69.800000000000011,78.98,72.86,69.080000000000013,78.080000000000013,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-09",8,9,2018,"2018-08-09",4,0,"02:00:00",2,54.5,69.98,57.2,59,73.94,71.960000000000008,62.24,72.86,57.74,64.94,69.98,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-09",8,9,2018,"2018-08-09",4,0,"09:00:00",9,61.7,82.039999999999992,69.800000000000011,64.400000000000006,80.960000000000008,80.06,66.740000000000009,84.92,69.080000000000013,77.180000000000007,82.039999999999992,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-09",8,9,2018,"2018-08-09",4,0,"19:00:00",19,66.02,82.039999999999992,77,71.599999999999994,69.800000000000011,86,70.16,86,77.72,75.02,73.94,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-10",8,10,2018,"2018-08-10",5,0,"02:00:00",2,48.019999999999996,69.080000000000013,55.400000000000006,62.6,68,71.599999999999994,61.16,73.400000000000006,51.8,66.740000000000009,69.98,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-10",8,10,2018,"2018-08-10",5,0,"12:00:00",12,75.92,84.92,78.800000000000011,78.800000000000011,82.039999999999992,86,74.12,86,80.240000000000009,82.4,84.92,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-10",8,10,2018,"2018-08-10",5,0,"16:00:00",16,80.960000000000008,89.06,80.599999999999994,82.4,87.080000000000013,89.06,73.039999999999992,89.960000000000008,83.66,77.900000000000006,87.080000000000013,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["1989-08-10",8,10,2018,"2018-08-10",5,0,"21:00:00",21,59,73.94,71.599999999999994,75.2,71.06,78.080000000000013,65.84,78.98,76.099999999999994,74.84,75.02,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-11",8,11,2018,"2018-08-11",6,0,"06:00:00",6,56.66,66.02,68,66.2,66.02,69.080000000000013,57.019999999999996,68.900000000000006,56.66,69.800000000000011,64.94,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-11",8,11,2018,"2018-08-11",6,0,"14:00:00",14,75.92,82.94,71.599999999999994,66.2,82.94,82.039999999999992,73.22,84.92,68.36,74.12,80.960000000000008,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-11",8,11,2018,"2018-08-11",6,0,"20:00:00",20,69.080000000000013,75.02,66.2,69.800000000000011,68,73.94,63.14,75.92,70.7,68,69.98,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-12",8,12,2018,"2018-08-12",7,0,"07:00:00",7,62.06,66.02,62.6,66.2,64.039999999999992,66.02,55.58,68,65.84,69.800000000000011,66.02,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-12",8,12,2018,"2018-08-12",7,0,"13:00:00",13,89.06,75.02,75.2,77,77,75.92,70.16,78.98,88.34,78.800000000000011,73.94,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-12",8,12,2018,"2018-08-12",7,0,1,24,66.92,64.039999999999992,60.8,60.8,66.92,64.039999999999992,53.6,64.94,68,69.800000000000011,62.6,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-13",8,13,2018,"2018-08-13",1,0,"03:00:00",{"$f":"H5384*24","v":3},62.06,62.96,57.2,60.8,64.94,64.400000000000006,53.6,62.6,64.94,69.800000000000011,57.2,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-13",8,13,2018,"2018-08-13",1,0,"09:00:00",9,80.960000000000008,69.800000000000011,62.6,68,71.599999999999994,69.800000000000011,59,69.800000000000011,78.62,72.680000000000007,69.98,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-13",8,13,2018,"2018-08-13",1,0,"17:00:00",17,78.98,78.98,75.2,75.2,80.06,77,71.78,78.98,75.02,78.62,73.039999999999992,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["1989-08-14",8,14,2018,"2018-08-14",2,0,"02:00:00",2,69.98,55.040000000000006,55.400000000000006,57.2,57.019999999999996,57.92,52.519999999999996,54.86,72.680000000000007,66.740000000000009,55.94,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-14",8,14,2018,"2018-08-14",2,0,"07:00:00",7,64.039999999999992,57.92,53.6,59,62.96,60.980000000000004,50,59.900000000000006,65.300000000000011,71.06,62.06,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-14",8,14,2018,"2018-08-14",2,0,"19:00:00",19,64.94,71.960000000000008,78.800000000000011,80.599999999999994,69.080000000000013,75.02,69.44,75.92,65.300000000000011,74.300000000000011,68,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-14",8,14,2018,"2018-08-14",2,0,1,24,64.039999999999992,62.06,69.800000000000011,71.599999999999994,66.02,66.02,58.28,64.94,63.680000000000007,67.819999999999993,59,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-15",8,15,2018,"2018-08-15",3,0,"12:00:00",12,82.039999999999992,77,80.599999999999994,78.800000000000011,75.2,75.02,72.680000000000007,75.92,83.48,81.86,78.98,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-15",8,15,2018,"2018-08-15",3,0,"14:00:00",14,82.039999999999992,75.92,84.2,82.4,77,78.080000000000013,73.94,79.88,83.48,79.52,77,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["1989-08-15",8,15,2018,"2018-08-15",3,0,"21:00:00",21,69.98,71.06,64.400000000000006,69.800000000000011,71.960000000000008,71.06,64.580000000000013,71.960000000000008,73.759999999999991,70.16,68,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-16",8,16,2018,"2018-08-16",4,0,"04:00:00",4,66.92,64.400000000000006,62.6,66.2,66.92,64.039999999999992,58.64,64.94,65.66,66.02,62.96,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-16",8,16,2018,"2018-08-16",4,0,"14:00:00",14,78.98,75.02,82.4,84.2,73.400000000000006,77,70.34,80.599999999999994,76.460000000000008,80.240000000000009,75.92,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["1989-08-17",8,17,2018,"2018-08-17",5,0,"01:00:00",1,51.980000000000004,66.2,68,69.800000000000011,64.94,73.400000000000006,60.44,71.960000000000008,58.46,69.800000000000011,68,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-17",8,17,2018,"2018-08-17",5,0,"07:00:00",7,53.96,66.02,64.400000000000006,69.800000000000011,62.6,69.800000000000011,59.72,69.800000000000011,57.2,66.2,68,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-17",8,17,2018,"2018-08-17",5,0,"15:00:00",15,71.06,87.98,89.6,87.800000000000011,84.02,87.080000000000013,74.300000000000011,88.88,71.78,77,89.06,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["1989-08-17",8,17,2018,"2018-08-17",5,0,1,24,66.02,60.980000000000004,66.2,68,57.019999999999996,73.039999999999992,58.82,71.960000000000008,65.84,66.02,69.98,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-18",8,18,2018,"2018-08-18",6,0,"01:00:00",1,66.2,60.08,64.400000000000006,66.2,57.019999999999996,66.92,57.379999999999995,68,66.2,64.759999999999991,66.02,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-18",8,18,2018,"2018-08-18",6,0,"14:00:00",14,69.080000000000013,84.02,87.800000000000011,87.800000000000011,80.960000000000008,84.92,72.5,86,70.88,81.319999999999993,82.94,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-18",8,18,2018,"2018-08-18",6,0,"18:00:00",18,69.98,80.06,87.800000000000011,80.599999999999994,73.039999999999992,80.960000000000008,67.28,81.86,72.14,81.319999999999993,75.02,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-18",8,18,2018,"2018-08-18",6,0,1,24,53.06,66.02,69.800000000000011,71.599999999999994,62.06,69.98,55.58,66.92,58.1,68.900000000000006,66.02,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-19",8,19,2018,"2018-08-19",7,0,"11:00:00",11,78.080000000000013,80.06,80.599999999999994,80.599999999999994,80.06,82.94,72.680000000000007,86,74.48,72.14,80.960000000000008,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-19",8,19,2018,"2018-08-19",7,0,"21:00:00",21,64.94,73.039999999999992,71.599999999999994,73.400000000000006,68,78.080000000000013,67.099999999999994,77,66.92,66.38,66.92,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-20",8,20,2018,"2018-08-20",1,0,"04:00:00",4,55.94,64.039999999999992,68,69.800000000000011,57.92,69.98,59.36,66.92,56.66,57.379999999999995,68,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-20",8,20,2018,"2018-08-20",1,0,"11:00:00",11,75.92,75.02,80.599999999999994,78.800000000000011,71.960000000000008,75.92,62.6,78.98,76.460000000000008,74.12,77,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-20",8,20,2018,"2018-08-20",1,0,"13:00:00",13,78.98,78.080000000000013,84.2,80.599999999999994,75.02,80.06,64.94,80.960000000000008,78.98,73.580000000000013,80.06,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-21",8,21,{"$f":"$AO$4","v":2018},"2018-08-21",2,{"$f":"COUNTIF($AM$34:$AM$43,E5574)","v":0},"01:00:00",1,51.08,56.66,66.2,71.599999999999994,50,60.980000000000004,46.58,54.86,53.06,63.319999999999993,58.82,null,{"$f":"SUMPRODUCT($J$2:$T$2,J5574:T5574)","v":0},null,null,{"$f":"OR(B5574<=$AO$14,B5574>=$AN$14)*(F5574<6)*(I5574>$AN$15)*(I5574<=$AO$15)*(G5574<>1)","v":0},{"$f":"OR(B5574<=$AO$14,B5574>=$AN$14)*(Y5574=0)","v":0},{"$f":"AND(B5574>=$AN$24,B5574<=$AO$24)*(F5574<6)*(I5574>$AN$25)*(I5574<=$AO$25)*(G5574<>1)","v":0},{"$f":"AND(B5574>=$AN$24,B5574<=$AO$24)*(AA5574=0)","v":1},{"$f":"OR(B5574<=$AO$19,B5574>=$AN$19)*(F5574<6)*(I5574>$AN$20)*(I5574<=$AO$20)","v":0},{"$f":"AND(B5574>=$AN$29,B5574<=$AO$29)*(F5574<6)*(I5574>$AN$30)*(I5574<=$AO$30)","v":0},{"$f":"IF(OR(E5574=$AM$34,E5574=$AM$35,E5574=$AM$36,E5574=$AM$37,E5574=$AM$38,E5574=$AM$39,E5574=$AM$40,E5574=$AM$41,E5574=$AM$42,E5574=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E5574>=$AM$47,E5574<=$AN$47),AND(E5574>=$AM$48,E5574<=$AN$48),AND(E5574>=$AM$49,E5574<=$AN$49),AND(E5574>=$AM$50,E5574<=$AN$50),AND(E5574>=$AM$51,E5574<=$AN$51)),0,1)*AE5574","v":0},{"$f":"(B5574>=5)*(B5574<=10)","v":1},{"$f":"1*OR(B5574<=4,B5574>=11)","v":0},{"$f":"LOOKUP(B5574,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE5574:AI5574)*((F5574<6)*(I5574>$AO$7)*(I5574<=$AP$7)+(F5574=6)*(I5574>$AO$8)*(I5574<=$AP$8)+(F5574>=7)*(I5574>$AO$9)*(I5574<=$AP$9))","v":0}]
["1989-08-21",8,21,2018,"2018-08-21",2,0,"06:00:00",6,50,54.14,68,71.599999999999994,48.2,55.94,45.86,51.980000000000004,57.2,57.74,51.980000000000004,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-21",8,21,2018,"2018-08-21",2,0,"18:00:00",18,73.94,69.98,77,71.599999999999994,71.06,73.039999999999992,62.78,75.92,80.599999999999994,69.98,68,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-21",8,21,2018,"2018-08-21",2,0,"23:00:00",23,60.08,64.94,66.2,68,62.96,68,58.64,66.92,66.2,62.96,62.06,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-22",8,22,2018,"2018-08-22",3,0,"08:00:00",8,69.98,64.039999999999992,60.8,68,64.400000000000006,66.2,57.2,68,65.300000000000011,69.080000000000013,64.94,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-22",8,22,2018,"2018-08-22",3,0,"16:00:00",16,78.080000000000013,66.92,80.599999999999994,78.800000000000011,68,68,62.42,68.900000000000006,79.7,75.38,66.2,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["1989-08-22",8,22,2018,"2018-08-22",3,0,"22:00:00",22,64.039999999999992,62.06,64.400000000000006,64.400000000000006,64.039999999999992,62.96,56.480000000000004,63.86,63.5,65.300000000000011,62.06,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-23",8,23,2018,"2018-08-23",4,0,"01:00:00",1,62.6,62.6,60.8,62.6,62.96,64.400000000000006,55.400000000000006,65.84,60.8,61.519999999999996,62.06,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-23",8,23,2018,"2018-08-23",4,0,"12:00:00",12,60.980000000000004,64.039999999999992,75.2,75.2,62.6,62.6,61.16,63.86,63.14,80.78,62.96,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-23",8,23,2018,{"$f":"DATE(D5639,B5639,C5639)","v":"2018-08-23"},{"$f":"WEEKDAY(E5639,2)","v":4},0,"18:00:00",18,60.08,64.039999999999992,73.400000000000006,69.800000000000011,64.94,64.039999999999992,55.76,64.400000000000006,65.66,72.86,62.96,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-24",8,24,2018,"2018-08-24",5,0,"02:00:00",2,47.480000000000004,62.06,68,66.2,60.8,62.6,53.24,62.96,50.36,61.519999999999996,62.06,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-24",8,24,2018,"2018-08-24",5,0,"11:00:00",11,71.06,69.98,75.2,75.2,73.039999999999992,69.800000000000011,63.86,68,69.800000000000011,80.960000000000008,69.080000000000013,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-24",8,24,2018,"2018-08-24",5,0,"19:00:00",19,60.08,66.02,73.400000000000006,77,69.080000000000013,62.96,62.42,62.6,69.62,72.680000000000007,64.94,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-25",8,25,2018,"2018-08-25",6,0,"04:00:00",4,53.42,59,69.800000000000011,66.2,62.06,60.8,54.14,60.8,51.620000000000005,61.16,60.8,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-25",8,25,2018,"2018-08-25",6,0,"09:00:00",9,63.14,60.8,66.2,71.599999999999994,64.400000000000006,62.06,54.86,61.88,65.48,77,60.8,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-25",8,25,2018,"2018-08-25",6,0,"13:00:00",13,82.039999999999992,62.6,71.599999999999994,68,64.400000000000006,64.400000000000006,57.2,64.400000000000006,82.4,78.800000000000011,62.6,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-25",8,25,2018,"2018-08-25",6,0,"23:00:00",23,57.019999999999996,64.039999999999992,66.2,69.800000000000011,62.6,64.94,55.040000000000006,63.86,61.16,66.92,62.96,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-26",8,26,2018,"2018-08-26",7,0,"06:00:00",6,57.92,55.400000000000006,64.400000000000006,66.2,59,60.980000000000004,54.32,59.900000000000006,60.26,66.2,62.96,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-26",8,26,2018,"2018-08-26",7,0,"13:00:00",13,80.06,80.06,73.400000000000006,78.800000000000011,78.98,80.960000000000008,68.36,79.88,81.86,77,80.960000000000008,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-26",8,26,2018,"2018-08-26",7,0,"23:00:00",23,71.599999999999994,64.039999999999992,59,62.6,62.96,66.02,55.040000000000006,60.980000000000004,69.080000000000013,64.94,64.039999999999992,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-27",8,27,2018,"2018-08-27",1,0,"06:00:00",6,66.92,55.94,55.400000000000006,62.6,50,60.08,52.34,59,64.94,60.620000000000005,59,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-27",8,27,2018,"2018-08-27",1,0,"16:00:00",16,82.039999999999992,75.02,73.400000000000006,73.400000000000006,73.039999999999992,75.92,63.319999999999993,77,83.84,76.819999999999993,73.94,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["1989-08-27",8,27,2018,"2018-08-27",1,0,"20:00:00",20,68,64.039999999999992,62.6,64.400000000000006,55.040000000000006,66.92,55.040000000000006,63.86,69.080000000000013,65.84,62.96,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-28",8,28,2018,"2018-08-28",2,0,"01:00:00",1,53.06,50,53.6,57.2,48.92,55.94,46.94,53.96,58.1,62.6,57.92,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-28",8,28,2018,"2018-08-28",2,0,"10:00:00",10,75.92,71.960000000000008,64.400000000000006,71.599999999999994,68,73.039999999999992,60.08,73.94,73.580000000000013,78.44,73.94,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-28",8,28,2018,"2018-08-28",2,0,"18:00:00",18,73.94,78.98,75.2,73.400000000000006,73.94,80.06,67.819999999999993,80.960000000000008,79.7,76.099999999999994,77,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-29",8,29,2018,"2018-08-29",3,0,"03:00:00",{"$f":"H5768*24","v":3},55.040000000000006,55.94,53.6,57.2,55.400000000000006,64.039999999999992,50,57.92,56.66,73.039999999999992,62.06,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-29",8,29,2018,"2018-08-29",3,0,"09:00:00",9,68,77,55.400000000000006,64.400000000000006,71.06,78.080000000000013,64.580000000000013,79.88,67.64,69.98,80.960000000000008,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-29",8,29,2018,"2018-08-29",3,0,"20:00:00",20,68,80.06,64.400000000000006,66.2,68,82.94,71.06,73.94,76.28,70.88,77,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-29",8,29,2018,"2018-08-29",3,0,"23:00:00",23,64.039999999999992,66.02,62.6,66.2,62.96,73.039999999999992,62.42,66.92,69.800000000000011,65.12,69.080000000000013,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-30",8,30,2018,"2018-08-30",4,0,"13:00:00",13,71.960000000000008,89.960000000000008,78.800000000000011,78.800000000000011,89.06,89.06,79.52,89.960000000000008,73.400000000000006,73.759999999999991,87.98,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-30",8,30,2018,"2018-08-30",4,0,"20:00:00",20,57.019999999999996,80.960000000000008,69.800000000000011,69.800000000000011,69.98,80.960000000000008,71.42,74.84,64.580000000000013,63.680000000000007,80.06,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-30",8,30,2018,"2018-08-30",4,0,"22:00:00",22,51.08,69.080000000000013,66.2,68,66.02,77,68.900000000000006,70.88,60.620000000000005,61.88,77,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1989-08-31",8,31,2018,"2018-08-31",5,0,"06:00:00",6,46.94,62.96,60.8,62.6,62.6,69.080000000000013,65.300000000000011,64.94,54.14,57.379999999999995,69.98,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1989-08-31",8,31,2018,"2018-08-31",5,0,"15:00:00",15,75.02,93.92,84.2,82.4,93.02,95,82.4,95,77.180000000000007,81.680000000000007,93.02,null,0,null,null,0,0,1,0,0,1,1,1,0,1,0,1,0]
["1989-08-31",8,31,2018,"2018-08-31",5,0,"20:00:00",20,58.28,73.759999999999991,67.64,72.5,68.72,79.52,71.240000000000009,76.460000000000008,60.26,69.259999999999991,78.259999999999991,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1976-09-01",9,1,2018,"2018-09-01",6,0,"08:00:00",8,57.019999999999996,60.980000000000004,60.980000000000004,66.92,66.02,68,50,69.98,68.900000000000006,69.98,71.06,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1976-09-01",9,1,2018,"2018-09-01",6,0,"17:00:00",17,69.080000000000013,80.06,75.92,77,77,80.06,69.259999999999991,78.080000000000013,81.5,79.88,80.06,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1976-09-02",9,2,2018,"2018-09-02",7,0,"01:00:00",1,55.040000000000006,66.92,66.02,67.64,62.96,73.94,51.8,71.06,64.400000000000006,72.319999999999993,69.080000000000013,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1976-09-02",9,2,2018,"2018-09-02",7,0,"07:00:00",7,60.08,66.92,64.039999999999992,66.92,62.96,71.06,50,69.98,60.980000000000004,70.16,68,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1976-09-02",9,2,2018,"2018-09-02",7,0,"10:00:00",10,75.92,80.960000000000008,75.02,75.92,73.039999999999992,73.94,68,73.94,73.039999999999992,75.2,77,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1976-09-02",9,2,2018,"2018-09-02",7,0,"17:00:00",17,80.06,80.960000000000008,75.02,75.38,75.92,80.960000000000008,73.22,75.02,78.800000000000011,73.580000000000013,75.92,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1976-09-03",9,3,2018,"2018-09-03",1,1,"03:00:00",3,66.92,53.06,51.8,55.040000000000006,51.8,62.96,66.2,59,59,61.88,62.06,null,0,null,null,0,0,0,1,0,0,0,1,0,1,0,1,0]
["1976-09-03",9,3,2018,"2018-09-03",1,1,"14:00:00",14,87.98,78.98,75.92,73.94,75.02,78.98,81.14,78.98,70.88,72.5,75.02,null,0,null,null,0,0,0,1,0,0,0,1,0,1,0,1,0]
["1976-09-03",9,3,2018,"2018-09-03",1,1,"20:00:00",20,71.960000000000008,69.080000000000013,68.900000000000006,62.06,57.019999999999996,71.960000000000008,75.38,69.080000000000013,59,64.400000000000006,62.96,null,0,null,null,0,0,0,1,0,0,0,1,0,1,0,1,0]
["1976-09-04",9,4,2018,"2018-09-04",2,0,"04:00:00",4,64.94,48.92,51.44,51.08,46.04,57.019999999999996,66.02,51.980000000000004,58.28,54.14,56.480000000000004,null,0,null,null,0,0,0,1,0,0,1,1,0,1,0,1,0]
["1976-09-04",9,4,2018,"2018-09-04",2,0,"13:00:00",13,80.06,77,71.960000000000008,73.039999999999992,73.039999999999992,75.92,74.300000000000011,73.94,73.94,73.22,75.92,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1976-09-04",9,4,2018,"2018-09-04",2,0,"18:00:00",18,73.039999999999992,75.02,68,69.080000000000013,69.080000000000013,73.039999999999992,68.180000000000007,71.06,75.38,66.2,68,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1976-09-04",9,4,2018,"2018-09-04",2,0,"22:00:00",22,57.019999999999996,62.06,62.06,57.019999999999996,55.040000000000006,60.980000000000004,53.6,57.92,60.980000000000004,59.36,55.040000000000006,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1976-09-05",9,5,2018,"2018-09-05",3,0,"11:00:00",11,78.080000000000013,75.02,71.960000000000008,71.960000000000008,73.94,73.94,73.039999999999992,75.02,61.519999999999996,73.400000000000006,73.94,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1976-09-05",9,5,2018,"2018-09-05",3,0,"15:00:00",15,84.02,78.98,78.080000000000013,75.92,78.98,75.92,80.78,77,63.5,71.960000000000008,75.02,null,0,null,null,0,0,1,0,0,0,1,1,0,1,0,1,0]
["1976-09-06",9,6,{"$f":"$AO$4","v":2018},"2018-09-06",4,{"$f":"COUNTIF($AM$34:$AM$43,E5958)","v":0},"01:00:00",1,66.02,51.08,51.08,53.06,53.06,57.019999999999996,70.52,53.06,63.14,54.86,51.08,null,{"$f":"SUMPRODUCT($J$2:$T$2,J5958:T5958)","v":0},null,null,{"$f":"OR(B5958<=$AO$14,B5958>=$AN$14)*(F5958<6)*(I5958>$AN$15)*(I5958<=$AO$15)*(G5958<>1)","v":0},{"$f":"OR(B5958<=$AO$14,B5958>=$AN$14)*(Y5958=0)","v":0},{"$f":"AND(B5958>=$AN$24,B5958<=$AO$24)*(F5958<6)*(I5958>$AN$25)*(I5958<=$AO$25)*(G5958<>1)","v":0},{"$f":"AND(B5958>=$AN$24,B5958<=$AO$24)*(AA5958=0)","v":1},{"$f":"OR(B5958<=$AO$19,B5958>=$AN$19)*(F5958<6)*(I5958>$AN$20)*(I5958<=$AO$20)","v":0},{"$f":"AND(B5958>=$AN$29,B5958<=$AO$29)*(F5958<6)*(I5958>$AN$30)*(I5958<=$AO$30)","v":0},{"$f":"IF(OR(E5958=$AM$34,E5958=$AM$35,E5958=$AM$36,E5958=$AM$37,E5958=$AM$38,E5958=$AM$39,E5958=$AM$40,E5958=$AM$41,E5958=$AM$42,E5958=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E5958>=$AM$47,E5958<=$AN$47),AND(E5958>=$AM$48,E5958<=$AN$48),AND(E5958>=$AM$49,E5958<=$AN$49),AND(E5958>=$AM$50,E5958<=$AN$50),AND(E5958>=$AM$51,E5958<=$AN$51)),0,1)*AE5958","v":1},{"$f":"(B5958>=5)*(B5958<=10)","v":1},{"$f":"1*OR(B5958<=4,B5958>=11)","v":0},{"$f":"LOOKUP(B5958,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE5958:AI5958)*((F5958<6)*(I5958>$AO$7)*(I5958<=$AP$7)+(F5958=6)*(I5958>$AO$8)*(I5958<=$AP$8)+(F5958>=7)*(I5958>$AO$9)*(I5958<=$AP$9))","v":0}]
["1976-09-06",9,6,2018,"2018-09-06",4,0,"08:00:00",8,78.98,51.980000000000004,55.040000000000006,62.06,53.96,59,69.62,57.92,66.38,60.8,60.980000000000004,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-06",9,6,2018,"2018-09-06",4,0,"15:00:00",15,77,80.960000000000008,78.080000000000013,73.94,82.039999999999992,78.080000000000013,70.16,78.080000000000013,76.28,73.400000000000006,75.02,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-07",9,7,2018,"2018-09-07",5,0,"01:00:00",1,46.4,69.080000000000013,66.2,64.94,57.92,64.039999999999992,45.68,64.400000000000006,66.2,60.8,62.06,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-07",9,7,2018,"2018-09-07",5,0,"05:00:00",5,48.019999999999996,64.94,64.94,62.06,60.08,64.039999999999992,45.14,62.96,64.400000000000006,60.8,60.08,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-07",9,7,2018,"2018-09-07",5,0,"10:00:00",10,64.94,66.92,68,66.02,71.599999999999994,69.080000000000013,59.72,68,70.52,66.2,66.92,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-07",9,7,2018,"2018-09-07",5,0,"19:00:00",19,55.040000000000006,69.98,71.06,69.98,73.039999999999992,69.98,59,69.98,71.240000000000009,66.2,68,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-08",9,8,2018,"2018-09-08",6,0,"03:00:00",3,49.82,68,68,66.2,62.06,68,48.56,68,63.680000000000007,66.56,64.94,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-08",9,8,2018,"2018-09-08",6,0,"12:00:00",12,54.32,71.06,75.2,73.039999999999992,78.98,71.960000000000008,54.32,71.960000000000008,80.240000000000009,69.080000000000013,69.080000000000013,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-08",9,8,2018,{"$f":"DATE(D6023,B6023,C6023)","v":"2018-09-08"},{"$f":"WEEKDAY(E6023,2)","v":6},0,"18:00:00",18,53.96,73.039999999999992,75.02,71.06,73.94,73.94,49.64,75.2,73.580000000000013,69.800000000000011,69.080000000000013,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-09",9,9,2018,"2018-09-09",7,0,"05:00:00",5,35.06,64.94,62.6,64.400000000000006,64.039999999999992,68,31.82,68,61.16,66.2,66.02,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-09",9,9,2018,"2018-09-09",7,0,"11:00:00",11,57.019999999999996,75.02,75.2,73.039999999999992,75.02,75.02,51.980000000000004,75.92,77.36,75.2,71.960000000000008,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-09",9,9,2018,"2018-09-09",7,0,"14:00:00",14,62.96,80.06,80.599999999999994,75.92,82.94,80.960000000000008,57.019999999999996,82.039999999999992,80.06,76.099999999999994,78.080000000000013,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-10",9,10,2018,"2018-09-10",1,0,"01:00:00",1,39.92,69.98,69.800000000000011,69.98,71.960000000000008,71.960000000000008,39.74,71.960000000000008,60.620000000000005,67.28,66.92,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-10",9,10,2018,"2018-09-10",1,0,"07:00:00",7,39.019999999999996,73.039999999999992,71.599999999999994,73.039999999999992,73.94,73.94,40.1,73.94,55.58,71.599999999999994,73.039999999999992,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-10",9,10,2018,"2018-09-10",1,0,"15:00:00",15,59,93.02,86,84.92,87.080000000000013,89.06,54.32,89.960000000000008,71.240000000000009,92.48,89.960000000000008,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-10",9,10,2018,"2018-09-10",1,0,1,24,50.540000000000006,62.96,62.6,64.039999999999992,62.06,71.06,50.36,68,51.08,66.92,64.94,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-11",9,11,2018,"2018-09-11",2,0,"05:00:00",5,55.040000000000006,64.039999999999992,64.94,62.06,60.08,69.080000000000013,51.620000000000005,66.92,51.620000000000005,65.84,62.96,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-11",9,11,2018,"2018-09-11",2,0,"17:00:00",17,68,78.98,78.080000000000013,75.02,75.92,77,64.22,78.080000000000013,58.82,70.52,71.960000000000008,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-11",9,11,2018,"2018-09-11",2,0,"22:00:00",22,60.980000000000004,68,73.400000000000006,68,71.960000000000008,69.080000000000013,59,69.98,52.7,68,66.92,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-12",9,12,2018,"2018-09-12",3,0,"02:00:00",2,60.980000000000004,68,73.400000000000006,66.92,69.080000000000013,68,57.56,66.92,45.14,68,66.02,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-12",9,12,2018,"2018-09-12",3,0,"12:00:00",12,73.94,75.92,73.94,71.960000000000008,75.02,73.94,66.2,73.94,65.66,73.400000000000006,71.06,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-12",9,12,2018,"2018-09-12",3,0,"19:00:00",19,68,66.02,60.08,62.96,59,69.98,62.42,69.080000000000013,56.120000000000005,67.460000000000008,64.94,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-13",9,13,2018,"2018-09-13",4,0,"02:00:00",2,56.480000000000004,53.06,46.04,48.92,44.96,55.040000000000006,51.8,50,49.82,53.6,51.980000000000004,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-13",9,13,2018,"2018-09-13",4,0,"12:00:00",12,78.080000000000013,73.94,69.080000000000013,69.080000000000013,71.06,71.960000000000008,68.900000000000006,71.960000000000008,71.960000000000008,70.34,69.98,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-13",9,13,2018,"2018-09-13",4,0,"16:00:00",16,82.039999999999992,77,73.94,73.039999999999992,73.94,78.080000000000013,75.02,77,77,69.62,75.02,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-14",9,14,2018,"2018-09-14",5,0,"05:00:00",5,51.08,46.94,44.6,50,48.92,51.08,50,48.019999999999996,49.82,51.8,48.019999999999996,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-14",9,14,2018,"2018-09-14",5,0,"13:00:00",13,80.06,84.02,78.98,80.960000000000008,80.06,82.039999999999992,74.300000000000011,80.960000000000008,79.52,83.300000000000011,82.039999999999992,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-14",9,14,2018,"2018-09-14",5,0,"14:00:00",14,80.960000000000008,84.02,80.06,80.960000000000008,80.960000000000008,82.94,74.66,82.039999999999992,81.319999999999993,84.92,84.02,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-14",9,14,2018,"2018-09-14",5,0,"23:00:00",23,51.08,60.980000000000004,57.92,68,57.019999999999996,68,55.400000000000006,66.92,54.86,67.460000000000008,64.94,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-15",9,15,2018,"2018-09-15",6,0,"07:00:00",7,51.08,62.96,59,65.12,60.980000000000004,66.02,55.400000000000006,66.92,53.24,66.92,64.94,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-15",9,15,2018,"2018-09-15",6,0,"13:00:00",13,80.06,84.02,78.080000000000013,75.92,75.02,84.92,73.22,84.92,80.240000000000009,85.1,82.94,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-15",9,15,2018,"2018-09-15",6,0,1,24,57.019999999999996,53.96,48.92,51.08,48.92,59,53.6,57.019999999999996,56.84,54.68,53.96,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-16",9,16,2018,"2018-09-16",7,0,"10:00:00",10,78.080000000000013,64.94,62.06,62.06,60.980000000000004,64.94,73.039999999999992,62.96,64.759999999999991,63.680000000000007,64.039999999999992,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-16",9,16,{"$f":"$AO$4","v":2018},"2018-09-16",7,{"$f":"COUNTIF($AM$34:$AM$43,E6214)","v":0},"17:00:00",17,78.98,73.039999999999992,68,66.92,68,71.06,77.539999999999992,71.06,62.42,62.42,64.039999999999992,null,{"$f":"SUMPRODUCT($J$2:$T$2,J6214:T6214)","v":0},null,null,{"$f":"OR(B6214<=$AO$14,B6214>=$AN$14)*(F6214<6)*(I6214>$AN$15)*(I6214<=$AO$15)*(G6214<>1)","v":0},{"$f":"OR(B6214<=$AO$14,B6214>=$AN$14)*(Y6214=0)","v":0},{"$f":"AND(B6214>=$AN$24,B6214<=$AO$24)*(F6214<6)*(I6214>$AN$25)*(I6214<=$AO$25)*(G6214<>1)","v":0},{"$f":"AND(B6214>=$AN$24,B6214<=$AO$24)*(AA6214=0)","v":1},{"$f":"OR(B6214<=$AO$19,B6214>=$AN$19)*(F6214<6)*(I6214>$AN$20)*(I6214<=$AO$20)","v":0},{"$f":"AND(B6214>=$AN$29,B6214<=$AO$29)*(F6214<6)*(I6214>$AN$30)*(I6214<=$AO$30)","v":0},{"$f":"IF(OR(E6214=$AM$34,E6214=$AM$35,E6214=$AM$36,E6214=$AM$37,E6214=$AM$38,E6214=$AM$39,E6214=$AM$40,E6214=$AM$41,E6214=$AM$42,E6214=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E6214>=$AM$47,E6214<=$AN$47),AND(E6214>=$AM$48,E6214<=$AN$48),AND(E6214>=$AM$49,E6214<=$AN$49),AND(E6214>=$AM$50,E6214<=$AN$50),AND(E6214>=$AM$51,E6214<=$AN$51)),0,1)*AE6214","v":1},{"$f":"(B6214>=5)*(B6214<=10)","v":1},{"$f":"1*OR(B6214<=4,B6214>=11)","v":0},{"$f":"LOOKUP(B6214,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE6214:AI6214)*((F6214<6)*(I6214>$AO$7)*(I6214<=$AP$7)+(F6214=6)*(I6214>$AO$8)*(I6214<=$AP$8)+(F6214>=7)*(I6214>$AO$9)*(I6214<=$AP$9))","v":0}]
["1976-09-16",9,16,2018,"2018-09-16",7,0,1,24,60.980000000000004,46.94,46.76,46.94,44.06,53.96,62.24,50,48.56,50.36,48.019999999999996,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-17",9,17,2018,"2018-09-17",1,0,"02:00:00",2,60.980000000000004,46.04,46.76,46.04,42.980000000000004,51.08,60.44,46.04,44.96,49.28,49.82,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-17",9,17,2018,"2018-09-17",1,0,"10:00:00",10,78.98,64.039999999999992,62.06,62.96,60.620000000000005,66.02,71.78,66.92,49.46,68.36,68,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-17",9,17,2018,"2018-09-17",1,0,"19:00:00",19,66.02,64.94,59,60.980000000000004,57.92,66.02,68.72,66.02,50,61.16,60.980000000000004,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-18",9,18,2018,"2018-09-18",2,0,"07:00:00",7,60.980000000000004,53.06,44.6,51.08,46.04,49.82,60.44,53.96,42.980000000000004,55.22,51.980000000000004,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-18",9,18,2018,"2018-09-18",2,0,"12:00:00",12,78.080000000000013,75.92,73.039999999999992,71.06,71.960000000000008,73.94,68.36,73.94,65.66,74.300000000000011,75.02,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-18",9,18,2018,"2018-09-18",2,0,"21:00:00",21,68,68,66.92,68,71.06,69.080000000000013,62.42,68,62.78,66.02,64.94,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-19",9,19,2018,"2018-09-19",3,0,"06:00:00",6,60.08,66.02,62.6,64.039999999999992,64.94,66.02,55.58,66.02,54.14,66.2,64.039999999999992,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-19",9,19,2018,"2018-09-19",3,0,"14:00:00",14,66.02,75.92,75.02,73.94,73.400000000000006,75.92,58.82,75.92,61.7,75.2,75.02,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-19",9,19,2018,"2018-09-19",3,0,"20:00:00",20,59,71.06,68,69.080000000000013,66.02,75.02,49.82,71.960000000000008,68.900000000000006,71.599999999999994,71.06,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-19",9,19,2018,"2018-09-19",3,0,"23:00:00",23,57.92,68,66.92,66.92,66.02,71.960000000000008,51.980000000000004,69.98,68.900000000000006,71.78,69.080000000000013,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-20",9,20,2018,"2018-09-20",4,0,"10:00:00",10,52.16,69.98,70.52,66.2,69.080000000000013,69.98,51.08,69.800000000000011,53.24,69.800000000000011,69.800000000000011,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-20",9,20,2018,"2018-09-20",4,0,"16:00:00",16,56.120000000000005,73.94,71.599999999999994,69.800000000000011,75.02,71.06,54.32,71.06,63.5,71.599999999999994,71.06,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-20",9,20,2018,"2018-09-20",4,0,1,24,46.94,68,68,66.2,68,68,50.900000000000006,68,41.36,66.56,66.02,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-21",9,21,2018,"2018-09-21",5,0,"09:00:00",9,51.980000000000004,71.960000000000008,69.800000000000011,71.06,60.980000000000004,71.06,50.900000000000006,69.98,44.24,69.800000000000011,69.98,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-21",9,21,2018,"2018-09-21",5,0,"17:00:00",17,59,84.92,78.98,80.06,75.92,80.960000000000008,55.76,78.98,63.319999999999993,73.759999999999991,78.98,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-22",9,22,2018,{"$f":"DATE(D6343,B6343,C6343)","v":"2018-09-22"},{"$f":"WEEKDAY(E6343,2)","v":6},0,"02:00:00",2,69.080000000000013,62.96,60.8,62.96,59,64.94,63.86,62.96,42.08,65.66,62.06,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-22",9,22,2018,"2018-09-22",6,0,"07:00:00",7,57.019999999999996,55.040000000000006,59,62.96,55.94,64.94,52.16,64.94,46.4,67.099999999999994,66.02,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-22",9,22,2018,"2018-09-22",6,0,"11:00:00",11,51.980000000000004,75.92,70.88,75.02,77,75.92,51.8,77,60.980000000000004,79.34,77,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-22",9,22,2018,"2018-09-22",6,0,"21:00:00",21,43.34,66.02,57.92,64.94,59,66.02,42.44,62.96,50.900000000000006,62.96,64.94,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-23",9,23,2018,"2018-09-23",7,0,"04:00:00",4,33.08,51.980000000000004,51.8,53.96,51.08,59,31.64,53.96,45.32,56.66,59,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-23",9,23,2018,"2018-09-23",7,0,"11:00:00",11,52.7,75.02,75.02,75.92,73.94,80.06,52.34,80.06,59.18,77.180000000000007,78.98,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-23",9,23,2018,"2018-09-23",7,0,"21:00:00",21,46.04,66.92,68.180000000000007,71.06,60.08,69.080000000000013,46.22,64.94,59.18,65.66,62.06,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-24",9,24,2018,"2018-09-24",1,0,"04:00:00",4,35.78,62.06,55.94,66.92,62.96,64.94,35.6,62.96,59.900000000000006,65.12,62.06,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-24",9,24,2018,"2018-09-24",1,0,"14:00:00",14,55.94,66.92,73.94,66.2,62.06,71.960000000000008,51.26,75.92,64.94,72.5,68,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-24",9,24,2018,{"$f":"DATE(D6407,B6407,C6407)","v":"2018-09-24"},{"$f":"WEEKDAY(E6407,2)","v":1},0,"18:00:00",18,46.22,60.980000000000004,62.6,59,59,64.039999999999992,45.14,64.94,57.92,64.400000000000006,60.980000000000004,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-24",9,24,2018,"2018-09-24",1,0,"23:00:00",23,37.04,59,53.96,55.400000000000006,50,57.019999999999996,36.86,55.94,44.96,58.82,57.019999999999996,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-25",9,25,2018,"2018-09-25",2,0,"08:00:00",8,38.299999999999997,51.980000000000004,47.84,51.980000000000004,48.019999999999996,55.040000000000006,35.6,50.72,42.8,57.2,55.94,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-25",9,25,2018,"2018-09-25",2,0,"16:00:00",16,53.96,64.94,62.06,60.980000000000004,62.96,64.94,50.900000000000006,64.039999999999992,60.8,64.400000000000006,62.96,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-25",9,25,2018,"2018-09-25",2,0,"22:00:00",22,53.6,48.2,47.120000000000005,51.08,45.86,51.08,48.2,46.04,45.68,52.7,51.08,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-26",9,26,2018,"2018-09-26",3,0,"09:00:00",9,64.94,47.66,46.22,46.04,43.879999999999995,49.1,53.6,49.28,48.379999999999995,50.900000000000006,49.46,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-26",9,26,2018,"2018-09-26",3,0,"15:00:00",15,77,64.039999999999992,62.06,60.08,62.96,64.94,74.300000000000011,64.94,70.34,63.86,62.06,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-27",9,27,2018,"2018-09-27",4,0,"02:00:00",2,55.94,37.94,41.54,40.82,36.86,40.82,54.68,41.36,51.08,47.3,43.34,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-27",9,27,2018,"2018-09-27",4,0,"05:00:00",5,49.28,36.5,38.659999999999997,37.94,33.08,37.76,49.28,38.119999999999997,50.540000000000006,45.14,41.18,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-27",9,27,2018,"2018-09-27",4,0,"11:00:00",{"$f":"H6472*24","v":11},56.3,57.92,59,57.92,57.019999999999996,60.980000000000004,56.66,60.980000000000004,58.82,60.980000000000004,60.980000000000004,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-27",9,27,2018,"2018-09-27",4,0,"19:00:00",19,55.94,57.019999999999996,57.74,59,51.980000000000004,59,53.96,57.019999999999996,58.46,54.5,53.96,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-28",9,28,2018,"2018-09-28",5,0,"04:00:00",4,51.980000000000004,55.94,55.400000000000006,53.96,55.94,59,49.82,60.8,54.5,59,53.96,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-28",9,28,2018,"2018-09-28",5,0,"09:00:00",9,53.6,59,57.2,56.3,57.92,60.08,49.1,60.980000000000004,49.46,59,57.92,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-28",9,28,2018,"2018-09-28",5,0,"21:00:00",21,51.08,53.06,51.8,58.82,56.120000000000005,59,49.64,57.92,46.76,57.74,55.400000000000006,null,0,null,null,0,0,1,0,0,0,1,1,1,1,0,1,0]
["1976-09-29",9,29,2018,"2018-09-29",6,0,"06:00:00",6,50,57.92,53.78,55.400000000000006,51.08,57.92,45.14,59,39.200000000000003,56.3,55.94,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-29",9,29,2018,"2018-09-29",6,0,"08:00:00",8,46.22,57.019999999999996,55.400000000000006,55.400000000000006,53.06,57.019999999999996,45.14,57.019999999999996,42.08,55.94,55.94,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-29",9,29,2018,"2018-09-29",6,0,"15:00:00",15,60.980000000000004,57.019999999999996,57.019999999999996,57.019999999999996,60.980000000000004,55.040000000000006,57.56,55.040000000000006,48.379999999999995,58.46,55.94,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-30",9,30,2018,"2018-09-30",7,0,"05:00:00",5,40.28,48.379999999999995,48.92,46.4,46.94,50,37.04,50,49.28,49.1,46.94,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-30",9,30,2018,"2018-09-30",7,0,"08:00:00",8,42.620000000000005,44.06,48.2,46.76,46.22,53.06,40.82,53.06,49.46,53.96,51.980000000000004,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1976-09-30",9,30,2018,"2018-09-30",7,0,"15:00:00",15,59,66.02,64.039999999999992,62.06,64.94,62.96,53.96,64.039999999999992,57.2,60.44,64.039999999999992,null,0,null,null,0,0,0,1,0,0,1,1,1,1,0,1,0]
["1986-10-01",10,1,2018,"2018-10-01",1,0,"01:00:00",1,57.379999999999995,61.519999999999996,57.2,62.24,42.620000000000005,62.96,54.32,62.42,45.68,62.6,45.86,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-01",10,1,2018,"2018-10-01",1,0,"05:00:00",5,57.379999999999995,61.519999999999996,57.2,62.24,42.08,62.42,53.42,62.6,43.34,62.6,46.94,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-01",10,1,2018,"2018-10-01",1,0,"18:00:00",18,46.04,51.980000000000004,48.2,55.400000000000006,60.980000000000004,55.94,47.84,60.8,53.96,63.86,53.06,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-02",10,2,2018,"2018-10-02",2,0,"02:00:00",2,46.4,53.06,46.4,51.8,51.8,53.06,41,54.86,48.2,53.42,51.8,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-02",10,2,2018,"2018-10-02",2,0,"03:00:00",3,46.4,51.980000000000004,46.4,51.8,51.8,53.06,42.8,53.6,48.379999999999995,53.6,50,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-02",10,2,2018,"2018-10-02",2,0,"16:00:00",16,50,57.2,60.8,57.2,75.92,60.980000000000004,48.2,60.8,56.3,59.900000000000006,53.06,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-02",10,2,2018,"2018-10-02",2,0,"20:00:00",20,55.400000000000006,57.019999999999996,57.2,55.400000000000006,62.06,57.92,50,57.92,51.8,59.36,50,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-03",10,3,2018,"2018-10-03",3,0,"02:00:00",2,50,57.019999999999996,55.400000000000006,55.400000000000006,48.92,57.2,49.64,57.2,52.16,57.2,50,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-03",10,3,2018,"2018-10-03",3,0,"13:00:00",13,64.400000000000006,62.06,60.8,59,73.039999999999992,64.94,58.1,65.84,54.5,62.6,53.96,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-03",10,3,2018,"2018-10-03",3,0,"23:00:00",23,51.980000000000004,51.980000000000004,51.8,53.6,48.2,57.019999999999996,51.26,53.96,52.7,55.400000000000006,53.06,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-04",10,4,2018,"2018-10-04",4,0,"06:00:00",6,48.2,51.8,51.8,55.400000000000006,43.52,55.400000000000006,48.379999999999995,55.400000000000006,47.3,56.3,50,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-04",10,4,2018,"2018-10-04",4,0,"13:00:00",13,53.6,55.400000000000006,53.6,57.2,64.039999999999992,57.019999999999996,53.06,55.400000000000006,67.460000000000008,57.2,69.98,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-04",10,4,2018,"2018-10-04",4,0,"15:00:00",15,53.6,57.2,55.400000000000006,60.8,64.94,57.2,52.879999999999995,56.84,68,57.2,64.94,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-05",10,5,2018,"2018-10-05",5,0,"03:00:00",3,50,53.96,53.6,55.400000000000006,57.92,55.040000000000006,46.22,55.94,53.6,54.86,53.06,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-05",10,5,2018,"2018-10-05",5,0,"08:00:00",8,43.52,53.06,51.8,53.6,53.6,53.96,42.620000000000005,55.94,52.7,55.400000000000006,55.94,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-05",10,5,2018,"2018-10-05",5,0,"17:00:00",17,48.019999999999996,57.019999999999996,57.2,55.400000000000006,60.980000000000004,57.019999999999996,46.04,56.84,60.8,55.58,55.040000000000006,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-06",10,6,2018,"2018-10-06",6,0,"01:00:00",1,33.44,38.840000000000003,37.94,39.380000000000003,52.34,41,32.18,40.82,45.5,42.26,42.980000000000004,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-06",10,6,2018,"2018-10-06",6,0,"10:00:00",10,35.78,45.86,44.6,43.7,51.980000000000004,47.84,35.42,48.379999999999995,56.120000000000005,52.16,57.92,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-06",10,6,2018,"2018-10-06",6,0,"18:00:00",18,37.94,50,53.6,47.84,51.8,53.96,37.76,47.84,57.2,52.879999999999995,51.980000000000004,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-06",10,6,2018,"2018-10-06",6,0,1,24,26.96,39.380000000000003,37.4,39.200000000000003,51.8,42.08,21.2,41.18,46.4,44.06,42.980000000000004,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-07",10,7,2018,"2018-10-07",7,0,"03:00:00",3,24.98,38.299999999999997,36.86,41,53.6,39.92,21.2,37.94,44.78,42.8,41,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-07",10,7,2018,"2018-10-07",7,0,"14:00:00",14,53.96,60.08,60.8,60.8,69.800000000000011,62.06,54.32,62.96,71.960000000000008,59.36,73.94,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-07",10,7,2018,"2018-10-07",7,0,"20:00:00",20,46.94,50,46.4,48.2,60.08,51.980000000000004,46.04,47.84,51.08,49.46,53.96,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-08",10,8,2018,"2018-10-08",1,1,"04:00:00",4,40.28,48.56,42.8,48.74,46.04,44.96,40.28,48.74,45.32,48.74,46.94,null,0,null,null,0,1,0,0,0,0,0,1,0,1,0,1,0]
["1986-10-08",10,8,2018,"2018-10-08",1,1,"13:00:00",13,73.94,78.080000000000013,69.800000000000011,75.2,62.06,78.98,72.5,77.900000000000006,73.039999999999992,78.080000000000013,75.92,null,0,null,null,0,1,0,0,0,0,0,1,0,1,0,1,0]
["1986-10-08",10,8,2018,"2018-10-08",1,1,"21:00:00",21,57.019999999999996,63.319999999999993,53.6,57.2,41.9,60.980000000000004,55.58,55.94,57.92,60.26,51.980000000000004,null,0,null,null,0,1,0,0,0,0,0,1,0,1,0,1,0]
["1986-10-09",10,9,2018,"2018-10-09",2,0,"06:00:00",6,47.66,55.94,48.92,51.8,37.4,56.3,46.4,56.84,48.74,57.56,48.379999999999995,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-09",10,9,2018,"2018-10-09",2,0,"15:00:00",15,80.960000000000008,84.02,80.599999999999994,82.4,62.96,84.92,75.38,84.92,62.24,83.66,64.039999999999992,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-09",10,9,2018,"2018-10-09",2,0,"20:00:00",20,60.44,60.08,57.2,59,46.58,64.039999999999992,58.82,61.88,55.22,61.519999999999996,60.08,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-09",10,9,2018,"2018-10-09",2,0,1,24,54.68,59.540000000000006,57.74,55.400000000000006,39.200000000000003,57.019999999999996,52.34,53.96,55.400000000000006,58.82,59,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-10",10,10,2018,"2018-10-10",3,0,"10:00:00",10,61.519999999999996,73.039999999999992,68.36,69.800000000000011,45.86,75.02,62.06,75.92,53.6,76.099999999999994,53.06,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-10",10,10,{"$f":"$AO$4","v":2018},"2018-10-10",3,{"$f":"COUNTIF($AM$34:$AM$43,E6790)","v":0},"17:00:00",17,66.02,78.080000000000013,75.2,75.2,60.980000000000004,77,67.64,73.94,49.1,73.22,50,null,{"$f":"SUMPRODUCT($J$2:$T$2,J6790:T6790)","v":0},null,null,{"$f":"OR(B6790<=$AO$14,B6790>=$AN$14)*(F6790<6)*(I6790>$AN$15)*(I6790<=$AO$15)*(G6790<>1)","v":1},{"$f":"OR(B6790<=$AO$14,B6790>=$AN$14)*(Y6790=0)","v":0},{"$f":"AND(B6790>=$AN$24,B6790<=$AO$24)*(F6790<6)*(I6790>$AN$25)*(I6790<=$AO$25)*(G6790<>1)","v":0},{"$f":"AND(B6790>=$AN$24,B6790<=$AO$24)*(AA6790=0)","v":0},{"$f":"OR(B6790<=$AO$19,B6790>=$AN$19)*(F6790<6)*(I6790>$AN$20)*(I6790<=$AO$20)","v":0},{"$f":"AND(B6790>=$AN$29,B6790<=$AO$29)*(F6790<6)*(I6790>$AN$30)*(I6790<=$AO$30)","v":0},{"$f":"IF(OR(E6790=$AM$34,E6790=$AM$35,E6790=$AM$36,E6790=$AM$37,E6790=$AM$38,E6790=$AM$39,E6790=$AM$40,E6790=$AM$41,E6790=$AM$42,E6790=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E6790>=$AM$47,E6790<=$AN$47),AND(E6790>=$AM$48,E6790<=$AN$48),AND(E6790>=$AM$49,E6790<=$AN$49),AND(E6790>=$AM$50,E6790<=$AN$50),AND(E6790>=$AM$51,E6790<=$AN$51)),0,1)*AE6790","v":1},{"$f":"(B6790>=5)*(B6790<=10)","v":1},{"$f":"1*OR(B6790<=4,B6790>=11)","v":0},{"$f":"LOOKUP(B6790,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE6790:AI6790)*((F6790<6)*(I6790>$AO$7)*(I6790<=$AP$7)+(F6790=6)*(I6790>$AO$8)*(I6790<=$AP$8)+(F6790>=7)*(I6790>$AO$9)*(I6790<=$AP$9))","v":0}]
["1986-10-10",10,10,2018,"2018-10-10",3,0,1,24,43.34,50,53.6,53.6,46.94,57.92,44.24,55.94,42.980000000000004,53.78,46.04,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-11",10,11,2018,"2018-10-11",4,0,"10:00:00",10,48.56,60.980000000000004,55.400000000000006,59,55.040000000000006,60.980000000000004,48.2,59.900000000000006,45.5,61.519999999999996,53.06,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-11",10,11,2018,"2018-10-11",4,0,"14:00:00",14,69.98,66.92,68,64.400000000000006,68,66.92,62.42,66.92,51.980000000000004,60.8,57.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-12",10,12,2018,"2018-10-12",5,0,"03:00:00",3,41.54,44.96,48.2,46.4,42.44,50,40.64,48.92,33.619999999999997,49.1,37.4,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-12",10,12,2018,"2018-10-12",5,0,"04:00:00",4,41.72,48.019999999999996,48.2,46.4,41,50,40.82,47.84,32.18,48.74,36.14,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-12",10,12,2018,"2018-10-12",5,0,"12:00:00",12,54.32,57.019999999999996,59,57.2,59,57.92,53.42,57.2,59.36,58.1,60.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-12",10,12,2018,"2018-10-12",5,0,"21:00:00",21,50,53.6,53.6,53.6,53.96,55.400000000000006,47.66,55.400000000000006,47.480000000000004,56.480000000000004,49.28,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-13",10,13,2018,"2018-10-13",6,0,"05:00:00",5,48.92,53.96,55.400000000000006,53.6,43.52,55.94,46.58,55.94,43.7,55.400000000000006,42.980000000000004,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-13",10,13,2018,"2018-10-13",6,0,"11:00:00",{"$f":"H6856*24","v":11},53.6,55.400000000000006,57.2,53.6,57.019999999999996,57.2,50.900000000000006,57.2,54.5,58.28,64.039999999999992,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-13",10,13,2018,"2018-10-13",6,0,"22:00:00",22,53.96,57.019999999999996,57.2,57.2,47.66,57.92,48.2,57.2,49.28,57.92,48.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-14",10,14,2018,"2018-10-14",7,0,"01:00:00",1,53.6,53.24,57.2,57.2,43.879999999999995,57.019999999999996,50,57.2,44.78,57.2,48.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-14",10,14,2018,"2018-10-14",7,0,"15:00:00",15,62.06,64.400000000000006,64.400000000000006,60.8,62.96,64.400000000000006,57.019999999999996,64.400000000000006,61.7,62.6,66.02,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-14",10,14,2018,"2018-10-14",7,0,"22:00:00",22,60.980000000000004,64.400000000000006,62.6,64.400000000000006,57.2,62.96,55.58,62.6,50.18,61.88,51.980000000000004,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-14",10,14,2018,"2018-10-14",7,0,1,24,57.2,62.6,57.2,62.6,55.94,62.6,54.86,62.6,46.4,60.8,48.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-15",10,15,2018,"2018-10-15",1,0,"08:00:00",8,48.019999999999996,53.6,51.8,53.6,51.980000000000004,55.040000000000006,46.58,55.94,36.14,56.3,42.620000000000005,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-15",10,15,2018,"2018-10-15",1,0,"17:00:00",17,55.040000000000006,55.400000000000006,55.400000000000006,57.2,60.980000000000004,53.96,48.92,53.96,51.980000000000004,57.379999999999995,53.06,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-15",10,15,2018,"2018-10-15",1,0,"22:00:00",22,43.879999999999995,51.8,55.400000000000006,50,51.08,55.94,42.26,55.94,34.880000000000003,56.120000000000005,39.92,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-16",10,16,2018,"2018-10-16",2,0,"10:00:00",10,45.14,55.400000000000006,55.400000000000006,53.6,57.92,57.92,45.14,59,43.7,58.82,48.92,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-16",10,16,2018,"2018-10-16",2,0,"19:00:00",19,45.68,48.2,55.400000000000006,50,53.96,53.96,44.24,55.94,46.04,54.14,46.94,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-17",10,17,2018,"2018-10-17",3,0,"03:00:00",3,46.04,51.8,53.6,51.8,51.08,53.06,43.16,53.96,37.4,55.400000000000006,39.200000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-17",10,17,2018,"2018-10-17",3,0,"09:00:00",9,42.08,53.6,49.1,51.8,55.040000000000006,55.94,41.18,56.84,42.26,57.92,46.4,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-17",10,17,2018,"2018-10-17",3,0,"12:00:00",12,47.84,57.92,57.2,57.2,69.080000000000013,62.06,47.3,61.88,59.540000000000006,61.88,60.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-17",10,17,2018,"2018-10-17",3,0,"19:00:00",19,45.14,53.06,48.2,53.6,51.980000000000004,55.040000000000006,45.86,55.040000000000006,59.36,54.5,60.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-18",10,18,2018,"2018-10-18",4,0,"05:00:00",5,39.56,44.6,43.7,44.6,53.6,44.06,37.76,43.879999999999995,55.040000000000006,47.84,60.08,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-18",10,18,2018,"2018-10-18",4,0,"16:00:00",16,53.06,59,60.8,57.2,60.08,60.980000000000004,54.68,62.96,71.78,60.8,73.039999999999992,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-18",10,18,2018,"2018-10-18",4,0,"22:00:00",22,42.08,51.08,48.92,44.6,46.04,48.92,44.42,53.78,52.879999999999995,57.379999999999995,59,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-19",10,19,2018,"2018-10-19",5,0,"06:00:00",6,39.019999999999996,47.480000000000004,44.6,44.6,35.6,48.019999999999996,39.92,45.86,49.1,52.16,51.08,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-19",10,19,2018,"2018-10-19",5,0,"15:00:00",15,53.06,50,53.6,51.8,62.06,51.8,52.879999999999995,53.6,60.26,52.879999999999995,55.040000000000006,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-19",10,19,2018,"2018-10-19",5,0,"16:00:00",16,53.06,50,51.8,50,60.980000000000004,51.980000000000004,49.82,53.6,63.680000000000007,52.879999999999995,63.14,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-20",10,20,2018,"2018-10-20",6,0,"05:00:00",5,47.66,53.06,53.6,50.18,50,53.06,48.2,53.6,60.8,53.6,60.980000000000004,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-20",10,20,2018,"2018-10-20",6,0,"09:00:00",9,47.66,53.96,55.400000000000006,50.540000000000006,47.3,53.96,46.4,53.6,64.759999999999991,55.58,71.06,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-20",10,20,2018,"2018-10-20",6,0,"19:00:00",19,51.08,55.94,57.2,56.84,46.04,57.019999999999996,54.68,57.92,54.14,58.46,60.08,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-21",10,21,2018,"2018-10-21",7,0,"02:00:00",2,44.96,48.019999999999996,50,51.620000000000005,36.32,51.08,48.379999999999995,54.32,44.24,51.980000000000004,49.82,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-21",10,21,{"$f":"$AO$4","v":2018},"2018-10-21",7,{"$f":"COUNTIF($AM$34:$AM$43,E7046)","v":0},"09:00:00",9,44.96,55.040000000000006,48.2,50,37.4,53.96,46.04,54.86,43.879999999999995,56.3,50.36,null,{"$f":"SUMPRODUCT($J$2:$T$2,J7046:T7046)","v":0},null,null,{"$f":"OR(B7046<=$AO$14,B7046>=$AN$14)*(F7046<6)*(I7046>$AN$15)*(I7046<=$AO$15)*(G7046<>1)","v":0},{"$f":"OR(B7046<=$AO$14,B7046>=$AN$14)*(Y7046=0)","v":1},{"$f":"AND(B7046>=$AN$24,B7046<=$AO$24)*(F7046<6)*(I7046>$AN$25)*(I7046<=$AO$25)*(G7046<>1)","v":0},{"$f":"AND(B7046>=$AN$24,B7046<=$AO$24)*(AA7046=0)","v":0},{"$f":"OR(B7046<=$AO$19,B7046>=$AN$19)*(F7046<6)*(I7046>$AN$20)*(I7046<=$AO$20)","v":0},{"$f":"AND(B7046>=$AN$29,B7046<=$AO$29)*(F7046<6)*(I7046>$AN$30)*(I7046<=$AO$30)","v":0},{"$f":"IF(OR(E7046=$AM$34,E7046=$AM$35,E7046=$AM$36,E7046=$AM$37,E7046=$AM$38,E7046=$AM$39,E7046=$AM$40,E7046=$AM$41,E7046=$AM$42,E7046=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E7046>=$AM$47,E7046<=$AN$47),AND(E7046>=$AM$48,E7046<=$AN$48),AND(E7046>=$AM$49,E7046<=$AN$49),AND(E7046>=$AM$50,E7046<=$AN$50),AND(E7046>=$AM$51,E7046<=$AN$51)),0,1)*AE7046","v":1},{"$f":"(B7046>=5)*(B7046<=10)","v":1},{"$f":"1*OR(B7046<=4,B7046>=11)","v":0},{"$f":"LOOKUP(B7046,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE7046:AI7046)*((F7046<6)*(I7046>$AO$7)*(I7046<=$AP$7)+(F7046=6)*(I7046>$AO$8)*(I7046<=$AP$8)+(F7046>=7)*(I7046>$AO$9)*(I7046<=$AP$9))","v":0}]
["1986-10-21",10,21,2018,"2018-10-21",7,0,"19:00:00",19,48.92,53.06,51.8,51.26,53.06,55.94,46.22,54.86,51.44,53.06,53.6,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-22",10,22,2018,"2018-10-22",1,0,"02:00:00",2,42.980000000000004,46.22,44.6,46.4,46.58,51.08,39.200000000000003,50.900000000000006,50,50.36,55.040000000000006,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-22",10,22,2018,"2018-10-22",1,0,"04:00:00",4,40.46,46.94,44.6,46.76,46.04,50,38.840000000000003,50,50,50.540000000000006,55.94,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-22",10,22,2018,"2018-10-22",1,0,"16:00:00",16,48.019999999999996,53.96,53.6,51.8,50.18,53.96,44.96,55.94,57.56,56.120000000000005,64.94,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-22",10,22,2018,"2018-10-22",1,0,"21:00:00",21,42.26,42.980000000000004,44.42,46.22,42.620000000000005,48.019999999999996,41,46.94,59,50.36,62.06,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-23",10,23,2018,"2018-10-23",2,0,"06:00:00",6,34.700000000000003,38.119999999999997,37.4,39.380000000000003,33.26,37.94,32.54,38.299999999999997,54.32,40.1,62.06,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-23",10,23,2018,"2018-10-23",2,0,"14:00:00",14,45.5,51.980000000000004,51.8,50.36,51.980000000000004,53.06,45.5,52.879999999999995,48.2,52.879999999999995,57.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-23",10,23,2018,"2018-10-23",2,0,"20:00:00",20,40.46,46.04,42.980000000000004,45.86,41,44.96,39.200000000000003,47.120000000000005,41.9,49.82,44.96,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-24",10,24,2018,"2018-10-24",3,0,"07:00:00",7,33.08,34.700000000000003,34.700000000000003,36.32,30.02,35.6,28.4,35.78,36.68,41.72,42.08,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-24",10,24,2018,"2018-10-24",3,0,"13:00:00",13,55.040000000000006,51.08,51.8,54.5,43.16,55.040000000000006,52.16,59,44.78,58.28,51.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-24",10,24,2018,"2018-10-24",3,0,"16:00:00",16,53.06,55.040000000000006,57.2,55.58,46.94,57.92,51.620000000000005,59,50.18,55.76,53.06,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-25",10,25,2018,"2018-10-25",4,0,"03:00:00",3,43.16,46.94,46.22,46.4,35.06,46.4,41.54,46.4,40.46,50,45.5,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-25",10,25,2018,"2018-10-25",4,0,"09:00:00",9,40.64,45.32,42.8,44.78,35.6,46.4,39.56,46.58,40.64,48.56,50,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-25",10,25,2018,"2018-10-25",4,0,"17:00:00",17,44.06,53.96,53.6,51.8,42.980000000000004,53.96,42.980000000000004,54.86,45.5,52.879999999999995,51.08,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-26",10,26,2018,"2018-10-26",5,0,"02:00:00",2,34.520000000000003,39.92,37.76,39.56,28.04,39.019999999999996,32.9,41.36,36.5,43.34,41,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-26",10,26,2018,"2018-10-26",5,0,"07:00:00",7,30.02,39.019999999999996,37.4,39.200000000000003,33.08,41,17.600000000000001,41,32.54,42.620000000000005,37.4,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-26",10,26,2018,"2018-10-26",5,0,"19:00:00",{"$f":"H7176*24","v":19},38.480000000000004,44.96,42.8,44.6,43.34,44.96,37.58,44.96,34.880000000000003,45.5,39.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-26",10,26,2018,"2018-10-26",5,0,1,24,33.979999999999997,42.980000000000004,42.8,42.8,42.08,46.04,33.799999999999997,45.86,32.36,45.32,37.04,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-27",10,27,2018,"2018-10-27",6,0,"04:00:00",4,34.700000000000003,41,41,41,39.019999999999996,42.8,33.619999999999997,44.6,35.6,42.980000000000004,35.06,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-27",10,27,2018,"2018-10-27",6,0,"14:00:00",14,36.32,39.92,36.68,39.200000000000003,51.08,39.200000000000003,34.700000000000003,39.200000000000003,38.659999999999997,39.380000000000003,46.04,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-27",10,27,2018,"2018-10-27",6,0,"21:00:00",21,33.979999999999997,33.26,32.18,33.26,36.14,33.799999999999997,10.399999999999999,33.799999999999997,32,36.5,37.22,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-28",10,28,2018,"2018-10-28",7,0,"04:00:00",4,32,30.02,30.2,32,33.979999999999997,33.08,8.5999999999999979,31.1,25.52,35.42,32.54,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-28",10,28,2018,"2018-10-28",7,0,"14:00:00",14,36.86,42.980000000000004,41,42.8,46.94,44.06,35.96,44.96,39.019999999999996,45.14,44.06,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-28",10,28,2018,"2018-10-28",7,0,"18:00:00",18,28.94,37.04,34.700000000000003,36.68,39.56,39.019999999999996,10.399999999999999,38.119999999999997,35.06,39.74,41,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-29",10,29,2018,"2018-10-29",1,0,"07:00:00",7,23,26.060000000000002,28.4,26.6,19.939999999999998,30.92,14,30.02,39.92,35.6,48.92,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-29",10,29,2018,"2018-10-29",1,0,"15:00:00",15,37.94,40.64,37.4,39.56,42.44,42.26,37.22,42.26,41.36,44.6,42.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-29",10,29,2018,"2018-10-29",1,0,"16:00:00",16,35.96,39.56,35.6,37.4,42.08,41.18,35.96,41,39.380000000000003,44.42,42.08,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-30",10,30,2018,"2018-10-30",2,0,"01:00:00",1,32,33.619999999999997,32,33.08,28.04,34.880000000000003,12.2,34.520000000000003,37.58,40.1,41,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-30",10,30,2018,"2018-10-30",2,0,"09:00:00",9,33.799999999999997,35.06,32.36,34.159999999999997,32,36.32,32,36.14,37.04,41.18,42.08,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-30",10,30,2018,"2018-10-30",2,0,"18:00:00",18,32.54,37.4,34.700000000000003,36.14,38.119999999999997,39.380000000000003,33.619999999999997,39.74,41,45.5,44.96,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-30",10,30,2018,"2018-10-30",2,0,1,24,21.02,32.54,26.6,32,33.08,34.340000000000003,14,34.340000000000003,44.78,42.44,46.94,null,0,null,null,0,1,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-31",10,31,2018,"2018-10-31",3,0,"11:00:00",11,41,41.54,40.82,42.8,39.200000000000003,42.980000000000004,43.16,43.879999999999995,43.34,46.04,53.06,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1986-10-31",10,31,2018,"2018-10-31",3,0,"14:00:00",14,48.019999999999996,44.96,46.4,46.4,43.7,50,45.32,50,47.120000000000005,51.8,51.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,1,0,1,0]
["1978-11-01",11,1,2018,"2018-11-01",4,0,"04:00:00",4,33.44,32.36,38.840000000000003,33.619999999999997,32,34.159999999999997,50.18,33.979999999999997,35.24,39.92,38.480000000000004,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-01",11,1,2018,"2018-11-01",4,0,"11:00:00",11,34.700000000000003,43.52,42.8,44.96,41,44.06,51.8,44.06,39.019999999999996,50.540000000000006,48.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-01",11,1,2018,"2018-11-01",4,0,"13:00:00",13,34.880000000000003,50,41,46.94,46.04,50,50.18,48.92,38.659999999999997,52.519999999999996,50,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-02",11,2,2018,"2018-11-02",5,0,"01:00:00",1,32.36,46.04,37.4,46.94,42.980000000000004,50,41,46.94,35.42,35.24,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-02",11,2,2018,"2018-11-02",5,0,"06:00:00",6,33.979999999999997,48.92,34.880000000000003,50.72,44.06,50,38.299999999999997,47.3,33.619999999999997,33.619999999999997,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-02",11,2,2018,"2018-11-02",5,0,"11:00:00",11,32,53.06,37.4,56.120000000000005,55.400000000000006,55.040000000000006,41.54,53.6,35.6,44.24,42.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-02",11,2,2018,"2018-11-02",5,0,"23:00:00",23,30.02,59,34.700000000000003,57.2,62.96,60.980000000000004,38.659999999999997,55.94,32.36,46.04,44.06,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-03",11,3,2018,"2018-11-03",6,0,"08:00:00",8,28.94,59,33.799999999999997,60.980000000000004,62.06,60.980000000000004,36.14,62.06,31.28,48.92,48.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-03",11,3,2018,"2018-11-03",6,0,"16:00:00",16,38.659999999999997,66.92,51.8,64.400000000000006,62.06,66.02,39.74,68,44.24,63.319999999999993,62.06,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-03",11,3,2018,"2018-11-03",6,0,"22:00:00",22,37.04,48.019999999999996,40.1,46.94,46.94,51.08,35.6,51.08,35.96,46.76,44.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-04",11,4,2018,"2018-11-04",7,0,"01:00:00",1,26.060000000000002,42.980000000000004,37.94,42.980000000000004,39.019999999999996,46.94,34.520000000000003,46.04,33.799999999999997,44.96,44.06,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-04",11,4,2018,"2018-11-04",7,0,"12:00:00",12,41,51.980000000000004,48.2,50,43.7,51.980000000000004,37.04,51.08,46.76,53.6,50,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-04",11,4,2018,"2018-11-04",7,0,"18:00:00",18,39.92,46.94,51.8,45.5,44.06,50,33.979999999999997,46.94,46.76,51.44,50,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-05",11,5,2018,"2018-11-05",1,0,"02:00:00",2,37.04,39.92,48.019999999999996,42.08,39.56,42.980000000000004,33.26,42.980000000000004,43.16,47.480000000000004,45.86,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-05",11,5,2018,"2018-11-05",1,0,"11:00:00",11,48.2,48.92,57.2,46.94,46.58,55.040000000000006,34.340000000000003,55.040000000000006,52.519999999999996,53.6,51.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-05",11,5,2018,"2018-11-05",1,0,"19:00:00",19,42.44,53.06,47.84,51.08,48.92,55.94,14,55.94,44.24,41.36,39.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-06",11,6,2018,"2018-11-06",2,0,"04:00:00",4,35.06,57.019999999999996,37.94,59,59,59,15.8,60.980000000000004,35.96,32.72,26.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-06",11,6,{"$f":"$AO$4","v":2018},"2018-11-06",2,{"$f":"COUNTIF($AM$34:$AM$43,E7430)","v":0},"09:00:00",9,33.979999999999997,60.08,37.4,60.8,59,62.96,8.5999999999999979,64.039999999999992,38.299999999999997,36.32,33.44,null,{"$f":"SUMPRODUCT($J$2:$T$2,J7430:T7430)","v":0},null,null,{"$f":"OR(B7430<=$AO$14,B7430>=$AN$14)*(F7430<6)*(I7430>$AN$15)*(I7430<=$AO$15)*(G7430<>1)","v":1},{"$f":"OR(B7430<=$AO$14,B7430>=$AN$14)*(Y7430=0)","v":0},{"$f":"AND(B7430>=$AN$24,B7430<=$AO$24)*(F7430<6)*(I7430>$AN$25)*(I7430<=$AO$25)*(G7430<>1)","v":0},{"$f":"AND(B7430>=$AN$24,B7430<=$AO$24)*(AA7430=0)","v":0},{"$f":"OR(B7430<=$AO$19,B7430>=$AN$19)*(F7430<6)*(I7430>$AN$20)*(I7430<=$AO$20)","v":0},{"$f":"AND(B7430>=$AN$29,B7430<=$AO$29)*(F7430<6)*(I7430>$AN$30)*(I7430<=$AO$30)","v":0},{"$f":"IF(OR(E7430=$AM$34,E7430=$AM$35,E7430=$AM$36,E7430=$AM$37,E7430=$AM$38,E7430=$AM$39,E7430=$AM$40,E7430=$AM$41,E7430=$AM$42,E7430=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E7430>=$AM$47,E7430<=$AN$47),AND(E7430>=$AM$48,E7430<=$AN$48),AND(E7430>=$AM$49,E7430<=$AN$49),AND(E7430>=$AM$50,E7430<=$AN$50),AND(E7430>=$AM$51,E7430<=$AN$51)),0,1)*AE7430","v":1},{"$f":"(B7430>=5)*(B7430<=10)","v":0},{"$f":"1*OR(B7430<=4,B7430>=11)","v":1},{"$f":"LOOKUP(B7430,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE7430:AI7430)*((F7430<6)*(I7430>$AO$7)*(I7430<=$AP$7)+(F7430=6)*(I7430>$AO$8)*(I7430<=$AP$8)+(F7430>=7)*(I7430>$AO$9)*(I7430<=$AP$9))","v":0}]
["1978-11-06",11,6,2018,"2018-11-06",2,0,"13:00:00",13,43.52,64.039999999999992,42.8,60.8,62.96,66.92,6.8000000000000007,66.92,44.06,47.84,48.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-06",11,6,2018,"2018-11-06",2,0,"23:00:00",23,36.14,46.94,42.8,42.980000000000004,42.08,48.019999999999996,5,48.019999999999996,41.54,44.6,46.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-07",11,7,2018,"2018-11-07",3,0,"06:00:00",6,33.799999999999997,35.6,39.200000000000003,34.700000000000003,30.02,37.94,1.3999999999999986,37.94,37.22,44.6,42.980000000000004,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-07",11,7,2018,"2018-11-07",3,0,"13:00:00",13,34.159999999999997,44.96,42.8,41,37.04,46.04,10.399999999999999,44.96,39.92,49.1,48.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-07",11,7,2018,"2018-11-07",3,0,"23:00:00",23,32,35.6,34.520000000000003,35.06,35.96,37.94,21.2,35.96,32.72,42.26,39.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-08",11,8,2018,"2018-11-08",4,0,"06:00:00",6,28.04,32.18,33.799999999999997,35.06,28.04,33.619999999999997,19.399999999999999,34.159999999999997,32.36,34.700000000000003,30.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-08",11,8,2018,"2018-11-08",4,0,"16:00:00",16,32.54,44.06,44.6,41,40.46,44.96,19.399999999999999,44.06,38.480000000000004,45.68,46.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-08",11,8,2018,"2018-11-08",4,0,"20:00:00",20,33.08,30.02,37.4,34.520000000000003,33.26,35.06,15.8,30.92,36.32,39.380000000000003,35.96,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-09",11,9,{"$f":"$AO$4","v":2018},"2018-11-09",5,{"$f":"COUNTIF($AM$34:$AM$43,E7494)","v":0},"01:00:00",1,32,24.98,37.58,23,23,28.94,15.8,26.060000000000002,35.6,35.24,28.94,null,{"$f":"SUMPRODUCT($J$2:$T$2,J7494:T7494)","v":0},null,null,{"$f":"OR(B7494<=$AO$14,B7494>=$AN$14)*(F7494<6)*(I7494>$AN$15)*(I7494<=$AO$15)*(G7494<>1)","v":0},{"$f":"OR(B7494<=$AO$14,B7494>=$AN$14)*(Y7494=0)","v":1},{"$f":"AND(B7494>=$AN$24,B7494<=$AO$24)*(F7494<6)*(I7494>$AN$25)*(I7494<=$AO$25)*(G7494<>1)","v":0},{"$f":"AND(B7494>=$AN$24,B7494<=$AO$24)*(AA7494=0)","v":0},{"$f":"OR(B7494<=$AO$19,B7494>=$AN$19)*(F7494<6)*(I7494>$AN$20)*(I7494<=$AO$20)","v":0},{"$f":"AND(B7494>=$AN$29,B7494<=$AO$29)*(F7494<6)*(I7494>$AN$30)*(I7494<=$AO$30)","v":0},{"$f":"IF(OR(E7494=$AM$34,E7494=$AM$35,E7494=$AM$36,E7494=$AM$37,E7494=$AM$38,E7494=$AM$39,E7494=$AM$40,E7494=$AM$41,E7494=$AM$42,E7494=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E7494>=$AM$47,E7494<=$AN$47),AND(E7494>=$AM$48,E7494<=$AN$48),AND(E7494>=$AM$49,E7494<=$AN$49),AND(E7494>=$AM$50,E7494<=$AN$50),AND(E7494>=$AM$51,E7494<=$AN$51)),0,1)*AE7494","v":1},{"$f":"(B7494>=5)*(B7494<=10)","v":0},{"$f":"1*OR(B7494<=4,B7494>=11)","v":1},{"$f":"LOOKUP(B7494,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE7494:AI7494)*((F7494<6)*(I7494>$AO$7)*(I7494<=$AP$7)+(F7494=6)*(I7494>$AO$8)*(I7494<=$AP$8)+(F7494>=7)*(I7494>$AO$9)*(I7494<=$AP$9))","v":0}]
["1978-11-09",11,9,2018,"2018-11-09",5,0,"10:00:00",10,37.04,33.979999999999997,42.8,33.799999999999997,32,34.700000000000003,17.600000000000001,34.700000000000003,38.840000000000003,44.06,43.34,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-09",11,9,2018,"2018-11-09",5,0,"18:00:00",18,34.159999999999997,41,41.9,41,37.94,41,21.2,41.36,39.74,46.58,50,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-10",11,10,2018,"2018-11-10",6,0,"03:00:00",3,21.92,39.92,32.36,40.46,39.92,42.980000000000004,17.600000000000001,42.08,32.54,40.28,37.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-10",11,10,2018,"2018-11-10",6,0,"09:00:00",9,33.08,32.54,33.44,30.02,28.04,35.06,17.600000000000001,36.5,34.520000000000003,47.480000000000004,45.68,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-10",11,10,2018,"2018-11-10",6,0,"20:00:00",20,33.799999999999997,23,42.44,21.02,21.92,24.98,33.979999999999997,24.98,40.28,49.1,49.64,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-10",11,10,2018,"2018-11-10",6,0,"23:00:00",23,30.02,21.92,38.299999999999997,21.02,21.92,23,32.72,23,34.700000000000003,44.06,42.980000000000004,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-11",11,11,2018,"2018-11-11",7,0,"05:00:00",5,24.08,21.02,36.32,17.96,19.04,21.92,32.18,21.02,34.880000000000003,36.32,34.700000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-11",11,11,2018,"2018-11-11",7,0,"13:00:00",13,51.44,33.979999999999997,57.2,32,33.08,32.72,38.299999999999997,33.08,53.78,50.540000000000006,50,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-11",11,11,2018,"2018-11-11",7,0,"22:00:00",22,37.4,21.92,48.379999999999995,24.98,24.08,24.98,23.9,24.08,44.24,45.14,42.980000000000004,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-12",11,12,2018,"2018-11-12",1,1,"06:00:00",6,40.1,21.02,48.2,23,21.92,24.08,30.2,19.939999999999998,42.8,44.42,41,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1978-11-12",11,12,2018,"2018-11-12",1,1,"15:00:00",15,48.92,42.980000000000004,57.2,39.92,39.019999999999996,44.06,46.4,44.06,51.620000000000005,47.480000000000004,44.06,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1978-11-12",11,12,2018,"2018-11-12",1,1,"20:00:00",20,38.840000000000003,28.04,43.52,32.36,26.060000000000002,30.92,36.5,28.94,41.54,40.82,39.92,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1978-11-13",11,13,2018,"2018-11-13",2,0,"08:00:00",8,32,28.94,28.4,32,30.02,32,36.14,33.08,33.44,32.72,33.979999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-13",11,13,2018,"2018-11-13",2,0,"10:00:00",10,35.06,33.08,37.04,33.26,32,33.979999999999997,44.6,34.340000000000003,35.06,37.58,36.86,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-13",11,13,2018,"2018-11-13",2,0,"17:00:00",17,35.06,33.979999999999997,42.8,34.340000000000003,32.72,33.979999999999997,54.32,35.24,39.74,42.08,42.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-14",11,14,2018,"2018-11-14",3,0,"07:00:00",7,28.04,34.520000000000003,30.2,35.06,33.08,34.340000000000003,49.82,34.340000000000003,32,44.78,44.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-14",11,14,2018,{"$f":"DATE(D7623,B7623,C7623)","v":"2018-11-14"},{"$f":"WEEKDAY(E7623,2)","v":3},0,"10:00:00",10,33.08,35.96,33.44,35.96,32.54,35.6,37.76,35.42,34.520000000000003,49.64,48.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-14",11,14,2018,"2018-11-14",3,0,"17:00:00",17,28.04,37.94,35.6,39.200000000000003,35.06,37.94,34.520000000000003,37.94,33.619999999999997,51.26,51.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-15",11,15,2018,"2018-11-15",4,0,"03:00:00",3,24.98,33.799999999999997,28.4,34.520000000000003,32.18,33.979999999999997,23,33.979999999999997,27.32,41,39.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-15",11,15,2018,"2018-11-15",4,0,"07:00:00",7,21.92,28.94,26.6,30.92,32,33.08,19.399999999999999,30.02,24.8,37.94,35.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-15",11,15,2018,"2018-11-15",4,0,"20:00:00",20,17.059999999999999,32.9,26.6,33.08,28.94,33.799999999999997,32,34.159999999999997,25.16,47.120000000000005,48.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-16",11,16,2018,"2018-11-16",5,0,"04:00:00",4,15.98,33.08,19.399999999999999,33.08,32.54,33.979999999999997,32,34.520000000000003,17.600000000000001,43.7,42.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-16",11,16,2018,"2018-11-16",5,0,"05:00:00",5,19.04,33.26,19.399999999999999,32.9,32.36,34.700000000000003,33.799999999999997,34.880000000000003,19.399999999999999,43.34,42.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-16",11,16,2018,"2018-11-16",5,0,"18:00:00",18,32,39.92,36.32,39.200000000000003,37.04,42.08,33.799999999999997,42.8,36.14,50,48.92,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-16",11,16,2018,"2018-11-16",5,0,"22:00:00",22,30.92,39.019999999999996,35.24,39.92,36.5,41.72,32,41,34.340000000000003,51.44,46.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-17",11,17,2018,"2018-11-17",6,0,"04:00:00",4,30.02,35.24,33.799999999999997,34.520000000000003,37.04,36.86,32,37.58,32.72,55.22,51.980000000000004,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-17",11,17,2018,"2018-11-17",6,0,"15:00:00",15,33.08,35.96,32.72,33.619999999999997,37.04,39.019999999999996,37.76,39.92,33.26,53.78,55.040000000000006,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-18",11,18,2018,"2018-11-18",7,0,"01:00:00",1,33.979999999999997,26.96,37.04,26.96,19.939999999999998,28.94,15.8,26.060000000000002,34.880000000000003,46.04,46.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-18",11,18,2018,"2018-11-18",7,0,"08:00:00",8,32,19.939999999999998,30.2,26.96,23,26.96,23,26.060000000000002,33.799999999999997,47.84,48.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-18",11,18,2018,"2018-11-18",7,0,"15:00:00",15,26.96,37.76,28.4,36.5,34.880000000000003,39.56,37.76,42.08,30.38,58.46,55.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-18",11,18,2018,"2018-11-18",7,0,"17:00:00",17,23,36.32,26.6,35.96,34.880000000000003,38.299999999999997,33.619999999999997,39.380000000000003,26.96,51.08,48.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-19",11,19,2018,"2018-11-19",1,0,"05:00:00",5,19.04,45.32,21.2,39.56,39.019999999999996,49.1,24.8,50.36,22.46,41,37.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-19",11,19,2018,"2018-11-19",1,0,"10:00:00",10,24.08,50,26.6,48.74,46.94,55.94,28.4,55.400000000000006,26.96,49.64,46.58,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-19",11,19,2018,"2018-11-19",1,0,"19:00:00",{"$f":"H7752*24","v":19},17.059999999999999,35.96,24.8,34.340000000000003,32.36,39.019999999999996,28.4,37.94,23.9,49.64,48.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-20",11,20,2018,"2018-11-20",2,0,"03:00:00",3,15.079999999999998,32.54,28.4,30.92,33.08,33.799999999999997,30.2,34.340000000000003,26.060000000000002,42.980000000000004,41,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-20",11,20,2018,"2018-11-20",2,0,"12:00:00",12,33.08,34.159999999999997,37.4,33.08,33.08,36.5,39.92,37.04,33.979999999999997,49.64,50,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-20",11,20,2018,"2018-11-20",2,0,"18:00:00",18,26.96,34.700000000000003,32.18,33.08,32,37.94,30.2,37.04,31.82,47.120000000000005,46.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-21",11,21,2018,"2018-11-21",3,0,"05:00:00",5,19.939999999999998,30.92,24.8,26.96,24.08,35.06,32,32.72,24.08,46.4,44.96,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["1978-11-21",11,21,2018,"2018-11-21",3,0,"11:00:00",11,21.92,42.980000000000004,28.4,40.28,41,42.980000000000004,42.08,46.94,26.6,48.2,48.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1978-11-21",11,21,2018,"2018-11-21",3,0,"14:00:00",14,21.92,53.06,28.4,53.06,53.96,57.92,45.5,59,26.6,41,41,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1978-11-22",11,22,2018,"2018-11-22",4,1,"01:00:00",1,17.96,41,15.8,39.019999999999996,37.04,42.980000000000004,32,45.14,19.399999999999999,33.26,30.92,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1978-11-22",11,22,2018,"2018-11-22",4,1,"07:00:00",7,10.940000000000001,37.4,12.2,37.4,32.18,39.019999999999996,30.2,41.54,14.719999999999999,32.18,28.94,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1978-11-22",11,22,2018,"2018-11-22",4,1,"15:00:00",15,30.92,39.92,37.4,39.019999999999996,37.94,42.08,44.6,42.980000000000004,34.340000000000003,35.78,33.979999999999997,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1978-11-22",11,22,2018,"2018-11-22",4,1,1,24,33.26,35.06,39.200000000000003,34.159999999999997,32,35.96,32,35.06,35.6,32,30.02,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["1978-11-23",11,23,2018,"2018-11-23",5,0,"05:00:00",5,35.96,28.94,41,26.060000000000002,26.96,30.02,30.2,30.02,37.58,30.92,28.94,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["1978-11-23",11,23,2018,"2018-11-23",5,0,"17:00:00",17,41.18,35.06,50,33.979999999999997,30.02,37.04,42.980000000000004,37.04,47.120000000000005,37.94,35.96,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1978-11-23",11,23,2018,"2018-11-23",5,0,"22:00:00",22,36.32,28.04,42.26,30.02,30.02,28.94,33.08,26.96,42.26,34.159999999999997,32.72,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["1978-11-24",11,24,2018,"2018-11-24",6,0,"02:00:00",2,37.04,24.08,38.299999999999997,28.04,30.92,26.96,33.799999999999997,26.060000000000002,39.380000000000003,33.44,32,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-24",11,24,2018,"2018-11-24",6,0,"12:00:00",12,49.1,42.980000000000004,62.6,39.019999999999996,38.119999999999997,44.96,49.46,43.16,55.58,39.56,39.200000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-24",11,24,2018,"2018-11-24",6,0,"19:00:00",19,55.040000000000006,38.119999999999997,62.6,38.480000000000004,35.78,39.200000000000003,39.019999999999996,39.74,59.36,35.96,33.619999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-25",11,25,2018,{"$f":"DATE(D7879,B7879,C7879)","v":"2018-11-25"},{"$f":"WEEKDAY(E7879,2)","v":7},0,"02:00:00",2,55.94,34.340000000000003,62.6,34.340000000000003,33.08,35.42,37.04,36.32,56.3,32.36,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-25",11,25,2018,"2018-11-25",7,0,"12:00:00",12,50,51.980000000000004,55.400000000000006,48.019999999999996,45.5,53.06,33.08,53.06,54.5,37.4,35.24,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-25",11,25,2018,"2018-11-25",7,0,"16:00:00",16,46.04,53.96,53.6,48.92,48.019999999999996,55.94,8.5999999999999979,55.040000000000006,50.72,39.200000000000003,36.68,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-26",11,26,2018,"2018-11-26",1,0,"05:00:00",5,35.96,44.96,37.94,42.980000000000004,39.92,46.94,-0.39999999999999858,46.94,35.24,39.56,36.14,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-26",11,26,2018,"2018-11-26",1,0,"06:00:00",6,33.979999999999997,44.06,36.68,41,37.04,46.04,-0.39999999999999858,44.96,34.159999999999997,39.380000000000003,35.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-26",11,26,2018,"2018-11-26",1,0,"14:00:00",14,32,39.019999999999996,33.799999999999997,36.14,35.06,42.08,-0.39999999999999858,44.06,32.18,42.620000000000005,39.380000000000003,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-26",11,26,2018,"2018-11-26",1,0,"23:00:00",23,30.02,30.02,22.46,30.02,32,32.54,-0.39999999999999858,33.44,32,40.46,38.299999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-27",11,27,2018,"2018-11-27",2,0,"07:00:00",7,24.98,32.36,24.8,30.92,30.92,32.9,6.8000000000000007,33.619999999999997,30.2,36.86,35.42,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-27",11,27,2018,"2018-11-27",2,0,"13:00:00",13,26.96,37.76,30.2,34.520000000000003,33.08,41,6.8000000000000007,42.980000000000004,31.1,43.7,42.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-27",11,27,2018,"2018-11-27",2,0,1,24,19.939999999999998,19.939999999999998,26.6,17.96,15.98,23,3.1999999999999993,23,27.5,38.840000000000003,37.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-28",11,28,2018,"2018-11-28",3,0,"03:00:00",3,15.079999999999998,17.96,26.6,17.059999999999999,14,21.02,5,19.939999999999998,26.42,37.94,37.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-28",11,28,2018,"2018-11-28",3,0,"17:00:00",17,21.92,35.06,28.4,33.979999999999997,35.42,37.04,8.5999999999999979,37.04,27.14,41,39.56,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-28",11,28,2018,"2018-11-28",3,0,1,24,8.0599999999999987,36.86,17.600000000000001,33.979999999999997,34.159999999999997,39.019999999999996,5.8999999999999986,39.019999999999996,20.299999999999997,33.979999999999997,32.72,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-29",11,29,2018,"2018-11-29",4,0,"02:00:00",2,17.059999999999999,41,12.2,37.94,36.68,42.08,6.8000000000000007,42.8,20.479999999999997,33.44,33.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-29",11,29,2018,"2018-11-29",4,0,"10:00:00",10,14,47.120000000000005,15.8,44.96,46.04,51.980000000000004,10.399999999999999,48.74,14.899999999999999,35.42,34.700000000000003,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-29",11,29,2018,"2018-11-29",4,0,"19:00:00",19,8.0599999999999987,39.92,21.2,37.4,35.96,42.980000000000004,6.8000000000000007,42.08,18.14,37.4,34.340000000000003,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-29",11,29,2018,"2018-11-29",4,0,1,24,5,32.36,24.8,30.02,24.98,33.979999999999997,8.5999999999999979,34.520000000000003,15.620000000000001,26.78,24.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-30",11,30,2018,"2018-11-30",5,0,"12:00:00",12,32.54,35.06,39.200000000000003,33.44,32.9,36.68,5,37.04,36.5,40.82,37.22,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-30",11,30,2018,"2018-11-30",5,0,"21:00:00",21,36.86,38.119999999999997,41,35.78,35.42,40.82,2.3000000000000007,39.92,39.200000000000003,47.3,43.52,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["1978-11-30",11,30,2018,"2018-11-30",5,0,"23:00:00",23,35.78,37.76,33.44,35.78,34.340000000000003,40.64,0.14000000000000057,41.72,27.86,43.52,29.12,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-01",12,1,2018,"2018-12-01",6,0,"06:00:00",6,33.26,38.659999999999997,29.3,36.32,33.979999999999997,39.56,-4.3599999999999994,41.54,14.719999999999999,37.94,17.240000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-01",12,1,2018,"2018-12-01",6,0,"20:00:00",20,28.04,42.08,60.8,39.019999999999996,38.659999999999997,42.980000000000004,8.5999999999999979,44.06,25.7,45.14,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-01",12,1,2018,"2018-12-01",6,0,"23:00:00",23,21.02,42.980000000000004,62.96,37.94,38.480000000000004,44.96,10.399999999999999,44.6,25.52,46.4,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-02",12,2,2018,"2018-12-02",7,0,"10:00:00",10,28.94,44.96,59,44.06,44.06,48.019999999999996,10.399999999999999,50,32.9,48.2,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-02",12,2,2018,"2018-12-02",7,0,"16:00:00",16,35.6,48.92,53.06,46.04,46.04,48.92,14,48.92,35.24,49.82,30.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-02",12,2,2018,"2018-12-02",7,0,1,24,33.799999999999997,39.92,39.019999999999996,37.94,38.480000000000004,41,14,42.08,29.3,40.64,26.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-03",12,3,2018,"2018-12-03",1,0,"09:00:00",9,30.2,35.96,33.979999999999997,35.96,36.14,36.68,17.600000000000001,37.22,27.86,38.480000000000004,28.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-03",12,3,2018,"2018-12-03",1,0,"17:00:00",17,28.04,44.42,34.700000000000003,42.08,39.92,46.04,12.2,44.96,30.92,45.68,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-03",12,3,2018,"2018-12-03",1,0,"18:00:00",18,26.060000000000002,42.08,34.520000000000003,39.92,38.119999999999997,44.96,8.5999999999999979,44.06,30.56,44.78,30.02,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["2003-12-04",12,4,2018,"2018-12-04",2,0,"07:00:00",7,14,35.96,23,34.700000000000003,33.619999999999997,37.04,14.18,37.04,26.24,36.5,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-04",12,4,2018,"2018-12-04",2,0,"11:00:00",11,39.200000000000003,41,38.299999999999997,39.019999999999996,35.78,41,16.340000000000003,41,30.2,43.7,33.979999999999997,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-04",12,4,2018,"2018-12-04",2,0,"21:00:00",21,35.6,34.520000000000003,37.4,33.619999999999997,32.36,35.42,12.2,35.06,30.2,37.04,32,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-05",12,5,2018,"2018-12-05",3,0,"04:00:00",4,34.700000000000003,32,35.42,30.92,33.08,32.36,14,32.72,23.9,33.44,30.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-05",12,5,2018,"2018-12-05",3,0,"11:00:00",11,44.06,34.159999999999997,46.4,32.72,33.08,35.6,14,37.04,32.54,36.14,34.880000000000003,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-05",12,5,2018,"2018-12-05",3,0,"21:00:00",21,38.659999999999997,24.08,42.26,26.060000000000002,26.060000000000002,30.02,3.1999999999999993,26.060000000000002,29.84,27.32,34.340000000000003,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-06",12,6,2018,"2018-12-06",4,0,"04:00:00",4,39.92,24.08,37.94,21.92,24.08,26.96,1.3999999999999986,24.98,26.24,25.52,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-06",12,6,2018,"2018-12-06",4,0,"06:00:00",6,39.019999999999996,26.060000000000002,37.22,24.08,26.060000000000002,28.04,1.3999999999999986,28.04,26.060000000000002,27.14,24.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-06",12,6,2018,"2018-12-06",4,0,"18:00:00",18,39.380000000000003,28.04,33.979999999999997,28.94,26.96,28.04,6.8000000000000007,26.6,27.86,32.36,28.04,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["2003-12-06",12,6,2018,"2018-12-06",4,0,"23:00:00",23,37.94,24.08,32.36,28.94,26.96,26.060000000000002,3.1999999999999993,21.92,28.4,28.04,26.060000000000002,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-07",12,7,2018,"2018-12-07",5,0,"08:00:00",8,35.24,19.939999999999998,28.04,30.92,26.96,21.02,-2.2000000000000028,19.04,16.88,29.3,19.939999999999998,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-07",12,7,2018,"2018-12-07",5,0,"16:00:00",16,35.6,39.019999999999996,33.08,37.76,35.96,39.56,-2.2000000000000028,39.74,25.52,37.58,24.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-07",12,7,2018,"2018-12-07",5,0,"22:00:00",22,34.159999999999997,32,26.96,33.08,28.94,32.36,-5.8000000000000043,32.9,14.54,34.880000000000003,15.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-08",12,8,{"$f":"$AO$4","v":2018},"2018-12-08",6,{"$f":"COUNTIF($AM$34:$AM$43,E8198)","v":0},"09:00:00",9,26.6,33.08,26.6,30.2,30.92,32.36,6.259999999999998,32.72,1.759999999999998,34.700000000000003,14,null,{"$f":"SUMPRODUCT($J$2:$T$2,J8198:T8198)","v":0},null,null,{"$f":"OR(B8198<=$AO$14,B8198>=$AN$14)*(F8198<6)*(I8198>$AN$15)*(I8198<=$AO$15)*(G8198<>1)","v":0},{"$f":"OR(B8198<=$AO$14,B8198>=$AN$14)*(Y8198=0)","v":1},{"$f":"AND(B8198>=$AN$24,B8198<=$AO$24)*(F8198<6)*(I8198>$AN$25)*(I8198<=$AO$25)*(G8198<>1)","v":0},{"$f":"AND(B8198>=$AN$24,B8198<=$AO$24)*(AA8198=0)","v":0},{"$f":"OR(B8198<=$AO$19,B8198>=$AN$19)*(F8198<6)*(I8198>$AN$20)*(I8198<=$AO$20)","v":0},{"$f":"AND(B8198>=$AN$29,B8198<=$AO$29)*(F8198<6)*(I8198>$AN$30)*(I8198<=$AO$30)","v":0},{"$f":"IF(OR(E8198=$AM$34,E8198=$AM$35,E8198=$AM$36,E8198=$AM$37,E8198=$AM$38,E8198=$AM$39,E8198=$AM$40,E8198=$AM$41,E8198=$AM$42,E8198=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E8198>=$AM$47,E8198<=$AN$47),AND(E8198>=$AM$48,E8198<=$AN$48),AND(E8198>=$AM$49,E8198<=$AN$49),AND(E8198>=$AM$50,E8198<=$AN$50),AND(E8198>=$AM$51,E8198<=$AN$51)),0,1)*AE8198","v":1},{"$f":"(B8198>=5)*(B8198<=10)","v":0},{"$f":"1*OR(B8198<=4,B8198>=11)","v":1},{"$f":"LOOKUP(B8198,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE8198:AI8198)*((F8198<6)*(I8198>$AO$7)*(I8198<=$AP$7)+(F8198=6)*(I8198>$AO$8)*(I8198<=$AP$8)+(F8198>=7)*(I8198>$AO$9)*(I8198<=$AP$9))","v":0}]
["2003-12-08",12,8,2018,"2018-12-08",6,0,"15:00:00",15,30.02,35.96,30.02,33.08,34.159999999999997,35.96,13.279999999999998,37.04,29.66,37.76,30.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-08",12,8,2018,"2018-12-08",6,0,"18:00:00",18,19.939999999999998,34.520000000000003,26.96,33.08,32.18,35.96,15.8,37.04,27.5,37.04,28.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-09",12,9,2018,"2018-12-09",7,0,"05:00:00",5,30.92,32.36,24.8,32.36,30.02,32.36,23,32.9,33.619999999999997,34.520000000000003,38.119999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-09",12,9,2018,"2018-12-09",7,0,"11:00:00",11,30.02,35.06,26.6,33.979999999999997,32.54,37.04,33.619999999999997,36.5,35.6,37.04,39.200000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-09",12,9,2018,"2018-12-09",7,0,"19:00:00",19,32,33.08,26.6,32.54,33.08,34.340000000000003,35.78,35.06,41,36.5,48.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-10",12,10,2018,"2018-12-10",1,0,"04:00:00",4,33.979999999999997,30.92,19.939999999999998,28.94,30.02,32,43.16,30.92,47.3,30.56,51.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-10",12,10,2018,"2018-12-10",1,0,"09:00:00",9,30.2,30.92,24.98,26.96,26.96,30.02,42.26,30.92,47.120000000000005,32.36,51.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-10",12,10,2018,"2018-12-10",1,0,"21:00:00",21,15.98,24.08,28.4,21.92,23,26.060000000000002,34.700000000000003,26.060000000000002,38.119999999999997,24.62,42.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-11",12,11,2018,"2018-12-11",2,0,"06:00:00",6,15.079999999999998,17.96,33.44,17.96,19.939999999999998,19.04,2.1199999999999974,19.04,26.96,18.5,30.2,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-11",12,11,2018,"2018-12-11",2,0,"08:00:00",8,14,19.04,34.520000000000003,17.96,19.939999999999998,19.939999999999998,9.14,19.04,25.34,20.479999999999997,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-11",12,11,2018,"2018-12-11",2,0,"15:00:00",15,28.94,24.08,41,21.92,23,26.96,26.6,26.96,31.1,26.24,32,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-11",12,11,2018,"2018-12-11",2,0,"22:00:00",22,12.02,10.039999999999999,33.26,10.940000000000001,6.0799999999999983,15.98,1.3999999999999986,12.02,24.259999999999998,16.52,23,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-12",12,12,2018,"2018-12-12",3,0,"08:00:00",8,10.940000000000001,5,19.04,8.5999999999999979,3.019999999999996,10.039999999999999,-5.8000000000000043,8.0599999999999987,21.560000000000002,12.740000000000002,21.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-12",12,12,2018,"2018-12-12",3,0,"15:00:00",15,37.58,30.02,46.04,28.94,24.98,30.92,-2.2000000000000028,32,28.4,30.38,28.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-13",12,13,2018,"2018-12-13",4,0,"01:00:00",1,14,26.96,32.9,24.8,24.08,26.96,6.8000000000000007,26.6,17.240000000000002,26.78,21.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-13",12,13,2018,"2018-12-13",4,0,"05:00:00",5,8.9599999999999973,28.04,30.02,26.6,26.96,30.02,8.5999999999999979,28.4,17.600000000000001,32.18,19.939999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-13",12,13,2018,{"$f":"DATE(D8327,B8327,C8327)","v":"2018-12-13"},{"$f":"WEEKDAY(E8327,2)","v":4},0,"18:00:00",18,33.08,33.799999999999997,37.4,32.36,33.619999999999997,34.159999999999997,24.8,34.700000000000003,28.94,34.880000000000003,35.06,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["2003-12-13",12,13,2018,"2018-12-13",4,0,"19:00:00",{"$f":"H8328*24","v":19},33.799999999999997,24.98,36.5,30.92,32.36,32,23.9,32.72,29.3,33.44,37.22,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["2003-12-14",12,14,2018,"2018-12-14",5,0,"03:00:00",3,30.92,32,37.94,32,35.06,33.979999999999997,30.2,30.02,32,32.72,40.64,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-14",12,14,2018,"2018-12-14",5,0,"16:00:00",16,32.9,34.700000000000003,46.94,32.72,32.36,37.94,39.200000000000003,39.380000000000003,41,37.4,46.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-14",12,14,2018,"2018-12-14",5,0,"20:00:00",20,33.08,33.08,39.56,33.979999999999997,30.92,34.340000000000003,37.22,34.700000000000003,40.82,35.96,46.94,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-15",12,15,2018,"2018-12-15",6,0,"02:00:00",2,30.92,32.72,26.060000000000002,30.92,33.08,33.979999999999997,41.36,33.979999999999997,39.74,35.6,44.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-15",12,15,2018,"2018-12-15",6,0,"13:00:00",13,37.94,34.700000000000003,33.799999999999997,33.44,33.979999999999997,37.94,32.54,37.04,39.019999999999996,39.019999999999996,42.980000000000004,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-15",12,15,2018,"2018-12-15",6,0,"16:00:00",16,37.4,32,33.44,30.92,28.94,34.159999999999997,12.2,34.520000000000003,36.14,35.6,43.16,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-16",12,16,2018,"2018-12-16",7,0,"06:00:00",6,36.86,21.92,28.04,19.04,23,24.08,-7.6000000000000014,24.98,21.38,26.42,24.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-16",12,16,2018,"2018-12-16",7,0,"13:00:00",13,34.700000000000003,21.02,30.92,17.96,17.96,21.02,4.4599999999999973,21.92,26.78,24.439999999999998,28.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-16",12,16,2018,"2018-12-16",7,0,"15:00:00",15,35.06,17.96,30.92,15.079999999999998,15.079999999999998,19.04,7.6999999999999993,19.04,28.04,17.78,30.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-17",12,17,2018,"2018-12-17",1,0,"03:00:00",3,28.94,-3.9999999999999147E-2,14,-2.2000000000000028,-0.94000000000000483,1.9400000000000013,12.2,1.9400000000000013,24.439999999999998,1.5800000000000018,24.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-17",12,17,2018,"2018-12-17",1,0,"08:00:00",8,26.060000000000002,-0.94000000000000483,10.039999999999999,-4,-7.0600000000000023,-3.9999999999999147E-2,14,-3.9999999999999147E-2,24.62,0.68000000000000327,24.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-17",12,17,2018,"2018-12-17",1,0,"17:00:00",17,17.059999999999999,12.02,21.02,3.9200000000000017,1.0399999999999991,15.98,15.8,10.940000000000001,26.42,10.399999999999999,26.060000000000002,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-18",12,18,2018,"2018-12-18",2,0,"01:00:00",1,3.9200000000000017,3.019999999999996,17.600000000000001,3.019999999999996,3.019999999999996,12.920000000000002,10.399999999999999,10.940000000000001,26.42,10.399999999999999,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-18",12,18,2018,"2018-12-18",2,0,"10:00:00",10,8.9599999999999973,10.940000000000001,19.399999999999999,12.2,10.940000000000001,17.96,5,15.8,27.32,20.84,30.2,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-18",12,18,2018,"2018-12-18",2,0,"18:00:00",18,6.0799999999999983,17.96,21.02,19.399999999999999,21.92,21.02,3.1999999999999993,23,27.32,23.54,26.96,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["2003-12-18",12,18,2018,"2018-12-18",2,0,1,24,-0.94000000000000483,24.08,19.939999999999998,24.08,24.08,26.060000000000002,-13,26.6,16.159999999999997,27.68,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-19",12,19,2018,"2018-12-19",3,0,"03:00:00",{"$f":"H8456*24","v":3},1.0399999999999991,26.060000000000002,19.04,24.8,30.92,26.96,-13,32.18,9.86,28.4,12.920000000000002,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-19",12,19,2018,"2018-12-19",3,0,"14:00:00",14,24.08,51.08,28.04,47.480000000000004,42.980000000000004,53.06,-14.800000000000004,53.96,12.379999999999999,51.8,17.059999999999999,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-19",12,19,2018,"2018-12-19",3,0,"20:00:00",20,32.9,35.6,6.98,32.36,30.92,37.94,-9.3999999999999986,38.299999999999997,10.579999999999998,37.94,14,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-20",12,20,2018,"2018-12-20",4,0,"04:00:00",4,28.94,17.059999999999999,-5.980000000000004,12.920000000000002,12.02,19.939999999999998,5,21.02,7.1599999999999966,20.84,10.039999999999999,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-20",12,20,2018,"2018-12-20",4,0,"13:00:00",13,23,19.04,33.08,17.96,17.96,19.939999999999998,10.579999999999998,21.02,14.899999999999999,20.66,26.060000000000002,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-20",12,20,2018,"2018-12-20",4,0,"21:00:00",21,5,1.0399999999999991,17.059999999999999,1.9400000000000013,-3.9999999999999147E-2,12.02,3.9200000000000017,10.940000000000001,15.259999999999998,12.740000000000002,15.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-21",12,21,2018,"2018-12-21",5,0,"06:00:00",6,8.5999999999999979,-5.980000000000004,15.079999999999998,-4,-5.0800000000000054,3.9200000000000017,-5.0800000000000054,3.019999999999996,7.879999999999999,10.039999999999999,10.039999999999999,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-21",12,21,2018,"2018-12-21",5,0,"07:00:00",7,12.02,-7.0600000000000023,14,-5.8000000000000043,-5.980000000000004,3.019999999999996,-4.7199999999999989,1.0399999999999991,4.6400000000000006,10.399999999999999,10.039999999999999,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-21",12,21,2018,"2018-12-21",5,0,"15:00:00",15,24.8,26.060000000000002,30.2,23,23,30.92,21.92,32,23.72,32.36,30.02,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-21",12,21,2018,"2018-12-21",5,0,"16:00:00",16,26.96,24.98,30.2,21.92,24.08,30.92,21.2,30.92,25.34,30.38,28.04,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-21",12,21,{"$f":"$AO$4","v":2018},"2018-12-21",5,{"$f":"COUNTIF($AM$34:$AM$43,E8518)","v":0},"17:00:00",17,28.4,24.98,30.2,19.04,23,30.02,20.479999999999997,30.02,23.9,29.84,26.96,null,{"$f":"SUMPRODUCT($J$2:$T$2,J8518:T8518)","v":0},null,null,{"$f":"OR(B8518<=$AO$14,B8518>=$AN$14)*(F8518<6)*(I8518>$AN$15)*(I8518<=$AO$15)*(G8518<>1)","v":1},{"$f":"OR(B8518<=$AO$14,B8518>=$AN$14)*(Y8518=0)","v":0},{"$f":"AND(B8518>=$AN$24,B8518<=$AO$24)*(F8518<6)*(I8518>$AN$25)*(I8518<=$AO$25)*(G8518<>1)","v":0},{"$f":"AND(B8518>=$AN$24,B8518<=$AO$24)*(AA8518=0)","v":0},{"$f":"OR(B8518<=$AO$19,B8518>=$AN$19)*(F8518<6)*(I8518>$AN$20)*(I8518<=$AO$20)","v":0},{"$f":"AND(B8518>=$AN$29,B8518<=$AO$29)*(F8518<6)*(I8518>$AN$30)*(I8518<=$AO$30)","v":0},{"$f":"IF(OR(E8518=$AM$34,E8518=$AM$35,E8518=$AM$36,E8518=$AM$37,E8518=$AM$38,E8518=$AM$39,E8518=$AM$40,E8518=$AM$41,E8518=$AM$42,E8518=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E8518>=$AM$47,E8518<=$AN$47),AND(E8518>=$AM$48,E8518<=$AN$48),AND(E8518>=$AM$49,E8518<=$AN$49),AND(E8518>=$AM$50,E8518<=$AN$50),AND(E8518>=$AM$51,E8518<=$AN$51)),0,1)*AE8518","v":1},{"$f":"(B8518>=5)*(B8518<=10)","v":0},{"$f":"1*OR(B8518<=4,B8518>=11)","v":1},{"$f":"LOOKUP(B8518,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE8518:AI8518)*((F8518<6)*(I8518>$AO$7)*(I8518<=$AP$7)+(F8518=6)*(I8518>$AO$8)*(I8518<=$AP$8)+(F8518>=7)*(I8518>$AO$9)*(I8518<=$AP$9))","v":0}]
["2003-12-21",12,21,2018,{"$f":"DATE(D8519,B8519,C8519)","v":"2018-12-21"},{"$f":"WEEKDAY(E8519,2)","v":5},0,"18:00:00",18,28.4,24.98,28.4,17.96,19.939999999999998,30.02,17.420000000000002,30.02,21.560000000000002,28.94,26.96,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["2003-12-21",12,21,2018,"2018-12-21",5,0,"19:00:00",{"$f":"H8520*24","v":19},30.2,26.060000000000002,30.2,16.88,15.98,30.02,15.8,30.2,21.02,29.66,26.060000000000002,null,0,null,null,1,0,0,0,1,0,1,1,1,0,1,1,0]
["2003-12-21",12,21,2018,"2018-12-21",5,0,"20:00:00",20,30.2,26.060000000000002,30.2,15.98,12.920000000000002,30.02,14.36,30.2,20.299999999999997,32,26.060000000000002,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-21",12,21,2018,"2018-12-21",5,0,"21:00:00",21,30.2,19.04,28.94,15.079999999999998,15.079999999999998,28.04,13.459999999999997,26.060000000000002,20.84,29.48,26.060000000000002,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-21",12,21,2018,"2018-12-21",5,0,"22:00:00",22,30.2,15.98,28.94,19.939999999999998,14,26.96,10.039999999999999,21.92,20.12,27.68,24.98,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-21",12,21,2018,"2018-12-21",5,0,"23:00:00",23,32.54,15.98,28.4,21.92,12.920000000000002,28.04,7.34,19.04,17.059999999999999,28.04,24.08,null,0,null,null,1,0,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-21",12,21,2018,"2018-12-21",5,0,1,24,33.08,14,28.94,23,19.939999999999998,26.060000000000002,15.8,23,13.64,28.22,23,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"01:00:00",1,33.799999999999997,14,28.94,23,21.02,26.96,15.8,26.060000000000002,11.120000000000001,28.4,23,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"02:00:00",2,34.700000000000003,14,28.94,21.92,19.939999999999998,26.060000000000002,15.8,26.96,11.659999999999997,28.58,19.939999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"03:00:00",3,35.6,21.02,30.02,22.46,19.939999999999998,26.060000000000002,15.8,24.08,10.940000000000001,27.86,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"04:00:00",4,36.14,17.059999999999999,30.02,23,15.98,26.060000000000002,16.159999999999997,21.02,9.32,27.14,19.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"05:00:00",5,36.32,17.059999999999999,30.02,19.939999999999998,17.96,24.08,15.98,23,7.6999999999999993,25.88,17.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"06:00:00",6,39.019999999999996,12.920000000000002,30.02,19.939999999999998,19.939999999999998,23,17.600000000000001,21.02,7.6999999999999993,25.34,21.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"07:00:00",7,37.4,10.039999999999999,30.02,19.939999999999998,19.939999999999998,19.939999999999998,17.600000000000001,19.04,7.6999999999999993,24.439999999999998,17.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"08:00:00",8,34.700000000000003,10.039999999999999,30.02,19.04,17.059999999999999,21.02,19.399999999999999,17.059999999999999,7.52,25.88,19.939999999999998,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"09:00:00",9,33.979999999999997,15.98,32,23.54,19.939999999999998,24.08,17.600000000000001,28.94,10.399999999999999,29.3,21.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"10:00:00",10,34.159999999999997,24.98,35.06,28.04,26.060000000000002,28.94,17.600000000000001,33.08,13.099999999999998,33.26,26.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"11:00:00",11,35.6,24.98,35.96,33.08,33.979999999999997,32.72,18.14,33.08,17.059999999999999,32.9,32,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"12:00:00",12,35.6,34.520000000000003,32.9,35.96,37.94,35.96,18.86,36.14,22.1,35.96,33.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"13:00:00",13,35.96,38.659999999999997,33.26,36.14,34.340000000000003,41,32.18,42.08,27.32,39.92,33.979999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"14:00:00",14,35.78,41,35.06,36.86,35.06,41,33.26,42.08,32.9,40.64,37.22,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"15:00:00",15,35.78,39.380000000000003,35.06,37.4,35.78,41,33.08,42.08,34.520000000000003,42.620000000000005,38.119999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"16:00:00",16,35.06,39.019999999999996,33.979999999999997,37.4,35.78,39.019999999999996,33.26,39.019999999999996,35.06,39.92,39.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"17:00:00",17,35.24,36.5,36.5,35.96,35.06,37.04,17.600000000000001,37.58,34.880000000000003,39.200000000000003,38.840000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"18:00:00",18,32.36,33.979999999999997,34.520000000000003,32.72,30.92,34.340000000000003,17.600000000000001,33.979999999999997,27.68,36.68,36.32,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"19:00:00",19,33.08,32.54,32.18,33.08,28.04,33.08,16.159999999999997,33.26,27.32,35.6,34.520000000000003,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"20:00:00",20,33.08,30.92,30.2,32,24.98,33.08,15.8,26.060000000000002,26.42,34.159999999999997,33.44,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"21:00:00",21,32.72,26.96,30.2,30.02,23,30.02,15.8,26.96,24.259999999999998,33.26,32.72,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"22:00:00",22,28.04,26.96,30.92,30.02,26.060000000000002,30.02,15.8,26.060000000000002,25.7,33.08,33.979999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,"23:00:00",23,28.94,26.96,30.2,30.92,26.96,28.94,19.399999999999999,26.060000000000002,28.4,32.54,30.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-22",12,22,2018,"2018-12-22",6,0,1,24,32.54,24.98,30.2,30.02,26.96,30.02,19.939999999999998,26.96,21.560000000000002,29.84,33.979999999999997,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"01:00:00",1,30.02,26.96,30.2,30.02,28.04,28.94,19.399999999999999,26.060000000000002,21.560000000000002,29.48,33.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"02:00:00",2,30.02,26.96,30.2,30.02,28.94,28.94,19.399999999999999,24.98,20.84,28.22,28.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"03:00:00",3,30.92,26.060000000000002,28.4,28.04,30.02,26.96,21.38,26.96,19.939999999999998,28.759999999999998,30.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"04:00:00",4,30.2,24.98,28.4,28.04,30.02,28.04,21.2,26.96,19.759999999999998,28.04,28.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"05:00:00",5,30.2,24.98,28.4,26.96,30.02,28.04,23,30.92,17.96,27.32,30.02,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"06:00:00",6,30.2,30.2,26.96,26.060000000000002,30.02,28.94,21.2,30.2,15.620000000000001,30.02,26.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"07:00:00",7,30.2,28.94,26.6,30.2,30.02,30.02,23,28.4,15.440000000000001,30.2,24.98,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"08:00:00",8,30.2,30.02,26.6,28.4,28.94,30.02,23,28.04,15.259999999999998,29.84,26.96,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"09:00:00",9,30.2,28.94,26.6,28.4,30.02,30.02,26.6,30.02,15.8,30.2,32,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"10:00:00",10,32,30.02,30.2,28.4,30.02,30.02,26.6,30.2,21.38,31.28,37.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"11:00:00",11,33.799999999999997,30.92,37.4,30.2,30.92,30.02,32.72,30.2,26.24,32.54,36.14,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"12:00:00",12,33.799999999999997,30.92,34.520000000000003,32,32,30.02,36.32,30.2,35.24,32.72,40.28,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"13:00:00",13,33.799999999999997,32,38.119999999999997,32,32,30.02,41,32.36,41.36,33.619999999999997,44.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"14:00:00",14,33.799999999999997,32,39.019999999999996,32,32,33.08,41,33.799999999999997,43.7,34.700000000000003,48.92,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"15:00:00",15,33.979999999999997,32.36,37.94,32,32,33.619999999999997,42.44,34.700000000000003,44.96,35.42,50,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"16:00:00",16,33.799999999999997,33.08,37.04,30.2,32,34.520000000000003,42.08,35.42,45.14,35.78,46.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"17:00:00",17,33.799999999999997,33.08,37.58,28.4,24.08,34.159999999999997,40.28,35.06,45.32,35.42,46.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"18:00:00",18,26.6,21.92,36.5,26.6,23,32,36.68,32.9,42.26,33.26,42.980000000000004,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"19:00:00",19,24.8,24.08,36.14,26.6,26.96,28.04,36.68,32.18,42.08,32.72,42.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"20:00:00",20,23,23,36.32,28.94,28.04,26.060000000000002,38.480000000000004,32.36,42.26,32.9,42.08,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"21:00:00",21,21.2,26.060000000000002,35.96,28.94,28.04,24.98,38.840000000000003,26.060000000000002,41.36,32.54,46.94,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"22:00:00",22,19.399999999999999,28.94,34.880000000000003,30.02,32,28.94,36.68,32,40.64,32.72,44.6,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,"23:00:00",23,17.600000000000001,28.94,33.979999999999997,30.02,32.36,26.060000000000002,35.24,28.04,40.46,32.54,46.04,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-23",12,23,2018,"2018-12-23",7,0,1,24,14,32,33.979999999999997,31.82,32.9,33.979999999999997,35.24,32.36,40.28,32.36,42.980000000000004,null,0,null,null,0,1,0,0,0,0,1,1,1,0,1,1,0]
["2003-12-24",12,24,2018,"2018-12-24",1,0,"01:00:00",1,12.2,33.619999999999997,32.36,32.54,33.979999999999997,33.619999999999997,32.72,34.159999999999997,38.480000000000004,33.26,42.08,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-24",12,24,2018,"2018-12-24",1,0,"02:00:00",2,6.0799999999999983,33.979999999999997,30.02,33.44,34.159999999999997,34.520000000000003,10.399999999999999,35.24,37.22,33.44,42.08,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-24",12,24,2018,"2018-12-24",1,0,"03:00:00",3,8.9599999999999973,35.06,30.92,33.799999999999997,33.979999999999997,35.06,10.399999999999999,35.78,36.32,33.979999999999997,39.92,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-24",12,24,2018,"2018-12-24",1,0,"04:00:00",4,8.0599999999999987,33.979999999999997,30.92,33.619999999999997,33.26,33.979999999999997,8.5999999999999979,35.42,34.159999999999997,34.159999999999997,37.94,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-24",12,24,2018,"2018-12-24",1,0,"05:00:00",5,6.0799999999999983,33.619999999999997,28.94,33.08,32,33.979999999999997,10.399999999999999,34.700000000000003,32.72,33.979999999999997,35.96,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-24",12,24,2018,"2018-12-24",1,0,"06:00:00",6,6.0799999999999983,24.08,28.94,27.5,19.04,24.08,10.759999999999998,28.04,29.84,32.54,33.979999999999997,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-24",12,24,2018,"2018-12-24",1,0,"07:00:00",7,6.0799999999999983,21.92,26.060000000000002,24.08,19.04,24.08,13.459999999999997,19.04,29.3,30.38,33.979999999999997,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-24",12,24,2018,"2018-12-24",1,0,"08:00:00",8,5,21.92,24.08,26.060000000000002,17.96,26.060000000000002,14.719999999999999,19.939999999999998,28.4,31.1,33.44,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-24",12,24,{"$f":"$AO$4","v":2018},"2018-12-24",1,{"$f":"COUNTIF($AM$34:$AM$43,E8582)","v":0},"09:00:00",9,6.98,21.02,26.96,33.08,21.02,30.92,19.04,30.92,27.68,33.799999999999997,33.26,null,{"$f":"SUMPRODUCT($J$2:$T$2,J8582:T8582)","v":0},null,null,{"$f":"OR(B8582<=$AO$14,B8582>=$AN$14)*(F8582<6)*(I8582>$AN$15)*(I8582<=$AO$15)*(G8582<>1)","v":1},{"$f":"OR(B8582<=$AO$14,B8582>=$AN$14)*(Y8582=0)","v":0},{"$f":"AND(B8582>=$AN$24,B8582<=$AO$24)*(F8582<6)*(I8582>$AN$25)*(I8582<=$AO$25)*(G8582<>1)","v":0},{"$f":"AND(B8582>=$AN$24,B8582<=$AO$24)*(AA8582=0)","v":0},{"$f":"OR(B8582<=$AO$19,B8582>=$AN$19)*(F8582<6)*(I8582>$AN$20)*(I8582<=$AO$20)","v":0},{"$f":"AND(B8582>=$AN$29,B8582<=$AO$29)*(F8582<6)*(I8582>$AN$30)*(I8582<=$AO$30)","v":0},{"$f":"IF(OR(E8582=$AM$34,E8582=$AM$35,E8582=$AM$36,E8582=$AM$37,E8582=$AM$38,E8582=$AM$39,E8582=$AM$40,E8582=$AM$41,E8582=$AM$42,E8582=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E8582>=$AM$47,E8582<=$AN$47),AND(E8582>=$AM$48,E8582<=$AN$48),AND(E8582>=$AM$49,E8582<=$AN$49),AND(E8582>=$AM$50,E8582<=$AN$50),AND(E8582>=$AM$51,E8582<=$AN$51)),0,1)*AE8582","v":0},{"$f":"(B8582>=5)*(B8582<=10)","v":0},{"$f":"1*OR(B8582<=4,B8582>=11)","v":1},{"$f":"LOOKUP(B8582,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE8582:AI8582)*((F8582<6)*(I8582>$AO$7)*(I8582<=$AP$7)+(F8582=6)*(I8582>$AO$8)*(I8582<=$AP$8)+(F8582>=7)*(I8582>$AO$9)*(I8582<=$AP$9))","v":0}]
["2003-12-24",12,24,2018,{"$f":"DATE(D8583,B8583,C8583)","v":"2018-12-24"},{"$f":"WEEKDAY(E8583,2)","v":1},0,"10:00:00",10,8.0599999999999987,33.08,28.94,33.979999999999997,24.98,33.979999999999997,20.299999999999997,34.700000000000003,28.759999999999998,33.979999999999997,34.880000000000003,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-24",12,24,2018,"2018-12-24",1,0,"11:00:00",{"$f":"H8584*24","v":11},12.02,36.5,30.02,33.619999999999997,33.44,37.04,21.560000000000002,39.019999999999996,29.84,36.32,37.04,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-24",12,24,2018,"2018-12-24",1,0,"12:00:00",12,14,38.299999999999997,30.92,35.42,34.700000000000003,39.92,23.54,41,30.74,37.94,37.22,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-24",12,24,2018,"2018-12-24",1,0,"13:00:00",13,15.079999999999998,42.08,32,39.019999999999996,36.86,42.08,25.52,42.980000000000004,32.54,41,39.92,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-24",12,24,2018,"2018-12-24",1,0,"14:00:00",14,15.98,42.08,32.72,38.840000000000003,37.58,42.980000000000004,28.58,44.06,33.44,42.44,41,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-24",12,24,2018,"2018-12-24",1,0,"15:00:00",15,15.98,42.980000000000004,33.44,39.92,37.94,44.06,26.6,44.06,33.799999999999997,42.8,39.92,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-24",12,24,2018,"2018-12-24",1,0,"16:00:00",16,12.920000000000002,42.08,32.18,39.019999999999996,37.58,42.980000000000004,28.04,43.52,32.9,40.64,39.74,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-24",12,24,2018,"2018-12-24",1,0,"17:00:00",17,8.0599999999999987,39.74,32.36,37.58,36.5,40.82,14,41.54,32.54,41.18,38.659999999999997,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-24",12,24,2018,"2018-12-24",1,0,"18:00:00",18,3.9200000000000017,35.78,28.04,33.979999999999997,33.08,36.68,14,35.96,29.3,37.94,35.06,null,0,null,null,1,0,0,0,1,0,1,1,0,0,1,1,0]
["2003-12-24",12,24,2018,"2018-12-24",1,0,"19:00:00",19,-0.94000000000000483,34.520000000000003,28.04,33.08,26.060000000000002,34.880000000000003,15.8,35.42,28.4,37.04,33.44,null,0,null,null,1,0,0,0,1,0,1,1,0,0,1,1,0]
["2003-12-24",12,24,2018,"2018-12-24",1,0,"20:00:00",20,-4,33.619999999999997,26.060000000000002,33.08,28.04,33.979999999999997,20.66,34.340000000000003,28.04,35.96,32.18,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-24",12,24,2018,"2018-12-24",1,0,"21:00:00",21,-2.9200000000000017,33.08,24.98,30.92,28.04,33.44,17.420000000000002,33.799999999999997,27.86,35.24,30.02,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-24",12,24,2018,"2018-12-24",1,0,"22:00:00",22,-5.0800000000000054,32.72,21.02,30.02,26.060000000000002,33.08,12.740000000000002,33.619999999999997,26.24,34.340000000000003,28.04,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-24",12,24,2018,"2018-12-24",1,0,"23:00:00",23,-5.0800000000000054,32.18,23,28.04,26.96,32.9,11.3,33.44,25.7,33.979999999999997,26.96,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-24",12,24,2018,"2018-12-24",1,0,1,24,-5.980000000000004,32.9,21.2,35.06,26.060000000000002,33.44,9.68,34.159999999999997,25.34,33.979999999999997,26.96,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"01:00:00",1,-5.0800000000000054,33.08,26.060000000000002,28.04,24.98,33.619999999999997,7.34,34.159999999999997,23.9,34.159999999999997,26.96,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"02:00:00",2,-4,33.08,26.6,30.02,26.060000000000002,33.619999999999997,7.1599999999999966,34.340000000000003,22.64,33.799999999999997,26.96,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"03:00:00",3,-2.019999999999996,33.26,26.6,32,26.96,34.159999999999997,7.6999999999999993,34.880000000000003,22.64,34.159999999999997,24.08,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"04:00:00",4,-2.019999999999996,33.08,26.6,30.02,28.04,34.159999999999997,7.34,35.06,23,33.799999999999997,24.08,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"05:00:00",5,-2.9200000000000017,32.72,32,30.92,28.04,33.979999999999997,8.4200000000000017,34.880000000000003,22.82,34.159999999999997,23,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"06:00:00",6,-4,33.799999999999997,33.799999999999997,28.04,28.94,35.24,6.259999999999998,35.96,21.92,35.6,21.92,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"07:00:00",7,-2.9200000000000017,33.799999999999997,33.799999999999997,28.04,28.94,35.96,4.6400000000000006,36.14,21.2,35.24,23,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"08:00:00",8,1.0399999999999991,34.520000000000003,35.06,28.94,32.36,35.96,3.5599999999999987,35.96,20.479999999999997,36.14,23,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"09:00:00",9,3.9200000000000017,35.06,35.6,30.92,33.44,37.04,4.4599999999999973,37.94,21.2,35.96,26.060000000000002,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"10:00:00",10,6.8000000000000007,37.76,37.4,33.619999999999997,35.06,38.840000000000003,12.02,39.200000000000003,24.62,39.200000000000003,30.92,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"11:00:00",11,8.9599999999999973,38.119999999999997,39.92,35.96,35.6,38.659999999999997,20.66,37.4,24.8,39.200000000000003,33.979999999999997,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"12:00:00",12,10.399999999999999,35.96,42.980000000000004,35.06,35.06,35.96,23.54,37.4,26.24,37.4,35.96,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"13:00:00",13,12.2,35.6,46.22,34.880000000000003,35.06,37.94,26.96,37.4,29.48,39.200000000000003,32.72,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"14:00:00",14,17.600000000000001,35.96,46.76,34.700000000000003,35.06,37.94,27.86,37.94,31.28,39.200000000000003,34.340000000000003,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"15:00:00",15,17.600000000000001,37.04,48.019999999999996,35.6,35.96,38.840000000000003,27.32,39.380000000000003,31.46,39.200000000000003,34.340000000000003,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"16:00:00",16,17.600000000000001,38.840000000000003,51.980000000000004,37.4,37.76,41,26.24,41,31.1,39.200000000000003,33.979999999999997,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"17:00:00",17,17.600000000000001,41,51.980000000000004,37.04,37.04,42.08,24.98,42.08,31.46,40.82,33.979999999999997,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"18:00:00",18,17.96,39.019999999999996,51.8,38.299999999999997,38.299999999999997,41,25.34,38.659999999999997,28.58,39.92,30.92,null,0,null,null,0,1,0,0,1,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"19:00:00",19,17.96,39.380000000000003,51.08,39.019999999999996,39.200000000000003,37.94,21.92,39.74,27.32,39.74,28.94,null,0,null,null,0,1,0,0,1,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"20:00:00",20,19.04,38.840000000000003,48.74,39.019999999999996,39.92,39.019999999999996,17.78,37.94,26.060000000000002,37.4,30.02,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"21:00:00",21,19.399999999999999,38.840000000000003,53.06,39.92,39.019999999999996,39.019999999999996,17.600000000000001,38.119999999999997,25.16,37.58,28.04,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"22:00:00",22,19.399999999999999,38.840000000000003,53.96,39.019999999999996,37.58,37.76,17.78,37.94,22.28,37.76,28.94,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,"23:00:00",23,19.399999999999999,38.659999999999997,55.040000000000006,39.019999999999996,35.96,37.4,17.96,37.58,22.82,37.4,28.04,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["2003-12-25",12,25,2018,"2018-12-25",2,1,1,24,19.399999999999999,38.299999999999997,55.040000000000006,39.019999999999996,36.68,37.4,17.96,37.76,23.36,36.14,26.96,null,0,null,null,0,1,0,0,0,0,0,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"01:00:00",1,19.399999999999999,38.840000000000003,57.92,39.019999999999996,37.4,39.019999999999996,18.14,38.480000000000004,23.36,37.58,26.96,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"02:00:00",2,19.399999999999999,39.019999999999996,57.019999999999996,38.119999999999997,37.4,39.019999999999996,20.12,39.019999999999996,23.9,37.58,28.94,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"03:00:00",3,19.399999999999999,39.019999999999996,57.92,39.019999999999996,39.019999999999996,37.94,22.28,37.94,23.9,37.94,28.94,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"04:00:00",4,19.04,37.04,59,35.6,35.06,37.04,21.02,37.04,22.1,35.78,26.96,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"05:00:00",5,19.399999999999999,37.04,59,36.32,35.78,36.86,23,37.22,19.579999999999998,36.86,26.96,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"06:00:00",6,19.939999999999998,34.880000000000003,60.980000000000004,34.340000000000003,33.08,34.340000000000003,24.259999999999998,34.520000000000003,17.600000000000001,35.24,24.98,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"07:00:00",7,21.2,35.42,60.8,35.06,33.979999999999997,34.700000000000003,24.8,34.700000000000003,15.98,36.32,24.08,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"08:00:00",8,23,35.96,60.8,35.24,33.979999999999997,35.24,25.16,35.06,15.8,36.5,24.08,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"09:00:00",9,28.04,36.14,60.980000000000004,33.979999999999997,32.54,36.14,27.68,35.96,15.98,37.04,26.060000000000002,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"10:00:00",10,26.6,37.04,60.8,32.72,33.08,39.019999999999996,27.86,39.74,20.299999999999997,39.92,30.02,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"11:00:00",11,24.8,37.04,57.2,32,32,37.94,28.04,41,25.7,38.840000000000003,30.92,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"12:00:00",12,26.060000000000002,35.24,57.019999999999996,33.08,30.92,38.840000000000003,28.58,40.28,31.64,38.659999999999997,32,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"13:00:00",13,26.060000000000002,34.700000000000003,55.94,33.979999999999997,32,38.119999999999997,28.94,39.380000000000003,34.159999999999997,38.480000000000004,33.08,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"14:00:00",14,26.060000000000002,34.520000000000003,53.96,33.979999999999997,32,37.04,31.1,37.04,35.6,38.299999999999997,33.979999999999997,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"15:00:00",15,26.6,35.06,53.06,33.08,32,37.04,28.94,37.04,35.24,37.22,33.08,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"16:00:00",16,24.08,33.08,51.08,30.02,30.02,36.14,29.3,37.22,34.700000000000003,35.06,32,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"17:00:00",17,21.02,32.36,51.980000000000004,28.04,26.96,34.700000000000003,27.68,35.6,33.08,34.700000000000003,30.02,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"18:00:00",18,14,28.04,47.120000000000005,26.96,24.98,28.94,27.5,30.92,30.02,32.36,28.04,null,0,null,null,1,0,0,0,1,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"19:00:00",19,12.02,28.04,48.92,24.98,21.92,28.94,26.060000000000002,28.04,30.02,27.86,26.96,null,0,null,null,1,0,0,0,1,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"20:00:00",20,8.0599999999999987,28.04,46.4,21.92,19.939999999999998,28.04,25.52,28.04,31.64,27.68,26.96,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"21:00:00",21,8.0599999999999987,24.08,44.06,19.939999999999998,17.059999999999999,26.96,25.16,26.96,31.1,25.34,26.96,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"22:00:00",22,6.0799999999999983,24.08,42.980000000000004,17.059999999999999,12.02,24.98,24.8,26.060000000000002,31.1,22.64,26.96,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,"23:00:00",23,6.0799999999999983,24.08,42.8,15.98,14,24.08,23,24.08,30.56,23.9,28.04,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-26",12,26,2018,"2018-12-26",3,0,1,24,8.9599999999999973,19.939999999999998,40.1,15.079999999999998,8.0599999999999987,23,26.6,19.939999999999998,30.02,20.84,28.94,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,{"$f":"$AO$4","v":2018},"2018-12-27",4,{"$f":"COUNTIF($AM$34:$AM$43,E8646)","v":0},"01:00:00",1,8.0599999999999987,17.96,35.96,12.02,10.039999999999999,21.02,24.259999999999998,19.04,29.84,20.299999999999997,28.94,null,{"$f":"SUMPRODUCT($J$2:$T$2,J8646:T8646)","v":0},null,null,{"$f":"OR(B8646<=$AO$14,B8646>=$AN$14)*(F8646<6)*(I8646>$AN$15)*(I8646<=$AO$15)*(G8646<>1)","v":0},{"$f":"OR(B8646<=$AO$14,B8646>=$AN$14)*(Y8646=0)","v":1},{"$f":"AND(B8646>=$AN$24,B8646<=$AO$24)*(F8646<6)*(I8646>$AN$25)*(I8646<=$AO$25)*(G8646<>1)","v":0},{"$f":"AND(B8646>=$AN$24,B8646<=$AO$24)*(AA8646=0)","v":0},{"$f":"OR(B8646<=$AO$19,B8646>=$AN$19)*(F8646<6)*(I8646>$AN$20)*(I8646<=$AO$20)","v":0},{"$f":"AND(B8646>=$AN$29,B8646<=$AO$29)*(F8646<6)*(I8646>$AN$30)*(I8646<=$AO$30)","v":0},{"$f":"IF(OR(E8646=$AM$34,E8646=$AM$35,E8646=$AM$36,E8646=$AM$37,E8646=$AM$38,E8646=$AM$39,E8646=$AM$40,E8646=$AM$41,E8646=$AM$42,E8646=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E8646>=$AM$47,E8646<=$AN$47),AND(E8646>=$AM$48,E8646<=$AN$48),AND(E8646>=$AM$49,E8646<=$AN$49),AND(E8646>=$AM$50,E8646<=$AN$50),AND(E8646>=$AM$51,E8646<=$AN$51)),0,1)*AE8646","v":0},{"$f":"(B8646>=5)*(B8646<=10)","v":0},{"$f":"1*OR(B8646<=4,B8646>=11)","v":1},{"$f":"LOOKUP(B8646,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE8646:AI8646)*((F8646<6)*(I8646>$AO$7)*(I8646<=$AP$7)+(F8646=6)*(I8646>$AO$8)*(I8646<=$AP$8)+(F8646>=7)*(I8646>$AO$9)*(I8646<=$AP$9))","v":0}]
["2003-12-27",12,27,2018,{"$f":"DATE(D8647,B8647,C8647)","v":"2018-12-27"},{"$f":"WEEKDAY(E8647,2)","v":4},0,"02:00:00",2,3.9200000000000017,17.96,33.44,12.02,8.9599999999999973,19.939999999999998,26.6,17.96,29.3,19.22,28.94,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,2018,"2018-12-27",4,0,"03:00:00",{"$f":"H8648*24","v":3},6.0799999999999983,15.98,33.08,10.940000000000001,6.98,19.04,28.4,15.98,29.3,18.86,28.94,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,2018,"2018-12-27",4,0,"04:00:00",4,3.9200000000000017,12.02,30.92,10.039999999999999,6.98,17.96,26.6,15.079999999999998,28.94,17.420000000000002,28.94,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,2018,"2018-12-27",4,0,"05:00:00",5,1.9400000000000013,12.02,30.2,8.9599999999999973,8.0599999999999987,17.96,28.4,14,28.759999999999998,16.88,28.94,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,2018,"2018-12-27",4,0,"06:00:00",6,1.9400000000000013,10.039999999999999,30.02,10.039999999999999,10.940000000000001,17.059999999999999,30.2,12.02,28.58,18.5,30.02,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,2018,"2018-12-27",4,0,"07:00:00",7,1.9400000000000013,10.039999999999999,28.94,8.9599999999999973,6.0799999999999983,17.059999999999999,30.2,12.920000000000002,29.12,18.5,30.02,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,2018,"2018-12-27",4,0,"08:00:00",8,3.019999999999996,10.039999999999999,28.4,10.039999999999999,6.98,17.059999999999999,30.2,12.920000000000002,29.66,19.399999999999999,30.02,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,2018,"2018-12-27",4,0,"09:00:00",9,8.9599999999999973,15.98,28.04,14,10.039999999999999,19.939999999999998,32,18.5,29.66,22.82,30.2,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,2018,"2018-12-27",4,0,"10:00:00",10,12.920000000000002,19.04,28.04,17.96,15.079999999999998,23,32,24.08,29.66,24.98,32.9,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,2018,"2018-12-27",4,0,"11:00:00",11,19.04,19.04,30.02,21.92,19.04,26.060000000000002,32,26.96,30.2,28.04,33.799999999999997,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,2018,"2018-12-27",4,0,"12:00:00",12,32.18,28.04,28.94,24.08,24.08,30.02,32,30.02,30.56,30.2,35.06,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,2018,"2018-12-27",4,0,"13:00:00",13,34.700000000000003,30.92,30.02,24.98,28.04,32,32,30.2,32.36,30.74,37.4,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,2018,"2018-12-27",4,0,"14:00:00",14,35.06,30.92,30.92,28.04,28.94,33.08,33.799999999999997,32.54,32.9,31.82,39.019999999999996,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,2018,"2018-12-27",4,0,"15:00:00",15,35.42,32,30.02,28.04,28.94,32.36,32,33.26,34.880000000000003,32,41.36,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,2018,"2018-12-27",4,0,"16:00:00",16,34.700000000000003,32,28.94,28.04,30.02,33.44,32.9,33.979999999999997,36.86,33.26,42.26,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,2018,"2018-12-27",4,0,"17:00:00",17,33.44,32,26.96,28.04,28.94,32.54,33.26,32.9,37.58,33.26,42.44,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,2018,"2018-12-27",4,0,"18:00:00",18,30.02,33.08,28.04,28.4,28.94,32.54,34.880000000000003,33.08,38.299999999999997,33.619999999999997,42.08,null,0,null,null,1,0,0,0,1,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,2018,"2018-12-27",4,0,"19:00:00",19,30.02,33.979999999999997,28.04,28.04,30.02,32,35.42,32.54,39.200000000000003,33.619999999999997,41.36,null,0,null,null,1,0,0,0,1,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,2018,"2018-12-27",4,0,"20:00:00",20,33.08,33.979999999999997,26.96,30.02,30.92,33.979999999999997,35.6,32.72,39.200000000000003,33.799999999999997,41.54,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,2018,"2018-12-27",4,0,"21:00:00",21,33.799999999999997,33.08,26.060000000000002,30.2,33.08,32.18,36.86,33.26,40.46,33.979999999999997,41,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,2018,"2018-12-27",4,0,"22:00:00",22,35.6,32.54,26.060000000000002,30.2,35.96,33.799999999999997,38.119999999999997,34.880000000000003,41.36,35.24,41.72,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,2018,"2018-12-27",4,0,"23:00:00",23,34.520000000000003,34.880000000000003,24.98,32,33.08,36.5,38.119999999999997,37.58,41.54,37.04,42.08,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-27",12,27,2018,"2018-12-27",4,0,1,24,35.96,36.5,26.060000000000002,33.799999999999997,33.979999999999997,37.04,36.86,39.200000000000003,40.64,37.4,42.980000000000004,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"01:00:00",1,38.299999999999997,39.74,26.060000000000002,36.68,36.86,39.92,33.979999999999997,42.08,38.480000000000004,41.18,39.92,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"02:00:00",2,40.46,41.72,24.08,38.299999999999997,38.480000000000004,42.980000000000004,32.54,42.8,36.86,41,39.92,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"03:00:00",3,42.8,43.879999999999995,21.92,40.28,41,46.04,15.8,46.76,36.5,45.5,38.840000000000003,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"04:00:00",4,42.8,48.019999999999996,24.08,43.7,42.08,51.08,15.8,53.06,36.14,50,38.299999999999997,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"05:00:00",5,39.200000000000003,48.019999999999996,23,44.06,44.06,51.08,15.8,53.06,36.5,51.8,38.299999999999997,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"06:00:00",6,37.4,48.92,21.02,45.68,44.78,51.980000000000004,15.8,51.980000000000004,35.06,51.8,37.4,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"07:00:00",7,39.92,48.019999999999996,19.04,45.86,45.14,51.980000000000004,15.8,51.980000000000004,34.880000000000003,52.34,37.4,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"08:00:00",8,39.200000000000003,48.019999999999996,19.939999999999998,46.58,48.019999999999996,51.980000000000004,15.8,51.980000000000004,35.06,51.8,37.04,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"09:00:00",9,37.94,48.92,28.04,44.96,48.019999999999996,51.980000000000004,14.899999999999999,51.980000000000004,35.24,52.34,36.86,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"10:00:00",10,36.86,50,30.92,46.94,48.019999999999996,51.8,32.9,53.06,36.86,51.8,40.28,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"11:00:00",11,32.54,50,32,48.92,48.019999999999996,53.96,32.54,53.6,37.58,52.519999999999996,42.08,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"12:00:00",12,35.96,51.980000000000004,33.979999999999997,48.92,46.04,53.06,33.08,55.040000000000006,39.56,52.16,44.06,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"13:00:00",13,35.96,51.980000000000004,32.54,46.94,44.96,51.980000000000004,34.159999999999997,53.06,41,51.44,44.06,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"14:00:00",14,32.18,51.980000000000004,33.619999999999997,46.04,42.980000000000004,51.08,34.520000000000003,53.06,39.380000000000003,51.980000000000004,44.96,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"15:00:00",15,30.92,46.94,34.340000000000003,44.06,42.08,50,34.880000000000003,50,39.92,51.08,44.96,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"16:00:00",16,26.96,44.96,33.979999999999997,41,39.92,46.94,33.619999999999997,46.04,39.200000000000003,46.94,42.980000000000004,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"17:00:00",17,21.92,44.96,32.36,39.92,39.92,44.06,12.2,42.980000000000004,37.76,44.24,41,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"18:00:00",18,19.399999999999999,42.08,26.96,39.019999999999996,37.22,42.08,12.2,41,34.700000000000003,42.980000000000004,39.019999999999996,null,0,null,null,1,0,0,0,1,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"19:00:00",19,17.600000000000001,41,26.96,37.94,37.04,41,12.2,41,33.979999999999997,41.9,37.04,null,0,null,null,1,0,0,0,1,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"20:00:00",20,15.8,38.840000000000003,26.060000000000002,37.04,36.68,38.840000000000003,11.659999999999997,39.92,33.08,40.64,35.96,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"21:00:00",21,14,37.76,21.92,37.04,36.32,37.58,10.940000000000001,37.94,32.18,40.1,35.96,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"22:00:00",22,12.920000000000002,36.5,23,37.04,35.42,36.5,10.399999999999999,36.86,25.7,37.94,33.26,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,"23:00:00",23,12.2,35.6,21.92,34.880000000000003,34.520000000000003,35.42,10.399999999999999,35.96,34.880000000000003,36.86,32.36,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-28",12,28,2018,"2018-12-28",5,0,1,24,12.2,35.6,23,35.06,34.340000000000003,35.42,8.5999999999999979,35.78,30.92,36.5,32,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,2018,"2018-12-29",6,0,"01:00:00",1,10.940000000000001,34.880000000000003,24.08,34.159999999999997,33.619999999999997,34.700000000000003,8.5999999999999979,35.24,33.08,35.96,32.36,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,2018,"2018-12-29",6,0,"02:00:00",2,10.399999999999999,34.520000000000003,23,33.44,33.08,34.700000000000003,8.5999999999999979,35.06,30.92,35.78,33.08,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,2018,"2018-12-29",6,0,"03:00:00",3,8.9599999999999973,34.159999999999997,23,33.26,33.26,34.159999999999997,8.5999999999999979,34.700000000000003,28.759999999999998,35.24,33.26,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,2018,"2018-12-29",6,0,"04:00:00",4,8.5999999999999979,33.44,24.8,32.36,32.54,33.619999999999997,6.8000000000000007,34.340000000000003,27.14,34.880000000000003,32,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,2018,"2018-12-29",6,0,"05:00:00",5,6.8000000000000007,33.979999999999997,30.92,32.72,32.9,33.979999999999997,7.1599999999999966,35.06,25.34,35.42,26.96,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,2018,"2018-12-29",6,0,"06:00:00",6,6.0799999999999983,33.799999999999997,32,32.36,32.18,33.979999999999997,3.9200000000000017,34.340000000000003,23.72,35.96,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,2018,"2018-12-29",6,0,"07:00:00",7,5,34.159999999999997,30.2,32.54,32.18,34.340000000000003,0.68000000000000327,34.880000000000003,22.46,35.06,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,2018,"2018-12-29",6,0,"08:00:00",8,5,34.159999999999997,33.08,32.72,32.18,34.159999999999997,-3.9999999999999147E-2,33.979999999999997,21.2,34.700000000000003,24.98,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,2018,"2018-12-29",6,0,"09:00:00",9,6.98,34.159999999999997,33.799999999999997,32.9,32.36,34.520000000000003,-3.9999999999999147E-2,34.700000000000003,21.02,35.78,30.02,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,2018,"2018-12-29",6,0,"10:00:00",10,10.039999999999999,35.06,32.9,32.9,35.06,35.96,0.68000000000000327,36.14,21.560000000000002,36.5,33.08,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,2018,"2018-12-29",6,0,"11:00:00",11,14,37.04,34.880000000000003,33.799999999999997,32.54,37.04,-0.75999999999999801,37.94,33.44,37.58,37.04,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,2018,"2018-12-29",6,0,"12:00:00",12,15.98,36.5,35.96,35.06,32.72,39.019999999999996,-1.3000000000000043,39.019999999999996,33.619999999999997,38.659999999999997,39.019999999999996,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,2018,"2018-12-29",6,0,"13:00:00",13,17.059999999999999,36.86,37.58,35.06,32.72,37.94,21.2,37.94,35.96,38.840000000000003,39.92,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,2018,"2018-12-29",6,0,"14:00:00",14,17.96,36.86,39.380000000000003,35.06,32.54,38.119999999999997,21.2,39.019999999999996,35.96,40.46,39.92,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,2018,"2018-12-29",6,0,"15:00:00",15,17.96,36.68,42.980000000000004,34.520000000000003,32.18,37.94,21.2,37.94,36.14,38.119999999999997,39.92,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,2018,"2018-12-29",6,0,"16:00:00",16,17.059999999999999,35.24,42.08,32.72,33.08,37.04,23,37.04,35.6,37.58,37.94,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,{"$f":"$AO$4","v":2018},"2018-12-29",6,{"$f":"COUNTIF($AM$34:$AM$43,E8710)","v":0},"17:00:00",17,12.920000000000002,34.340000000000003,41,32,33.08,35.96,23,35.96,33.979999999999997,36.5,35.96,null,{"$f":"SUMPRODUCT($J$2:$T$2,J8710:T8710)","v":0},null,null,{"$f":"OR(B8710<=$AO$14,B8710>=$AN$14)*(F8710<6)*(I8710>$AN$15)*(I8710<=$AO$15)*(G8710<>1)","v":0},{"$f":"OR(B8710<=$AO$14,B8710>=$AN$14)*(Y8710=0)","v":1},{"$f":"AND(B8710>=$AN$24,B8710<=$AO$24)*(F8710<6)*(I8710>$AN$25)*(I8710<=$AO$25)*(G8710<>1)","v":0},{"$f":"AND(B8710>=$AN$24,B8710<=$AO$24)*(AA8710=0)","v":0},{"$f":"OR(B8710<=$AO$19,B8710>=$AN$19)*(F8710<6)*(I8710>$AN$20)*(I8710<=$AO$20)","v":0},{"$f":"AND(B8710>=$AN$29,B8710<=$AO$29)*(F8710<6)*(I8710>$AN$30)*(I8710<=$AO$30)","v":0},{"$f":"IF(OR(E8710=$AM$34,E8710=$AM$35,E8710=$AM$36,E8710=$AM$37,E8710=$AM$38,E8710=$AM$39,E8710=$AM$40,E8710=$AM$41,E8710=$AM$42,E8710=$AM$43),0,1)","v":1},1,{"$f":"IF(OR(AND(E8710>=$AM$47,E8710<=$AN$47),AND(E8710>=$AM$48,E8710<=$AN$48),AND(E8710>=$AM$49,E8710<=$AN$49),AND(E8710>=$AM$50,E8710<=$AN$50),AND(E8710>=$AM$51,E8710<=$AN$51)),0,1)*AE8710","v":0},{"$f":"(B8710>=5)*(B8710<=10)","v":0},{"$f":"1*OR(B8710<=4,B8710>=11)","v":1},{"$f":"LOOKUP(B8710,$AM$57:$AM$68,$AN$57:$AN$68)","v":1},{"$f":"LOOKUP($AO$10,$AE$5:$AI$5,AE8710:AI8710)*((F8710<6)*(I8710>$AO$7)*(I8710<=$AP$7)+(F8710=6)*(I8710>$AO$8)*(I8710<=$AP$8)+(F8710>=7)*(I8710>$AO$9)*(I8710<=$AP$9))","v":0}]
["2003-12-29",12,29,2018,{"$f":"DATE(D8711,B8711,C8711)","v":"2018-12-29"},{"$f":"WEEKDAY(E8711,2)","v":6},0,"18:00:00",18,14,35.06,38.480000000000004,30.92,32,33.08,23,33.44,34.700000000000003,35.06,35.06,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,2018,"2018-12-29",6,0,"19:00:00",{"$f":"H8712*24","v":19},12.920000000000002,33.979999999999997,37.94,30.02,32,35.06,24.8,32.36,32,34.159999999999997,33.979999999999997,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,2018,"2018-12-29",6,0,"20:00:00",20,12.02,33.979999999999997,37.04,30.02,30.92,35.06,23,30.92,34.700000000000003,33.44,35.06,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,2018,"2018-12-29",6,0,"21:00:00",21,10.039999999999999,33.08,37.94,28.94,30.02,33.979999999999997,23,30.92,32.9,32.72,34.700000000000003,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,2018,"2018-12-29",6,0,"22:00:00",22,12.02,32,39.200000000000003,28.94,28.94,33.08,21.2,30.02,32.36,32.36,34.520000000000003,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,2018,"2018-12-29",6,0,"23:00:00",23,6.0799999999999983,32,39.019999999999996,28.94,28.94,33.08,23,30.02,32,29.66,33.799999999999997,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-29",12,29,2018,"2018-12-29",6,0,1,24,3.9200000000000017,30.92,37.94,28.04,28.94,33.08,24.8,30.02,30.92,32.18,33.619999999999997,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"01:00:00",1,3.019999999999996,30.92,35.96,28.04,28.04,32,26.6,28.94,30.2,29.12,32.9,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"02:00:00",2,3.019999999999996,30.92,35.06,28.04,28.04,30.92,26.6,28.04,30.2,27.86,32.36,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"03:00:00",3,3.019999999999996,30.02,35.06,28.04,28.04,30.02,23,28.04,30.2,27.5,32,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"04:00:00",4,1.9400000000000013,28.94,33.44,28.04,26.96,28.04,24.8,26.060000000000002,30.2,27.14,28.94,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"05:00:00",5,1.9400000000000013,28.94,32.54,26.96,28.04,28.04,26.6,24.98,29.84,26.96,28.04,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"06:00:00",6,3.019999999999996,26.96,32,24.98,30.02,28.04,30.2,24.98,29.3,28.4,28.04,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"07:00:00",7,3.019999999999996,28.04,30.92,24.8,30.02,28.04,30.2,24.98,28.94,29.84,28.04,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"08:00:00",8,3.9200000000000017,28.04,30.92,24.8,30.02,28.04,24.8,24.98,28.22,30.2,28.04,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"09:00:00",9,6.98,28.94,32,24.08,30.02,28.94,33.799999999999997,26.6,27.5,28.4,26.96,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"10:00:00",10,10.940000000000001,30.02,30.92,24.08,30.92,30.02,23,28.94,27.32,32,26.96,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"11:00:00",11,14,30.02,30.92,24.98,30.92,30.02,12.2,28.94,26.060000000000002,33.799999999999997,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"12:00:00",12,17.059999999999999,30.92,30.02,24.98,30.02,32,8.5999999999999979,30.2,25.52,34.520000000000003,24.98,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"13:00:00",13,19.939999999999998,30.02,28.94,24.8,30.02,30.92,8.5999999999999979,28.4,25.16,35.42,24.98,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"14:00:00",14,19.399999999999999,30.92,30.02,26.6,30.02,32,8.5999999999999979,32.18,25.34,35.78,24.98,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"15:00:00",15,19.399999999999999,33.08,28.04,26.6,30.02,33.08,8.5999999999999979,32.18,25.52,35.42,24.98,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"16:00:00",16,19.399999999999999,33.979999999999997,26.96,26.6,30.02,32.54,8.5999999999999979,32.54,25.7,36.14,24.98,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"17:00:00",17,19.939999999999998,33.979999999999997,26.060000000000002,26.6,30.02,33.08,8.5999999999999979,33.26,26.24,37.22,24.98,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"18:00:00",18,21.2,32.36,24.08,26.6,30.02,33.619999999999997,8.5999999999999979,33.619999999999997,25.52,38.480000000000004,24.98,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"19:00:00",19,21.2,32.72,23,26.6,30.02,33.799999999999997,8.5999999999999979,33.799999999999997,26.24,41,24.98,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"20:00:00",20,21.92,32.54,21.02,26.6,30.02,33.44,8.5999999999999979,33.619999999999997,26.24,38.299999999999997,24.98,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"21:00:00",21,21.2,32.54,17.96,26.6,28.94,33.26,8.5999999999999979,33.619999999999997,26.060000000000002,36.68,24.98,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"22:00:00",22,21.92,28.94,19.939999999999998,26.6,28.4,32.72,8.5999999999999979,33.08,26.42,35.6,24.8,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,"23:00:00",23,23,28.94,17.059999999999999,26.6,30.02,30.2,8.5999999999999979,32.18,26.6,33.08,24.98,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-30",12,30,2018,"2018-12-30",7,0,1,24,24.08,30.02,15.98,28.4,28.04,32.72,8.5999999999999979,33.26,26.6,33.44,24.98,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"01:00:00",1,24.8,32.54,14,30.92,28.04,33.799999999999997,9.5,34.340000000000003,26.6,34.520000000000003,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"02:00:00",2,24.98,32.72,14,32,32,33.799999999999997,10.399999999999999,34.159999999999997,27.5,35.06,26.060000000000002,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"03:00:00",3,24.8,32.72,12.920000000000002,32,33.08,33.799999999999997,10.399999999999999,34.159999999999997,27.5,35.42,32.54,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"04:00:00",4,26.6,32,12.920000000000002,32,33.979999999999997,33.08,12.2,33.619999999999997,28.4,34.880000000000003,34.700000000000003,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"05:00:00",5,26.96,32,14,32,33.08,32.54,12.2,33.26,28.759999999999998,34.159999999999997,35.24,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"06:00:00",6,28.04,32,12.920000000000002,32,33.08,32.72,14,33.26,29.3,33.979999999999997,34.880000000000003,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"07:00:00",7,28.94,32,14,32,32,32.36,14,32.72,30.02,33.799999999999997,34.880000000000003,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"08:00:00",8,30.02,32,15.079999999999998,32,30.92,32,14,32.36,30.2,33.44,34.700000000000003,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"09:00:00",9,30.92,30.02,17.059999999999999,33.08,33.08,32,15.8,32,31.1,33.26,34.159999999999997,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"10:00:00",10,30.2,32.18,19.939999999999998,33.979999999999997,33.979999999999997,33.26,15.8,33.44,32,33.799999999999997,34.700000000000003,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"11:00:00",11,35.06,33.44,24.08,33.979999999999997,35.06,35.06,17.600000000000001,34.880000000000003,32.9,35.06,34.340000000000003,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"12:00:00",12,35.6,33.979999999999997,26.060000000000002,32.18,35.96,35.42,19.399999999999999,35.6,34.159999999999997,35.96,33.979999999999997,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"13:00:00",13,35.6,33.979999999999997,28.04,32.18,35.06,35.96,19.399999999999999,36.32,32.54,36.68,33.44,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"14:00:00",14,35.6,33.799999999999997,32,32,35.06,35.96,21.2,35.6,32.54,36.32,33.44,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"15:00:00",15,35.96,33.799999999999997,33.08,33.979999999999997,33.08,35.06,21.2,35.06,32.18,36.32,33.08,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"16:00:00",16,35.6,32.36,32.18,32,30.92,33.979999999999997,21.2,34.700000000000003,32.18,35.06,33.08,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"17:00:00",17,33.799999999999997,35.06,33.08,30.92,30.92,33.08,19.399999999999999,33.44,32.9,35.24,33.799999999999997,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"18:00:00",18,32.18,33.08,33.08,30.02,30.02,32,17.600000000000001,30.92,32.72,33.44,33.979999999999997,null,0,null,null,1,0,0,0,1,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"19:00:00",19,32.72,33.08,33.979999999999997,28.04,28.04,30.02,7.6999999999999993,30.02,32.9,32.54,32.72,null,0,null,null,1,0,0,0,1,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"20:00:00",20,32.54,33.08,35.06,28.04,28.04,30.02,15.8,28.94,32.54,31.28,33.08,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"21:00:00",21,32,28.94,35.06,26.060000000000002,26.060000000000002,28.94,14,28.04,32.36,30.74,33.619999999999997,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"22:00:00",22,32,28.04,32.54,24.98,24.98,28.04,14,26.96,32.36,29.48,33.08,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,"23:00:00",23,35.6,28.04,33.619999999999997,24.08,24.08,28.04,14,24.98,32,27.68,32.72,null,0,null,null,1,0,0,0,0,0,1,1,0,0,1,1,0]
["2003-12-31",12,31,2018,"2018-12-31",1,0,1,24,37.4,26.060000000000002,33.44,21.92,23,26.060000000000002,14,24.98,32,26.96,32,null,0,null,null,0,1,0,0,0,0,1,1,0,0,1,1,0]

{"sheet":"ECMs","index":3,"n_rows":27,"n_cols":27,"rows_kept":27,"cut":false,"hidden":true,"merged":[[3,8,3,10],[1,17,9,24],[17,17,24,24],[17,26,24,33],[27,17,34,24],[27,26,34,33]]}
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"General Instructions for Use of Mass Save Small Buildings Calculation Tool"]
[]
[]
[null,null,null,null,null,null,null,null,"<<< Click here to begin"]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Cell Color Descriptions"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Protected cell with formula or generic input; these cells cannot be changed"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"User Input Cell; these cells require an input by the user and are refernced in calculations"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Highlights tables where User Inputs will be required"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Workspace Tab",null,null,null,null,null,null,null,null,"Project Info Tab"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"ECM Summary Tab",null,null,null,null,null,null,null,null,"Individual ECM Calculation Tabs"]

{"sheet":"Project Info","index":4,"n_rows":143,"n_cols":28,"rows_kept":143,"cut":false,"hidden":false,"merged":[[26,2,26,4],[27,2,27,4],[28,2,28,4],[29,2,29,4],[30,2,30,4],[8,5,8,7],[8,8,8,10],[22,2,22,4],[20,2,20,4],[6,5,6,7],[6,8,6,10],[7,5,7,7],[7,8,7,10],[17,8,17,9],[18,8,18,9],[21,2,21,4],[4,2,4,4],[5,2,5,4],[2,5,2,7],[2,8,2,10],[3,5,3,7],[4,5,4,7],[5,5,5,7],[3,8,3,10],[4,8,4,10],[5,8,5,10],[1,16,29,24],[4,14,5,14],[2,2,2,4],[17,2,17,4],[19,2,19,4],[3,2,3,4],[18,2,18,4],[7,2,7,4],[14,2,14,4],[15,2,15,4],[16,2,16,4],[11,2,11,4],[12,2,12,4],[6,2,6,4],[8,2,8,4],[13,2,13,3]]}
["Contact Information",null,null,null,null,null,null,null,null,null,null,null,"Tool Version:",null,{"$f":"Instructions!T9","v":"v2026.02.19"},null,"Facility Description"]
[null,null,"Customer",null,null,"Electric PA",null,null,"Gas PA"]
["Company"]
["Contact Name"]
["Contact Email",null,null,null,null,null,null,null,null,null,null,null,"All Required Project",null,{"$f":"IF(OR(ISBLANK(F3),ISBLANK(I3),ISBLANK(C15),ISBLANK(C16),ISBLANK(C17),ISBLANK(C18),ISBLANK(C19),ISBLANK(C20),ISBLANK(C21),ISBLANK(C22),ISBLANK(C23),ISBLANK(I15),ISBLANK(J15),ISBLANK(I16),ISBLANK(J16),ISBLANK(I17),ISBLANK(J17),ISBLANK(I18),ISBLANK(I19)),\"NO\",\"Yes\")","v":"NO"}]
["Contact Phone",null,null,null,null,null,null,null,null,null,null,null,"Info Inputs Complete?"]
["Account #(s)",null,null,null,null,null,null,null,null,null,null,null,"*All required inputs must be complete"]
["Application #",null,null,null,null,null,null,null,null,null,null,null,"for the tool to calculate as intended."]
["TA Vendor"]
[]
["Project Information",null,null,null,null,null,"General Building Hours of Operation",null,null,null,null,"Monthly/Seasonal",null,"Must enter a value for each"]
["Project Name",null,null,null,null,null,"(Times must be entered in 0 - 24 hr format)",null,null,null,null," Bldg Hours Diversity",null,"month (0 - 100%). If left blank,"]
["Street Address",null,null,null,null,null,null,null,null,null,null,"(if variable)",null,"default of 100% is assumed."]
["City","Zip Code",null,null,null,null,null,null,"Start","End",null,"Month","Usage Div.","Default"]
["State",null,"NH",null,null,null,"Weekdays",null,null,null,null,"Jan",null,1,"<<"]
["Weather Data Location (TMYx)",null,null,null,null,null,"Saturday",null,null,null,null,"Feb",null,1,"<<"]
["Building Area, ft² (excluding parking garage)",null,null,null,null,null,"Sunday",null,null,null,null,"Mar",null,1,"<<"]
["Building Type",null,null,null,null,null,"Holiday Closures?",null,"1-Standard US Holidays",null,null,"Apr",null,1,"<<"]
["Program Year",null,null,null,null,null,"Seasonal Bldg Hours?",null,"Constant Year-Round",null,null,"May",null,1,"<<"]
["Permitting Code",null,"2018 IECC / ASHRAE 90.1-2016",null,null,null,"If building is not used, enter \"0\" for Start and End",null,null,null,null,"Jun",null,1,"<<"]
["Fossil Fuel Type",null,null,null,null,null,"Entered Annual Operating Hours",null,null,{"$f":"SUM(F44:F67)","v":0},null,"Jul",null,1,"<<"]
["Number of Building Floors",null,null,null,null,null,null,null,null,null,null,"Aug",null,1,"<<"]
["Program Path ",null,null,null,null,null,null,null,null,null,null,"Sep",null,1,"<<"]
[null,null,null,null,null,null,null,null,null,null,null,"Oct",null,1,"<<"]
["Project Design and Construction Schedule",null,null,null,null,null,null,null,null,null,null,"Nov",null,1,"<<"]
["Phase",null,"Estimated Completion Date",null,null,null,null,null,null,null,null,"Dec",null,1,"<<"]
["Schematic Design (SD)"]
["Design Development (DD)"]
["Construction Documents (CD)"]
["Construction Start"]
["Construction Completion"]
[]
[]
[]
[]
[]
[]
[]
[]
["Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
["OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer"]
["Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand"]
["From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours"]
[100,105,{"$f":"TMYx!BZ15","v":102},{"$f":"TMYx!CA15","v":76},{"$f":"TMYx!CB15","v":40},{"$f":"TMYx!AT15","v":0},{"$f":"TMYx!AU15","v":0},{"$f":"TMYx!AV15","v":0},{"$f":"TMYx!AW15","v":0},{"$f":"TMYx!AX15","v":0},{"$f":"TMYx!AY15","v":0},{"$f":"TMYx!AZ15","v":0}]
[95,100,{"$f":"TMYx!BZ16","v":95.219272727272724},{"$f":"TMYx!CA16","v":74.534025272781079},{"$f":"TMYx!CB16","v":37.923296058061368},{"$f":"TMYx!AT16","v":0},{"$f":"TMYx!AU16","v":0},{"$f":"TMYx!AV16","v":0},{"$f":"TMYx!AW16","v":0},{"$f":"TMYx!AX16","v":0},{"$f":"TMYx!AY16","v":0},{"$f":"TMYx!AZ16","v":0}]
[90,95,{"$f":"TMYx!BZ17","v":92.016049160256074},{"$f":"TMYx!CA17","v":72.911561930607689},{"$f":"TMYx!CB17","v":36.467095439351091},{"$f":"TMYx!AT17","v":0},{"$f":"TMYx!AU17","v":0},{"$f":"TMYx!AV17","v":0},{"$f":"TMYx!AW17","v":0},{"$f":"TMYx!AX17","v":0},{"$f":"TMYx!AY17","v":0},{"$f":"TMYx!AZ17","v":0}]
[85,90,{"$f":"TMYx!BZ18","v":87.457811360655285},{"$f":"TMYx!CA18","v":70.80538329449476},{"$f":"TMYx!CB18","v":34.679413213566804},{"$f":"TMYx!AT18","v":0},{"$f":"TMYx!AU18","v":0},{"$f":"TMYx!AV18","v":0},{"$f":"TMYx!AW18","v":0},{"$f":"TMYx!AX18","v":0},{"$f":"TMYx!AY18","v":0},{"$f":"TMYx!AZ18","v":0}]
[80,85,{"$f":"TMYx!BZ19","v":82.136788830239965},{"$f":"TMYx!CA19","v":67.872393622439333},{"$f":"TMYx!CB19","v":32.296248223809314},{"$f":"TMYx!AT19","v":0},{"$f":"TMYx!AU19","v":0},{"$f":"TMYx!AV19","v":0},{"$f":"TMYx!AW19","v":0},{"$f":"TMYx!AX19","v":0},{"$f":"TMYx!AY19","v":0},{"$f":"TMYx!AZ19","v":0}]
[75,80,{"$f":"TMYx!BZ20","v":76.988400157585886},{"$f":"TMYx!CA20","v":65.129261896908645},{"$f":"TMYx!CB20","v":30.190476812806729},{"$f":"TMYx!AT20","v":0},{"$f":"TMYx!AU20","v":0},{"$f":"TMYx!AV20","v":0},{"$f":"TMYx!AW20","v":0},{"$f":"TMYx!AX20","v":0},{"$f":"TMYx!AY20","v":0},{"$f":"TMYx!AZ20","v":0}]
[70,75,{"$f":"TMYx!BZ21","v":72.457982050814195},{"$f":"TMYx!CA21","v":63.604425012889301},{"$f":"TMYx!CB21","v":29.088683095945193},{"$f":"TMYx!AT21","v":0},{"$f":"TMYx!AU21","v":0},{"$f":"TMYx!AV21","v":0},{"$f":"TMYx!AW21","v":0},{"$f":"TMYx!AX21","v":0},{"$f":"TMYx!AY21","v":0},{"$f":"TMYx!AZ21","v":0}]
[65,70,{"$f":"TMYx!BZ22","v":67.815831070966169},{"$f":"TMYx!CA22","v":61.631331368130574},{"$f":"TMYx!CB22","v":27.661514889731574},{"$f":"TMYx!AT22","v":0},{"$f":"TMYx!AU22","v":0},{"$f":"TMYx!AV22","v":0},{"$f":"TMYx!AW22","v":0},{"$f":"TMYx!AX22","v":0},{"$f":"TMYx!AY22","v":0},{"$f":"TMYx!AZ22","v":0}]
[60,65,{"$f":"TMYx!BZ23","v":62.535961472271332},{"$f":"TMYx!CA23","v":57.135476922863582},{"$f":"TMYx!CB23","v":24.623037157728302},{"$f":"TMYx!AT23","v":0},{"$f":"TMYx!AU23","v":0},{"$f":"TMYx!AV23","v":0},{"$f":"TMYx!AW23","v":0},{"$f":"TMYx!AX23","v":0},{"$f":"TMYx!AY23","v":0},{"$f":"TMYx!AZ23","v":0}]
[55,60,{"$f":"TMYx!BZ24","v":57.125792270740902},{"$f":"TMYx!CA24","v":52.596971157053673},{"$f":"TMYx!CB24","v":21.818001539159841},{"$f":"TMYx!AT24","v":0},{"$f":"TMYx!AU24","v":0},{"$f":"TMYx!AV24","v":0},{"$f":"TMYx!AW24","v":0},{"$f":"TMYx!AX24","v":0},{"$f":"TMYx!AY24","v":0},{"$f":"TMYx!AZ24","v":0}]
[50,55,{"$f":"TMYx!BZ25","v":52.235698854337961},{"$f":"TMYx!CA25","v":48.022768090099298},{"$f":"TMYx!CB25","v":19.246640192796217},{"$f":"TMYx!AT25","v":0},{"$f":"TMYx!AU25","v":0},{"$f":"TMYx!AV25","v":0},{"$f":"TMYx!AW25","v":0},{"$f":"TMYx!AX25","v":0},{"$f":"TMYx!AY25","v":0},{"$f":"TMYx!AZ25","v":0}]
[45,50,{"$f":"TMYx!BZ26","v":47.459170258371508},{"$f":"TMYx!CA26","v":43.465397050422162},{"$f":"TMYx!CB26","v":16.894183241713304},{"$f":"TMYx!AT26","v":0},{"$f":"TMYx!AU26","v":0},{"$f":"TMYx!AV26","v":0},{"$f":"TMYx!AW26","v":0},{"$f":"TMYx!AX26","v":0},{"$f":"TMYx!AY26","v":0},{"$f":"TMYx!AZ26","v":0}]
[40,45,{"$f":"TMYx!BZ27","v":42.677030404888129},{"$f":"TMYx!CA27","v":38.812544504634097},{"$f":"TMYx!CB27","v":14.690265649465921},{"$f":"TMYx!AT27","v":0},{"$f":"TMYx!AU27","v":0},{"$f":"TMYx!AV27","v":0},{"$f":"TMYx!AW27","v":0},{"$f":"TMYx!AX27","v":0},{"$f":"TMYx!AY27","v":0},{"$f":"TMYx!AZ27","v":0}]
[35,40,{"$f":"TMYx!BZ28","v":37.333046773755832},{"$f":"TMYx!CA28","v":33.904706919479686},{"$f":"TMYx!CB28","v":12.53841602318813},{"$f":"TMYx!AT28","v":0},{"$f":"TMYx!AU28","v":0},{"$f":"TMYx!AV28","v":0},{"$f":"TMYx!AW28","v":0},{"$f":"TMYx!AX28","v":0},{"$f":"TMYx!AY28","v":0},{"$f":"TMYx!AZ28","v":0}]
[30,35,{"$f":"TMYx!BZ29","v":32.638179845662044},{"$f":"TMYx!CA29","v":29.547170928664851},{"$f":"TMYx!CB29","v":10.728972818165861},{"$f":"TMYx!AT29","v":0},{"$f":"TMYx!AU29","v":0},{"$f":"TMYx!AV29","v":0},{"$f":"TMYx!AW29","v":0},{"$f":"TMYx!AX29","v":0},{"$f":"TMYx!AY29","v":0},{"$f":"TMYx!AZ29","v":0}]
[25,30,{"$f":"TMYx!BZ30","v":27.529264646850947},{"$f":"TMYx!CA30","v":24.652717392657845},{"$f":"TMYx!CB30","v":8.8041305482613303},{"$f":"TMYx!AT30","v":0},{"$f":"TMYx!AU30","v":0},{"$f":"TMYx!AV30","v":0},{"$f":"TMYx!AW30","v":0},{"$f":"TMYx!AX30","v":0},{"$f":"TMYx!AY30","v":0},{"$f":"TMYx!AZ30","v":0}]
[20,25,{"$f":"TMYx!BZ31","v":22.998111483544687},{"$f":"TMYx!CA31","v":20.383306659827422},{"$f":"TMYx!CB31","v":7.246164547543378},{"$f":"TMYx!AT31","v":0},{"$f":"TMYx!AU31","v":0},{"$f":"TMYx!AV31","v":0},{"$f":"TMYx!AW31","v":0},{"$f":"TMYx!AX31","v":0},{"$f":"TMYx!AY31","v":0},{"$f":"TMYx!AZ31","v":0}]
[15,20,{"$f":"TMYx!BZ32","v":17.808510327474309},{"$f":"TMYx!CA32","v":15.420865796304254},{"$f":"TMYx!CB32","v":5.5490484131518292},{"$f":"TMYx!AT32","v":0},{"$f":"TMYx!AU32","v":0},{"$f":"TMYx!AV32","v":0},{"$f":"TMYx!AW32","v":0},{"$f":"TMYx!AX32","v":0},{"$f":"TMYx!AY32","v":0},{"$f":"TMYx!AZ32","v":0}]
[10,15,{"$f":"TMYx!BZ33","v":12.269931130346862},{"$f":"TMYx!CA33","v":10.318264913023604},{"$f":"TMYx!CB33","v":3.9082824916941998},{"$f":"TMYx!AT33","v":0},{"$f":"TMYx!AU33","v":0},{"$f":"TMYx!AV33","v":0},{"$f":"TMYx!AW33","v":0},{"$f":"TMYx!AX33","v":0},{"$f":"TMYx!AY33","v":0},{"$f":"TMYx!AZ33","v":0}]
[5,10,{"$f":"TMYx!BZ34","v":7.3137581369917548},{"$f":"TMYx!CA34","v":5.7052382449247707},{"$f":"TMYx!CB34","v":2.5019418419888937},{"$f":"TMYx!AT34","v":0},{"$f":"TMYx!AU34","v":0},{"$f":"TMYx!AV34","v":0},{"$f":"TMYx!AW34","v":0},{"$f":"TMYx!AX34","v":0},{"$f":"TMYx!AY34","v":0},{"$f":"TMYx!AZ34","v":0}]
[0,5,{"$f":"TMYx!BZ35","v":2.6119461836144886},{"$f":"TMYx!CA35","v":1.2699770062067783},{"$f":"TMYx!CB35","v":1.2046477897733283},{"$f":"TMYx!AT35","v":0},{"$f":"TMYx!AU35","v":0},{"$f":"TMYx!AV35","v":0},{"$f":"TMYx!AW35","v":0},{"$f":"TMYx!AX35","v":0},{"$f":"TMYx!AY35","v":0},{"$f":"TMYx!AZ35","v":0}]
[-5,0,{"$f":"TMYx!BZ36","v":-1.6731398516793925},{"$f":"TMYx!CA36","v":-2.7083318773557807},{"$f":"TMYx!CB36","v":7.9391832815876459E-2},{"$f":"TMYx!AT36","v":0},{"$f":"TMYx!AU36","v":0},{"$f":"TMYx!AV36","v":0},{"$f":"TMYx!AW36","v":0},{"$f":"TMYx!AX36","v":0},{"$f":"TMYx!AY36","v":0},{"$f":"TMYx!AZ36","v":0}]
[-10,-5,{"$f":"TMYx!BZ37","v":-6.5729865085377277},{"$f":"TMYx!CA37","v":-7.2465935998252222},{"$f":"TMYx!CB37","v":-1.168423365310433},{"$f":"TMYx!AT37","v":0},{"$f":"TMYx!AU37","v":0},{"$f":"TMYx!AV37","v":0},{"$f":"TMYx!AW37","v":0},{"$f":"TMYx!AX37","v":0},{"$f":"TMYx!AY37","v":0},{"$f":"TMYx!AZ37","v":0}]
[-15,-10,{"$f":"TMYx!BZ38","v":-15.32570353422995},{"$f":"TMYx!CA38","v":-15.707838211108999},{"$f":"TMYx!CB38","v":-3.4051318156661381},{"$f":"TMYx!AT38","v":0},{"$f":"TMYx!AU38","v":0},{"$f":"TMYx!AV38","v":0},{"$f":"TMYx!AW38","v":0},{"$f":"TMYx!AX38","v":0},{"$f":"TMYx!AY38","v":0},{"$f":"TMYx!AZ38","v":0}]
[]
[]
["Unoccupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
["OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer"]
["Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand"]
["From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours"]
[100,105,{"$f":"TMYx!BZ15","v":102},{"$f":"TMYx!CA15","v":76},{"$f":"TMYx!CB15","v":40},{"$f":"TMYx!BD15","v":0},{"$f":"TMYx!BE15","v":0},{"$f":"TMYx!BF15","v":0},{"$f":"TMYx!BG15","v":0},{"$f":"TMYx!BH15","v":0},{"$f":"TMYx!BI15","v":0},{"$f":"TMYx!BJ15","v":0}]
[95,100,{"$f":"TMYx!BZ16","v":95.219272727272724},{"$f":"TMYx!CA16","v":74.534025272781079},{"$f":"TMYx!CB16","v":37.923296058061368},{"$f":"TMYx!BD16","v":0},{"$f":"TMYx!BE16","v":0},{"$f":"TMYx!BF16","v":0},{"$f":"TMYx!BG16","v":0},{"$f":"TMYx!BH16","v":0},{"$f":"TMYx!BI16","v":0},{"$f":"TMYx!BJ16","v":0}]
[90,95,{"$f":"TMYx!BZ17","v":92.016049160256074},{"$f":"TMYx!CA17","v":72.911561930607689},{"$f":"TMYx!CB17","v":36.467095439351091},{"$f":"TMYx!BD17","v":0},{"$f":"TMYx!BE17","v":0},{"$f":"TMYx!BF17","v":0},{"$f":"TMYx!BG17","v":0},{"$f":"TMYx!BH17","v":0},{"$f":"TMYx!BI17","v":0},{"$f":"TMYx!BJ17","v":0}]
[85,90,{"$f":"TMYx!BZ18","v":87.457811360655285},{"$f":"TMYx!CA18","v":70.80538329449476},{"$f":"TMYx!CB18","v":34.679413213566804},{"$f":"TMYx!BD18","v":0},{"$f":"TMYx!BE18","v":0},{"$f":"TMYx!BF18","v":0},{"$f":"TMYx!BG18","v":0},{"$f":"TMYx!BH18","v":0},{"$f":"TMYx!BI18","v":0},{"$f":"TMYx!BJ18","v":0}]
[80,85,{"$f":"TMYx!BZ19","v":82.136788830239965},{"$f":"TMYx!CA19","v":67.872393622439333},{"$f":"TMYx!CB19","v":32.296248223809314},{"$f":"TMYx!BD19","v":0},{"$f":"TMYx!BE19","v":0},{"$f":"TMYx!BF19","v":0},{"$f":"TMYx!BG19","v":0},{"$f":"TMYx!BH19","v":0},{"$f":"TMYx!BI19","v":0},{"$f":"TMYx!BJ19","v":0}]
[75,80,{"$f":"TMYx!BZ20","v":76.988400157585886},{"$f":"TMYx!CA20","v":65.129261896908645},{"$f":"TMYx!CB20","v":30.190476812806729},{"$f":"TMYx!BD20","v":0},{"$f":"TMYx!BE20","v":0},{"$f":"TMYx!BF20","v":0},{"$f":"TMYx!BG20","v":0},{"$f":"TMYx!BH20","v":0},{"$f":"TMYx!BI20","v":0},{"$f":"TMYx!BJ20","v":0}]
[70,75,{"$f":"TMYx!BZ21","v":72.457982050814195},{"$f":"TMYx!CA21","v":63.604425012889301},{"$f":"TMYx!CB21","v":29.088683095945193},{"$f":"TMYx!BD21","v":0},{"$f":"TMYx!BE21","v":0},{"$f":"TMYx!BF21","v":0},{"$f":"TMYx!BG21","v":0},{"$f":"TMYx!BH21","v":0},{"$f":"TMYx!BI21","v":0},{"$f":"TMYx!BJ21","v":0}]
[65,70,{"$f":"TMYx!BZ22","v":67.815831070966169},{"$f":"TMYx!CA22","v":61.631331368130574},{"$f":"TMYx!CB22","v":27.661514889731574},{"$f":"TMYx!BD22","v":0},{"$f":"TMYx!BE22","v":0},{"$f":"TMYx!BF22","v":0},{"$f":"TMYx!BG22","v":0},{"$f":"TMYx!BH22","v":0},{"$f":"TMYx!BI22","v":0},{"$f":"TMYx!BJ22","v":0}]
[60,65,{"$f":"TMYx!BZ23","v":62.535961472271332},{"$f":"TMYx!CA23","v":57.135476922863582},{"$f":"TMYx!CB23","v":24.623037157728302},{"$f":"TMYx!BD23","v":0},{"$f":"TMYx!BE23","v":0},{"$f":"TMYx!BF23","v":0},{"$f":"TMYx!BG23","v":0},{"$f":"TMYx!BH23","v":0},{"$f":"TMYx!BI23","v":0},{"$f":"TMYx!BJ23","v":0}]
[55,60,{"$f":"TMYx!BZ24","v":57.125792270740902},{"$f":"TMYx!CA24","v":52.596971157053673},{"$f":"TMYx!CB24","v":21.818001539159841},{"$f":"TMYx!BD24","v":0},{"$f":"TMYx!BE24","v":0},{"$f":"TMYx!BF24","v":0},{"$f":"TMYx!BG24","v":0},{"$f":"TMYx!BH24","v":0},{"$f":"TMYx!BI24","v":0},{"$f":"TMYx!BJ24","v":0}]
[50,55,{"$f":"TMYx!BZ25","v":52.235698854337961},{"$f":"TMYx!CA25","v":48.022768090099298},{"$f":"TMYx!CB25","v":19.246640192796217},{"$f":"TMYx!BD25","v":0},{"$f":"TMYx!BE25","v":0},{"$f":"TMYx!BF25","v":0},{"$f":"TMYx!BG25","v":0},{"$f":"TMYx!BH25","v":0},{"$f":"TMYx!BI25","v":0},{"$f":"TMYx!BJ25","v":0}]
[45,50,{"$f":"TMYx!BZ26","v":47.459170258371508},{"$f":"TMYx!CA26","v":43.465397050422162},{"$f":"TMYx!CB26","v":16.894183241713304},{"$f":"TMYx!BD26","v":0},{"$f":"TMYx!BE26","v":0},{"$f":"TMYx!BF26","v":0},{"$f":"TMYx!BG26","v":0},{"$f":"TMYx!BH26","v":0},{"$f":"TMYx!BI26","v":0},{"$f":"TMYx!BJ26","v":0}]
[40,45,{"$f":"TMYx!BZ27","v":42.677030404888129},{"$f":"TMYx!CA27","v":38.812544504634097},{"$f":"TMYx!CB27","v":14.690265649465921},{"$f":"TMYx!BD27","v":0},{"$f":"TMYx!BE27","v":0},{"$f":"TMYx!BF27","v":0},{"$f":"TMYx!BG27","v":0},{"$f":"TMYx!BH27","v":0},{"$f":"TMYx!BI27","v":0},{"$f":"TMYx!BJ27","v":0}]
[35,40,{"$f":"TMYx!BZ28","v":37.333046773755832},{"$f":"TMYx!CA28","v":33.904706919479686},{"$f":"TMYx!CB28","v":12.53841602318813},{"$f":"TMYx!BD28","v":0},{"$f":"TMYx!BE28","v":0},{"$f":"TMYx!BF28","v":0},{"$f":"TMYx!BG28","v":0},{"$f":"TMYx!BH28","v":0},{"$f":"TMYx!BI28","v":0},{"$f":"TMYx!BJ28","v":0}]
[30,35,{"$f":"TMYx!BZ29","v":32.638179845662044},{"$f":"TMYx!CA29","v":29.547170928664851},{"$f":"TMYx!CB29","v":10.728972818165861},{"$f":"TMYx!BD29","v":0},{"$f":"TMYx!BE29","v":0},{"$f":"TMYx!BF29","v":0},{"$f":"TMYx!BG29","v":0},{"$f":"TMYx!BH29","v":0},{"$f":"TMYx!BI29","v":0},{"$f":"TMYx!BJ29","v":0}]
[25,30,{"$f":"TMYx!BZ30","v":27.529264646850947},{"$f":"TMYx!CA30","v":24.652717392657845},{"$f":"TMYx!CB30","v":8.8041305482613303},{"$f":"TMYx!BD30","v":0},{"$f":"TMYx!BE30","v":0},{"$f":"TMYx!BF30","v":0},{"$f":"TMYx!BG30","v":0},{"$f":"TMYx!BH30","v":0},{"$f":"TMYx!BI30","v":0},{"$f":"TMYx!BJ30","v":0}]
[20,25,{"$f":"TMYx!BZ31","v":22.998111483544687},{"$f":"TMYx!CA31","v":20.383306659827422},{"$f":"TMYx!CB31","v":7.246164547543378},{"$f":"TMYx!BD31","v":0},{"$f":"TMYx!BE31","v":0},{"$f":"TMYx!BF31","v":0},{"$f":"TMYx!BG31","v":0},{"$f":"TMYx!BH31","v":0},{"$f":"TMYx!BI31","v":0},{"$f":"TMYx!BJ31","v":0}]
[15,20,{"$f":"TMYx!BZ32","v":17.808510327474309},{"$f":"TMYx!CA32","v":15.420865796304254},{"$f":"TMYx!CB32","v":5.5490484131518292},{"$f":"TMYx!BD32","v":0},{"$f":"TMYx!BE32","v":0},{"$f":"TMYx!BF32","v":0},{"$f":"TMYx!BG32","v":0},{"$f":"TMYx!BH32","v":0},{"$f":"TMYx!BI32","v":0},{"$f":"TMYx!BJ32","v":0}]
[10,15,{"$f":"TMYx!BZ33","v":12.269931130346862},{"$f":"TMYx!CA33","v":10.318264913023604},{"$f":"TMYx!CB33","v":3.9082824916941998},{"$f":"TMYx!BD33","v":0},{"$f":"TMYx!BE33","v":0},{"$f":"TMYx!BF33","v":0},{"$f":"TMYx!BG33","v":0},{"$f":"TMYx!BH33","v":0},{"$f":"TMYx!BI33","v":0},{"$f":"TMYx!BJ33","v":0}]
[5,10,{"$f":"TMYx!BZ34","v":7.3137581369917548},{"$f":"TMYx!CA34","v":5.7052382449247707},{"$f":"TMYx!CB34","v":2.5019418419888937},{"$f":"TMYx!BD34","v":0},{"$f":"TMYx!BE34","v":0},{"$f":"TMYx!BF34","v":0},{"$f":"TMYx!BG34","v":0},{"$f":"TMYx!BH34","v":0},{"$f":"TMYx!BI34","v":0},{"$f":"TMYx!BJ34","v":0}]
[0,5,{"$f":"TMYx!BZ35","v":2.6119461836144886},{"$f":"TMYx!CA35","v":1.2699770062067783},{"$f":"TMYx!CB35","v":1.2046477897733283},{"$f":"TMYx!BD35","v":8760},{"$f":"TMYx!BE35","v":2672},{"$f":"TMYx!BF35","v":3160},{"$f":"TMYx!BG35","v":1344},{"$f":"TMYx!BH35","v":1584},{"$f":"TMYx!BI35","v":88},{"$f":"TMYx!BJ35","v":264}]
[-5,0,{"$f":"TMYx!BZ36","v":-1.6731398516793925},{"$f":"TMYx!CA36","v":-2.7083318773557807},{"$f":"TMYx!CB36","v":7.9391832815876459E-2},{"$f":"TMYx!BD36","v":0},{"$f":"TMYx!BE36","v":0},{"$f":"TMYx!BF36","v":0},{"$f":"TMYx!BG36","v":0},{"$f":"TMYx!BH36","v":0},{"$f":"TMYx!BI36","v":0},{"$f":"TMYx!BJ36","v":0}]
[-10,-5,{"$f":"TMYx!BZ37","v":-6.5729865085377277},{"$f":"TMYx!CA37","v":-7.2465935998252222},{"$f":"TMYx!CB37","v":-1.168423365310433},{"$f":"TMYx!BD37","v":0},{"$f":"TMYx!BE37","v":0},{"$f":"TMYx!BF37","v":0},{"$f":"TMYx!BG37","v":0},{"$f":"TMYx!BH37","v":0},{"$f":"TMYx!BI37","v":0},{"$f":"TMYx!BJ37","v":0}]
[-15,-10,{"$f":"TMYx!BZ38","v":-15.32570353422995},{"$f":"TMYx!CA38","v":-15.707838211108999},{"$f":"TMYx!CB38","v":-3.4051318156661381},{"$f":"TMYx!BD38","v":0},{"$f":"TMYx!BE38","v":0},{"$f":"TMYx!BF38","v":0},{"$f":"TMYx!BG38","v":0},{"$f":"TMYx!BH38","v":0},{"$f":"TMYx!BI38","v":0},{"$f":"TMYx!BJ38","v":0}]
[]
["Bldg","Bldg",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Monthly"]
["Start","End","Bldg",null,"Bldg",null,null,null,null,null,null,null,null,null,null,null,null,null,"Monthly/Seasonal",null,"Hours",null,"Program","Fossil Fuel",null,"Fuel","Fuel","Program"]
["Hours","Hours","Location",null,"Type",null,"Electric PA List",null,null,"Gas PA List",null,null,"Permitting Codes",null,null,"Holiday Closures",null,null,"Bldg Hours",null,"Diversity","State","Year","Types",null,"Conversion","Unit","Path"]
[0,24,"Berlin",null,"Automotive facility",null,"Eversource",null,null,"Eversource Gas",null,null,"2015 IECC / ASHRAE 90.1-2013",null,null,"1-Standard US Holidays",null,null,"Constant Year-Round",null,1,"MA",2025,"Natural Gas",null,10,"therms","High Performance Buildings"]
[1,23,"Concord",null,"Convention center",null,"Unitil Electric",null,null,"Unitil Gas",null,null,"2018 IECC / ASHRAE 90.1-2016",null,null,"2-No Holidays",null,null,"Vary by Month/Season",null,0.9,"RI",2026,"Oil",null,1,"MMBtu","Systems Pathway"]
[2,22,"Keene",null,"Courthouse",null,"Liberty Electric - NH",null,null,"Liberty Gas",null,null,null,null,null,null,null,null,null,null,0.8,"NH",2027,"Propane",null,1,"MMBtu","Other/NA"]
[3,21,"Laconia",null,"Daycare",null,"NH Electric Co-Op",null,null,"None/Other",null,null,null,null,null,null,null,null,null,null,0.7,null,null,"None/All-Electric",null,"NA","NA"]
[4,20,"Lebanon",null,"Dining: bar/lounge/leisure",null,"None/Default/Muni",null,null,null,null,null,null,null,null,null,null,null,null,null,0.6]
[5,19,"Manchester",null,"Dining: Cafeteria/Fast Food",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.5]
[6,18,"Mt. Washington",null,"Dining: Family",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4]
[7,17,"Nashua",null,"Dormitory",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.3]
[8,16,"Plymouth",null,"Education - College/University",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.2]
[9,15,"Portsmouth",null,"Education - Community College",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.1]
[10,14,"Rochester",null,"Education - K-12 School",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[11,13,null,null,"Exercise center"]
[12,12,null,null,"Fire station"]
[13,11,null,null,"Grocery"]
[14,10,null,null,"Gymnasium"]
[15,9,null,null,"Health/Medical - Clinic"]
[16,8,null,null,"Hospital"]
[17,7,null,null,"Hotel/Motel/Lodging"]
[18,6,null,null,"Industrial/Manufacturing - 1 Shift"]
[19,5,null,null,"Industrial/Manufacturing - 2 Shifts"]
[20,4,null,null,"Industrial/Manufacturing - 3 Shifts"]
[21,3,null,null,"Library"]
[22,2,null,null,"Motion picture theater"]
[23,1,null,null,"Multifamily"]
[null,0,null,null,"Museum"]
[null,null,null,null,"Nursing Home"]
[null,null,null,null,"Office - Medium/Large ( > 20,000 ft²)"]
[null,null,null,null,"Office - Small ( < 20,000 ft²)"]
[null,null,null,null,"Parking garage"]
[null,null,null,null,"Penitentiary"]
[null,null,null,null,"Performing arts theater"]
[null,null,null,null,"Police station"]
[null,null,null,null,"Post office"]
[null,null,null,null,"Religious Worship/Church"]
[null,null,null,null,"Retail"]
[null,null,null,null,"Sports arena"]
[null,null,null,null,"Storage Facility"]
[null,null,null,null,"Town hall"]
[null,null,null,null,"Transportation"]
[null,null,null,null,"Warehouse - Distribution Center"]
[null,null,null,null,"Warehouse - Inactive Storage"]
[null,null,null,null,"Workshop"]

{"sheet":"ECM Summary","index":5,"n_rows":74,"n_cols":33,"rows_kept":74,"cut":false,"hidden":false,"merged":[[9,2,20,2],[21,2,24,2],[9,4,9,7],[10,4,10,7],[11,4,11,7],[12,4,12,7],[13,4,13,7],[24,4,24,7],[14,4,14,7],[15,4,15,7],[16,4,16,7],[17,4,17,7],[18,4,18,7],[2,8,2,10],[23,4,23,7],[19,4,19,7],[20,4,20,7],[21,4,21,7],[22,4,22,7]]}
["Tool Version:",null,{"$f":"Instructions!T9","v":"v2026.02.19"}]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,{"$f":"IF('Project Info'!O5<>\"Yes\",\"WARNING: All required Project Info inputs have not been entered. This could cause unintended results (See Project Info sheet).\",\"\")","v":"WARNING: All required Project Info inputs have not been entered. This could cause unintended results (See Project Info sheet)."}]
[null,null,null,"SUMMARY OF ENERGY CONSERVATION MEASURES",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"(OPTIONAL)"]
[null,null,null,null,null,null,null,null,"Calculate","Annual Savings",null,null,"Electric Peak Savings",null,null,null,null,null,null,null,"Increm.","Payback","Payback","Total","Incentive Breakdown",null,"Included in",null,"Program ","Fuel","Measure","Measure","Total"]
[null,null,null,"ECM","Description",null,null,null,"ECM","Electric",{"$f":"C32","v":0},"Energy Cost","Winter","Winter","Summer","Summer","Overall","Max","Avg. kW","Avg. kW","Cost","w/o Incentive","with Incentive","Incentive","Electric","Fossil Fuel","Current",null,"Type","Savings","Code","Life","Savings"]
[null,null,null,null,null,null,null,null,"?","kWh",{"$f":"F32","v":{"$error":"#N/A"}},"$","On Peak %","Off Peak %","On Peak %","Off Peak %","%OnPeak","kW","Summer","Winter","$","years","years","$","$","$","Design?","1/0",null,"Type","(BCR)","years","MMBTU"]
[null,null,"Standard Tool Measures",{"$f":"IF(I10=\"Yes\",MAX(D$9:D9)+1,\"\")","v":""},"Bldg Envelope",null,null,null,"No",{"$f":"IF($I10<>\"Yes\",\"\",INDIRECT(CONCATENATE(\"'\",$E10,\"'!H3\")))","v":""},{"$f":"IF($I10<>\"Yes\",\"\",INDIRECT(CONCATENATE(\"'\",$E10,\"'!H4\")))","v":""},{"$f":"IF($I10<>\"Yes\",\"\",J10*$E$31+K10*$E$32)","v":""},{"$f":"IF($I10<>\"Yes\",\"\",INDIRECT(CONCATENATE(\"'\",$E10,\"'!A15\")))","v":""},{"$f":"IF($I10<>\"Yes\",\"\",INDIRECT(CONCATENATE(\"'\",$E10,\"'!B15\")))","v":""},{"$f":"IF($I10<>\"Yes\",\"\",INDIRECT(CONCATENATE(\"'\",$E10,\"'!C15\")))","v":""},{"$f":"IF($I10<>\"Yes\",\"\",INDIRECT(CONCATENATE(\"'\",$E10,\"'!D15\")))","v":""},{"$f":"IF(I10<>\"Yes\",\"\",M10+O10)","v":""},{"$f":"IF($I10<>\"Yes\",\"\",INDIRECT(CONCATENATE(\"'\",$E10,\"'!D4\")))","v":""},{"$f":"IF($I10<>\"Yes\",\"\",INDIRECT(CONCATENATE(\"'\",$E10,\"'!D5\")))","v":""},{"$f":"IF($I10<>\"Yes\",\"\",INDIRECT(CONCATENATE(\"'\",$E10,\"'!D6\")))","v":""},{"$f":"IF($I10<>\"Yes\",\"\",INDIRECT(CONCATENATE(\"'\",$E10,\"'!D9\")))","v":""},{"$f":"IF($I10<>\"Yes\",\"\",IF(U10=\"NA\",\"NA\",U10/L10))","v":""},{"$f":"IF($I10<>\"Yes\",\"\",IF(U10=\"NA\",\"NA\",(U10-X10)/L10))","v":""},{"$f":"IF($I10<>\"Yes\",\"\",INDIRECT(CONCATENATE(\"'\",$E10,\"'!H7\")))","v":""},{"$f":"IF($I10<>\"Yes\",\"\",$J$31*INDIRECT(CONCATENATE(\"'\",$E10,\"'!H3\")))","v":""},{"$f":"IF($I10<>\"Yes\",\"\",$J$32*INDIRECT(CONCATENATE(\"'\",$E10,\"'!H4\")))","v":""},null,{"$f":"1*(AA10=$A$55)","v":0},"Custom",{"$f":"IF(AND(J10>0,K10>0),\"Dual\",IF(J10>0,\"Electric\",IF(K10>0,\"Gas\",\"\")))","v":"Dual"},"Building Shell",25,{"$f":"IF(I10<>$A$55,\"\",(J10*3.412+K10*100)/1000)","v":""}]
[null,null,null,{"$f":"IF(I11=\"Yes\",MAX(D$9:D10)+1,\"\")","v":""},"Interior Lighting",null,null,null,"No","","","",{"$f":"IF($I11<>\"Yes\",\"\",INDIRECT(CONCATENATE(\"'\",$E11,\"'!A15\")))","v":""},{"$f":"IF($I11<>\"Yes\",\"\",INDIRECT(CONCATENATE(\"'\",$E11,\"'!B15\")))","v":""},{"$f":"IF($I11<>\"Yes\",\"\",INDIRECT(CONCATENATE(\"'\",$E11,\"'!C15\")))","v":""},{"$f":"IF($I11<>\"Yes\",\"\",INDIRECT(CONCATENATE(\"'\",$E11,\"'!D15\")))","v":""},{"$f":"IF(I11<>\"Yes\",\"\",M11+O11)","v":""},{"$f":"IF($I11<>\"Yes\",\"\",INDIRECT(CONCATENATE(\"'\",$E11,\"'!D4\")))","v":""},{"$f":"IF($I11<>\"Yes\",\"\",INDIRECT(CONCATENATE(\"'\",$E11,\"'!D5\")))","v":""},{"$f":"IF($I11<>\"Yes\",\"\",INDIRECT(CONCATENATE(\"'\",$E11,\"'!D6\")))","v":""},"",{"$f":"IF($I11<>\"Yes\",\"\",IF(U11=\"NA\",\"NA\",U11/L11))","v":""},{"$f":"IF($I11<>\"Yes\",\"\",IF(U11=\"NA\",\"NA\",(U11-X11)/L11))","v":""},"",{"$f":"IF($I11<>\"Yes\",\"\",X11)","v":""},{"$f":"IF($I11<>\"Yes\",\"\",0)","v":""},null,{"$f":"1*(AA11=$A$55)","v":0},"Prescriptive","Electric","Lighting - Interior",15,""]
[null,null,null,{"$f":"IF(I12=\"Yes\",MAX(D$9:D11)+1,\"\")","v":""},"Exterior Lighting",null,null,null,"No","","","","","","","","","","","","","","","",{"$f":"IF($I12<>\"Yes\",\"\",X12)","v":""},{"$f":"IF($I12<>\"Yes\",\"\",0)","v":""},null,{"$f":"1*(AA12=$A$55)","v":0},"Prescriptive","Electric","Lighting - Exterior",15,""]
[null,null,null,{"$f":"IF(I13=\"Yes\",MAX(D$9:D12)+1,\"\")","v":""},"Unitary HVAC (RTU, AC, HP, VRF)",null,null,null,"No","","","","","","","","","","","","","","","",{"$f":"IF($I13<>\"Yes\",\"\",$J$31*INDIRECT(CONCATENATE(\"'\",$E13,\"'!H3\")))","v":""},{"$f":"IF($I13<>\"Yes\",\"\",$J$32*INDIRECT(CONCATENATE(\"'\",$E13,\"'!H4\")))","v":""},null,0,"Custom","Electric","HVAC Equipment and Systems",15,""]
[null,null,null,{"$f":"IF(I14=\"Yes\",MAX(D$9:D13)+1,\"\")","v":""},"High Efficiency Chillers",null,null,null,"No","","","","","","","","","","","","","","","",{"$f":"IF($I14<>\"Yes\",\"\",$J$31*INDIRECT(CONCATENATE(\"'\",$E14,\"'!H3\")))","v":""},{"$f":"IF($I14<>\"Yes\",\"\",$J$32*INDIRECT(CONCATENATE(\"'\",$E14,\"'!H4\")))","v":""},null,0,"Custom","Electric","Chillers",20,""]
[null,null,null,{"$f":"IF(I15=\"Yes\",MAX(D$9:D14)+1,\"\")","v":""},"Variable Frequency Drives",null,null,null,"No","","","","","","","","","","","","","","","",{"$f":"IF($I15<>\"Yes\",\"\",X15)","v":""},{"$f":"IF($I15<>\"Yes\",\"\",0)","v":""},null,0,"Prescriptive","Electric","VFD on HVAC Equipment",15,""]
[null,null,null,{"$f":"IF(I16=\"Yes\",MAX(D$9:D15)+1,\"\")","v":""},"Energy Recovery",null,null,null,"No","","","","","","","","","","","","","","","",{"$f":"IF($I16<>\"Yes\",\"\",$J$31*INDIRECT(CONCATENATE(\"'\",$E16,\"'!H3\")))","v":""},{"$f":"IF($I16<>\"Yes\",\"\",$J$32*INDIRECT(CONCATENATE(\"'\",$E16,\"'!H4\")))","v":""},null,0,"Custom",{"$f":"IF(AND(J16>0,K16>0),\"Dual\",IF(J16>0,\"Electric\",IF(K16>0,\"Gas\",\"\")))","v":"Dual"},{"$f":"IF(AD16=\"Electric\",\"HVAC Equipment and Systems\", \"Heat recovery, HVAC\")","v":"Heat recovery, HVAC"},15,""]
[null,null,null,{"$f":"IF(I17=\"Yes\",MAX(D$9:D16)+1,\"\")","v":""},"Demand Control Ventilation",null,null,null,"No","","","","","","","","","","","","","","","","","",null,0,"Custom",{"$f":"IF(AND(J17>0,K17>0),\"Dual\",IF(J17>0,\"Electric\",IF(K17>0,\"Gas\",\"\")))","v":"Dual"},"EMS / controls, HVAC",10,""]
[null,null,null,{"$f":"IF(I18=\"Yes\",MAX(D$9:D17)+1,\"\")","v":""},"Variable Flow Kitchen Hood",null,null,null,"No","","","","","","","","","","","","","","","","","",null,0,"Custom",{"$f":"IF(AND(J18>0,K18>0),\"Dual\",IF(J18>0,\"Electric\",IF(K18>0,\"Gas\",\"\")))","v":"Dual"},"EMS / controls, HVAC",10,""]
[null,null,null,{"$f":"IF(I19=\"Yes\",MAX(D$9:D18)+1,\"\")","v":""},"Condensing Boilers",null,null,null,"No","","","","","","","","","","","","","","","",{"$f":"IF($I19<>\"Yes\",\"\",0)","v":""},{"$f":"IF($I19<>\"Yes\",\"\",X19)","v":""},null,0,"Custom","Gas","Boiler, HVAC",20,""]
[null,null,null,{"$f":"IF(I20=\"Yes\",MAX(D$9:D19)+1,\"\")","v":""},"DHW Heaters",null,null,null,"No","","","","","","","","","","","","","","","","","",null,0,"Custom",{"$f":"IF(AND(J20>0,K20>0),\"Dual\",IF(J20>0,\"Electric\",IF(K20>0,\"Gas\",\"\")))","v":"Dual"},{"$f":"IF(AD20=\"Gas\",\"Water heating, DHW\",\"Other\")","v":"Other"},15,""]
[null,null,null,{"$f":"IF(I21=\"Yes\",MAX(D$9:D20)+1,\"\")","v":""},"Low Flow DHW Fixtures",null,null,null,"No",{"$f":"IF($I21<>\"Yes\",\"\",INDIRECT(CONCATENATE(\"'\",$E21,\"'!H3\")))","v":""},"","","","","","","","","","","","","","","","",null,0,"Custom",{"$f":"IF(AND(J21>0,K21>0),\"Dual\",IF(J21>0,\"Electric\",IF(K21>0,\"Gas\",\"\")))","v":"Dual"},{"$f":"IF(AD21=\"Gas\",\"Water heating, DHW\",\"Other\")","v":"Other"},10,""]
[null,null,"User-Defined Measures",{"$f":"IF(I22=\"Yes\",MAX(D$9:D21)+1,\"\")","v":""},null,null,null,null,null,{"$f":"IF($I22<>\"Yes\",\"\",'User Defined 1'!$H$3)","v":""},{"$f":"IF($I22<>\"Yes\",\"\",'User Defined 1'!$H$4)","v":""},"",{"$f":"IF($I22<>\"Yes\",\"\",'User Defined 1'!$A$15)","v":""},{"$f":"IF($I22<>\"Yes\",\"\",'User Defined 1'!$B$15)","v":""},{"$f":"IF($I22<>\"Yes\",\"\",'User Defined 1'!$C$15)","v":""},{"$f":"IF($I22<>\"Yes\",\"\",'User Defined 1'!$D$15)","v":""},{"$f":"IF(I22<>\"Yes\",\"\",M22+O22)","v":""},{"$f":"IF($I22<>\"Yes\",\"\",'User Defined 1'!$D$4)","v":""},{"$f":"IF($I22<>\"Yes\",\"\",'User Defined 1'!$D$5)","v":""},{"$f":"IF($I22<>\"Yes\",\"\",'User Defined 1'!$D$6)","v":""},{"$f":"IF($I22<>\"Yes\",\"\",'User Defined 1'!$H$5)","v":""},{"$f":"IF($I22<>\"Yes\",\"\",IF(U22=\"NA\",\"NA\",U22/L22))","v":""},"",{"$f":"IF($I22<>\"Yes\",\"\",IF('User Defined 1'!$H$7>0,'User Defined 1'!$H$7,'User Defined 1'!$H$6))","v":""},{"$f":"IF($I22<>\"Yes\",\"\",$J$31*'User Defined 1'!$H$3)","v":""},{"$f":"IF($I22<>\"Yes\",\"\",$J$32*'User Defined 1'!$H$4)","v":""},null,0,{"$f":"IF($I22<>\"Yes\",\"\",'User Defined 1'!$H$17)","v":""},{"$f":"IF($I22<>\"Yes\",\"\",'User Defined 1'!$H$18)","v":""},{"$f":"IF($I22<>\"Yes\",\"\",'User Defined 1'!$H$19)","v":""},{"$f":"IF($I22<>\"Yes\",\"\",'User Defined 1'!$H$20)","v":""},""]
[null,null,null,{"$f":"IF(I23=\"Yes\",MAX(D$9:D22)+1,\"\")","v":""},null,null,null,null,null,{"$f":"IF($I23<>\"Yes\",\"\",'User Defined 2'!$H$3)","v":""},{"$f":"IF($I23<>\"Yes\",\"\",'User Defined 2'!$H$4)","v":""},"",{"$f":"IF($I23<>\"Yes\",\"\",'User Defined 2'!$A$15)","v":""},{"$f":"IF($I23<>\"Yes\",\"\",'User Defined 2'!$B$15)","v":""},{"$f":"IF($I23<>\"Yes\",\"\",'User Defined 2'!$C$15)","v":""},{"$f":"IF($I23<>\"Yes\",\"\",'User Defined 2'!$D$15)","v":""},{"$f":"IF(I23<>\"Yes\",\"\",M23+O23)","v":""},{"$f":"IF($I23<>\"Yes\",\"\",'User Defined 2'!$D$4)","v":""},{"$f":"IF($I23<>\"Yes\",\"\",'User Defined 2'!$D$5)","v":""},{"$f":"IF($I23<>\"Yes\",\"\",'User Defined 2'!$D$6)","v":""},{"$f":"IF($I23<>\"Yes\",\"\",'User Defined 2'!$H$5)","v":""},{"$f":"IF($I23<>\"Yes\",\"\",IF(U23=\"NA\",\"NA\",U23/L23))","v":""},"",{"$f":"IF($I23<>\"Yes\",\"\",IF('User Defined 2'!$H$7>0,'User Defined 2'!$H$7,'User Defined 2'!$H$6))","v":""},{"$f":"IF($I23<>\"Yes\",\"\",$J$31*'User Defined 2'!$H$3)","v":""},{"$f":"IF($I23<>\"Yes\",\"\",$J$32*'User Defined 2'!$H$4)","v":""},null,0,{"$f":"IF($I23<>\"Yes\",\"\",'User Defined 2'!$H$17)","v":""},{"$f":"IF($I23<>\"Yes\",\"\",'User Defined 2'!$H$18)","v":""},{"$f":"IF($I23<>\"Yes\",\"\",'User Defined 2'!$H$19)","v":""},{"$f":"IF($I23<>\"Yes\",\"\",'User Defined 2'!$H$20)","v":""},""]
[null,null,null,{"$f":"IF(I24=\"Yes\",MAX(D$9:D23)+1,\"\")","v":""},null,null,null,null,null,{"$f":"IF($I24<>\"Yes\",\"\",'User Defined 3'!$H$3)","v":""},{"$f":"IF($I24<>\"Yes\",\"\",'User Defined 3'!$H$4)","v":""},"",{"$f":"IF($I24<>\"Yes\",\"\",'User Defined 3'!$A$15)","v":""},{"$f":"IF($I24<>\"Yes\",\"\",'User Defined 3'!$B$15)","v":""},{"$f":"IF($I24<>\"Yes\",\"\",'User Defined 3'!$C$15)","v":""},{"$f":"IF($I24<>\"Yes\",\"\",'User Defined 3'!$D$15)","v":""},{"$f":"IF(I24<>\"Yes\",\"\",M24+O24)","v":""},{"$f":"IF($I24<>\"Yes\",\"\",'User Defined 3'!$D$4)","v":""},{"$f":"IF($I24<>\"Yes\",\"\",'User Defined 3'!$D$5)","v":""},{"$f":"IF($I24<>\"Yes\",\"\",'User Defined 3'!$D$6)","v":""},{"$f":"IF($I24<>\"Yes\",\"\",'User Defined 3'!$H$5)","v":""},{"$f":"IF($I24<>\"Yes\",\"\",IF(U24=\"NA\",\"NA\",U24/L24))","v":""},"",{"$f":"IF($I24<>\"Yes\",\"\",IF('User Defined 3'!$H$7>0,'User Defined 3'!$H$7,'User Defined 3'!$H$6))","v":""},{"$f":"IF($I24<>\"Yes\",\"\",$J$31*'User Defined 3'!$H$3)","v":""},{"$f":"IF($I24<>\"Yes\",\"\",$J$32*'User Defined 3'!$H$4)","v":""},null,0,{"$f":"IF($I24<>\"Yes\",\"\",'User Defined 3'!$H$17)","v":""},{"$f":"IF($I24<>\"Yes\",\"\",'User Defined 3'!$H$18)","v":""},{"$f":"IF($I24<>\"Yes\",\"\",'User Defined 3'!$H$19)","v":""},{"$f":"IF($I24<>\"Yes\",\"\",'User Defined 3'!$H$20)","v":""},""]
[null,null,null,{"$f":"IF(I25=\"Yes\",MAX(D$9:D24)+1,\"\")","v":""},null,null,null,null,null,{"$f":"IF($I25<>\"Yes\",\"\",'User Defined 4'!$H$3)","v":""},{"$f":"IF($I25<>\"Yes\",\"\",'User Defined 4'!$H$4)","v":""},"",{"$f":"IF($I25<>\"Yes\",\"\",'User Defined 3'!$A$15)","v":""},{"$f":"IF($I25<>\"Yes\",\"\",'User Defined 3'!$B$15)","v":""},{"$f":"IF($I25<>\"Yes\",\"\",'User Defined 3'!$C$15)","v":""},{"$f":"IF($I25<>\"Yes\",\"\",'User Defined 3'!$D$15)","v":""},{"$f":"IF(I25<>\"Yes\",\"\",M25+O25)","v":""},{"$f":"IF($I25<>\"Yes\",\"\",'User Defined 3'!$D$4)","v":""},{"$f":"IF($I25<>\"Yes\",\"\",'User Defined 3'!$D$5)","v":""},{"$f":"IF($I25<>\"Yes\",\"\",'User Defined 3'!$D$6)","v":""},{"$f":"IF($I25<>\"Yes\",\"\",'User Defined 4'!$H$5)","v":""},{"$f":"IF($I25<>\"Yes\",\"\",IF(U25=\"NA\",\"NA\",U25/L25))","v":""},"",{"$f":"IF($I25<>\"Yes\",\"\",IF('User Defined 4'!$H$7>0,'User Defined 4'!$H$7,'User Defined 4'!$H$6))","v":""},{"$f":"IF($I25<>\"Yes\",\"\",$J$31*'User Defined 4'!$H$3)","v":""},{"$f":"IF($I25<>\"Yes\",\"\",$J$32*'User Defined 4'!$H$4)","v":""},null,0,{"$f":"IF($I25<>\"Yes\",\"\",'User Defined 4'!$H$17)","v":""},{"$f":"IF($I25<>\"Yes\",\"\",'User Defined 4'!$H$18)","v":""},{"$f":"IF($I25<>\"Yes\",\"\",'User Defined 4'!$H$19)","v":""},{"$f":"IF($I25<>\"Yes\",\"\",'User Defined 4'!$H$20)","v":""},""]
[null,null,null,"TOTAL","Total Potential Project Savings",null,null,null,null,{"$f":"SUMIFS(J10:J25,$I$10:$I$25,\"Yes\")","v":0},{"$f":"SUMIFS(K10:K25,$I$10:$I$25,\"Yes\")","v":0},{"$f":"SUMIFS(L10:L25,$I$10:$I$25,\"Yes\")","v":0},{"$f":"SUMPRODUCT(M10:M25,J10:J25)/J26","v":{"$error":"#DIV/0!"}},null,null,null,null,{"$f":"SUMIFS(R10:R25,$I$10:$I$25,\"Yes\")","v":0},{"$f":"SUMIFS(S10:S25,$I$10:$I$25,\"Yes\")","v":0},{"$f":"SUMIFS(T10:T25,$I$10:$I$25,\"Yes\")","v":0},{"$f":"SUMIFS(U10:U25,$I$10:$I$25,\"Yes\")","v":0},{"$f":"U26/L26","v":{"$error":"#DIV/0!"}},{"$f":"(U26-X26)/L26","v":{"$error":"#DIV/0!"}},{"$f":"SUM(X10:X25)","v":0},{"$f":"SUM(Y10:Y25)","v":0},0,null,null,null,null,null,{"$f":"IFERROR(SUMPRODUCT(AF10:AF25,AG10:AG25)/AG26,0)","v":0},{"$f":"SUM(AG10:AG25)","v":0}]
[null,null,null,null,"Savings from ECMs Included in Current Design",null,null,null,null,{"$f":"SUMPRODUCT(J10:J25,$AB$10:$AB$25)","v":0},{"$f":"SUMPRODUCT(K10:K25,$AB$10:$AB$25)","v":0},0,null,null,null,null,null,0,0,0,0,{"$f":"U27/L27","v":{"$error":"#DIV/0!"}},{"$f":"(U27-X27)/L27","v":{"$error":"#DIV/0!"}},{"$f":"SUMPRODUCT(X10:X25,$AB$10:$AB$25)","v":0},0,0]
[]
[null,null,"Utility Energy Rates (Price)",null,null,null,null,"PA Custom Incentive Rates"]
[null,null,null,null,"Rate","Unit",null,null,null,"Rate","Unit"]
[null,null,"Electric",null,{"$f":"IF(E36>0,E36,'PA Impacts'!$Y$3)","v":0.1593},"kWh",null,"Electric",null,{"$f":"IF(J36>0, J36, 'PA Impacts'!F4)","v":0.28000000000000003},"kWh"]
[null,null,{"$f":"'Project Info'!$C$21","v":0},null,{"$f":"IF(E37>0,E37,LOOKUP(C32,'PA Impacts'!$U$3:$U$6,'PA Impacts'!$Y$3:$Y$6))","v":{"$error":"#N/A"}},{"$f":"LOOKUP(C32,'Project Info'!$X$102:$X$105,'Project Info'!$AA$102:$AA$105)","v":{"$error":"#N/A"}},null,{"$f":"'Project Info'!$C$21","v":0},null,{"$f":"IF(J37>0,J37,'PA Impacts'!F7)","v":0},{"$f":"LOOKUP(H32,'Project Info'!$X$102:$X$105,'Project Info'!$AA$102:$AA$105)","v":{"$error":"#N/A"}}]
[null,null,"Optional: Override Default Values",null,null,null,null,"Optional: Override Default Values"]
[null,null,"Utility Energy Rates (Price) Override",null,null,null,null,"PA Custom Incentive Rates Override"]
[null,null,null,null,"Rate","Unit",null,null,null,"Rate","Unit"]
[null,null,"Electric",null,null,"kWh",null,"Electric",null,null,"kWh"]
[null,null,{"$f":"'Project Info'!$C$21","v":0},null,null,{"$f":"LOOKUP(C37,'Project Info'!$X$102:$X$105,'Project Info'!$AA$102:$AA$105)","v":{"$error":"#N/A"}},null,{"$f":"'Project Info'!$C$21","v":0},null,null,{"$f":"LOOKUP(C37,'Project Info'!$X$102:$X$105,'Project Info'!$AA$102:$AA$105)","v":{"$error":"#N/A"}}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Yes"]
["No"]
[]
["Measures"]
[1,"Interior Lighting"]
[2,"Exterior Lighting"]
[3,"Energy Recovery"]
[4,"Condensing Boilers"]
[5,"High Efficiency Chillers"]
[6,"Condensing DHW Heaters"]
[7,"High Efficiency VRF Systems"]
[8,"Demand Control Ventilation"]
[9,"Variable Speed Kitchen Exhaust"]
[10,"VFDs (Pumps/Fans)"]
[11,"High Performance Split AC Units"]
[12,"High Efficiency Rooftop Units"]
[13,"Occupancy Based HVAC Controls"]
[14,"Static Pressure Reduction"]
[15,"Envelope Insulation"]
[16,"Enhanced Garage Door Insulation"]

{"sheet":"PA Impacts","index":6,"n_rows":118,"n_cols":26,"rows_kept":118,"cut":false,"hidden":true,"merged":[[53,1,53,4],[54,1,54,4],[55,1,55,4],[56,1,56,4],[60,1,60,4],[57,1,57,4],[58,1,58,4],[59,1,59,4],[51,1,51,4],[52,1,52,4],[41,1,41,4],[42,1,42,4],[43,1,43,4],[44,1,44,4],[45,1,45,4],[46,1,46,4],[47,1,47,4],[48,1,48,4],[49,1,49,4],[50,1,50,4],[10,0,10,1],[11,0,16,1],[11,2,11,3],[12,2,12,3],[13,2,13,3],[14,2,14,3],[15,2,15,3],[16,2,16,3],[17,0,18,1],[17,2,17,3],[18,2,18,3],[19,0,19,1],[20,0,20,1],[19,2,19,3],[20,2,20,3],[21,2,21,3],[22,2,22,3],[23,2,23,3],[24,0,25,1],[24,2,24,3],[25,2,25,3],[26,0,28,1],[26,2,26,3],[27,2,27,3],[28,2,28,3],[29,0,34,1],[29,2,29,3],[30,2,30,3],[31,2,31,3],[32,2,32,3],[33,2,33,3],[34,2,34,3]]}
[null,"Project State:",{"$f":"'Project Info'!C15","v":"NH"},"Program:",{"$f":"'Project Info'!$C$23","v":0},null,null,null,"Overall Energy Impacts/Savings ",null,null,null,null,null,null,"Mass Save HEAT PUMP Metrics",null,null,null,null,"Default Utility Rates"]
["PA Custom Incentive Rates",null,null,null,null,null,null,null,null,null,null,"Electric",{"$f":"I6","v":0},"Total","Fossil Fuel","Quantity of HPs (#)",null,null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AN3","v":0},null,null,"MA","NH","RI","This Project","Unit"]
["PA",null,null,"Unit",null,"Default",null,null,null,null,null,"Impacts","Impacts","Energy","Equivalent","HP Annual Savings (kWh)",null,null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AN4","v":{"$error":"#DIV/0!"}},null,"Electric",0.19700000000000001,0.1593,0.18,{"$f":"LOOKUP('Project Info'!$C$15,$V$2:$X$2,V3:X3)","v":0.1593},"kWh"]
[{"$f":"'Project Info'!F3","v":0},null,null,"Electric $/kWh Saved",null,{"$f":"IFERROR(VLOOKUP($E$1,$G$68:$J$70,2,FALSE),$H$70)","v":0.28000000000000003},null,null,"Fuel","Program Administrator",null,"(kWh)",{"$f":"IF(I6='Project Info'!X102,\"(therms)\",\"(MMBtu)\")","v":"(MMBtu)"},"MMBtu","kWh","HP Incremental Cost ($)",null,null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AN5","v":{"$error":"#DIV/0!"}},null,{"$f":"'Project Info'!X102","v":"Natural Gas"},0.97699999999999998,0.97499999999999998,0.88800000000000001,{"$f":"LOOKUP('Project Info'!$C$15,$V$2:$X$2,V4:X4)","v":0.97499999999999998},"therms"]
[{"$f":"'Project Info'!I3","v":0},null,null,"Gas $/therm Saved",null,{"$f":"IFERROR(VLOOKUP($E$1,$G$68:$J$70,3,FALSE),$I$70)","v":1.5},null,null,"Electric",{"$f":"IF('Project Info'!$F$3=\"\",\"Select PA in Project Info tab\", 'Project Info'!$F$3)","v":"Select PA in Project Info tab"},null,{"$f":"SUMIF('ECM Summary'!$J$10:$J$25,\">=0\")","v":0},{"$f":"SUMIF('ECM Summary'!$K$10:$K$25,\"<0\")","v":0},{"$f":"(L5*3.412+M5*IF($I$6='Project Info'!$X$102,100,1000))/1000","v":0},null,"HP Incentive ($)",null,null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AN6","v":{"$error":"#DIV/0!"}},null,{"$f":"'Project Info'!X103","v":"Oil"},20,17.5,20,{"$f":"LOOKUP('Project Info'!$C$15,$V$2:$X$2,V5:X5)","v":17.5},"MMBtu"]
["Purchased Fuels (Non-gas fossil fuel)",null,null,"Fuel $/MMBtu Saved",null,{"$f":"IFERROR(VLOOKUP($E$1,$G$68:$J$70,4,FALSE),$J$70)","v":0},null,null,{"$f":"'Project Info'!C21","v":0},{"$f":"IF('Project Info'!C21<>'Project Info'!X102,'PA Impacts'!J5,IF('Project Info'!$I$3=\"\",\"Select PA in Project Info tab\", 'Project Info'!I$3))","v":"Select PA in Project Info tab"},null,{"$f":"SUMIF('ECM Summary'!$J$10:$J$25,\"<0\")","v":0},{"$f":"SUMIF('ECM Summary'!$K$10:$K$25,\">=0\")","v":0},{"$f":"(L6*3.412+M6*IF($I$6='Project Info'!$X$102,100,1000))/1000","v":0},{"$f":"N6*1000000/3412","v":0},"HP Summer kW Saved (kW)",null,null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AN7","v":{"$error":"#DIV/0!"}},null,{"$f":"'Project Info'!X104","v":"Propane"},30,32.5,30,{"$f":"LOOKUP('Project Info'!$C$15,$V$2:$X$2,V6:X6)","v":32.5},"MMBtu"]
[null,null,null,null,"Fossil Fuel Rate for this Project",{"$f":"IF('Project Info'!C21='Project Info'!X105,0,IF('Project Info'!C21='Project Info'!X102,F5,F6))","v":0},null,null,null,"Total Project Impact",null,{"$f":"SUM(L5:L6)","v":0},{"$f":"SUM(M5:M6)","v":0},{"$f":"SUM(N5:N6)","v":0},null,"HP Winter kW Saved (kW)",null,null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AN8","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Quantity of ECMs Included",null,{"$f":"MAX('ECM Summary'!$D$10:$D$25)","v":0}]
["SCREENING TOOL INPUTS BY MEASURE",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"TOTAL"]
[null,null,null,null,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,"PROJECT"]
[null,null,"Measure Label",null,{"$f":"OFFSET('ECM Summary'!$D$9,MATCH('PA Impacts'!E10,'ECM Summary'!$D$10:$D$25,0),1)","v":{"$error":"#N/A"}},{"$f":"OFFSET('ECM Summary'!$D$9,MATCH('PA Impacts'!F10,'ECM Summary'!$D$10:$D$25,0),1)","v":{"$error":"#N/A"}},{"$f":"OFFSET('ECM Summary'!$D$9,MATCH('PA Impacts'!G10,'ECM Summary'!$D$10:$D$25,0),1)","v":{"$error":"#N/A"}},{"$f":"OFFSET('ECM Summary'!$D$9,MATCH('PA Impacts'!H10,'ECM Summary'!$D$10:$D$25,0),1)","v":{"$error":"#N/A"}},{"$f":"OFFSET('ECM Summary'!$D$9,MATCH('PA Impacts'!I10,'ECM Summary'!$D$10:$D$25,0),1)","v":{"$error":"#N/A"}},{"$f":"OFFSET('ECM Summary'!$D$9,MATCH('PA Impacts'!J10,'ECM Summary'!$D$10:$D$25,0),1)","v":{"$error":"#N/A"}},{"$f":"OFFSET('ECM Summary'!$D$9,MATCH('PA Impacts'!K10,'ECM Summary'!$D$10:$D$25,0),1)","v":{"$error":"#N/A"}},{"$f":"OFFSET('ECM Summary'!$D$9,MATCH('PA Impacts'!L10,'ECM Summary'!$D$10:$D$25,0),1)","v":{"$error":"#N/A"}},{"$f":"OFFSET('ECM Summary'!$D$9,MATCH('PA Impacts'!M10,'ECM Summary'!$D$10:$D$25,0),1)","v":{"$error":"#N/A"}},{"$f":"OFFSET('ECM Summary'!$D$9,MATCH('PA Impacts'!N10,'ECM Summary'!$D$10:$D$25,0),1)","v":{"$error":"#N/A"}},{"$f":"OFFSET('ECM Summary'!$D$9,MATCH('PA Impacts'!O10,'ECM Summary'!$D$10:$D$25,0),1)","v":{"$error":"#N/A"}},{"$f":"OFFSET('ECM Summary'!$D$9,MATCH('PA Impacts'!P10,'ECM Summary'!$D$10:$D$25,0),1)","v":{"$error":"#N/A"}},{"$f":"OFFSET('ECM Summary'!$D$9,MATCH('PA Impacts'!Q10,'ECM Summary'!$D$10:$D$25,0),1)","v":{"$error":"#N/A"}},{"$f":"OFFSET('ECM Summary'!$D$9,MATCH('PA Impacts'!R10,'ECM Summary'!$D$10:$D$25,0),1)","v":{"$error":"#N/A"}},{"$f":"OFFSET('ECM Summary'!$D$9,MATCH('PA Impacts'!S10,'ECM Summary'!$D$10:$D$25,0),1)","v":{"$error":"#N/A"}},{"$f":"OFFSET('ECM Summary'!$D$9,MATCH('PA Impacts'!T10,'ECM Summary'!$D$10:$D$25,0),1)","v":{"$error":"#N/A"}}]
["Measure Information",null,"Include in project",null,{"$f":"1*(E$10<=$W$8)*(LOOKUP(E$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$I$10:$I$25)=\"Yes\")","v":{"$error":"#N/A"}},{"$f":"1*(F$10<=$W$8)*(LOOKUP(F$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$I$10:$I$25)=\"Yes\")","v":{"$error":"#N/A"}},{"$f":"1*(G$10<=$W$8)*(LOOKUP(G$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$I$10:$I$25)=\"Yes\")","v":{"$error":"#N/A"}},{"$f":"1*(H$10<=$W$8)*(LOOKUP(H$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$I$10:$I$25)=\"Yes\")","v":{"$error":"#N/A"}},{"$f":"1*(I$10<=$W$8)*(LOOKUP(I$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$I$10:$I$25)=\"Yes\")","v":{"$error":"#N/A"}},{"$f":"1*(J$10<=$W$8)*(LOOKUP(J$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$I$10:$I$25)=\"Yes\")","v":{"$error":"#N/A"}},{"$f":"1*(K$10<=$W$8)*(LOOKUP(K$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$I$10:$I$25)=\"Yes\")","v":{"$error":"#N/A"}},{"$f":"1*(L$10<=$W$8)*(LOOKUP(L$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$I$10:$I$25)=\"Yes\")","v":{"$error":"#N/A"}},{"$f":"1*(M$10<=$W$8)*(LOOKUP(M$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$I$10:$I$25)=\"Yes\")","v":{"$error":"#N/A"}},{"$f":"1*(N$10<=$W$8)*(LOOKUP(N$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$I$10:$I$25)=\"Yes\")","v":{"$error":"#N/A"}},{"$f":"1*(O$10<=$W$8)*(LOOKUP(O$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$I$10:$I$25)=\"Yes\")","v":{"$error":"#N/A"}},{"$f":"1*(P$10<=$W$8)*(LOOKUP(P$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$I$10:$I$25)=\"Yes\")","v":{"$error":"#N/A"}},{"$f":"1*(Q$10<=$W$8)*(LOOKUP(Q$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$I$10:$I$25)=\"Yes\")","v":{"$error":"#N/A"}},{"$f":"1*(R$10<=$W$8)*(LOOKUP(R$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$I$10:$I$25)=\"Yes\")","v":{"$error":"#N/A"}},{"$f":"1*(S$10<=$W$8)*(LOOKUP(S$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$I$10:$I$25)=\"Yes\")","v":{"$error":"#N/A"}},{"$f":"1*(T$10<=$W$8)*(LOOKUP(T$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$I$10:$I$25)=\"Yes\")","v":{"$error":"#N/A"}}]
[null,null,"Initiative",null,"New Buildings & Major Renovation","New Buildings & Major Renovation","New Buildings & Major Renovation","New Buildings & Major Renovation","New Buildings & Major Renovation","New Buildings & Major Renovation","New Buildings & Major Renovation","New Buildings & Major Renovation","New Buildings & Major Renovation","New Buildings & Major Renovation","New Buildings & Major Renovation","New Buildings & Major Renovation","New Buildings & Major Renovation","New Buildings & Major Renovation","New Buildings & Major Renovation","New Buildings & Major Renovation"]
[null,null,"Fuel  Savings Type",null,{"$f":"IF(E$10<=$W$8,LOOKUP(E$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AD$10:$AD$25),\"\")","v":""},{"$f":"IF(F$10<=$W$8,LOOKUP(F$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AD$10:$AD$25),\"\")","v":""},{"$f":"IF(G$10<=$W$8,LOOKUP(G$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AD$10:$AD$25),\"\")","v":""},{"$f":"IF(H$10<=$W$8,LOOKUP(H$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AD$10:$AD$25),\"\")","v":""},{"$f":"IF(I$10<=$W$8,LOOKUP(I$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AD$10:$AD$25),\"\")","v":""},{"$f":"IF(J$10<=$W$8,LOOKUP(J$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AD$10:$AD$25),\"\")","v":""},{"$f":"IF(K$10<=$W$8,LOOKUP(K$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AD$10:$AD$25),\"\")","v":""},{"$f":"IF(L$10<=$W$8,LOOKUP(L$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AD$10:$AD$25),\"\")","v":""},{"$f":"IF(M$10<=$W$8,LOOKUP(M$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AD$10:$AD$25),\"\")","v":""},{"$f":"IF(N$10<=$W$8,LOOKUP(N$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AD$10:$AD$25),\"\")","v":""},{"$f":"IF(O$10<=$W$8,LOOKUP(O$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AD$10:$AD$25),\"\")","v":""},{"$f":"IF(P$10<=$W$8,LOOKUP(P$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AD$10:$AD$25),\"\")","v":""},{"$f":"IF(Q$10<=$W$8,LOOKUP(Q$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AD$10:$AD$25),\"\")","v":""},{"$f":"IF(R$10<=$W$8,LOOKUP(R$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AD$10:$AD$25),\"\")","v":""},{"$f":"IF(S$10<=$W$8,LOOKUP(S$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AD$10:$AD$25),\"\")","v":""},{"$f":"IF(T$10<=$W$8,LOOKUP(T$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AD$10:$AD$25),\"\")","v":""}]
[null,null,"Measure",null,{"$f":"IF(E$10<=$W$8,LOOKUP(E$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AE$10:$AE$25),\"\")","v":""},{"$f":"IF(F$10<=$W$8,LOOKUP(F$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AE$10:$AE$25),\"\")","v":""},{"$f":"IF(G$10<=$W$8,LOOKUP(G$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AE$10:$AE$25),\"\")","v":""},{"$f":"IF(H$10<=$W$8,LOOKUP(H$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AE$10:$AE$25),\"\")","v":""},{"$f":"IF(I$10<=$W$8,LOOKUP(I$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AE$10:$AE$25),\"\")","v":""},{"$f":"IF(J$10<=$W$8,LOOKUP(J$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AE$10:$AE$25),\"\")","v":""},{"$f":"IF(K$10<=$W$8,LOOKUP(K$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AE$10:$AE$25),\"\")","v":""},{"$f":"IF(L$10<=$W$8,LOOKUP(L$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AE$10:$AE$25),\"\")","v":""},{"$f":"IF(M$10<=$W$8,LOOKUP(M$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AE$10:$AE$25),\"\")","v":""},{"$f":"IF(N$10<=$W$8,LOOKUP(N$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AE$10:$AE$25),\"\")","v":""},{"$f":"IF(O$10<=$W$8,LOOKUP(O$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AE$10:$AE$25),\"\")","v":""},{"$f":"IF(P$10<=$W$8,LOOKUP(P$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AE$10:$AE$25),\"\")","v":""},{"$f":"IF(Q$10<=$W$8,LOOKUP(Q$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AE$10:$AE$25),\"\")","v":""},{"$f":"IF(R$10<=$W$8,LOOKUP(R$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AE$10:$AE$25),\"\")","v":""},{"$f":"IF(S$10<=$W$8,LOOKUP(S$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AE$10:$AE$25),\"\")","v":""},{"$f":"IF(T$10<=$W$8,LOOKUP(T$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AE$10:$AE$25),\"\")","v":""}]
[null,null,"Estimated Useful Life (Years)",null,{"$f":"IF(E$10<=$W$8,LOOKUP(E$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(F$10<=$W$8,LOOKUP(F$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(G$10<=$W$8,LOOKUP(G$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(H$10<=$W$8,LOOKUP(H$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(I$10<=$W$8,LOOKUP(I$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(J$10<=$W$8,LOOKUP(J$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(K$10<=$W$8,LOOKUP(K$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(L$10<=$W$8,LOOKUP(L$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(M$10<=$W$8,LOOKUP(M$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(N$10<=$W$8,LOOKUP(N$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(O$10<=$W$8,LOOKUP(O$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(P$10<=$W$8,LOOKUP(P$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(Q$10<=$W$8,LOOKUP(Q$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(R$10<=$W$8,LOOKUP(R$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(S$10<=$W$8,LOOKUP(S$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(T$10<=$W$8,LOOKUP(T$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IFERROR(SUMPRODUCT(E16:T16,$E$36:$T$36)/$U$36,0)","v":0}]
[null,null,"Override Life (Optional)",null,{"$f":"IF(E$10<=$W$8,LOOKUP(E$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(F$10<=$W$8,LOOKUP(F$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(G$10<=$W$8,LOOKUP(G$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(H$10<=$W$8,LOOKUP(H$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(I$10<=$W$8,LOOKUP(I$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(J$10<=$W$8,LOOKUP(J$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(K$10<=$W$8,LOOKUP(K$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(L$10<=$W$8,LOOKUP(L$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(M$10<=$W$8,LOOKUP(M$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(N$10<=$W$8,LOOKUP(N$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(O$10<=$W$8,LOOKUP(O$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(P$10<=$W$8,LOOKUP(P$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(Q$10<=$W$8,LOOKUP(Q$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(R$10<=$W$8,LOOKUP(R$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(S$10<=$W$8,LOOKUP(S$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IF(T$10<=$W$8,LOOKUP(T$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$AF$10:$AF$25),\"\")","v":""},{"$f":"IFERROR(SUMPRODUCT(E17:T17,$E$36:$T$36)/$U$36,0)","v":0}]
["Measure Costs",null,"Proposed Cost ($)",null,{"$f":"IF(E$10<=$W$8,LOOKUP(E$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$U$10:$U$25),\"\")","v":""},{"$f":"IF(F$10<=$W$8,LOOKUP(F$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$U$10:$U$25),\"\")","v":""},{"$f":"IF(G$10<=$W$8,LOOKUP(G$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$U$10:$U$25),\"\")","v":""},{"$f":"IF(H$10<=$W$8,LOOKUP(H$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$U$10:$U$25),\"\")","v":""},{"$f":"IF(I$10<=$W$8,LOOKUP(I$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$U$10:$U$25),\"\")","v":""},{"$f":"IF(J$10<=$W$8,LOOKUP(J$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$U$10:$U$25),\"\")","v":""},{"$f":"IF(K$10<=$W$8,LOOKUP(K$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$U$10:$U$25),\"\")","v":""},{"$f":"IF(L$10<=$W$8,LOOKUP(L$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$U$10:$U$25),\"\")","v":""},{"$f":"IF(M$10<=$W$8,LOOKUP(M$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$U$10:$U$25),\"\")","v":""},{"$f":"IF(N$10<=$W$8,LOOKUP(N$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$U$10:$U$25),\"\")","v":""},{"$f":"IF(O$10<=$W$8,LOOKUP(O$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$U$10:$U$25),\"\")","v":""},{"$f":"IF(P$10<=$W$8,LOOKUP(P$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$U$10:$U$25),\"\")","v":""},{"$f":"IF(Q$10<=$W$8,LOOKUP(Q$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$U$10:$U$25),\"\")","v":""},{"$f":"IF(R$10<=$W$8,LOOKUP(R$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$U$10:$U$25),\"\")","v":""},{"$f":"IF(S$10<=$W$8,LOOKUP(S$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$U$10:$U$25),\"\")","v":""},{"$f":"IF(T$10<=$W$8,LOOKUP(T$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$U$10:$U$25),\"\")","v":""},{"$f":"SUM(E18:T18)","v":0}]
[null,null,"Baseline Cost ($)",null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,{"$f":"SUM(E19:T19)","v":0}]
["Gross Electric Energy",null,"Energy (kWh)",null,{"$f":"IF(E$10<=$W$8,LOOKUP(E$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$J$10:$J$25),\"\")","v":""},{"$f":"IF(F$10<=$W$8,LOOKUP(F$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$J$10:$J$25),\"\")","v":""},{"$f":"IF(G$10<=$W$8,LOOKUP(G$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$J$10:$J$25),\"\")","v":""},{"$f":"IF(H$10<=$W$8,LOOKUP(H$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$J$10:$J$25),\"\")","v":""},{"$f":"IF(I$10<=$W$8,LOOKUP(I$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$J$10:$J$25),\"\")","v":""},{"$f":"IF(J$10<=$W$8,LOOKUP(J$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$J$10:$J$25),\"\")","v":""},{"$f":"IF(K$10<=$W$8,LOOKUP(K$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$J$10:$J$25),\"\")","v":""},{"$f":"IF(L$10<=$W$8,LOOKUP(L$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$J$10:$J$25),\"\")","v":""},{"$f":"IF(M$10<=$W$8,LOOKUP(M$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$J$10:$J$25),\"\")","v":""},{"$f":"IF(N$10<=$W$8,LOOKUP(N$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$J$10:$J$25),\"\")","v":""},{"$f":"IF(O$10<=$W$8,LOOKUP(O$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$J$10:$J$25),\"\")","v":""},{"$f":"IF(P$10<=$W$8,LOOKUP(P$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$J$10:$J$25),\"\")","v":""},{"$f":"IF(Q$10<=$W$8,LOOKUP(Q$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$J$10:$J$25),\"\")","v":""},{"$f":"IF(R$10<=$W$8,LOOKUP(R$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$J$10:$J$25),\"\")","v":""},{"$f":"IF(S$10<=$W$8,LOOKUP(S$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$J$10:$J$25),\"\")","v":""},{"$f":"IF(T$10<=$W$8,LOOKUP(T$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$J$10:$J$25),\"\")","v":""},0]
["(Savings and Penalties)",null,"% Summer On Peak",null,{"$f":"IF(E$10<=$W$8,LOOKUP(E$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$O$10:$O$25),\"\")","v":""},{"$f":"IF(F$10<=$W$8,LOOKUP(F$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$O$10:$O$25),\"\")","v":""},{"$f":"IF(G$10<=$W$8,LOOKUP(G$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$O$10:$O$25),\"\")","v":""},{"$f":"IF(H$10<=$W$8,LOOKUP(H$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$O$10:$O$25),\"\")","v":""},{"$f":"IF(I$10<=$W$8,LOOKUP(I$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$O$10:$O$25),\"\")","v":""},{"$f":"IF(J$10<=$W$8,LOOKUP(J$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$O$10:$O$25),\"\")","v":""},{"$f":"IF(K$10<=$W$8,LOOKUP(K$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$O$10:$O$25),\"\")","v":""},{"$f":"IF(L$10<=$W$8,LOOKUP(L$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$O$10:$O$25),\"\")","v":""},{"$f":"IF(M$10<=$W$8,LOOKUP(M$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$O$10:$O$25),\"\")","v":""},{"$f":"IF(N$10<=$W$8,LOOKUP(N$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$O$10:$O$25),\"\")","v":""},{"$f":"IF(O$10<=$W$8,LOOKUP(O$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$O$10:$O$25),\"\")","v":""},{"$f":"IF(P$10<=$W$8,LOOKUP(P$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$O$10:$O$25),\"\")","v":""},{"$f":"IF(Q$10<=$W$8,LOOKUP(Q$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$O$10:$O$25),\"\")","v":""},{"$f":"IF(R$10<=$W$8,LOOKUP(R$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$O$10:$O$25),\"\")","v":""},{"$f":"IF(S$10<=$W$8,LOOKUP(S$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$O$10:$O$25),\"\")","v":""},{"$f":"IF(T$10<=$W$8,LOOKUP(T$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$O$10:$O$25),\"\")","v":""},{"$f":"IFERROR(SUMPRODUCT(E21:T21,$E$20:$T$20)/$U$20,0)","v":0}]
[null,null,"% Summer Off Peak",null,{"$f":"IF(E$10<=$W$8,LOOKUP(E$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$P$10:$P$25),\"\")","v":""},{"$f":"IF(F$10<=$W$8,LOOKUP(F$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$P$10:$P$25),\"\")","v":""},{"$f":"IF(G$10<=$W$8,LOOKUP(G$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$P$10:$P$25),\"\")","v":""},{"$f":"IF(H$10<=$W$8,LOOKUP(H$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$P$10:$P$25),\"\")","v":""},{"$f":"IF(I$10<=$W$8,LOOKUP(I$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$P$10:$P$25),\"\")","v":""},{"$f":"IF(J$10<=$W$8,LOOKUP(J$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$P$10:$P$25),\"\")","v":""},{"$f":"IF(K$10<=$W$8,LOOKUP(K$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$P$10:$P$25),\"\")","v":""},{"$f":"IF(L$10<=$W$8,LOOKUP(L$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$P$10:$P$25),\"\")","v":""},{"$f":"IF(M$10<=$W$8,LOOKUP(M$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$P$10:$P$25),\"\")","v":""},{"$f":"IF(N$10<=$W$8,LOOKUP(N$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$P$10:$P$25),\"\")","v":""},{"$f":"IF(O$10<=$W$8,LOOKUP(O$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$P$10:$P$25),\"\")","v":""},{"$f":"IF(P$10<=$W$8,LOOKUP(P$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$P$10:$P$25),\"\")","v":""},{"$f":"IF(Q$10<=$W$8,LOOKUP(Q$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$P$10:$P$25),\"\")","v":""},{"$f":"IF(R$10<=$W$8,LOOKUP(R$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$P$10:$P$25),\"\")","v":""},{"$f":"IF(S$10<=$W$8,LOOKUP(S$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$P$10:$P$25),\"\")","v":""},{"$f":"IF(T$10<=$W$8,LOOKUP(T$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$P$10:$P$25),\"\")","v":""},{"$f":"IFERROR(SUMPRODUCT(E22:T22,$E$20:$T$20)/$U$20,0)","v":0}]
[null,null,"% Winter On Peak",null,{"$f":"IF(E$10<=$W$8,LOOKUP(E$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$M$10:$M$25),\"\")","v":""},{"$f":"IF(F$10<=$W$8,LOOKUP(F$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$M$10:$M$25),\"\")","v":""},{"$f":"IF(G$10<=$W$8,LOOKUP(G$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$M$10:$M$25),\"\")","v":""},{"$f":"IF(H$10<=$W$8,LOOKUP(H$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$M$10:$M$25),\"\")","v":""},{"$f":"IF(I$10<=$W$8,LOOKUP(I$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$M$10:$M$25),\"\")","v":""},{"$f":"IF(J$10<=$W$8,LOOKUP(J$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$M$10:$M$25),\"\")","v":""},{"$f":"IF(K$10<=$W$8,LOOKUP(K$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$M$10:$M$25),\"\")","v":""},{"$f":"IF(L$10<=$W$8,LOOKUP(L$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$M$10:$M$25),\"\")","v":""},{"$f":"IF(M$10<=$W$8,LOOKUP(M$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$M$10:$M$25),\"\")","v":""},{"$f":"IF(N$10<=$W$8,LOOKUP(N$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$M$10:$M$25),\"\")","v":""},{"$f":"IF(O$10<=$W$8,LOOKUP(O$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$M$10:$M$25),\"\")","v":""},{"$f":"IF(P$10<=$W$8,LOOKUP(P$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$M$10:$M$25),\"\")","v":""},{"$f":"IF(Q$10<=$W$8,LOOKUP(Q$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$M$10:$M$25),\"\")","v":""},{"$f":"IF(R$10<=$W$8,LOOKUP(R$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$M$10:$M$25),\"\")","v":""},{"$f":"IF(S$10<=$W$8,LOOKUP(S$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$M$10:$M$25),\"\")","v":""},{"$f":"IF(T$10<=$W$8,LOOKUP(T$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$M$10:$M$25),\"\")","v":""},0]
[null,null,"% Winter Off Peak",null,{"$f":"IF(E$10<=$W$8,LOOKUP(E$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$N$10:$N$25),\"\")","v":""},{"$f":"IF(F$10<=$W$8,LOOKUP(F$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$N$10:$N$25),\"\")","v":""},{"$f":"IF(G$10<=$W$8,LOOKUP(G$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$N$10:$N$25),\"\")","v":""},{"$f":"IF(H$10<=$W$8,LOOKUP(H$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$N$10:$N$25),\"\")","v":""},{"$f":"IF(I$10<=$W$8,LOOKUP(I$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$N$10:$N$25),\"\")","v":""},{"$f":"IF(J$10<=$W$8,LOOKUP(J$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$N$10:$N$25),\"\")","v":""},{"$f":"IF(K$10<=$W$8,LOOKUP(K$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$N$10:$N$25),\"\")","v":""},{"$f":"IF(L$10<=$W$8,LOOKUP(L$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$N$10:$N$25),\"\")","v":""},{"$f":"IF(M$10<=$W$8,LOOKUP(M$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$N$10:$N$25),\"\")","v":""},{"$f":"IF(N$10<=$W$8,LOOKUP(N$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$N$10:$N$25),\"\")","v":""},{"$f":"IF(O$10<=$W$8,LOOKUP(O$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$N$10:$N$25),\"\")","v":""},{"$f":"IF(P$10<=$W$8,LOOKUP(P$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$N$10:$N$25),\"\")","v":""},{"$f":"IF(Q$10<=$W$8,LOOKUP(Q$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$N$10:$N$25),\"\")","v":""},{"$f":"IF(R$10<=$W$8,LOOKUP(R$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$N$10:$N$25),\"\")","v":""},{"$f":"IF(S$10<=$W$8,LOOKUP(S$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$N$10:$N$25),\"\")","v":""},{"$f":"IF(T$10<=$W$8,LOOKUP(T$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$N$10:$N$25),\"\")","v":""},0]
["Gross Electric Capacity (Savings and Penalties)",null,"Summer Peak kW",null,{"$f":"IF(E$10<=$W$8,LOOKUP(E$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$S$10:$S$25),\"\")","v":""},{"$f":"IF(F$10<=$W$8,LOOKUP(F$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$S$10:$S$25),\"\")","v":""},{"$f":"IF(G$10<=$W$8,LOOKUP(G$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$S$10:$S$25),\"\")","v":""},{"$f":"IF(H$10<=$W$8,LOOKUP(H$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$S$10:$S$25),\"\")","v":""},{"$f":"IF(I$10<=$W$8,LOOKUP(I$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$S$10:$S$25),\"\")","v":""},{"$f":"IF(J$10<=$W$8,LOOKUP(J$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$S$10:$S$25),\"\")","v":""},{"$f":"IF(K$10<=$W$8,LOOKUP(K$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$S$10:$S$25),\"\")","v":""},{"$f":"IF(L$10<=$W$8,LOOKUP(L$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$S$10:$S$25),\"\")","v":""},{"$f":"IF(M$10<=$W$8,LOOKUP(M$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$S$10:$S$25),\"\")","v":""},{"$f":"IF(N$10<=$W$8,LOOKUP(N$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$S$10:$S$25),\"\")","v":""},{"$f":"IF(O$10<=$W$8,LOOKUP(O$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$S$10:$S$25),\"\")","v":""},{"$f":"IF(P$10<=$W$8,LOOKUP(P$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$S$10:$S$25),\"\")","v":""},{"$f":"IF(Q$10<=$W$8,LOOKUP(Q$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$S$10:$S$25),\"\")","v":""},{"$f":"IF(R$10<=$W$8,LOOKUP(R$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$S$10:$S$25),\"\")","v":""},{"$f":"IF(S$10<=$W$8,LOOKUP(S$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$S$10:$S$25),\"\")","v":""},{"$f":"IF(T$10<=$W$8,LOOKUP(T$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$S$10:$S$25),\"\")","v":""},{"$f":"SUM(E25:T25)","v":0}]
[null,null,"Winter Peak kW",null,{"$f":"IF(E$10<=$W$8,LOOKUP(E$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$T$10:$T$25),\"\")","v":""},{"$f":"IF(F$10<=$W$8,LOOKUP(F$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$T$10:$T$25),\"\")","v":""},{"$f":"IF(G$10<=$W$8,LOOKUP(G$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$T$10:$T$25),\"\")","v":""},{"$f":"IF(H$10<=$W$8,LOOKUP(H$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$T$10:$T$25),\"\")","v":""},{"$f":"IF(I$10<=$W$8,LOOKUP(I$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$T$10:$T$25),\"\")","v":""},{"$f":"IF(J$10<=$W$8,LOOKUP(J$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$T$10:$T$25),\"\")","v":""},{"$f":"IF(K$10<=$W$8,LOOKUP(K$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$T$10:$T$25),\"\")","v":""},{"$f":"IF(L$10<=$W$8,LOOKUP(L$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$T$10:$T$25),\"\")","v":""},{"$f":"IF(M$10<=$W$8,LOOKUP(M$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$T$10:$T$25),\"\")","v":""},{"$f":"IF(N$10<=$W$8,LOOKUP(N$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$T$10:$T$25),\"\")","v":""},{"$f":"IF(O$10<=$W$8,LOOKUP(O$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$T$10:$T$25),\"\")","v":""},{"$f":"IF(P$10<=$W$8,LOOKUP(P$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$T$10:$T$25),\"\")","v":""},{"$f":"IF(Q$10<=$W$8,LOOKUP(Q$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$T$10:$T$25),\"\")","v":""},{"$f":"IF(R$10<=$W$8,LOOKUP(R$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$T$10:$T$25),\"\")","v":""},{"$f":"IF(S$10<=$W$8,LOOKUP(S$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$T$10:$T$25),\"\")","v":""},{"$f":"IF(T$10<=$W$8,LOOKUP(T$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$T$10:$T$25),\"\")","v":""},{"$f":"SUM(E26:T26)","v":0}]
["Gross Natural Gas",null,"Heating Season (Therms)",null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,{"$f":"SUM(E27:T27)","v":0}]
[null,null,"Year Round (Therms)",null,{"$f":"IF(E$10<=$W$8,LOOKUP(E$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Natural Gas\"),\"\")","v":""},{"$f":"IF(F$10<=$W$8,LOOKUP(F$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Natural Gas\"),\"\")","v":""},{"$f":"IF(G$10<=$W$8,LOOKUP(G$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Natural Gas\"),\"\")","v":""},{"$f":"IF(H$10<=$W$8,LOOKUP(H$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Natural Gas\"),\"\")","v":""},{"$f":"IF(I$10<=$W$8,LOOKUP(I$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Natural Gas\"),\"\")","v":""},{"$f":"IF(J$10<=$W$8,LOOKUP(J$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Natural Gas\"),\"\")","v":""},{"$f":"IF(K$10<=$W$8,LOOKUP(K$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Natural Gas\"),\"\")","v":""},{"$f":"IF(L$10<=$W$8,LOOKUP(L$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Natural Gas\"),\"\")","v":""},{"$f":"IF(M$10<=$W$8,LOOKUP(M$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Natural Gas\"),\"\")","v":""},{"$f":"IF(N$10<=$W$8,LOOKUP(N$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Natural Gas\"),\"\")","v":""},{"$f":"IF(O$10<=$W$8,LOOKUP(O$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Natural Gas\"),\"\")","v":""},{"$f":"IF(P$10<=$W$8,LOOKUP(P$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Natural Gas\"),\"\")","v":""},{"$f":"IF(Q$10<=$W$8,LOOKUP(Q$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Natural Gas\"),\"\")","v":""},{"$f":"IF(R$10<=$W$8,LOOKUP(R$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Natural Gas\"),\"\")","v":""},{"$f":"IF(S$10<=$W$8,LOOKUP(S$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Natural Gas\"),\"\")","v":""},{"$f":"IF(T$10<=$W$8,LOOKUP(T$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Natural Gas\"),\"\")","v":""},0]
[null,null,"Other (Therms)",null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
["Gross Non-Electric Non-Gas",null,"#2 Oil (MMbtu)",null,{"$f":"IF(E$10<=$W$8,LOOKUP(E$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Oil\"),\"\")","v":""},{"$f":"IF(F$10<=$W$8,LOOKUP(F$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Oil\"),\"\")","v":""},{"$f":"IF(G$10<=$W$8,LOOKUP(G$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Oil\"),\"\")","v":""},{"$f":"IF(H$10<=$W$8,LOOKUP(H$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Oil\"),\"\")","v":""},{"$f":"IF(I$10<=$W$8,LOOKUP(I$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Oil\"),\"\")","v":""},{"$f":"IF(J$10<=$W$8,LOOKUP(J$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Oil\"),\"\")","v":""},{"$f":"IF(K$10<=$W$8,LOOKUP(K$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Oil\"),\"\")","v":""},{"$f":"IF(L$10<=$W$8,LOOKUP(L$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Oil\"),\"\")","v":""},{"$f":"IF(M$10<=$W$8,LOOKUP(M$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Oil\"),\"\")","v":""},{"$f":"IF(N$10<=$W$8,LOOKUP(N$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Oil\"),\"\")","v":""},{"$f":"IF(O$10<=$W$8,LOOKUP(O$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Oil\"),\"\")","v":""},{"$f":"IF(P$10<=$W$8,LOOKUP(P$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Oil\"),\"\")","v":""},{"$f":"IF(Q$10<=$W$8,LOOKUP(Q$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Oil\"),\"\")","v":""},{"$f":"IF(R$10<=$W$8,LOOKUP(R$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Oil\"),\"\")","v":""},{"$f":"IF(S$10<=$W$8,LOOKUP(S$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Oil\"),\"\")","v":""},{"$f":"IF(T$10<=$W$8,LOOKUP(T$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Oil\"),\"\")","v":""},0]
[null,null,"Propane (MMbtu)",null,{"$f":"IF(E$10<=$W$8,LOOKUP(E$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Propane\"),\"\")","v":""},{"$f":"IF(F$10<=$W$8,LOOKUP(F$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Propane\"),\"\")","v":""},{"$f":"IF(G$10<=$W$8,LOOKUP(G$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Propane\"),\"\")","v":""},{"$f":"IF(H$10<=$W$8,LOOKUP(H$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Propane\"),\"\")","v":""},{"$f":"IF(I$10<=$W$8,LOOKUP(I$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Propane\"),\"\")","v":""},{"$f":"IF(J$10<=$W$8,LOOKUP(J$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Propane\"),\"\")","v":""},{"$f":"IF(K$10<=$W$8,LOOKUP(K$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Propane\"),\"\")","v":""},{"$f":"IF(L$10<=$W$8,LOOKUP(L$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Propane\"),\"\")","v":""},{"$f":"IF(M$10<=$W$8,LOOKUP(M$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Propane\"),\"\")","v":""},{"$f":"IF(N$10<=$W$8,LOOKUP(N$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Propane\"),\"\")","v":""},{"$f":"IF(O$10<=$W$8,LOOKUP(O$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Propane\"),\"\")","v":""},{"$f":"IF(P$10<=$W$8,LOOKUP(P$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Propane\"),\"\")","v":""},{"$f":"IF(Q$10<=$W$8,LOOKUP(Q$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Propane\"),\"\")","v":""},{"$f":"IF(R$10<=$W$8,LOOKUP(R$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Propane\"),\"\")","v":""},{"$f":"IF(S$10<=$W$8,LOOKUP(S$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Propane\"),\"\")","v":""},{"$f":"IF(T$10<=$W$8,LOOKUP(T$10,'ECM Summary'!$D$10:$D$25,'ECM Summary'!$K$10:$K$25)*($I$6=\"Propane\"),\"\")","v":""},0]
[null,null,"Water (Gallons)"]
[null,null,"Sewer (Gallons)"]
[null,null,"Annual $"]
[null,null,"One Time $"]
["TOTAL MMBTU Savings",null,null,null,{"$f":"IF(E$10<=$W$8,(E20*3.412+SUM(E27:E29)*100)/1000+E30+E31,0)","v":0},0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,{"$f":"SUM(E36:T36)","v":0}]
[]
["SUMMARY OF ENERGY CONSERVATION MEASURES"]
[null,null,null,null,null,"Include","Annual Savings",null,null,"Electric Peak Savings",null,null,null,null,null,null,"Increm.","Simple","Estimated"]
["ECM","Description",null,null,null,"ECM","Elec","Gas","Energy Cost","Winter","Winter","Summer","Summer","Max","Avg. kW","Avg. kW","Cost","Payback","Incentive"]
[null,null,null,null,null,"?","kWh","therms","$","On Peak %","Off Peak %","On Peak %","Off Peak %","kW","Summer","Winter","$","years","$"]
[{"$f":"'ECM Summary'!D10","v":""},{"$f":"'ECM Summary'!E10","v":"Bldg Envelope"},null,null,null,{"$f":"IF('ECM Summary'!I10=\"\",\"\",'ECM Summary'!I10)","v":"No"},{"$f":"'ECM Summary'!J10","v":""},{"$f":"'ECM Summary'!K10","v":""},{"$f":"'ECM Summary'!L10","v":""},{"$f":"'ECM Summary'!M10","v":""},{"$f":"'ECM Summary'!N10","v":""},{"$f":"'ECM Summary'!O10","v":""},{"$f":"'ECM Summary'!P10","v":""},{"$f":"'ECM Summary'!R10","v":""},{"$f":"'ECM Summary'!S10","v":""},{"$f":"'ECM Summary'!T10","v":""},{"$f":"'ECM Summary'!U10","v":""},{"$f":"'ECM Summary'!V10","v":""},{"$f":"'ECM Summary'!X10","v":""}]
[{"$f":"'ECM Summary'!D11","v":""},{"$f":"'ECM Summary'!E11","v":"Interior Lighting"},null,null,null,{"$f":"IF('ECM Summary'!I11=\"\",\"\",'ECM Summary'!I11)","v":"No"},{"$f":"'ECM Summary'!J11","v":""},{"$f":"'ECM Summary'!K11","v":""},{"$f":"'ECM Summary'!L11","v":""},{"$f":"'ECM Summary'!M11","v":""},{"$f":"'ECM Summary'!N11","v":""},{"$f":"'ECM Summary'!O11","v":""},{"$f":"'ECM Summary'!P11","v":""},{"$f":"'ECM Summary'!R11","v":""},{"$f":"'ECM Summary'!S11","v":""},{"$f":"'ECM Summary'!T11","v":""},{"$f":"'ECM Summary'!U11","v":""},{"$f":"'ECM Summary'!V11","v":""},{"$f":"'ECM Summary'!X11","v":""}]
[{"$f":"'ECM Summary'!D12","v":""},{"$f":"'ECM Summary'!E12","v":"Exterior Lighting"},null,null,null,{"$f":"IF('ECM Summary'!I12=\"\",\"\",'ECM Summary'!I12)","v":"No"},{"$f":"'ECM Summary'!J12","v":""},{"$f":"'ECM Summary'!K12","v":""},{"$f":"'ECM Summary'!L12","v":""},{"$f":"'ECM Summary'!M12","v":""},{"$f":"'ECM Summary'!N12","v":""},{"$f":"'ECM Summary'!O12","v":""},{"$f":"'ECM Summary'!P12","v":""},{"$f":"'ECM Summary'!R12","v":""},{"$f":"'ECM Summary'!S12","v":""},{"$f":"'ECM Summary'!T12","v":""},{"$f":"'ECM Summary'!U12","v":""},{"$f":"'ECM Summary'!V12","v":""},{"$f":"'ECM Summary'!X12","v":""}]
[{"$f":"'ECM Summary'!D13","v":""},{"$f":"'ECM Summary'!E13","v":"Unitary HVAC (RTU, AC, HP, VRF)"},null,null,null,{"$f":"IF('ECM Summary'!I13=\"\",\"\",'ECM Summary'!I13)","v":"No"},{"$f":"'ECM Summary'!J13","v":""},{"$f":"'ECM Summary'!K13","v":""},{"$f":"'ECM Summary'!L13","v":""},{"$f":"'ECM Summary'!M13","v":""},{"$f":"'ECM Summary'!N13","v":""},{"$f":"'ECM Summary'!O13","v":""},{"$f":"'ECM Summary'!P13","v":""},{"$f":"'ECM Summary'!R13","v":""},{"$f":"'ECM Summary'!S13","v":""},{"$f":"'ECM Summary'!T13","v":""},{"$f":"'ECM Summary'!U13","v":""},{"$f":"'ECM Summary'!V13","v":""},{"$f":"'ECM Summary'!X13","v":""}]
[{"$f":"'ECM Summary'!D14","v":""},{"$f":"'ECM Summary'!E14","v":"High Efficiency Chillers"},null,null,null,{"$f":"IF('ECM Summary'!I14=\"\",\"\",'ECM Summary'!I14)","v":"No"},{"$f":"'ECM Summary'!J14","v":""},{"$f":"'ECM Summary'!K14","v":""},{"$f":"'ECM Summary'!L14","v":""},{"$f":"'ECM Summary'!M14","v":""},{"$f":"'ECM Summary'!N14","v":""},{"$f":"'ECM Summary'!O14","v":""},{"$f":"'ECM Summary'!P14","v":""},{"$f":"'ECM Summary'!R14","v":""},{"$f":"'ECM Summary'!S14","v":""},{"$f":"'ECM Summary'!T14","v":""},{"$f":"'ECM Summary'!U14","v":""},{"$f":"'ECM Summary'!V14","v":""},{"$f":"'ECM Summary'!X14","v":""}]
[{"$f":"'ECM Summary'!D15","v":""},{"$f":"'ECM Summary'!E15","v":"Variable Frequency Drives"},null,null,null,{"$f":"IF('ECM Summary'!I15=\"\",\"\",'ECM Summary'!I15)","v":"No"},{"$f":"'ECM Summary'!J15","v":""},{"$f":"'ECM Summary'!K15","v":""},{"$f":"'ECM Summary'!L15","v":""},{"$f":"'ECM Summary'!M15","v":""},{"$f":"'ECM Summary'!N15","v":""},{"$f":"'ECM Summary'!O15","v":""},{"$f":"'ECM Summary'!P15","v":""},{"$f":"'ECM Summary'!R15","v":""},{"$f":"'ECM Summary'!S15","v":""},{"$f":"'ECM Summary'!T15","v":""},{"$f":"'ECM Summary'!U15","v":""},{"$f":"'ECM Summary'!V15","v":""},{"$f":"'ECM Summary'!X15","v":""}]
[{"$f":"'ECM Summary'!D16","v":""},{"$f":"'ECM Summary'!E16","v":"Energy Recovery"},null,null,null,{"$f":"IF('ECM Summary'!I16=\"\",\"\",'ECM Summary'!I16)","v":"No"},{"$f":"'ECM Summary'!J16","v":""},{"$f":"'ECM Summary'!K16","v":""},{"$f":"'ECM Summary'!L16","v":""},{"$f":"'ECM Summary'!M16","v":""},{"$f":"'ECM Summary'!N16","v":""},{"$f":"'ECM Summary'!O16","v":""},{"$f":"'ECM Summary'!P16","v":""},{"$f":"'ECM Summary'!R16","v":""},{"$f":"'ECM Summary'!S16","v":""},{"$f":"'ECM Summary'!T16","v":""},{"$f":"'ECM Summary'!U16","v":""},{"$f":"'ECM Summary'!V16","v":""},{"$f":"'ECM Summary'!X16","v":""}]
[{"$f":"'ECM Summary'!D17","v":""},{"$f":"'ECM Summary'!E17","v":"Demand Control Ventilation"},null,null,null,{"$f":"IF('ECM Summary'!I17=\"\",\"\",'ECM Summary'!I17)","v":"No"},{"$f":"'ECM Summary'!J17","v":""},{"$f":"'ECM Summary'!K17","v":""},{"$f":"'ECM Summary'!L17","v":""},{"$f":"'ECM Summary'!M17","v":""},{"$f":"'ECM Summary'!N17","v":""},{"$f":"'ECM Summary'!O17","v":""},{"$f":"'ECM Summary'!P17","v":""},{"$f":"'ECM Summary'!R17","v":""},{"$f":"'ECM Summary'!S17","v":""},{"$f":"'ECM Summary'!T17","v":""},{"$f":"'ECM Summary'!U17","v":""},{"$f":"'ECM Summary'!V17","v":""},{"$f":"'ECM Summary'!X17","v":""}]
[{"$f":"'ECM Summary'!D18","v":""},{"$f":"'ECM Summary'!E18","v":"Variable Flow Kitchen Hood"},null,null,null,{"$f":"IF('ECM Summary'!I18=\"\",\"\",'ECM Summary'!I18)","v":"No"},{"$f":"'ECM Summary'!J18","v":""},{"$f":"'ECM Summary'!K18","v":""},{"$f":"'ECM Summary'!L18","v":""},{"$f":"'ECM Summary'!M18","v":""},{"$f":"'ECM Summary'!N18","v":""},{"$f":"'ECM Summary'!O18","v":""},{"$f":"'ECM Summary'!P18","v":""},{"$f":"'ECM Summary'!R18","v":""},{"$f":"'ECM Summary'!S18","v":""},{"$f":"'ECM Summary'!T18","v":""},{"$f":"'ECM Summary'!U18","v":""},{"$f":"'ECM Summary'!V18","v":""},{"$f":"'ECM Summary'!X18","v":""}]
[{"$f":"'ECM Summary'!D19","v":""},{"$f":"'ECM Summary'!E19","v":"Condensing Boilers"},null,null,null,{"$f":"IF('ECM Summary'!I19=\"\",\"\",'ECM Summary'!I19)","v":"No"},{"$f":"'ECM Summary'!J19","v":""},{"$f":"'ECM Summary'!K19","v":""},{"$f":"'ECM Summary'!L19","v":""},{"$f":"'ECM Summary'!M19","v":""},{"$f":"'ECM Summary'!N19","v":""},{"$f":"'ECM Summary'!O19","v":""},{"$f":"'ECM Summary'!P19","v":""},{"$f":"'ECM Summary'!R19","v":""},{"$f":"'ECM Summary'!S19","v":""},{"$f":"'ECM Summary'!T19","v":""},{"$f":"'ECM Summary'!U19","v":""},{"$f":"'ECM Summary'!V19","v":""},{"$f":"'ECM Summary'!X19","v":""}]
[{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},null,null,null,{"$f":"IF('ECM Summary'!#REF!=\"\",\"\",'ECM Summary'!#REF!)","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}}]
[{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},null,null,null,{"$f":"IF('ECM Summary'!#REF!=\"\",\"\",'ECM Summary'!#REF!)","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}}]
[{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},null,null,null,{"$f":"IF('ECM Summary'!#REF!=\"\",\"\",'ECM Summary'!#REF!)","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}}]
[{"$f":"'ECM Summary'!D20","v":""},{"$f":"'ECM Summary'!E20","v":"DHW Heaters"},null,null,null,{"$f":"IF('ECM Summary'!I20=\"\",\"\",'ECM Summary'!I20)","v":"No"},{"$f":"'ECM Summary'!J20","v":""},{"$f":"'ECM Summary'!K20","v":""},{"$f":"'ECM Summary'!L20","v":""},{"$f":"'ECM Summary'!M20","v":""},{"$f":"'ECM Summary'!N20","v":""},{"$f":"'ECM Summary'!O20","v":""},{"$f":"'ECM Summary'!P20","v":""},{"$f":"'ECM Summary'!R20","v":""},{"$f":"'ECM Summary'!S20","v":""},{"$f":"'ECM Summary'!T20","v":""},{"$f":"'ECM Summary'!U20","v":""},{"$f":"'ECM Summary'!V20","v":""},{"$f":"'ECM Summary'!X20","v":""}]
[{"$f":"'ECM Summary'!D21","v":""},{"$f":"'ECM Summary'!E21","v":"Low Flow DHW Fixtures"},null,null,null,{"$f":"IF('ECM Summary'!I21=\"\",\"\",'ECM Summary'!I21)","v":"No"},{"$f":"'ECM Summary'!J21","v":""},{"$f":"'ECM Summary'!K21","v":""},{"$f":"'ECM Summary'!L21","v":""},{"$f":"'ECM Summary'!M21","v":""},{"$f":"'ECM Summary'!N21","v":""},{"$f":"'ECM Summary'!O21","v":""},{"$f":"'ECM Summary'!P21","v":""},{"$f":"'ECM Summary'!R21","v":""},{"$f":"'ECM Summary'!S21","v":""},{"$f":"'ECM Summary'!T21","v":""},{"$f":"'ECM Summary'!U21","v":""},{"$f":"'ECM Summary'!V21","v":""},{"$f":"'ECM Summary'!X21","v":""}]
[{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},null,null,null,{"$f":"IF('ECM Summary'!#REF!=\"\",\"\",'ECM Summary'!#REF!)","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}},{"$f":"'ECM Summary'!#REF!","v":{"$error":"#REF!"}}]
[{"$f":"'ECM Summary'!D22","v":""},{"$f":"'ECM Summary'!E22","v":0},null,null,null,{"$f":"IF('ECM Summary'!I22=\"\",\"\",'ECM Summary'!I22)","v":""},{"$f":"'ECM Summary'!J22","v":""},{"$f":"'ECM Summary'!K22","v":""},{"$f":"'ECM Summary'!L22","v":""},{"$f":"'ECM Summary'!M22","v":""},{"$f":"'ECM Summary'!N22","v":""},{"$f":"'ECM Summary'!O22","v":""},{"$f":"'ECM Summary'!P22","v":""},{"$f":"'ECM Summary'!R22","v":""},{"$f":"'ECM Summary'!S22","v":""},{"$f":"'ECM Summary'!T22","v":""},{"$f":"'ECM Summary'!U22","v":""},{"$f":"'ECM Summary'!V22","v":""},{"$f":"'ECM Summary'!X22","v":""}]
[{"$f":"'ECM Summary'!D23","v":""},{"$f":"'ECM Summary'!E23","v":0},null,null,null,{"$f":"IF('ECM Summary'!I23=\"\",\"\",'ECM Summary'!I23)","v":""},{"$f":"'ECM Summary'!J23","v":""},{"$f":"'ECM Summary'!K23","v":""},{"$f":"'ECM Summary'!L23","v":""},{"$f":"'ECM Summary'!M23","v":""},{"$f":"'ECM Summary'!N23","v":""},{"$f":"'ECM Summary'!O23","v":""},{"$f":"'ECM Summary'!P23","v":""},{"$f":"'ECM Summary'!R23","v":""},{"$f":"'ECM Summary'!S23","v":""},{"$f":"'ECM Summary'!T23","v":""},{"$f":"'ECM Summary'!U23","v":""},{"$f":"'ECM Summary'!V23","v":""},{"$f":"'ECM Summary'!X23","v":""}]
[{"$f":"'ECM Summary'!D24","v":""},{"$f":"'ECM Summary'!E24","v":0},null,null,null,{"$f":"IF('ECM Summary'!I24=\"\",\"\",'ECM Summary'!I24)","v":""},{"$f":"'ECM Summary'!J24","v":""},{"$f":"'ECM Summary'!K24","v":""},{"$f":"'ECM Summary'!L24","v":""},{"$f":"'ECM Summary'!M24","v":""},{"$f":"'ECM Summary'!N24","v":""},{"$f":"'ECM Summary'!O24","v":""},{"$f":"'ECM Summary'!P24","v":""},{"$f":"'ECM Summary'!R24","v":""},{"$f":"'ECM Summary'!S24","v":""},{"$f":"'ECM Summary'!T24","v":""},{"$f":"'ECM Summary'!U24","v":""},{"$f":"'ECM Summary'!V24","v":""},{"$f":"'ECM Summary'!X24","v":""}]
[{"$f":"'ECM Summary'!D25","v":""},{"$f":"'ECM Summary'!E25","v":0},null,null,null,{"$f":"IF('ECM Summary'!I25=\"\",\"\",'ECM Summary'!I25)","v":""},{"$f":"'ECM Summary'!J25","v":""},{"$f":"'ECM Summary'!K25","v":""},{"$f":"'ECM Summary'!L25","v":""},{"$f":"'ECM Summary'!M25","v":""},{"$f":"'ECM Summary'!N25","v":""},{"$f":"'ECM Summary'!O25","v":""},{"$f":"'ECM Summary'!P25","v":""},{"$f":"'ECM Summary'!R25","v":""},{"$f":"'ECM Summary'!S25","v":""},{"$f":"'ECM Summary'!T25","v":""},{"$f":"'ECM Summary'!U25","v":""},{"$f":"'ECM Summary'!V25","v":""},{"$f":"'ECM Summary'!X25","v":""}]
[{"$f":"'ECM Summary'!D26","v":"TOTAL"},null,null,null,null,{"$f":"IF('ECM Summary'!I26=\"\",\"\",'ECM Summary'!I26)","v":""},{"$f":"'ECM Summary'!J26","v":0},{"$f":"'ECM Summary'!K26","v":0},{"$f":"'ECM Summary'!L26","v":0},{"$f":"'ECM Summary'!M26","v":{"$error":"#DIV/0!"}},{"$f":"'ECM Summary'!N26","v":0},{"$f":"'ECM Summary'!O26","v":0},{"$f":"'ECM Summary'!P26","v":0},{"$f":"'ECM Summary'!R26","v":0},{"$f":"'ECM Summary'!S26","v":0},{"$f":"'ECM Summary'!T26","v":0},{"$f":"'ECM Summary'!U26","v":0},{"$f":"'ECM Summary'!V26","v":{"$error":"#DIV/0!"}},{"$f":"'ECM Summary'!X26","v":0}]
[]
[]
[null,null,null,null,null,null,null,"Custom Incentive Rates"]
[null,null,null,null,null,null,null,"Elec","Gas","Purch Fuel"]
[null,null,null,null,null,null,"Program","$/kWh","$/Therm","$/MMBTU"]
[null,null,null,null,null,null,{"$f":"'Project Info'!AB102","v":"High Performance Buildings"},0.4,2,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!AB103","v":"Systems Pathway"},0.28000000000000003,1.5,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!AB104","v":"Other/NA"},0.28000000000000003,1.5,0]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"Measure Types by Fuel Savings Type"]
["Program","Dual","Electric","Gas",null,null,"Measure","MeasureLife"]
["Custom","Building Shell","Building Shell","Boiler, HVAC",null,null,"Boiler, HVAC",20]
["Prescriptive","HVAC Equipment and Systems","Chillers","Boiler, non-HVAC",null,null,"Boiler, non-HVAC",20]
[null,"EMS / controls, HVAC","Combined Heat & Power","Building Shell",null,null,"Building Shell",25]
[null,"EMS / controls, non-HVAC","Compressed Air Equipment and Systems","EMS / controls, HVAC",null,null,"Chillers",20]
[null,"Equipment Insulation, HVAC","HVAC Equipment and Systems","EMS / controls, non-HVAC",null,null,"Combined Heat & Power",20]
[null,"Equipment Insulation, non-HVAC","Cooling Equipment","Equipment Insulation, HVAC",null,null,"Compressed Air Equipment and Systems",15]
[null,"Food Service ","EMS / controls, HVAC","Equipment Insulation, non-HVAC",null,null,"Cooling Equipment",15]
[null,"Heat recovery, HVAC","Food Service ","Food Service ",null,null,"EMS / controls, HVAC",10]
[null,"Heat recovery, non-HVAC","Fuel switching, HVAC","Fuel switching, HVAC",null,null,"EMS / controls, non-HVAC",10]
[null,"Other","Fuel switching, non-HVAC","Fuel switching, non-HVAC",null,null,"Equipment Insulation, HVAC",15]
[null,"Process Equipment","Lighting - Exterior","Furnace, HVAC",null,null,"Equipment Insulation, non-HVAC",15]
[null,"Process Equipment and Controls","Lighting - Exterior Controls","Furnace, non-HVAC",null,null,"Food Service ",15]
[null,null,"Lighting - Exterior with Controls","Heat recovery, HVAC",null,null,"Fuel switching, HVAC",15]
[null,null,"Lighting - Interior","Heat recovery, non-HVAC",null,null,"Fuel switching, non-HVAC",15]
[null,null,"Lighting - Interior Controls","Other, HVAC",null,null,"Furnace, HVAC",15]
[null,null,"Lighting - Interior with Controls","Other, non-HVAC",null,null,"Furnace, non-HVAC",15]
[null,null,"Other","Process Equipment",null,null,"Heat recovery, HVAC",15]
[null,null,"Process Equipment","Process Equipment and Controls",null,null,"Heat recovery, non-HVAC",15]
[null,null,"Process Equipment and Controls","Water heating, DHW",null,null,"HVAC Equipment and Systems",15]
[null,null,"Refrigeration, Commercial",null,null,null,"Lighting - Exterior",15]
[null,null,"Refrigeration, Industrial",null,null,null,"Lighting - Exterior Controls",10]
[null,null,"VFD on HVAC Equipment",null,null,null,"Lighting - Exterior with Controls",15]
[null,null,"VFD on non-HVAC Equipment",null,null,null,"Lighting - Interior",15]
[null,null,null,null,null,null,"Lighting - Interior Controls",10]
[null,null,null,null,null,null,"Lighting - Interior with Controls",15]
[null,null,null,null,null,null,"Other",15]
[null,null,null,null,null,null,"Other, HVAC",15]
[null,null,null,null,null,null,"Other, non-HVAC",15]
[null,null,null,null,null,null,"Process Equipment",15]
[null,null,null,null,null,null,"Process Equipment and Controls",15]
[null,null,null,null,null,null,"Refrigeration, Commercial",15]
[null,null,null,null,null,null,"Refrigeration, Industrial",20]
[null,null,null,null,null,null,"VFD on HVAC Equipment",15]
[null,null,null,null,null,null,"VFD on non-HVAC Equipment",15]
[null,null,null,null,null,null,"Water heating, DHW",15]

{"sheet":"Workspace","index":7,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Bldg Envelope","index":8,"n_rows":165,"n_cols":48,"rows_kept":165,"cut":false,"hidden":true,"merged":[[1,19,11,27],[153,7,153,9],[154,7,154,9],[38,7,38,9],[20,7,20,9],[21,7,21,9],[22,7,22,9],[28,7,28,9],[29,7,29,9],[30,7,30,9],[36,7,36,9],[37,7,37,9],[1,10,6,17],[155,7,155,9],[139,7,139,9],[140,7,140,9],[141,7,141,9],[146,7,146,9],[147,7,147,9],[148,7,148,9]]}
["Savings Summary",null,null,null,null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,null,null,"Notes (Optional)"]
["Annual kWh Savings",null,null,{"$f":"SUM(A14:D14)","v":{"$error":"#DIV/0!"}},null,null,null,"Value","Unit",null,"This measure considers savings from improved thermal performance of building envelope assemblies beyond the minimum requirements of the energy code.  Assemblies that could be considered in this measure include exterior walls, roofs, windows, and garage doors.\n\nNOTE: Table 3, 4, and 5 should be completed with all design information, even if the design does not exceed code (to account for any tradeoffs between assemblies)."]
["% On Peak",null,null,{"$f":"IF(D2<=0,0,MIN(1,A15+C15))","v":{"$error":"#DIV/0!"}},null,"Annual Electric Savings",null,{"$f":"D2","v":{"$error":"#DIV/0!"}},"kWh"]
["Max kW",null,null,{"$f":"MAX(AD52:AD75,AD82:AD105)","v":{"$error":"#DIV/0!"}},null,"Annual Fuel Savings",null,{"$f":"D7*C28","v":{"$error":"#DIV/0!"}},{"$f":"D20","v":{"$error":"#N/A"}}]
["Summer kW",null,null,{"$f":"(SUMPRODUCT(AD52:AD75,R52:R75)+SUMPRODUCT(AD82:AD105,R82:R105))/SUM(R52:R75,R82:R105)","v":{"$error":"#DIV/0!"}},null,"Incremental","Default Calc",{"$f":"$K$165","v":0},"$"]
["Winter kW",null,null,{"$f":"(SUMPRODUCT(AD52:AD75,Q52:Q75)+SUMPRODUCT(AD82:AD105,Q82:Q105))/SUM(Q52:Q75,Q82:Q105)","v":{"$error":"#DIV/0!"}},null,"Cost","Project Specific",null,"$ (Optional)"]
["Annual Fuel Savings (MMBtu)",null,null,{"$f":"(SUMPRODUCT($L$52:$L$75,AE52:AE75)+SUMPRODUCT($L$82:$L$105,AE82:AE105))/1000","v":{"$error":"#DIV/0!"}},null,"Estimated Incentive",null,{"$f":"IF(AND($C$24>=0,$C$25>=0),MAX(0,H3)*C24+MAX(0,H4)*C25,\"TBD\")","v":{"$error":"#DIV/0!"}},"$"]
["Incremental Cost (Default Calc)",null,null,{"$f":"$K$165","v":0}]
["Incremental Cost (for Summary)",null,null,{"$f":"IF(H6>0,H6,D8)","v":0},null,"Project Information Summary"]
["kWh Savings by Peak Period",null,null,null,null,null,"STATE",{"$f":"'Project Info'!C15","v":"NH"}]
["Winter","Winter","Summer","Summer",null,null,"Program Year",{"$f":"'Project Info'!C19","v":0}]
["On-Peak","Off-Peak","On-Peak","Off-Peak",null,null,"Code IECC Version",{"$f":"MID('Project Info'!C20,1,4)","v":"2018"},null,null,null,"**Climate Zone 6A only applies to certain NH locations."]
["kWh","kWh","kWh","kWh",null,null,"Electric PA",{"$f":"'Project Info'!F3","v":0},null,null,null,"The default zone for NH is 5A."]
[{"$f":"SUMPRODUCT($AD$52:$AD$75,M52:M75)+SUMPRODUCT($AD$82:$AD$105,M82:M105)","v":{"$error":"#DIV/0!"}},{"$f":"SUMPRODUCT($AD$52:$AD$75,N52:N75)+SUMPRODUCT($AD$82:$AD$105,N82:N105)","v":{"$error":"#DIV/0!"}},{"$f":"SUMPRODUCT($AD$52:$AD$75,O52:O75)+SUMPRODUCT($AD$82:$AD$105,O82:O105)","v":{"$error":"#DIV/0!"}},{"$f":"SUMPRODUCT($AD$52:$AD$75,P52:P75)+SUMPRODUCT($AD$82:$AD$105,P82:P105)","v":{"$error":"#DIV/0!"}},null,null,"Gas PA",{"$f":"'Project Info'!I3","v":0},null,null,null,null,"Set Climate Zone to 6A? (NH only, select \"Yes\" here to use Zone 6A.)"]
[{"$f":"ROUND(IF(A14<=0,0,A14/SUMIF($A$14:$D$14,\">0\")),2)","v":{"$error":"#DIV/0!"}},{"$f":"ROUND(IF(B14<=0,0,B14/SUMIF($A$14:$D$14,\">0\")),2)","v":{"$error":"#DIV/0!"}},{"$f":"ROUND(IF(C14<=0,0,C14/SUMIF($A$14:$D$14,\">0\")),2)","v":{"$error":"#DIV/0!"}},{"$f":"IF(SUM(A14:D14)=0,0,1-SUM(A15:C15))","v":{"$error":"#DIV/0!"}},null,"*NOTE: Baseline values are automated and cannot be changed."]
[]
["Utility Rates",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Climate Zone"]
[null,null,"Rate","Unit",null,null,"Table 3: Above Grade Opaque Wall Insulation",null,null,null,null,null,null,null,"(Optional)","5A","6A*",null,"Table 1: Heat & Cool Performance",null,null,null,"Base vs Design Envelope Performance Summary"]
["Electric",null,{"$f":"'ECM Summary'!$E$31","v":0.1593},"kWh",null,null,"Assembly","Assembly",null,null,"Area","Infill","c.i.","U-Value","Design","Baseline","Baseline",null,"Heating Fuel",null,null,null,null,null,"Total","Baseline","Proposed"]
[{"$f":"'ECM Summary'!$C$32","v":0},null,{"$f":"'ECM Summary'!$E$32","v":{"$error":"#N/A"}},{"$f":"'ECM Summary'!$F$32","v":{"$error":"#N/A"}},null,null,"No.","Type",null,null,"ft²","R-Value","R-Value","Btu/h·ft²·°F","U-Value","U-Value","U-Value",null,"Fossil Fuel Baseline Eff (%)",null,null,null,"Assembly",null,"Area","Average","Average"]
[null,null,null,null,null,null,1,null,null,null,null,null,null,{"$f":"IF(OR(H21=\"\",L21+M21=0),0,R140)","v":0},null,{"$f":"IF(OR(H21=\"\",AND(N21=0,O21=0)),0,LOOKUP(H21,$G$124:$G$127,IF($H$12=\"2015\",$I$124:$I$127,$J$124:$J$127)))","v":0},{"$f":"IF(OR(H21=\"\",AND(N21=0,O21=0)),0,LOOKUP(H21,$R$124:$R$127,IF($H$12=\"2015\",$T$124:$T$127,$U$124:$U$127)))","v":0},null,"Elec Heat Baseline COP",null,null,null,"Type",null,"ft²","U-Value","U-Value"]
["Custom Incentive Rates",null,null,null,null,null,2,null,null,null,null,null,null,{"$f":"IF(OR(H22=\"\",L22+M22=0),0,R141)","v":0},null,{"$f":"IF(OR(H22=\"\",AND(N22=0,O22=0)),0,LOOKUP(H22,$G$124:$G$127,IF($H$12=\"2015\",$I$124:$I$127,$J$124:$J$127)))","v":0},{"$f":"IF(OR(H22=\"\",AND(N22=0,O22=0)),0,LOOKUP(H22,$R$124:$R$127,IF($H$12=\"2015\",$T$124:$T$127,$U$124:$U$127)))","v":0},null,"Cooling Included?",null,null,null,"Opaque Walls",null,{"$f":"K24","v":0},{"$f":"IF(AND($H$10=\"NH\",$L$14=$G$108),Q24,P24)","v":0},{"$f":"N24","v":0}]
[null,null,"Rate","Unit",null,null,3,null,null,null,null,null,null,{"$f":"IF(OR(H23=\"\",L23+M23=0),0,R142)","v":0},null,{"$f":"IF(OR(H23=\"\",AND(N23=0,O23=0)),0,LOOKUP(H23,$G$124:$G$127,IF($H$12=\"2015\",$I$124:$I$127,$J$124:$J$127)))","v":0},0,null,"Cooling Baseline IEER or IPLV",null,null,null,"Roofs",null,{"$f":"K32","v":0},{"$f":"IF(AND($H$10=\"NH\",$L$14=$G$108),Q32,P32)","v":0},{"$f":"N32","v":0}]
["Electric",null,{"$f":"'ECM Summary'!$J$31","v":0.28000000000000003},"kWh",null,null,"Overall","Overall Performance",null,null,{"$f":"(H21<>\"\")*K21+(H22<>\"\")*K22+(H23<>\"\")*K23","v":0},null,null,{"$f":"IF(K24=0,0,((H21<>\"\")*K21*IF(O21=\"\",N21,O21)+(H22<>\"\")*K22*IF(O22=\"\",N22,O22)+(H23<>\"\")*K23*IF(O23=\"\",N23,O23))/K24)","v":0},null,{"$f":"IF(K24=0,0,((H21<>\"\")*K21*P21+(H22<>\"\")*K22*P22+(H23<>\"\")*K23*P23)/K24)","v":0},{"$f":"IF(K24=0,0,((H21<>\"\")*K21*Q21+(H22<>\"\")*K22*Q22+(H23<>\"\")*K23*Q23)/K24)","v":0},null,null,null,null,null,"Windows",null,{"$f":"K40","v":0},{"$f":"IF(AND($H$10=\"NH\",$L$14=$G$108),V40,T40)","v":0},{"$f":"P40","v":0}]
[{"$f":"'ECM Summary'!$H$32","v":0},null,{"$f":"'ECM Summary'!$J$32","v":0},{"$f":"'ECM Summary'!$K$32","v":{"$error":"#N/A"}},null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 2: Space Temp Setpoints",null,null,null,"Garage Doors",null,{"$f":"G45","v":0},{"$f":"IF(AND($H$10=\"NH\",$L$14=$G$108),J45,I45)","v":0},{"$f":"H45","v":0}]
[null,null,null,null,null,null,"Table 4: Exterior Roof Insulation",null,null,null,null,null,null,null,"(Optional)","5A","6A*",null,null,"Occ","Unocc",null,"\"UA\" Value (BTU/h·°F)",null,null,{"$f":"SUMPRODUCT($Y$22:$Y$25,Z22:Z25)","v":0},{"$f":"SUMPRODUCT($Y$22:$Y$25,AA22:AA25)","v":0}]
["Fossil Fuel",null,{"$f":"'Project Info'!C21","v":0},null,null,null,"Assembly","Assembly",null,null,"Area","Infill","c.i.","U-Value","Design","Baseline","Baseline",null,"Cooling"]
["Fuel Conversion",null,{"$f":"LOOKUP(C27,'Project Info'!X102:X104,'Project Info'!Z102:Z104)","v":{"$error":"#N/A"}},null,null,null,"No.","Type",null,null,"ft²","R-Value","R-Value","Btu/h·ft²·°F","U-Value","U-Value","U-Value",null,"Heating"]
[null,null,null,null,null,null,1,null,null,null,null,null,null,{"$f":"IF(OR(H29=\"\",L29+M29=0),0,R147)","v":0},null,{"$f":"IF(OR(H29=\"\",AND(N29=0,O29=0)),0,LOOKUP(H29,$G$117:$G$119,IF($H$12=\"2015\",$I$117:$I$119,$J$117:$J$119)))","v":0},{"$f":"IF(OR(H29=\"\",AND(N29=0,O29=0)),0,LOOKUP(H29,$R$117:$R$119,IF($H$12=\"2015\",$T$117:$T$119,$U$117:$U$119)))","v":0}]
[null,null,null,null,null,null,2,null,null,null,null,null,null,{"$f":"IF(OR(H30=\"\",L30+M30=0),0,R148)","v":0},null,{"$f":"IF(OR(H30=\"\",AND(N30=0,O30=0)),0,LOOKUP(H30,$G$117:$G$119,IF($H$12=\"2015\",$I$117:$I$119,$J$117:$J$119)))","v":0},{"$f":"IF(OR(H30=\"\",AND(N30=0,O30=0)),0,LOOKUP(H30,$R$117:$R$119,IF($H$12=\"2015\",$T$117:$T$119,$U$117:$U$119)))","v":0}]
[null,null,null,null,null,null,3,null,null,null,null,null,null,{"$f":"IF(OR(H31=\"\",L31+M31=0),0,R149)","v":0},null,{"$f":"IF(OR(H31=\"\",AND(N31=0,O31=0)),0,LOOKUP(H31,$G$117:$G$119,IF($H$12=\"2015\",$I$117:$I$119,$J$117:$J$119)))","v":0},0]
[null,null,null,null,null,null,"Overall","Overall Performance",null,null,{"$f":"(H29<>\"\")*K29+(H30<>\"\")*K30+(H31<>\"\")*K31","v":0},null,null,{"$f":"IF(K32=0,0,((H29<>\"\")*K29*IF(O29=\"\",N29,O29)+(H30<>\"\")*K30*IF(O30=\"\",N30,O30)+(H31<>\"\")*K31*IF(O31=\"\",N31,O31))/K32)","v":0},null,{"$f":"IF(K32=0,0,((H29<>\"\")*K29*P29+(H30<>\"\")*K30*P30+(H31<>\"\")*K31*P31)/K32)","v":0},{"$f":"IF(K32=0,0,((H29<>\"\")*K29*Q29+(H30<>\"\")*K30*Q30+(H31<>\"\")*K31*Q31)/K32)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Climate Zone"]
[null,null,null,null,null,null,"Table 5: Exterior Windows",null,null,null,null,null,null,null,null,null,null,"(Optional) Override",null,"5A",null,"6A*"]
[null,null,null,null,null,null,"Assembly","Frame",null,null,"Area","% Area","% Area","Center-of Glass",null,"Glass + Frame",null,"Glass + Frame",null,"Baseline Glass+Frame",null,"Baseline Glass+Frame"]
[null,null,null,null,null,null,"No.","Material",null,null,"ft²","Operable","Fixed","U-Value","SHGC","U-Value","SHGC","U-Value","SHGC","U-Value","SHGC","U-Value","SHGC"]
[null,null,null,null,null,null,1,null,null,null,null,null,{"$f":"IF(L37=\"\",$Q$108,1-L37)","v":0.85},null,null,{"$f":"IF(OR($H37=\"\",N37=0),0,IF(N37=\"\",T37,X154))","v":0},{"$f":"IF($H37=\"\",0,IF(O37=\"\",U37,Y154))","v":0},null,null,{"$f":"IF(OR(H37=\"\",AND(N37=0,R37=0)),0,$O$124*M37+$O$125*(1-M37))","v":0},{"$f":"IF(H37=\"\",0,IF($H$12=\"2015\",$O$129,$P$129))","v":0},{"$f":"IF(OR(H37=\"\",AND(N37=0,R37=0)),0,$Z$124*M37+$Z$125*(1-M37))","v":0},{"$f":"IF(H37=\"\",0,IF($H$12=\"2015\",$Z$129,$AA$129))","v":0}]
[null,null,null,null,null,null,2,null,null,null,null,null,{"$f":"IF(L38=\"\",$Q$108,1-L38)","v":0.85},null,null,{"$f":"IF(OR($H38=\"\",N38=0),0,IF(N38=\"\",T38,X155))","v":0},{"$f":"IF($H38=\"\",0,IF(O38=\"\",U38,Y155))","v":0},null,null,{"$f":"IF(OR(H38=\"\",AND(N38=0,R38=0)),0,$O$124*M38+$O$125*(1-M38))","v":0},{"$f":"IF(H38=\"\",0,IF($H$12=\"2015\",$O$129,$P$129))","v":0},{"$f":"IF(OR(H38=\"\",AND(N38=0,R38=0)),0,$Z$124*M38+$Z$125*(1-M38))","v":0},{"$f":"IF(H38=\"\",0,IF($H$12=\"2015\",$Z$129,$AA$129))","v":0}]
[null,null,null,null,null,null,3,null,null,null,null,null,{"$f":"IF(L39=\"\",$Q$108,1-L39)","v":0.85},null,null,{"$f":"IF(OR($H39=\"\",N39=0),0,IF(N39=\"\",T39,X156))","v":0},{"$f":"IF($H39=\"\",0,IF(O39=\"\",U39,Y156))","v":0},null,null,{"$f":"IF(OR(H39=\"\",AND(N39=0,R39=0)),0,$O$124*M39+$O$125*(1-M39))","v":0},{"$f":"IF(H39=\"\",0,IF($H$12=\"2015\",$O$129,$P$129))","v":0},0,0]
[null,null,null,null,null,null,"Overall","Overall Performance",null,null,{"$f":"(H37<>\"\")*K37+(H38<>\"\")*K38+(H39<>\"\")*K39","v":0},{"$f":"(1-M40)*(K40>0)","v":0},{"$f":"IF(K40=0,0,((H37<>\"\")*K37*M37+(H38<>\"\")*K38*M38+(H39<>\"\")*K39*M39)/K40)","v":0},null,null,{"$f":"IF(K40=0,0,(($H37<>\"\")*$K37*IF(R37=\"\",P37,R37)+($H38<>\"\")*$K38*IF(R38=\"\",P38,R38)+($H39<>\"\")*$K39*IF(R39=\"\",P39,R39))/$K40)","v":0},{"$f":"IF(K40=0,0,(($H37<>\"\")*$K37*IF(S37=\"\",Q37,S37)+($H38<>\"\")*$K38*IF(S38=\"\",Q38,S38)+($H39<>\"\")*$K39*IF(S39=\"\",Q39,S39))/$K40)","v":0},null,null,{"$f":"IF(K40=0,0,(($H37<>\"\")*$K37*T37+($H38<>\"\")*$K38*T38+($H39<>\"\")*$K39*T39)/$K40)","v":0},{"$f":"IF(K40=0,0,(($H37<>\"\")*$K37*U37+($H38<>\"\")*$K38*U38+($H39<>\"\")*$K39*U39)/$K40)","v":0},{"$f":"IF(K40=0,0,(($H37<>\"\")*$K37*V37+($H38<>\"\")*$K38*V38+($H39<>\"\")*$K39*V39)/$K40)","v":0},{"$f":"IF(K40=0,0,(($H37<>\"\")*$K37*W37+($H38<>\"\")*$K38*W38+($H39<>\"\")*$K39*W39)/$K40)","v":0}]
[]
[null,null,null,null,null,null,"Table 6: Garage Doors",null,"5A","6A*"]
[null,null,null,null,null,null,"Door Area","Overall","Baseline","Baseline"]
[null,null,null,null,null,null,"ft²","U-Value","U-Value","U-Value"]
[null,null,null,null,null,null,null,null,{"$f":"0.31*(G45>0)*(H45>0)","v":0},{"$f":"0.31*(G45>0)*(H45>0)","v":0}]
[]
[]
[null,null,null,null,null,null,"Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"End Use",null,null,"Total"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Perimeter","Perimeter","Cooling","Heating","Ext. Wall Heat Gain",null,"Load Reduction",null,"Demand Reduction",null,null,"Demand Reduction"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Cooling","Heating","Perf","Perf","Base","Design","Cooling","Heating","Cooling","Heating","Heating","Elec","Gas"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","Load?","Load?","EER","COP","MBH","MBH","MBH","MBH","kW","MBH","kW","kW","MBH"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A44","v":100},{"$f":"'Project Info'!B44","v":105},{"$f":"'Project Info'!C44","v":102},{"$f":"'Project Info'!D44","v":76},{"$f":"'Project Info'!E44","v":40},{"$f":"'Project Info'!F44","v":0},{"$f":"'Project Info'!G44","v":0},{"$f":"'Project Info'!H44","v":0},{"$f":"'Project Info'!I44","v":0},{"$f":"'Project Info'!J44","v":0},{"$f":"'Project Info'!K44","v":0},{"$f":"'Project Info'!L44","v":0},{"$f":"1*($I52>$L$110)*(T52=0)*($U$22=$G$108)","v":0},{"$f":"1*($I52<$L$111)","v":0},{"$f":"IF($U$22=$G$108,$U$23,1)","v":1},{"$f":"IF($U$19=$H$109,$U$21,$U$20)","v":0},{"$f":"($Z$22*$Y$22+$Z$23*$Y$23+$Z$24*$Y$24+$Z$25*$Y$25)*(($S52>0)*($I52-$T$27)+($T52>0)*($I52-$T$28))/1000","v":0},{"$f":"($N$24*$K$24+$N$32*$K$32+$P$40*$K$40+$H$45*$G$45)*(($S52>0)*($I52-$T$27)+($T52>0)*($I52-$T$28))/1000","v":0},{"$f":"(W52-X52)*(S52>0)","v":0},{"$f":"-1*(W52-X52)*(T52>0)","v":0},{"$f":"Y52/U52","v":0},{"$f":"Z52/V52*($U$19<>\"Electric\")","v":{"$error":"#DIV/0!"}},{"$f":"Z52/V52/3.412*($U$19=\"Electric\")","v":{"$error":"#DIV/0!"}},{"$f":"AA52+AC52","v":{"$error":"#DIV/0!"}},{"$f":"AB52","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A45","v":95},{"$f":"'Project Info'!B45","v":100},{"$f":"'Project Info'!C45","v":95.219272727272724},{"$f":"'Project Info'!D45","v":74.534025272781079},{"$f":"'Project Info'!E45","v":37.923296058061368},{"$f":"'Project Info'!F45","v":0},{"$f":"'Project Info'!G45","v":0},{"$f":"'Project Info'!H45","v":0},{"$f":"'Project Info'!I45","v":0},{"$f":"'Project Info'!J45","v":0},{"$f":"'Project Info'!K45","v":0},{"$f":"'Project Info'!L45","v":0},0,0,1,0,{"$f":"($Z$22*$Y$22+$Z$23*$Y$23+$Z$24*$Y$24+$Z$25*$Y$25)*(($S53>0)*($I53-$T$27)+($T53>0)*($I53-$T$28))/1000","v":0},0,0,{"$f":"-1*(W53-X53)*(T53>0)","v":0},{"$f":"Y53/U53","v":0},{"$f":"Z53/V53*($U$19<>\"Electric\")","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"},{"$f":"AA53+AC53","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A46","v":90},{"$f":"'Project Info'!B46","v":95},{"$f":"'Project Info'!C46","v":92.016049160256074},{"$f":"'Project Info'!D46","v":72.911561930607689},{"$f":"'Project Info'!E46","v":36.467095439351091},{"$f":"'Project Info'!F46","v":0},{"$f":"'Project Info'!G46","v":0},{"$f":"'Project Info'!H46","v":0},{"$f":"'Project Info'!I46","v":0},{"$f":"'Project Info'!J46","v":0},{"$f":"'Project Info'!K46","v":0},{"$f":"'Project Info'!L46","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A47","v":85},{"$f":"'Project Info'!B47","v":90},{"$f":"'Project Info'!C47","v":87.457811360655285},{"$f":"'Project Info'!D47","v":70.80538329449476},{"$f":"'Project Info'!E47","v":34.679413213566804},{"$f":"'Project Info'!F47","v":0},{"$f":"'Project Info'!G47","v":0},{"$f":"'Project Info'!H47","v":0},{"$f":"'Project Info'!I47","v":0},{"$f":"'Project Info'!J47","v":0},{"$f":"'Project Info'!K47","v":0},{"$f":"'Project Info'!L47","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A48","v":80},{"$f":"'Project Info'!B48","v":85},{"$f":"'Project Info'!C48","v":82.136788830239965},{"$f":"'Project Info'!D48","v":67.872393622439333},{"$f":"'Project Info'!E48","v":32.296248223809314},{"$f":"'Project Info'!F48","v":0},{"$f":"'Project Info'!G48","v":0},{"$f":"'Project Info'!H48","v":0},{"$f":"'Project Info'!I48","v":0},{"$f":"'Project Info'!J48","v":0},{"$f":"'Project Info'!K48","v":0},{"$f":"'Project Info'!L48","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A49","v":75},{"$f":"'Project Info'!B49","v":80},{"$f":"'Project Info'!C49","v":76.988400157585886},{"$f":"'Project Info'!D49","v":65.129261896908645},{"$f":"'Project Info'!E49","v":30.190476812806729},{"$f":"'Project Info'!F49","v":0},{"$f":"'Project Info'!G49","v":0},{"$f":"'Project Info'!H49","v":0},{"$f":"'Project Info'!I49","v":0},{"$f":"'Project Info'!J49","v":0},{"$f":"'Project Info'!K49","v":0},{"$f":"'Project Info'!L49","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A50","v":70},{"$f":"'Project Info'!B50","v":75},{"$f":"'Project Info'!C50","v":72.457982050814195},{"$f":"'Project Info'!D50","v":63.604425012889301},{"$f":"'Project Info'!E50","v":29.088683095945193},{"$f":"'Project Info'!F50","v":0},{"$f":"'Project Info'!G50","v":0},{"$f":"'Project Info'!H50","v":0},{"$f":"'Project Info'!I50","v":0},{"$f":"'Project Info'!J50","v":0},{"$f":"'Project Info'!K50","v":0},{"$f":"'Project Info'!L50","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A51","v":65},{"$f":"'Project Info'!B51","v":70},{"$f":"'Project Info'!C51","v":67.815831070966169},{"$f":"'Project Info'!D51","v":61.631331368130574},{"$f":"'Project Info'!E51","v":27.661514889731574},{"$f":"'Project Info'!F51","v":0},{"$f":"'Project Info'!G51","v":0},{"$f":"'Project Info'!H51","v":0},{"$f":"'Project Info'!I51","v":0},{"$f":"'Project Info'!J51","v":0},{"$f":"'Project Info'!K51","v":0},{"$f":"'Project Info'!L51","v":0},0,0,1,0,0,0,{"$f":"(W59-X59)*(S59>0)","v":0},{"$f":"-1*(W59-X59)*(T59>0)","v":0},0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A52","v":60},{"$f":"'Project Info'!B52","v":65},{"$f":"'Project Info'!C52","v":62.535961472271332},{"$f":"'Project Info'!D52","v":57.135476922863582},{"$f":"'Project Info'!E52","v":24.623037157728302},{"$f":"'Project Info'!F52","v":0},{"$f":"'Project Info'!G52","v":0},{"$f":"'Project Info'!H52","v":0},{"$f":"'Project Info'!I52","v":0},{"$f":"'Project Info'!J52","v":0},{"$f":"'Project Info'!K52","v":0},{"$f":"'Project Info'!L52","v":0},0,0,1,0,0,0,{"$f":"(W60-X60)*(S60>0)","v":0},{"$f":"-1*(W60-X60)*(T60>0)","v":0},0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A53","v":55},{"$f":"'Project Info'!B53","v":60},{"$f":"'Project Info'!C53","v":57.125792270740902},{"$f":"'Project Info'!D53","v":52.596971157053673},{"$f":"'Project Info'!E53","v":21.818001539159841},{"$f":"'Project Info'!F53","v":0},{"$f":"'Project Info'!G53","v":0},{"$f":"'Project Info'!H53","v":0},{"$f":"'Project Info'!I53","v":0},{"$f":"'Project Info'!J53","v":0},{"$f":"'Project Info'!K53","v":0},{"$f":"'Project Info'!L53","v":0},0,0,1,0,0,0,{"$f":"(W61-X61)*(S61>0)","v":0},{"$f":"-1*(W61-X61)*(T61>0)","v":0},0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A54","v":50},{"$f":"'Project Info'!B54","v":55},{"$f":"'Project Info'!C54","v":52.235698854337961},{"$f":"'Project Info'!D54","v":48.022768090099298},{"$f":"'Project Info'!E54","v":19.246640192796217},{"$f":"'Project Info'!F54","v":0},{"$f":"'Project Info'!G54","v":0},{"$f":"'Project Info'!H54","v":0},{"$f":"'Project Info'!I54","v":0},{"$f":"'Project Info'!J54","v":0},{"$f":"'Project Info'!K54","v":0},{"$f":"'Project Info'!L54","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A55","v":45},{"$f":"'Project Info'!B55","v":50},{"$f":"'Project Info'!C55","v":47.459170258371508},{"$f":"'Project Info'!D55","v":43.465397050422162},{"$f":"'Project Info'!E55","v":16.894183241713304},{"$f":"'Project Info'!F55","v":0},{"$f":"'Project Info'!G55","v":0},{"$f":"'Project Info'!H55","v":0},{"$f":"'Project Info'!I55","v":0},{"$f":"'Project Info'!J55","v":0},{"$f":"'Project Info'!K55","v":0},{"$f":"'Project Info'!L55","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A56","v":40},{"$f":"'Project Info'!B56","v":45},{"$f":"'Project Info'!C56","v":42.677030404888129},{"$f":"'Project Info'!D56","v":38.812544504634097},{"$f":"'Project Info'!E56","v":14.690265649465921},{"$f":"'Project Info'!F56","v":0},{"$f":"'Project Info'!G56","v":0},{"$f":"'Project Info'!H56","v":0},{"$f":"'Project Info'!I56","v":0},{"$f":"'Project Info'!J56","v":0},{"$f":"'Project Info'!K56","v":0},{"$f":"'Project Info'!L56","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A57","v":35},{"$f":"'Project Info'!B57","v":40},{"$f":"'Project Info'!C57","v":37.333046773755832},{"$f":"'Project Info'!D57","v":33.904706919479686},{"$f":"'Project Info'!E57","v":12.53841602318813},{"$f":"'Project Info'!F57","v":0},{"$f":"'Project Info'!G57","v":0},{"$f":"'Project Info'!H57","v":0},{"$f":"'Project Info'!I57","v":0},{"$f":"'Project Info'!J57","v":0},{"$f":"'Project Info'!K57","v":0},{"$f":"'Project Info'!L57","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A58","v":30},{"$f":"'Project Info'!B58","v":35},{"$f":"'Project Info'!C58","v":32.638179845662044},{"$f":"'Project Info'!D58","v":29.547170928664851},{"$f":"'Project Info'!E58","v":10.728972818165861},{"$f":"'Project Info'!F58","v":0},{"$f":"'Project Info'!G58","v":0},{"$f":"'Project Info'!H58","v":0},{"$f":"'Project Info'!I58","v":0},{"$f":"'Project Info'!J58","v":0},{"$f":"'Project Info'!K58","v":0},{"$f":"'Project Info'!L58","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A59","v":25},{"$f":"'Project Info'!B59","v":30},{"$f":"'Project Info'!C59","v":27.529264646850947},{"$f":"'Project Info'!D59","v":24.652717392657845},{"$f":"'Project Info'!E59","v":8.8041305482613303},{"$f":"'Project Info'!F59","v":0},{"$f":"'Project Info'!G59","v":0},{"$f":"'Project Info'!H59","v":0},{"$f":"'Project Info'!I59","v":0},{"$f":"'Project Info'!J59","v":0},{"$f":"'Project Info'!K59","v":0},{"$f":"'Project Info'!L59","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A60","v":20},{"$f":"'Project Info'!B60","v":25},{"$f":"'Project Info'!C60","v":22.998111483544687},{"$f":"'Project Info'!D60","v":20.383306659827422},{"$f":"'Project Info'!E60","v":7.246164547543378},{"$f":"'Project Info'!F60","v":0},{"$f":"'Project Info'!G60","v":0},{"$f":"'Project Info'!H60","v":0},{"$f":"'Project Info'!I60","v":0},{"$f":"'Project Info'!J60","v":0},{"$f":"'Project Info'!K60","v":0},{"$f":"'Project Info'!L60","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A61","v":15},{"$f":"'Project Info'!B61","v":20},{"$f":"'Project Info'!C61","v":17.808510327474309},{"$f":"'Project Info'!D61","v":15.420865796304254},{"$f":"'Project Info'!E61","v":5.5490484131518292},{"$f":"'Project Info'!F61","v":0},{"$f":"'Project Info'!G61","v":0},{"$f":"'Project Info'!H61","v":0},{"$f":"'Project Info'!I61","v":0},{"$f":"'Project Info'!J61","v":0},{"$f":"'Project Info'!K61","v":0},{"$f":"'Project Info'!L61","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A62","v":10},{"$f":"'Project Info'!B62","v":15},{"$f":"'Project Info'!C62","v":12.269931130346862},{"$f":"'Project Info'!D62","v":10.318264913023604},{"$f":"'Project Info'!E62","v":3.9082824916941998},{"$f":"'Project Info'!F62","v":0},{"$f":"'Project Info'!G62","v":0},{"$f":"'Project Info'!H62","v":0},{"$f":"'Project Info'!I62","v":0},{"$f":"'Project Info'!J62","v":0},{"$f":"'Project Info'!K62","v":0},{"$f":"'Project Info'!L62","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A63","v":5},{"$f":"'Project Info'!B63","v":10},{"$f":"'Project Info'!C63","v":7.3137581369917548},{"$f":"'Project Info'!D63","v":5.7052382449247707},{"$f":"'Project Info'!E63","v":2.5019418419888937},{"$f":"'Project Info'!F63","v":0},{"$f":"'Project Info'!G63","v":0},{"$f":"'Project Info'!H63","v":0},{"$f":"'Project Info'!I63","v":0},{"$f":"'Project Info'!J63","v":0},{"$f":"'Project Info'!K63","v":0},{"$f":"'Project Info'!L63","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A64","v":0},{"$f":"'Project Info'!B64","v":5},{"$f":"'Project Info'!C64","v":2.6119461836144886},{"$f":"'Project Info'!D64","v":1.2699770062067783},{"$f":"'Project Info'!E64","v":1.2046477897733283},{"$f":"'Project Info'!F64","v":0},{"$f":"'Project Info'!G64","v":0},{"$f":"'Project Info'!H64","v":0},{"$f":"'Project Info'!I64","v":0},{"$f":"'Project Info'!J64","v":0},{"$f":"'Project Info'!K64","v":0},{"$f":"'Project Info'!L64","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A65","v":-5},{"$f":"'Project Info'!B65","v":0},{"$f":"'Project Info'!C65","v":-1.6731398516793925},{"$f":"'Project Info'!D65","v":-2.7083318773557807},{"$f":"'Project Info'!E65","v":7.9391832815876459E-2},{"$f":"'Project Info'!F65","v":0},{"$f":"'Project Info'!G65","v":0},{"$f":"'Project Info'!H65","v":0},{"$f":"'Project Info'!I65","v":0},{"$f":"'Project Info'!J65","v":0},{"$f":"'Project Info'!K65","v":0},{"$f":"'Project Info'!L65","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A66","v":-10},{"$f":"'Project Info'!B66","v":-5},{"$f":"'Project Info'!C66","v":-6.5729865085377277},{"$f":"'Project Info'!D66","v":-7.2465935998252222},{"$f":"'Project Info'!E66","v":-1.168423365310433},{"$f":"'Project Info'!F66","v":0},{"$f":"'Project Info'!G66","v":0},{"$f":"'Project Info'!H66","v":0},{"$f":"'Project Info'!I66","v":0},{"$f":"'Project Info'!J66","v":0},{"$f":"'Project Info'!K66","v":0},{"$f":"'Project Info'!L66","v":0},0,1,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A67","v":-15},{"$f":"'Project Info'!B67","v":-10},{"$f":"'Project Info'!C67","v":-15.32570353422995},{"$f":"'Project Info'!D67","v":-15.707838211108999},{"$f":"'Project Info'!E67","v":-3.4051318156661381},{"$f":"'Project Info'!F67","v":0},{"$f":"'Project Info'!G67","v":0},{"$f":"'Project Info'!H67","v":0},{"$f":"'Project Info'!I67","v":0},{"$f":"'Project Info'!J67","v":0},{"$f":"'Project Info'!K67","v":0},{"$f":"'Project Info'!L67","v":0},0,1,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[]
[]
[null,null,null,null,null,null,"Unoccupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"End Use",null,null,"Total"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Perimeter","Perimeter","Cooling","Heating","Ext. Wall Heat Gain",null,"Load Reduction",null,"Demand Reduction",null,null,"Demand Reduction"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Cooling","Heating","Perf","Perf","Base","Design","Cooling","Heating","Cooling","Heating","Heating","Elec","Gas"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","Load?","Load?","EER","COP","MBH","MBH","MBH","MBH","kW","MBH","kW","kW","MBH"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A74","v":100},{"$f":"'Project Info'!B74","v":105},{"$f":"'Project Info'!C74","v":102},{"$f":"'Project Info'!D74","v":76},{"$f":"'Project Info'!E74","v":40},{"$f":"'Project Info'!F74","v":0},{"$f":"'Project Info'!G74","v":0},{"$f":"'Project Info'!H74","v":0},{"$f":"'Project Info'!I74","v":0},{"$f":"'Project Info'!J74","v":0},{"$f":"'Project Info'!K74","v":0},{"$f":"'Project Info'!L74","v":0},{"$f":"1*($I82>$M$110)*(T82=0)*($U$22=$G$108)","v":0},{"$f":"1*($I82<$M$111)","v":0},{"$f":"IF($U$22=$G$108,$U$23,1)","v":1},{"$f":"IF($U$19=$H$109,$U$21,$U$20)","v":0},{"$f":"($P$24*$K$24+$P$32*$K$32+$T$40*$K$40+$I$45*$G$45)*(($S82>0)*($I82-$U$27)+($T82>0)*($I82-$U$28))/1000","v":0},{"$f":"($N$24*$K$24+$N$32*$K$32+$P$40*$K$40+$H$45*$G$45)*(($S82>0)*($I82-$U$27)+($T82>0)*($I82-$U$28))/1000","v":0},{"$f":"(W82-X82)*(S82>0)","v":0},{"$f":"-1*(W82-X82)*(T82>0)","v":0},{"$f":"Y82/U82","v":0},{"$f":"Z82/V82*($U$19<>\"Electric\")","v":{"$error":"#DIV/0!"}},{"$f":"Z82/V82/3.412*($U$19=\"Electric\")","v":{"$error":"#DIV/0!"}},{"$f":"AA82+AC82","v":{"$error":"#DIV/0!"}},{"$f":"AB82","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A75","v":95},{"$f":"'Project Info'!B75","v":100},{"$f":"'Project Info'!C75","v":95.219272727272724},{"$f":"'Project Info'!D75","v":74.534025272781079},{"$f":"'Project Info'!E75","v":37.923296058061368},{"$f":"'Project Info'!F75","v":0},{"$f":"'Project Info'!G75","v":0},{"$f":"'Project Info'!H75","v":0},{"$f":"'Project Info'!I75","v":0},{"$f":"'Project Info'!J75","v":0},{"$f":"'Project Info'!K75","v":0},{"$f":"'Project Info'!L75","v":0},0,0,1,0,{"$f":"($P$24*$K$24+$P$32*$K$32+$T$40*$K$40+$I$45*$G$45)*(($S83>0)*($I83-$U$27)+($T83>0)*($I83-$U$28))/1000","v":0},{"$f":"($N$24*$K$24+$N$32*$K$32+$P$40*$K$40+$H$45*$G$45)*(($S83>0)*($I83-$U$27)+($T83>0)*($I83-$U$28))/1000","v":0},{"$f":"(W83-X83)*(S83>0)","v":0},{"$f":"-1*(W83-X83)*(T83>0)","v":0},{"$f":"Y83/U83","v":0},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$f":"AA83+AC83","v":{"$error":"#DIV/0!"}},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A76","v":90},{"$f":"'Project Info'!B76","v":95},{"$f":"'Project Info'!C76","v":92.016049160256074},{"$f":"'Project Info'!D76","v":72.911561930607689},{"$f":"'Project Info'!E76","v":36.467095439351091},{"$f":"'Project Info'!F76","v":0},{"$f":"'Project Info'!G76","v":0},{"$f":"'Project Info'!H76","v":0},{"$f":"'Project Info'!I76","v":0},{"$f":"'Project Info'!J76","v":0},{"$f":"'Project Info'!K76","v":0},{"$f":"'Project Info'!L76","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A77","v":85},{"$f":"'Project Info'!B77","v":90},{"$f":"'Project Info'!C77","v":87.457811360655285},{"$f":"'Project Info'!D77","v":70.80538329449476},{"$f":"'Project Info'!E77","v":34.679413213566804},{"$f":"'Project Info'!F77","v":0},{"$f":"'Project Info'!G77","v":0},{"$f":"'Project Info'!H77","v":0},{"$f":"'Project Info'!I77","v":0},{"$f":"'Project Info'!J77","v":0},{"$f":"'Project Info'!K77","v":0},{"$f":"'Project Info'!L77","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A78","v":80},{"$f":"'Project Info'!B78","v":85},{"$f":"'Project Info'!C78","v":82.136788830239965},{"$f":"'Project Info'!D78","v":67.872393622439333},{"$f":"'Project Info'!E78","v":32.296248223809314},{"$f":"'Project Info'!F78","v":0},{"$f":"'Project Info'!G78","v":0},{"$f":"'Project Info'!H78","v":0},{"$f":"'Project Info'!I78","v":0},{"$f":"'Project Info'!J78","v":0},{"$f":"'Project Info'!K78","v":0},{"$f":"'Project Info'!L78","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A79","v":75},{"$f":"'Project Info'!B79","v":80},{"$f":"'Project Info'!C79","v":76.988400157585886},{"$f":"'Project Info'!D79","v":65.129261896908645},{"$f":"'Project Info'!E79","v":30.190476812806729},{"$f":"'Project Info'!F79","v":0},{"$f":"'Project Info'!G79","v":0},{"$f":"'Project Info'!H79","v":0},{"$f":"'Project Info'!I79","v":0},{"$f":"'Project Info'!J79","v":0},{"$f":"'Project Info'!K79","v":0},{"$f":"'Project Info'!L79","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A80","v":70},{"$f":"'Project Info'!B80","v":75},{"$f":"'Project Info'!C80","v":72.457982050814195},{"$f":"'Project Info'!D80","v":63.604425012889301},{"$f":"'Project Info'!E80","v":29.088683095945193},{"$f":"'Project Info'!F80","v":0},{"$f":"'Project Info'!G80","v":0},{"$f":"'Project Info'!H80","v":0},{"$f":"'Project Info'!I80","v":0},{"$f":"'Project Info'!J80","v":0},{"$f":"'Project Info'!K80","v":0},{"$f":"'Project Info'!L80","v":0},0,0,1,0,0,0,{"$f":"(W88-X88)*(S88>0)","v":0},{"$f":"-1*(W88-X88)*(T88>0)","v":0},0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A81","v":65},{"$f":"'Project Info'!B81","v":70},{"$f":"'Project Info'!C81","v":67.815831070966169},{"$f":"'Project Info'!D81","v":61.631331368130574},{"$f":"'Project Info'!E81","v":27.661514889731574},{"$f":"'Project Info'!F81","v":0},{"$f":"'Project Info'!G81","v":0},{"$f":"'Project Info'!H81","v":0},{"$f":"'Project Info'!I81","v":0},{"$f":"'Project Info'!J81","v":0},{"$f":"'Project Info'!K81","v":0},{"$f":"'Project Info'!L81","v":0},0,0,1,0,0,0,{"$f":"(W89-X89)*(S89>0)","v":0},{"$f":"-1*(W89-X89)*(T89>0)","v":0},0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A82","v":60},{"$f":"'Project Info'!B82","v":65},{"$f":"'Project Info'!C82","v":62.535961472271332},{"$f":"'Project Info'!D82","v":57.135476922863582},{"$f":"'Project Info'!E82","v":24.623037157728302},{"$f":"'Project Info'!F82","v":0},{"$f":"'Project Info'!G82","v":0},{"$f":"'Project Info'!H82","v":0},{"$f":"'Project Info'!I82","v":0},{"$f":"'Project Info'!J82","v":0},{"$f":"'Project Info'!K82","v":0},{"$f":"'Project Info'!L82","v":0},0,0,1,0,0,0,{"$f":"(W90-X90)*(S90>0)","v":0},{"$f":"-1*(W90-X90)*(T90>0)","v":0},0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A83","v":55},{"$f":"'Project Info'!B83","v":60},{"$f":"'Project Info'!C83","v":57.125792270740902},{"$f":"'Project Info'!D83","v":52.596971157053673},{"$f":"'Project Info'!E83","v":21.818001539159841},{"$f":"'Project Info'!F83","v":0},{"$f":"'Project Info'!G83","v":0},{"$f":"'Project Info'!H83","v":0},{"$f":"'Project Info'!I83","v":0},{"$f":"'Project Info'!J83","v":0},{"$f":"'Project Info'!K83","v":0},{"$f":"'Project Info'!L83","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A84","v":50},{"$f":"'Project Info'!B84","v":55},{"$f":"'Project Info'!C84","v":52.235698854337961},{"$f":"'Project Info'!D84","v":48.022768090099298},{"$f":"'Project Info'!E84","v":19.246640192796217},{"$f":"'Project Info'!F84","v":0},{"$f":"'Project Info'!G84","v":0},{"$f":"'Project Info'!H84","v":0},{"$f":"'Project Info'!I84","v":0},{"$f":"'Project Info'!J84","v":0},{"$f":"'Project Info'!K84","v":0},{"$f":"'Project Info'!L84","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A85","v":45},{"$f":"'Project Info'!B85","v":50},{"$f":"'Project Info'!C85","v":47.459170258371508},{"$f":"'Project Info'!D85","v":43.465397050422162},{"$f":"'Project Info'!E85","v":16.894183241713304},{"$f":"'Project Info'!F85","v":0},{"$f":"'Project Info'!G85","v":0},{"$f":"'Project Info'!H85","v":0},{"$f":"'Project Info'!I85","v":0},{"$f":"'Project Info'!J85","v":0},{"$f":"'Project Info'!K85","v":0},{"$f":"'Project Info'!L85","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A86","v":40},{"$f":"'Project Info'!B86","v":45},{"$f":"'Project Info'!C86","v":42.677030404888129},{"$f":"'Project Info'!D86","v":38.812544504634097},{"$f":"'Project Info'!E86","v":14.690265649465921},{"$f":"'Project Info'!F86","v":0},{"$f":"'Project Info'!G86","v":0},{"$f":"'Project Info'!H86","v":0},{"$f":"'Project Info'!I86","v":0},{"$f":"'Project Info'!J86","v":0},{"$f":"'Project Info'!K86","v":0},{"$f":"'Project Info'!L86","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A87","v":35},{"$f":"'Project Info'!B87","v":40},{"$f":"'Project Info'!C87","v":37.333046773755832},{"$f":"'Project Info'!D87","v":33.904706919479686},{"$f":"'Project Info'!E87","v":12.53841602318813},{"$f":"'Project Info'!F87","v":0},{"$f":"'Project Info'!G87","v":0},{"$f":"'Project Info'!H87","v":0},{"$f":"'Project Info'!I87","v":0},{"$f":"'Project Info'!J87","v":0},{"$f":"'Project Info'!K87","v":0},{"$f":"'Project Info'!L87","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A88","v":30},{"$f":"'Project Info'!B88","v":35},{"$f":"'Project Info'!C88","v":32.638179845662044},{"$f":"'Project Info'!D88","v":29.547170928664851},{"$f":"'Project Info'!E88","v":10.728972818165861},{"$f":"'Project Info'!F88","v":0},{"$f":"'Project Info'!G88","v":0},{"$f":"'Project Info'!H88","v":0},{"$f":"'Project Info'!I88","v":0},{"$f":"'Project Info'!J88","v":0},{"$f":"'Project Info'!K88","v":0},{"$f":"'Project Info'!L88","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A89","v":25},{"$f":"'Project Info'!B89","v":30},{"$f":"'Project Info'!C89","v":27.529264646850947},{"$f":"'Project Info'!D89","v":24.652717392657845},{"$f":"'Project Info'!E89","v":8.8041305482613303},{"$f":"'Project Info'!F89","v":0},{"$f":"'Project Info'!G89","v":0},{"$f":"'Project Info'!H89","v":0},{"$f":"'Project Info'!I89","v":0},{"$f":"'Project Info'!J89","v":0},{"$f":"'Project Info'!K89","v":0},{"$f":"'Project Info'!L89","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A90","v":20},{"$f":"'Project Info'!B90","v":25},{"$f":"'Project Info'!C90","v":22.998111483544687},{"$f":"'Project Info'!D90","v":20.383306659827422},{"$f":"'Project Info'!E90","v":7.246164547543378},{"$f":"'Project Info'!F90","v":0},{"$f":"'Project Info'!G90","v":0},{"$f":"'Project Info'!H90","v":0},{"$f":"'Project Info'!I90","v":0},{"$f":"'Project Info'!J90","v":0},{"$f":"'Project Info'!K90","v":0},{"$f":"'Project Info'!L90","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A91","v":15},{"$f":"'Project Info'!B91","v":20},{"$f":"'Project Info'!C91","v":17.808510327474309},{"$f":"'Project Info'!D91","v":15.420865796304254},{"$f":"'Project Info'!E91","v":5.5490484131518292},{"$f":"'Project Info'!F91","v":0},{"$f":"'Project Info'!G91","v":0},{"$f":"'Project Info'!H91","v":0},{"$f":"'Project Info'!I91","v":0},{"$f":"'Project Info'!J91","v":0},{"$f":"'Project Info'!K91","v":0},{"$f":"'Project Info'!L91","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A92","v":10},{"$f":"'Project Info'!B92","v":15},{"$f":"'Project Info'!C92","v":12.269931130346862},{"$f":"'Project Info'!D92","v":10.318264913023604},{"$f":"'Project Info'!E92","v":3.9082824916941998},{"$f":"'Project Info'!F92","v":0},{"$f":"'Project Info'!G92","v":0},{"$f":"'Project Info'!H92","v":0},{"$f":"'Project Info'!I92","v":0},{"$f":"'Project Info'!J92","v":0},{"$f":"'Project Info'!K92","v":0},{"$f":"'Project Info'!L92","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A93","v":5},{"$f":"'Project Info'!B93","v":10},{"$f":"'Project Info'!C93","v":7.3137581369917548},{"$f":"'Project Info'!D93","v":5.7052382449247707},{"$f":"'Project Info'!E93","v":2.5019418419888937},{"$f":"'Project Info'!F93","v":0},{"$f":"'Project Info'!G93","v":0},{"$f":"'Project Info'!H93","v":0},{"$f":"'Project Info'!I93","v":0},{"$f":"'Project Info'!J93","v":0},{"$f":"'Project Info'!K93","v":0},{"$f":"'Project Info'!L93","v":0},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A94","v":0},{"$f":"'Project Info'!B94","v":5},{"$f":"'Project Info'!C94","v":2.6119461836144886},{"$f":"'Project Info'!D94","v":1.2699770062067783},{"$f":"'Project Info'!E94","v":1.2046477897733283},{"$f":"'Project Info'!F94","v":8760},{"$f":"'Project Info'!G94","v":2672},{"$f":"'Project Info'!H94","v":3160},{"$f":"'Project Info'!I94","v":1344},{"$f":"'Project Info'!J94","v":1584},{"$f":"'Project Info'!K94","v":88},{"$f":"'Project Info'!L94","v":264},0,0,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A95","v":-5},{"$f":"'Project Info'!B95","v":0},{"$f":"'Project Info'!C95","v":-1.6731398516793925},{"$f":"'Project Info'!D95","v":-2.7083318773557807},{"$f":"'Project Info'!E95","v":7.9391832815876459E-2},{"$f":"'Project Info'!F95","v":0},{"$f":"'Project Info'!G95","v":0},{"$f":"'Project Info'!H95","v":0},{"$f":"'Project Info'!I95","v":0},{"$f":"'Project Info'!J95","v":0},{"$f":"'Project Info'!K95","v":0},{"$f":"'Project Info'!L95","v":0},0,1,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A96","v":-10},{"$f":"'Project Info'!B96","v":-5},{"$f":"'Project Info'!C96","v":-6.5729865085377277},{"$f":"'Project Info'!D96","v":-7.2465935998252222},{"$f":"'Project Info'!E96","v":-1.168423365310433},{"$f":"'Project Info'!F96","v":0},{"$f":"'Project Info'!G96","v":0},{"$f":"'Project Info'!H96","v":0},{"$f":"'Project Info'!I96","v":0},{"$f":"'Project Info'!J96","v":0},{"$f":"'Project Info'!K96","v":0},{"$f":"'Project Info'!L96","v":0},0,1,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A97","v":-15},{"$f":"'Project Info'!B97","v":-10},{"$f":"'Project Info'!C97","v":-15.32570353422995},{"$f":"'Project Info'!D97","v":-15.707838211108999},{"$f":"'Project Info'!E97","v":-3.4051318156661381},{"$f":"'Project Info'!F97","v":0},{"$f":"'Project Info'!G97","v":0},{"$f":"'Project Info'!H97","v":0},{"$f":"'Project Info'!I97","v":0},{"$f":"'Project Info'!J97","v":0},{"$f":"'Project Info'!K97","v":0},{"$f":"'Project Info'!L97","v":0},0,1,1,0,0,0,0,0,0,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[]
[null,null,null,null,null,null,"Yes/No","Heating Fuel",null,"Threshold OA Temperatures"]
[null,null,null,null,null,null,"Yes","Fossil Fuel",null,"for Cool/Heat Loads",null,null,null,null,"Default % Fixed Windows",null,0.85]
[null,null,null,null,null,null,"No","Electric",null,null,null,"Occ","Unocc",null,"Econo High Limit",null,70,"°F"]
[null,null,null,null,null,null,null,null,null,"Cooling",null,{"$f":"T27-5","v":-5},{"$f":"U27","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Mass wall Effective c.i. R-values"]
[null,null,null,null,null,null,null,null,null,"Heating",null,{"$f":"T28-5","v":-5},{"$f":"U28","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Metal-Framed Wall Effective Infill R-Values",null,null,null,null,null,null,null,"Metal Bldg Wall Effective Infill R-Values",null,null,null,null,null,null,null,null,"Rated","Effective"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Rated","Effective",null,null,null,null,null,null,"Rated","Effective","Test w/ R-9.8 c.i.",null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,"Baseline Envelope Performance - Climate Zone 5A",null,null,null,null,null,null,null,null,null,null,"Baseline Envelope Performance - Climate Zone 6A",null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,11.4,{"$f":"1/0.09","v":11.111111111111111}]
[null,null,null,null,null,null,"Roof",null,"U-Value",null,null,null,"Window Frame",null,"Frame","Frame",null,"Roof",null,"U-Value",null,null,null,"Window Frame",null,"Frame","Frame",null,null,11,5.5,null,null,null,null,null,null,10,5.26,{"$f":"1/(AM114+9.8)","v":6.6401062416998669E-2},null,null,null,null,null,null,15,{"$f":"1/0.076","v":13.157894736842106}]
[null,null,null,null,null,null,null,null,"IECC","IECC","Assembly",null,"Material",null,"U-Value","SHGC",null,null,null,"IECC","IECC","Assembly",null,"Material",null,"U-Value","SHGC",null,null,13,6,null,null,null,null,null,null,11,5.43,{"$f":"1/(AM115+9.8)","v":6.5659881812212731E-2},null,null,null,null,null,null,16.8,{"$f":"1/0.071","v":14.084507042253522}]
[null,null,null,null,null,null,"Type",null,2015,2018,"R-Adder",null,"Aluminum/Metal",null,1,0.2,null,"Type",null,2015,2018,"R-Adder",null,"Aluminum/Metal",null,1,0.2,null,null,15,6.4,null,null,null,null,null,null,13,6,{"$f":"1/(AM116+9.8)","v":6.3291139240506319E-2},null,null,null,null,null,null,26,{"$f":"TREND(AV114:AV115,AU114:AU115,AU116)","v":18.820525492134088}]
[null,null,null,null,null,null,"Attic and Other",null,2.7E-2,2.7E-2,null,null,"Fiberglass",null,0.3,0.1,null,"Attic and Other",null,2.1000000000000001E-2,2.1000000000000001E-2,null,null,"Fiberglass",null,0.3,0.1,null,null,19,7.1,null,null,null,null,null,null,16,6.4,{"$f":"1/(AM117+9.8)","v":6.1728395061728385E-2}]
[null,null,null,null,null,null,"Insulation Entirely Above Deck",null,3.2000000000000001E-2,3.2000000000000001E-2,0.77700000000000002,null,"Vinyl",null,0.3,0.1,null,"Insulation Entirely Above Deck",null,3.2000000000000001E-2,3.2000000000000001E-2,0.77700000000000002,null,"Vinyl",null,0.3,0.1,null,null,21,7.4,null,null,null,null,null,null,19,6.8,{"$f":"1/(AM118+9.8)","v":6.0240963855421679E-2}]
[null,null,null,null,null,null,"Metal Buildings",null,3.5000000000000003E-2,3.5000000000000003E-2,null,null,"Wood",null,0.4,0.05,null,"Metal Buildings",null,3.1E-2,3.1E-2,null,null,"Wood",null,0.4,0.05,null,null,31,{"$f":"TREND(AE117:AE118,AD117:AD118,AD119)","v":8.9000000000000039},null,null,null,null,null,null,29,{"$f":"TREND(AM117:AM118,AL117:AL118,AL119)","v":8.1333333333333311}]
[null,null,null,null,null,null,null,null,null,null,null,null,"Z-Other",null,1,0.2,null,null,null,null,null,null,null,"Z-Other",null,1,0.2]
[null,null,null,null,null,null,"Walls",null,"U-Value",null,null,null,null,null,null,null,null,"Walls",null,"U-Value",null,null,null,null,null,null,null,null,null,"Wood-Framed Wall Effective Infill R-Values",null,null,null,null,null,null,null,"Wood-Framed Wall Effective Infill R-Values"]
[null,null,null,null,null,null,null,null,"IECC","IECC","Assembly",null,"Window Baseline",null,"IECC","IECC",null,null,null,"IECC","IECC","Assembly",null,"Window Baseline",null,"IECC","IECC",null,null,"Rated","Effective","Test w/ R-10 c.i.",null,null,null,null,null,"Rated","Effective","Code U-Value"]
[null,null,null,null,null,null,"Type",null,2015,2018,"R-Adder",null,"U-Values",null,2015,2018,null,"Type",null,2015,2018,"R-Adder",null,"U-Values",null,2015,2018,null,null,0,0,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,"Mass",null,0.09,0.09,-0.2888,null,"Fixed Assembly",null,0.38,0.38,null,"Mass",null,0.08,0.08,-0.2888,null,"Fixed Assembly",null,0.36,0.36,null,null,11,{"$f":"1/0.096","v":10.416666666666666},{"$f":"1/(AE124+10)","v":4.8979591836734698E-2},null,null,null,null,null,11,10.5,{"$f":"1/AM124","v":9.5238095238095233E-2}]
[null,null,null,null,null,null,"Metal Building",null,5.1999999999999998E-2,5.1999999999999998E-2,0,null,"Operables Assembly",null,0.45,0.45,null,"Metal Building",null,5.1999999999999998E-2,5.1999999999999998E-2,0,null,"Operables Assembly",null,0.43,0.43,null,null,13,{"$f":"1/0.086215","v":11.598909702487965},{"$f":"1/(AE125+10)","v":4.6298633300217489E-2},null,null,null,null,null,13,12.2,{"$f":"1/AM125","v":8.1967213114754106E-2}]
[null,null,null,null,null,null,"Metal Framed",null,6.4000000000000001E-2,6.4000000000000001E-2,2.2000000000000002,null,null,null,null,null,null,"Metal Framed",null,6.4000000000000001E-2,6.4000000000000001E-2,2.2000000000000002,null,null,null,null,null,null,null,15,{"$f":"1/0.083","v":12.048192771084336},{"$f":"1/(AE126+10)","v":4.5355191256830601E-2},null,null,null,null,null,15,13.2,{"$f":"1/AM126","v":7.575757575757576E-2}]
[null,null,null,null,null,null,"Wood Framed and Other",null,6.4000000000000001E-2,6.4000000000000001E-2,0.22600000000000001,null,"Window Baseline SHGC",null,"IECC","IECC",null,"Wood Framed and Other",null,5.0999999999999997E-2,5.0999999999999997E-2,0,null,"Window Baseline SHGC",null,"IECC","IECC",null,null,19,{"$f":"1/0.067","v":14.925373134328357},{"$f":"1/(AE127+10)","v":4.0119760479041922E-2},null,null,null,null,null,19,16.3,{"$f":"1/AM127","v":6.1349693251533742E-2}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,2015,2018,null,null,null,null,null,null,null,null,null,2015,2018,null,null,21,{"$f":"1/0.063","v":15.873015873015873},{"$f":"1/(AE128+10)","v":3.8650306748466257E-2},null,null,null,null,null,21,17.7,{"$f":"1/AM128","v":5.6497175141242938E-2}]
[null,null,null,null,null,null,"Garage Doors",null,"U-Value",null,null,null,"SHGC",null,0.4,0.38,null,"Garage Doors",null,"U-Value",null,null,null,"SHGC",null,0.4,0.4,null,null,31,{"$f":"TREND(AE127:AE128,AD127:AD128,AD129)","v":20.611229566453456}]
[null,null,null,null,null,null,null,null,"IECC","IECC",null,null,null,null,null,null,null,null,null,"IECC","IECC"]
[null,null,null,null,null,null,null,null,2015,2018,null,null,null,null,null,null,null,null,null,2015,2018,null,null,null,null,null,null,null,null,null,"Metal Bldg ROOF Effective Infill R-Values",null,null,null,null,null,null,null,"Wood-Framed Attic Effective Insulation R-Values"]
[null,null,null,null,null,null,"< 14% Glazing",null,0.31,0.31,null,null,null,null,null,null,null,"< 14% Glazing",null,0.31,0.31,null,null,null,null,null,null,null,null,null,"Rated","Effective","Test w/ no c.i.",null,null,null,null,null,"Rated","Eff R-value","Eff U-Value"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,{"$f":"1/AG134","v":8.695652173913043},0.115,null,null,null,null,null,11,{"$f":"1/AO134","v":10.989010989010989},9.0999999999999998E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,{"$f":"1/AG135","v":9.3457943925233646},0.107,null,null,null,null,null,13,12.345679012345679,8.1000000000000003E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,13,{"$f":"1/AG136","v":9.9009900990099009},0.10100000000000001,null,null,null,null,null,19,18.867924528301888,5.2999999999999999E-2]
[null,null,null,null,null,null,"Exterior Wall Assemblies - Design Case Overall U-value Calculation",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,16,{"$f":"1/AG137","v":10.416666666666666},9.6000000000000002E-2,null,null,null,null,null,30,29.411764705882351,3.4000000000000002E-2]
[null,null,null,null,null,null,"Assembly","Assembly",null,null,"Area","Infill","c.i.","U-Value Based on Wall Type",null,null,null,"U-Value",null,null,null,null,null,null,null,null,null,null,null,null,19,{"$f":"1/AG138","v":12.195121951219512},8.2000000000000003E-2,null,null,null,null,null,38,37.037037037037038,2.7E-2]
[null,null,null,null,null,null,"No.","Type",null,null,"ft²","R-Value","R-Value",{"$f":"G124","v":"Mass"},{"$f":"G125","v":"Metal Building"},{"$f":"G126","v":"Metal Framed"},{"$f":"G127","v":"Wood Framed and Other"},"Btu/h·ft²·°F",null,null,null,null,null,null,null,null,null,null,null,null,29,{"$f":"TREND(AF137:AF138,AE137:AE138,AE139)","v":18.12330623306233},null,null,null,null,null,null,49,47.619047619047613,2.1000000000000001E-2]
[null,null,null,null,null,null,1,{"$f":"H21","v":0},null,null,{"$f":"K21","v":0},{"$f":"L21","v":0},{"$f":"M21","v":0},{"$f":"1/(TREND(OFFSET($AD$112,MATCH(L140,$AD$113:$AD$118,1),1,2,1),OFFSET($AD$112,MATCH(L140,$AD$113:$AD$118,1),0,2,1),L140)+M140+$K$124)","v":-3.4626038781163433},{"$f":"1/(TREND(OFFSET($AL$112,MATCH(L140,$AL$113:$AL$118,1),1,2,1),OFFSET($AL$112,MATCH(L140,$AL$113:$AL$118,1),0,2,1),L140)+M140+$K$125)","v":2251799813685248},{"$f":"1/(TREND(OFFSET($AD$112,MATCH(L140,$AD$113:$AD$118,1),1,2,1),OFFSET($AD$112,MATCH(L140,$AD$113:$AD$118,1),0,2,1),L140)+M140+$K$126)","v":0.45454545454545453},{"$f":"1/(TREND(OFFSET($AD$122,MATCH(L140,$AD$123:$AD$128,1),1,2,1),OFFSET($AD$122,MATCH(L140,$AD$123:$AD$128,1),0,2,1),L140)+M140+$K$127)","v":4.4247787610619467},{"$f":"LOOKUP(H140,$N$139:$Q$139,N140:Q140)","v":{"$error":"#N/A"}},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,60,58.823529411764703,1.7000000000000001E-2]
[null,null,null,null,null,null,2,{"$f":"H22","v":0},null,null,{"$f":"K22","v":0},0,0,{"$f":"1/(TREND(OFFSET($AD$112,MATCH(L141,$AD$113:$AD$118,1),1,2,1),OFFSET($AD$112,MATCH(L141,$AD$113:$AD$118,1),0,2,1),L141)+M141+$K$124)","v":-3.4626038781163433},{"$f":"1/(TREND(OFFSET($AL$112,MATCH(L141,$AL$113:$AL$118,1),1,2,1),OFFSET($AL$112,MATCH(L141,$AL$113:$AL$118,1),0,2,1),L141)+M141+$K$125)","v":2251799813685248},{"$f":"1/(TREND(OFFSET($AD$112,MATCH(L141,$AD$113:$AD$118,1),1,2,1),OFFSET($AD$112,MATCH(L141,$AD$113:$AD$118,1),0,2,1),L141)+M141+$K$126)","v":0.45454545454545453},{"$f":"1/(TREND(OFFSET($AD$122,MATCH(L141,$AD$123:$AD$128,1),1,2,1),OFFSET($AD$122,MATCH(L141,$AD$123:$AD$128,1),0,2,1),L141)+M141+$K$127)","v":4.4247787610619467},{"$f":"LOOKUP(H141,$N$139:$Q$139,N141:Q141)","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,3,{"$f":"H23","v":0},null,null,0,0,0,{"$f":"1/(TREND(OFFSET($AD$112,MATCH(L142,$AD$113:$AD$118,1),1,2,1),OFFSET($AD$112,MATCH(L142,$AD$113:$AD$118,1),0,2,1),L142)+M142+$K$124)","v":-3.4626038781163433},{"$f":"1/(TREND(OFFSET($AL$112,MATCH(L142,$AL$113:$AL$118,1),1,2,1),OFFSET($AL$112,MATCH(L142,$AL$113:$AL$118,1),0,2,1),L142)+M142+$K$125)","v":2251799813685248},{"$f":"1/(TREND(OFFSET($AD$112,MATCH(L142,$AD$113:$AD$118,1),1,2,1),OFFSET($AD$112,MATCH(L142,$AD$113:$AD$118,1),0,2,1),L142)+M142+$K$126)","v":0.45454545454545453},{"$f":"1/(TREND(OFFSET($AD$122,MATCH(L142,$AD$123:$AD$128,1),1,2,1),OFFSET($AD$122,MATCH(L142,$AD$123:$AD$128,1),0,2,1),L142)+M142+$K$127)","v":4.4247787610619467},{"$f":"LOOKUP(H142,$N$139:$Q$139,N142:Q142)","v":{"$error":"#N/A"}}]
[]
[null,null,null,null,null,null,"Exterior ROOF Assemblies - Design Case Overall U-value Calculation"]
[null,null,null,null,null,null,"Assembly","Assembly",null,null,"Area","Infill","c.i.","U-Value Based on Wall Type",null,null,null,"U-Value"]
[null,null,null,null,null,null,"No.","Type",null,null,"ft²","R-Value","R-Value",{"$f":"G117","v":"Attic and Other"},{"$f":"G118","v":"Insulation Entirely Above Deck"},{"$f":"G119","v":"Metal Buildings"},null,"Btu/h·ft²·°F"]
[null,null,null,null,null,null,1,{"$f":"H29","v":0},null,null,{"$f":"K29","v":0},0,0,{"$f":"1/(TREND(OFFSET($AM$132,MATCH(L147,$AM$133:$AM$139,1),1,2,1),OFFSET($AM$132,MATCH(L147,$AM$133:$AM$139,1),0,2,1),L147)+M147)","v":{"$error":"#DIV/0!"}},{"$f":"1/(M147+$K$118)","v":1.287001287001287},{"$f":"1/(TREND(OFFSET($AE$132,MATCH(L147,$AE$133:$AE$138,1),1,2,1),OFFSET($AE$132,MATCH(L147,$AE$133:$AE$138,1),0,2,1),L147)+M147)","v":562949953421312},null,{"$f":"LOOKUP(H147,$N$146:$P$146,N147:P147)","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,2,{"$f":"H30","v":0},null,null,0,0,0,{"$f":"1/(TREND(OFFSET($AM$132,MATCH(L148,$AM$133:$AM$139,1),1,2,1),OFFSET($AM$132,MATCH(L148,$AM$133:$AM$139,1),0,2,1),L148)+M148)","v":{"$error":"#DIV/0!"}},{"$f":"1/(M148+$K$118)","v":1.287001287001287},{"$f":"1/(TREND(OFFSET($AE$132,MATCH(L148,$AE$133:$AE$138,1),1,2,1),OFFSET($AE$132,MATCH(L148,$AE$133:$AE$138,1),0,2,1),L148)+M148)","v":562949953421312},null,{"$f":"LOOKUP(H148,$N$146:$P$146,N148:P148)","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,3,{"$f":"H31","v":0},null,null,0,0,0,{"$f":"1/(TREND(OFFSET($AM$132,MATCH(L149,$AM$133:$AM$139,1),1,2,1),OFFSET($AM$132,MATCH(L149,$AM$133:$AM$139,1),0,2,1),L149)+M149)","v":{"$error":"#DIV/0!"}},1.287001287001287,{"$f":"1/(TREND(OFFSET($AE$132,MATCH(L149,$AE$133:$AE$138,1),1,2,1),OFFSET($AE$132,MATCH(L149,$AE$133:$AE$138,1),0,2,1),L149)+M149)","v":562949953421312},null,{"$f":"LOOKUP(H149,$N$146:$P$146,N149:P149)","v":{"$error":"#N/A"}}]
[]
[null,null,null,null,null,null,"Exterior ROOF Assemblies - Design Case Overall U-value Calculation"]
[null,null,null,null,null,null,"Assembly","Assembly",null,null,"Area","%","%","Center-of Glass",null,"Fixed","Oper.","Frame","Frame","Fixed Window",null,"Operable Window",null,"Average All Windows"]
[null,null,null,null,null,null,"No.","Type",null,null,"ft²","Operable","Fixed","U-Value","SHGC","%Glass","% Glass","U-Value","SHGC","U-Value","SHGC","U-Value","SHGC","U-Value","SHGC"]
[null,null,null,null,null,null,1,{"$f":"H37","v":0},null,null,{"$f":"K37","v":0},{"$f":"1-M154","v":0.15000000000000002},{"$f":"M37","v":0.85},0,0,0.88570000000000004,0.78569999999999995,{"$f":"IF(H154=0,0,LOOKUP(H154,$M$116:$M$120,$O$116:$O$120))","v":0},{"$f":"IF(H154=0,0,LOOKUP(H154,$M$116:$M$120,$P$116:$P$120))","v":0},{"$f":"IF(H154=0,0,P154*N154+(1-P154)*R154)","v":0},{"$f":"IF(H154=0,0,P154*O154+(1-P154)*S154)","v":0},{"$f":"IF(H154=0,0,Q154*N154+(1-Q154)*R154)","v":0},{"$f":"IF(H154=0,0,Q154*O154+(1-Q154)*S154)","v":0},{"$f":"IF(H154=0,T37,T154*M154+V154*(1-M154))","v":0},{"$f":"IF(H154=0,U37,U154*M154+W154*(1-M154))","v":0}]
[null,null,null,null,null,null,2,{"$f":"H38","v":0},null,null,{"$f":"K38","v":0},{"$f":"1-M155","v":0.15000000000000002},0.85,0,0,0.88570000000000004,0.78569999999999995,{"$f":"IF(H155=0,0,LOOKUP(H155,$M$116:$M$120,$O$116:$O$120))","v":0},{"$f":"IF(H155=0,0,LOOKUP(H155,$M$116:$M$120,$P$116:$P$120))","v":0},{"$f":"IF(H155=0,0,P155*N155+(1-P155)*R155)","v":0},{"$f":"IF(H155=0,0,P155*O155+(1-P155)*S155)","v":0},{"$f":"IF(H155=0,0,Q155*N155+(1-Q155)*R155)","v":0},{"$f":"IF(H155=0,0,Q155*O155+(1-Q155)*S155)","v":0},{"$f":"IF(H155=0,T38,T155*M155+V155*(1-M155))","v":0},{"$f":"IF(H155=0,U38,U155*M155+W155*(1-M155))","v":0}]
[null,null,null,null,null,null,3,{"$f":"H39","v":0},null,null,{"$f":"K39","v":0},{"$f":"1-M156","v":0.15000000000000002},0.85,0,0,0.88570000000000004,0.78569999999999995,{"$f":"IF(H156=0,0,LOOKUP(H156,$M$116:$M$120,$O$116:$O$120))","v":0},{"$f":"IF(H156=0,0,LOOKUP(H156,$M$116:$M$120,$P$116:$P$120))","v":0},{"$f":"IF(H156=0,0,P156*N156+(1-P156)*R156)","v":0},{"$f":"IF(H156=0,0,P156*O156+(1-P156)*S156)","v":0},{"$f":"IF(H156=0,0,Q156*N156+(1-Q156)*R156)","v":0},{"$f":"IF(H156=0,0,Q156*O156+(1-Q156)*S156)","v":0},{"$f":"IF(H156=0,T39,T156*M156+V156*(1-M156))","v":0},{"$f":"IF(H156=0,U39,U156*M156+W156*(1-M156))","v":0}]
[]
[null,null,null,null,null,null,"Incremental Cost Estimate"]
[null,null,null,null,null,null,null,"Area","U-Value","Cost","Incr."]
[null,null,null,null,null,null,"Assembly","ft²","Reduction","$/dU/ft²","Cost"]
[null,null,null,null,null,null,"Ext Walls",{"$f":"$K$24","v":0},{"$f":"$P$24-$N$24","v":0},{"$f":"0.6/0.024","v":25},{"$f":"MAX(0,J161*I161*H161)","v":0}]
[null,null,null,null,null,null,"Roofs",{"$f":"$K$32","v":0},{"$f":"$P$32-$N$32","v":0},{"$f":"0.6/0.004","v":150},{"$f":"MAX(0,J162*I162*H162)","v":0}]
[null,null,null,null,null,null,"Windows",{"$f":"$K$40","v":0},{"$f":"$T$40-$P$40","v":0},{"$f":"1.5/0.04","v":37.5},0]
[null,null,null,null,null,null,"Garage Doors",{"$f":"$G$45","v":0},{"$f":"IF($H$45=\"\",0,$I$45-$H$45)","v":0},{"$f":"J161","v":25},0]
[null,null,null,null,null,null,"Total Incremental Cost",null,null,null,{"$f":"SUM(K161:K164)","v":0}]

{"sheet":"Interior Lighting","index":9,"n_rows":164,"n_cols":42,"rows_kept":164,"cut":false,"hidden":true,"merged":[[6,10,12,17],[220,19,226,19],[213,19,219,19],[206,19,212,19],[1,10,4,17],[202,6,205,6],[176,24,179,24],[186,6,189,6],[190,6,193,6],[182,6,185,6],[176,23,179,23],[180,23,183,23],[180,24,183,24],[174,6,177,6],[168,23,171,23],[194,6,197,6],[198,6,201,6],[168,24,171,24],[178,6,181,6],[172,23,175,23],[172,24,175,24]]}
["Complete Savings Summary",null,null,null,null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,null,null,"Table 2: Baseline, Savings, and Incentive Calc Summary",null,null,null,null,null,"Table 2a: PARKING GARAGE Baseline, Savings, and Incentive Calc Summary"]
["Annual kWh Savings",null,null,{"$f":"H3","v":0},null,null,null,"Value","Unit",null,"This measure considers savings from a high performance interior lighting system design with reduced lighting power density below the baseline maximum allowable value.  Control-related savings are also considered for projects that meet the Tier 2 or Tier 3 Performance Lighting requirements.",null,null,null,null,null,null,null,null,null,"Bldg Area (ft²",{"$f":"'Project Info'!$C$17","v":0},null,null,null,null,"Parking Garage Area (ft²)",null,"<User Input"]
["% On Peak",null,null,{"$f":"MIN(1,A15+C15)","v":0},null,"Annual Electric Savings",null,{"$f":"V13+1*($K$23=$G$107)*AB13","v":0},"kWh",null,null,null,null,null,null,null,null,null,null,null,"Bldg Type",{"$f":"'Project Info'!$C$18","v":0},null,null,null,null,"Bldg Type",{"$f":"$I$138","v":"Parking garage"}]
["Max kW",null,null,{"$f":"MAX(AP111:AP134,AP141:AP164)","v":0},null,"Annual Fuel Savings",null,{"$f":"D7*C29","v":{"$error":"#N/A"}},{"$f":"D20","v":{"$error":"#N/A"}},null,null,null,null,null,null,null,null,null,null,null,"Baseline Bldg LPD (W/ft²)",{"$f":"IFERROR(LOOKUP(V3,$I$110:$I$151,$K$110:$K$151),0)","v":0},null,"Optional Override",null,null,"Baseline LPD (W/ft²)",{"$f":"IFERROR(LOOKUP(AB3,$I$110:$I$151,$K$110:$K$151),0)","v":0.13},null,"Optional Override"]
["Summer kW",null,null,{"$f":"(SUMPRODUCT(AP111:AP134,AM111:AM134)+SUMPRODUCT(AP141:AP164,AM141:AM164))/SUM(AM111:AM134,AM141:AM164)","v":0},null,"Incremental","Default Calc","NA","$",null,null,null,null,null,null,null,null,null,null,null,"Total Baseline Watts",{"$f":"V2*IF(W4>0,W4,V4)","v":0},null,null,null,null,"Total Baseline Watts",{"$f":"AB2*IF(AC4>0,AC4,AB4)","v":0}]
["Winter kW",null,null,{"$f":"(SUMPRODUCT(AP111:AP134,AL111:AL134)+SUMPRODUCT(AP141:AP164,AL141:AL164))/SUM(AL111:AL134,AL141:AL164)","v":0},null,"Cost","Project Specific",null,"$ (Optional)",null,"Notes (Optional)",null,null,null,null,null,null,null,null,null,"Total Proposed Watts",{"$f":"SUM(T30:T99)","v":0},null,"Optional Override",null,null,"Total Proposed Watts",{"$f":"SUM(AM30:AM99)","v":0},null,"Optional Override"]
["Annual Fuel Savings (MMBtu)",null,null,0,null,"Estimated Incentive",null,{"$f":"IF(V10=0,0,V16)+1*($K$23=$G$107)*IF(AB11=0,0,AB16)","v":0},"$",null,null,null,null,null,null,null,null,null,null,null,"Base Lighting Hours (EFLH)",{"$f":"LOOKUP($V$3,$I$110:$I$151,$L$110:$L$151)","v":{"$error":"#N/A"}},null,"Optional Override",null,null,"Base Lighting Hours (EFLH)",{"$f":"LOOKUP($AB$3,$I$110:$I$151,$L$110:$L$151)","v":6552},null,"Optional Override"]
["Incremental Cost (Default Calc)",null,null,"NA",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Values Used in Calculations",null,null,null,null,null,"Values Used in Calculations"]
["Incremental Cost (for Summary)",null,null,{"$f":"IF(H6>0,H6,D8)","v":"NA"},null,"Project Information Summary",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Baseline Watts",{"$f":"V5","v":0},null,null,null,null,"Total Baseline Watts",{"$f":"AB5","v":0}]
["kWh Savings by Peak Period",null,null,null,null,null,"STATE",{"$f":"'Project Info'!C15","v":"NH"},null,null,null,null,null,null,null,null,null,null,null,null,"Total Proposed Watts",{"$f":"IF(W6=\"\",V6,W6)","v":0},null,null,null,null,"Total Proposed Watts",{"$f":"IF(AC6=\"\",AB6,AC6)","v":0}]
["Winter","Winter","Summer","Summer",null,null,"Program Year",{"$f":"'Project Info'!C19","v":0},null,null,null,null,null,null,null,null,null,null,null,null,"Total Watts Saved vs. Baseline",{"$f":"MAX(0,V9-V10)","v":0},null,null,null,null,"Total Watts Saved vs. Baseline",{"$f":"MAX(0,AB9-AB10)","v":0}]
["On-Peak","Off-Peak","On-Peak","Off-Peak",null,null,"Code IECC Version",{"$f":"MID('Project Info'!C20,1,4)","v":"2018"},null,null,null,null,null,null,null,null,null,null,null,null,"Base Lighting Hours (EFLH)",{"$f":"IF(W7=\"\",V7,W7)","v":{"$error":"#N/A"}},null,null,null,null,"Base Lighting Hours (EFLH)",{"$f":"IF(AC7=\"\",AB7,AC7)","v":6552}]
["kWh","kWh","kWh","kWh",null,null,"Electric PA",{"$f":"'Project Info'!F3","v":0},null,null,null,null,null,null,null,null,null,null,null,null,"Annual Electric Savings (kWh)",{"$f":"IF(V10=0,0,V12*(V9-V10*(1-Y15))/1000)","v":0},null,null,null,null,"Annual Electric Savings (kWh)",{"$f":"IF(AB10=0,0,AB12*(AB9-AB10*(1-AE16))/1000)","v":0}]
[{"$f":"SUMPRODUCT(AH111:AH134,$AP$111:$AP$134)+SUMPRODUCT(AH141:AH164,$AP$141:$AP$164)","v":0},{"$f":"SUMPRODUCT(AI111:AI134,$AP$111:$AP$134)+SUMPRODUCT(AI141:AI164,$AP$141:$AP$164)","v":0},{"$f":"SUMPRODUCT(AJ111:AJ134,$AP$111:$AP$134)+SUMPRODUCT(AJ141:AJ164,$AP$141:$AP$164)","v":0},{"$f":"SUMPRODUCT(AK111:AK134,$AP$111:$AP$134)+SUMPRODUCT(AK141:AK164,$AP$141:$AP$164)","v":0},null,"*NOTE: Baseline values are automated and cannot be changed.",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"% DLC/ES Certified",{"$f":"IFERROR((SUMIFS($T$30:$T$99,$Q$30:$Q$99,$Q$100)+SUMIFS($T$30:$T$99,$Q$30:$Q$99,$Q$101))/$T$25,0)","v":0},null,null,null,null,"% DLC/ES Certified",{"$f":"IFERROR((SUMIFS($AM$30:$AM$99,$AJ$30:$AJ$99,$Q$100)+SUMIFS($AM$30:$AM$99,$AJ$30:$AJ$99,$Q$101))/$AM$25,0)","v":0}]
[{"$f":"ROUND(IF(A14<=0,0,A14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(B14<=0,0,B14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(C14<=0,0,C14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"IF(SUM(A14:D14)=0,0,1-SUM(A15:C15))","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Certified Designer/DLC Exemption?",null,null,null,null,null,"Certified Designer/DLC Exemption?"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Incentive $",{"$f":"IFERROR(MAX(0,V13*IF(OR(V15=$G$107,V14>=50%),$C$25,0)),0)","v":0},null,null,null,null,"Total Incentive $",{"$f":"IFERROR(MAX(0,AB13*IF(OR(AB15=$G$107,AB14>=50%),$C$25,0)),0)","v":0}]
["Utility Rates"]
[null,null,"Rate","Unit",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Scroll Right for Parking Garage Fixture Inputs >>>>>>>>>>>",null,null,null,null,null,null,null,null,null,null,null,"<<Performance Lighting Incentive Rate has been overridden "]
["Electric",null,{"$f":"'ECM Summary'!$E$31","v":0.1593},"kWh"]
[{"$f":"'ECM Summary'!$C$32","v":0},null,{"$f":"'ECM Summary'!$E$32","v":{"$error":"#N/A"}},{"$f":"'ECM Summary'!$F$32","v":{"$error":"#N/A"}},null,null,null,null,null,null,"**PARKING GARAGE area and lighting fixtures should NOT be included in the table below."]
[null,null,null,null,null,null,null,null,null,null,"A separate Parking Garage section is included to the right in this sheet. "]
["Custom Incentive Rates",null,null,null,null,null,null,null,null,null,"Select \"Yes\" below to include garage fixtures and use the separate input table."]
[null,null,"Rate","Unit",null,null,null,null,null,null,null,"Include Enclosed Parking Garage Lighting in Analysis? Scroll right for Parking Garage Input Tables >>"]
[]
["Electric",null,{"$f":"'ECM Summary'!$J$31","v":0.28000000000000003},"kWh",null,null,"Table 1: Interior Lighting Fixtures (Excluding Parking Garage)",null,null,null,null,null,null,null,null,null,null,null,"Total Design Watts:",{"$f":"SUM(T30:T99)","v":0},null,null,null,null,null,"Table 1a: PARKING GARAGE Lighting Fixtures",null,null,null,null,null,null,null,null,null,null,null,"Total Design Watts:",{"$f":"SUM(AM30:AM99)","v":0}]
[{"$f":"'ECM Summary'!$H$32","v":0},null,{"$f":"'ECM Summary'!$J$32","v":0},{"$f":"'ECM Summary'!$K$32","v":{"$error":"#N/A"}},null,null,1,2,3,null,null,null,4,null,null,null,5,6,7,8,9,null,null,null,null,1,2,3,null,null,null,4,null,null,null,5,6,7,8,9]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Tier 1","Qty","Wattage",null,"DLC/ES",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Tier 1","Qty","Wattage",null,"DLC/ES"]
["Fossil Fuel",null,{"$f":"'Project Info'!C21","v":0},null,null,null,"Fixture",null,null,null,null,null,null,null,null,null,"·DLC/ES·","Total Fixture","Fixture Power","Total Design","Certified",null,null,null,null,"Fixture",null,null,null,null,null,null,null,null,null,"·DLC/ES·","Total Fixture","Fixture Power","Total Design","Certified"]
["Fuel Conversion",null,{"$f":"LOOKUP(C28,'Project Info'!X102:X104,'Project Info'!Z102:Z104)","v":{"$error":"#N/A"}},null,null,null,"ID","Manufacturer","Model Number",null,null,null,"Fixture Type (Optional)",null,null,null,"Certified?","Qty","W/Fixture","Watts","?",null,null,null,null,"ID","Manufacturer","Model Number",null,null,null,"Fixture Type (Optional)",null,null,null,"Certified?","Qty","W/Fixture","Watts","?"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"R30*S30","v":0},{"$f":"IF(OR(Q30=$Q$100,Q30=$Q$101),1,0)","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"AK30*AL30","v":0},{"$f":"IF(OR(AJ30=$Q$100,AJ30=$Q$101),1,0)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"R62*S62","v":0},{"$f":"IF(OR(Q62=$Q$100,Q62=$Q$101),1,0)","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"AK62*AL62","v":0},{"$f":"IF(OR(AJ62=$Q$100,AJ62=$Q$101),1,0)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"R94*S94","v":0},{"$f":"IF(OR(Q94=$Q$100,Q94=$Q$101),1,0)","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"AK94*AL94","v":0},{"$f":"IF(OR(AJ94=$Q$100,AJ94=$Q$101),1,0)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"DLC",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"DLC"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"EnergyStar",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"EnergyStar"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[]
[]
[]
[null,null,null,null,null,null,"Yes/No",null,"LOOKUP TABLES"]
[null,null,null,null,null,null,"Yes",null,null,null,"Baseline LPD",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown",null,null,null,null,null,null,null,null,"Demand"]
[null,null,null,null,null,null,"No",null,null,null,"Based on NH ISP","Annual",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer",null,null,"Reduction"]
[null,null,null,null,null,null,"DNQ",null,"Building Type",null,"(60% of 2015 IECC)","EFLH","Source of Hrs","Note",null,null,null,null,null,null,null,null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Base","Design","Elec"]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E102","v":"Automotive facility"},null,0.48,4939,"2025 App",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","kW","kW","kW"]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E103","v":"Convention center"},null,0.61,5220,"2025 App","Double the Eval hours for Public Assembly (1 shift)",null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A44","v":100},{"$f":"'Project Info'!B44","v":105},{"$f":"'Project Info'!C44","v":102},{"$f":"'Project Info'!D44","v":76},{"$f":"'Project Info'!E44","v":40},{"$f":"'Project Info'!F44","v":0},{"$f":"'Project Info'!G44","v":0},{"$f":"'Project Info'!H44","v":0},{"$f":"'Project Info'!I44","v":0},{"$f":"'Project Info'!J44","v":0},{"$f":"'Project Info'!K44","v":0},{"$f":"'Project Info'!L44","v":0},{"$f":"$V$9/1000","v":0},{"$f":"$V$10/1000","v":0},{"$f":"AN111-AO111","v":0}]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E104","v":"Courthouse"},null,0.61,3425,"2025 App","Public Services (non food)",null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A45","v":95},{"$f":"'Project Info'!B45","v":100},{"$f":"'Project Info'!C45","v":95.219272727272724},{"$f":"'Project Info'!D45","v":74.534025272781079},{"$f":"'Project Info'!E45","v":37.923296058061368},{"$f":"'Project Info'!F45","v":0},{"$f":"'Project Info'!G45","v":0},{"$f":"'Project Info'!H45","v":0},{"$f":"'Project Info'!I45","v":0},{"$f":"'Project Info'!J45","v":0},{"$f":"'Project Info'!K45","v":0},{"$f":"'Project Info'!L45","v":0},0,0,{"$f":"AN112-AO112","v":0}]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E105","v":"Daycare"},null,{"$f":"K120","v":0.52},2590,"2025 App",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A46","v":90},{"$f":"'Project Info'!B46","v":95},{"$f":"'Project Info'!C46","v":92.016049160256074},{"$f":"'Project Info'!D46","v":72.911561930607689},{"$f":"'Project Info'!E46","v":36.467095439351091},{"$f":"'Project Info'!F46","v":0},{"$f":"'Project Info'!G46","v":0},{"$f":"'Project Info'!H46","v":0},{"$f":"'Project Info'!I46","v":0},{"$f":"'Project Info'!J46","v":0},{"$f":"'Project Info'!K46","v":0},{"$f":"'Project Info'!L46","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E106","v":"Dining: bar/lounge/leisure"},null,0.61,3613,"2025 App","Restaurant",null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A47","v":85},{"$f":"'Project Info'!B47","v":90},{"$f":"'Project Info'!C47","v":87.457811360655285},{"$f":"'Project Info'!D47","v":70.80538329449476},{"$f":"'Project Info'!E47","v":34.679413213566804},{"$f":"'Project Info'!F47","v":0},{"$f":"'Project Info'!G47","v":0},{"$f":"'Project Info'!H47","v":0},{"$f":"'Project Info'!I47","v":0},{"$f":"'Project Info'!J47","v":0},{"$f":"'Project Info'!K47","v":0},{"$f":"'Project Info'!L47","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E107","v":"Dining: Cafeteria/Fast Food"},null,0.54,5018,"2025 App","Restaurant 3 meals",null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A48","v":80},{"$f":"'Project Info'!B48","v":85},{"$f":"'Project Info'!C48","v":82.136788830239965},{"$f":"'Project Info'!D48","v":67.872393622439333},{"$f":"'Project Info'!E48","v":32.296248223809314},{"$f":"'Project Info'!F48","v":0},{"$f":"'Project Info'!G48","v":0},{"$f":"'Project Info'!H48","v":0},{"$f":"'Project Info'!I48","v":0},{"$f":"'Project Info'!J48","v":0},{"$f":"'Project Info'!K48","v":0},{"$f":"'Project Info'!L48","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E108","v":"Dining: Family"},null,0.56999999999999995,4315.5,"2025 App",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A49","v":75},{"$f":"'Project Info'!B49","v":80},{"$f":"'Project Info'!C49","v":76.988400157585886},{"$f":"'Project Info'!D49","v":65.129261896908645},{"$f":"'Project Info'!E49","v":30.190476812806729},{"$f":"'Project Info'!F49","v":0},{"$f":"'Project Info'!G49","v":0},{"$f":"'Project Info'!H49","v":0},{"$f":"'Project Info'!I49","v":0},{"$f":"'Project Info'!J49","v":0},{"$f":"'Project Info'!K49","v":0},{"$f":"'Project Info'!L49","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E109","v":"Dormitory"},null,0.34,3056,"2025 App",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A50","v":70},{"$f":"'Project Info'!B50","v":75},{"$f":"'Project Info'!C50","v":72.457982050814195},{"$f":"'Project Info'!D50","v":63.604425012889301},{"$f":"'Project Info'!E50","v":29.088683095945193},{"$f":"'Project Info'!F50","v":0},{"$f":"'Project Info'!G50","v":0},{"$f":"'Project Info'!H50","v":0},{"$f":"'Project Info'!I50","v":0},{"$f":"'Project Info'!J50","v":0},{"$f":"'Project Info'!K50","v":0},{"$f":"'Project Info'!L50","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E110","v":"Education - College/University"},null,0.52,4839,"2025 App","College/University",null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A51","v":65},{"$f":"'Project Info'!B51","v":70},{"$f":"'Project Info'!C51","v":67.815831070966169},{"$f":"'Project Info'!D51","v":61.631331368130574},{"$f":"'Project Info'!E51","v":27.661514889731574},{"$f":"'Project Info'!F51","v":0},{"$f":"'Project Info'!G51","v":0},{"$f":"'Project Info'!H51","v":0},{"$f":"'Project Info'!I51","v":0},{"$f":"'Project Info'!J51","v":0},{"$f":"'Project Info'!K51","v":0},{"$f":"'Project Info'!L51","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E111","v":"Education - Community College"},null,0.52,3255,"2025 App",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A52","v":60},{"$f":"'Project Info'!B52","v":65},{"$f":"'Project Info'!C52","v":62.535961472271332},{"$f":"'Project Info'!D52","v":57.135476922863582},{"$f":"'Project Info'!E52","v":24.623037157728302},{"$f":"'Project Info'!F52","v":0},{"$f":"'Project Info'!G52","v":0},{"$f":"'Project Info'!H52","v":0},{"$f":"'Project Info'!I52","v":0},{"$f":"'Project Info'!J52","v":0},{"$f":"'Project Info'!K52","v":0},{"$f":"'Project Info'!L52","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E112","v":"Education - K-12 School"},null,0.52,2788,"2025 App","School",null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A53","v":55},{"$f":"'Project Info'!B53","v":60},{"$f":"'Project Info'!C53","v":57.125792270740902},{"$f":"'Project Info'!D53","v":52.596971157053673},{"$f":"'Project Info'!E53","v":21.818001539159841},{"$f":"'Project Info'!F53","v":0},{"$f":"'Project Info'!G53","v":0},{"$f":"'Project Info'!H53","v":0},{"$f":"'Project Info'!I53","v":0},{"$f":"'Project Info'!J53","v":0},{"$f":"'Project Info'!K53","v":0},{"$f":"'Project Info'!L53","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E113","v":"Exercise center"},null,0.5,5468,"2025 App","From Eval - Grocery (assume similar hours)",null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A54","v":50},{"$f":"'Project Info'!B54","v":55},{"$f":"'Project Info'!C54","v":52.235698854337961},{"$f":"'Project Info'!D54","v":48.022768090099298},{"$f":"'Project Info'!E54","v":19.246640192796217},{"$f":"'Project Info'!F54","v":0},{"$f":"'Project Info'!G54","v":0},{"$f":"'Project Info'!H54","v":0},{"$f":"'Project Info'!I54","v":0},{"$f":"'Project Info'!J54","v":0},{"$f":"'Project Info'!K54","v":0},{"$f":"'Project Info'!L54","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E114","v":"Fire station"},null,0.4,5366,"2025 App","Public Order and Safety",null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A55","v":45},{"$f":"'Project Info'!B55","v":50},{"$f":"'Project Info'!C55","v":47.459170258371508},{"$f":"'Project Info'!D55","v":43.465397050422162},{"$f":"'Project Info'!E55","v":16.894183241713304},{"$f":"'Project Info'!F55","v":0},{"$f":"'Project Info'!G55","v":0},{"$f":"'Project Info'!H55","v":0},{"$f":"'Project Info'!I55","v":0},{"$f":"'Project Info'!J55","v":0},{"$f":"'Project Info'!K55","v":0},{"$f":"'Project Info'!L55","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E115","v":"Grocery"},null,{"$f":"K144","v":0.76},5468,"2025 App",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A56","v":40},{"$f":"'Project Info'!B56","v":45},{"$f":"'Project Info'!C56","v":42.677030404888129},{"$f":"'Project Info'!D56","v":38.812544504634097},{"$f":"'Project Info'!E56","v":14.690265649465921},{"$f":"'Project Info'!F56","v":0},{"$f":"'Project Info'!G56","v":0},{"$f":"'Project Info'!H56","v":0},{"$f":"'Project Info'!I56","v":0},{"$f":"'Project Info'!J56","v":0},{"$f":"'Project Info'!K56","v":0},{"$f":"'Project Info'!L56","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E116","v":"Gymnasium"},null,0.56000000000000005,5468,"2025 App","From Eval - Grocery (assume similar hours)",null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A57","v":35},{"$f":"'Project Info'!B57","v":40},{"$f":"'Project Info'!C57","v":37.333046773755832},{"$f":"'Project Info'!D57","v":33.904706919479686},{"$f":"'Project Info'!E57","v":12.53841602318813},{"$f":"'Project Info'!F57","v":0},{"$f":"'Project Info'!G57","v":0},{"$f":"'Project Info'!H57","v":0},{"$f":"'Project Info'!I57","v":0},{"$f":"'Project Info'!J57","v":0},{"$f":"'Project Info'!K57","v":0},{"$f":"'Project Info'!L57","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E117","v":"Health/Medical - Clinic"},null,0.54,3673,"2025 App",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A58","v":30},{"$f":"'Project Info'!B58","v":35},{"$f":"'Project Info'!C58","v":32.638179845662044},{"$f":"'Project Info'!D58","v":29.547170928664851},{"$f":"'Project Info'!E58","v":10.728972818165861},{"$f":"'Project Info'!F58","v":0},{"$f":"'Project Info'!G58","v":0},{"$f":"'Project Info'!H58","v":0},{"$f":"'Project Info'!I58","v":0},{"$f":"'Project Info'!J58","v":0},{"$f":"'Project Info'!K58","v":0},{"$f":"'Project Info'!L58","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E118","v":"Hospital"},null,0.63,5413,"2025 App",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A59","v":25},{"$f":"'Project Info'!B59","v":30},{"$f":"'Project Info'!C59","v":27.529264646850947},{"$f":"'Project Info'!D59","v":24.652717392657845},{"$f":"'Project Info'!E59","v":8.8041305482613303},{"$f":"'Project Info'!F59","v":0},{"$f":"'Project Info'!G59","v":0},{"$f":"'Project Info'!H59","v":0},{"$f":"'Project Info'!I59","v":0},{"$f":"'Project Info'!J59","v":0},{"$f":"'Project Info'!K59","v":0},{"$f":"'Project Info'!L59","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E119","v":"Hotel/Motel/Lodging"},null,0.52,4026,"2025 App","Lodging - Common Spaces",null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A60","v":20},{"$f":"'Project Info'!B60","v":25},{"$f":"'Project Info'!C60","v":22.998111483544687},{"$f":"'Project Info'!D60","v":20.383306659827422},{"$f":"'Project Info'!E60","v":7.246164547543378},{"$f":"'Project Info'!F60","v":0},{"$f":"'Project Info'!G60","v":0},{"$f":"'Project Info'!H60","v":0},{"$f":"'Project Info'!I60","v":0},{"$f":"'Project Info'!J60","v":0},{"$f":"'Project Info'!K60","v":0},{"$f":"'Project Info'!L60","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E120","v":"Industrial/Manufacturing - 1 Shift"},null,0.7,2857,"2025 App",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A61","v":15},{"$f":"'Project Info'!B61","v":20},{"$f":"'Project Info'!C61","v":17.808510327474309},{"$f":"'Project Info'!D61","v":15.420865796304254},{"$f":"'Project Info'!E61","v":5.5490484131518292},{"$f":"'Project Info'!F61","v":0},{"$f":"'Project Info'!G61","v":0},{"$f":"'Project Info'!H61","v":0},{"$f":"'Project Info'!I61","v":0},{"$f":"'Project Info'!J61","v":0},{"$f":"'Project Info'!K61","v":0},{"$f":"'Project Info'!L61","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E121","v":"Industrial/Manufacturing - 2 Shifts"},null,0.7,4730,"2025 App",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A62","v":10},{"$f":"'Project Info'!B62","v":15},{"$f":"'Project Info'!C62","v":12.269931130346862},{"$f":"'Project Info'!D62","v":10.318264913023604},{"$f":"'Project Info'!E62","v":3.9082824916941998},{"$f":"'Project Info'!F62","v":0},{"$f":"'Project Info'!G62","v":0},{"$f":"'Project Info'!H62","v":0},{"$f":"'Project Info'!I62","v":0},{"$f":"'Project Info'!J62","v":0},{"$f":"'Project Info'!K62","v":0},{"$f":"'Project Info'!L62","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E122","v":"Industrial/Manufacturing - 3 Shifts"},null,0.7,6631,"2025 App",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A63","v":5},{"$f":"'Project Info'!B63","v":10},{"$f":"'Project Info'!C63","v":7.3137581369917548},{"$f":"'Project Info'!D63","v":5.7052382449247707},{"$f":"'Project Info'!E63","v":2.5019418419888937},{"$f":"'Project Info'!F63","v":0},{"$f":"'Project Info'!G63","v":0},{"$f":"'Project Info'!H63","v":0},{"$f":"'Project Info'!I63","v":0},{"$f":"'Project Info'!J63","v":0},{"$f":"'Project Info'!K63","v":0},{"$f":"'Project Info'!L63","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E123","v":"Library"},null,0.71,2788,"2025 App","Same as Education",null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A64","v":0},{"$f":"'Project Info'!B64","v":5},{"$f":"'Project Info'!C64","v":2.6119461836144886},{"$f":"'Project Info'!D64","v":1.2699770062067783},{"$f":"'Project Info'!E64","v":1.2046477897733283},{"$f":"'Project Info'!F64","v":0},{"$f":"'Project Info'!G64","v":0},{"$f":"'Project Info'!H64","v":0},{"$f":"'Project Info'!I64","v":0},{"$f":"'Project Info'!J64","v":0},{"$f":"'Project Info'!K64","v":0},{"$f":"'Project Info'!L64","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E124","v":"Motion picture theater"},null,0.46,3613,"2025 App","From Bar/Lounge (assume similar hours)",null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A65","v":-5},{"$f":"'Project Info'!B65","v":0},{"$f":"'Project Info'!C65","v":-1.6731398516793925},{"$f":"'Project Info'!D65","v":-2.7083318773557807},{"$f":"'Project Info'!E65","v":7.9391832815876459E-2},{"$f":"'Project Info'!F65","v":0},{"$f":"'Project Info'!G65","v":0},{"$f":"'Project Info'!H65","v":0},{"$f":"'Project Info'!I65","v":0},{"$f":"'Project Info'!J65","v":0},{"$f":"'Project Info'!K65","v":0},{"$f":"'Project Info'!L65","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E125","v":"Multifamily"},null,0.31,4026,"2025 App","Commons Areas",null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A66","v":-10},{"$f":"'Project Info'!B66","v":-5},{"$f":"'Project Info'!C66","v":-6.5729865085377277},{"$f":"'Project Info'!D66","v":-7.2465935998252222},{"$f":"'Project Info'!E66","v":-1.168423365310433},{"$f":"'Project Info'!F66","v":0},{"$f":"'Project Info'!G66","v":0},{"$f":"'Project Info'!H66","v":0},{"$f":"'Project Info'!I66","v":0},{"$f":"'Project Info'!J66","v":0},{"$f":"'Project Info'!K66","v":0},{"$f":"'Project Info'!L66","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E126","v":"Museum"},null,0.61,2788,"2025 App","From Libraryr (assume similar hours)",null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A67","v":-15},{"$f":"'Project Info'!B67","v":-10},{"$f":"'Project Info'!C67","v":-15.32570353422995},{"$f":"'Project Info'!D67","v":-15.707838211108999},{"$f":"'Project Info'!E67","v":-3.4051318156661381},{"$f":"'Project Info'!F67","v":0},{"$f":"'Project Info'!G67","v":0},{"$f":"'Project Info'!H67","v":0},{"$f":"'Project Info'!I67","v":0},{"$f":"'Project Info'!J67","v":0},{"$f":"'Project Info'!K67","v":0},{"$f":"'Project Info'!L67","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E127","v":"Nursing Home"},null,{"$f":"K125","v":0.54},5413,"2025 App"]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E128","v":"Office - Medium/Large ( > 20,000 ft²)"},null,0.49,4181,"2025 App"]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E129","v":"Office - Small ( < 20,000 ft²)"},null,0.49,2567,"2025 App",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Unoccupied Hours",null,"Unoccupied Hrs Ltg Diversity (%)",null,0.15,"Bin Hours - Peak Period Breakdown",null,null,null,null,null,null,null,null,"Demand"]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E130","v":"Parking garage"},null,0.13,6552,"2025 App",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer",null,null,"Reduction"]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E131","v":"Penitentiary"},null,0.49,5413,"2025 App","From Nursing Home (assume similar hours)",null,null,null,null,null,null,null,null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Base","Design","Elec"]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E132","v":"Performing arts theater"},null,0.83,{"$f":"L132","v":3613},"2025 App","From Movie Theater (assume similar hours)",null,null,null,null,null,null,null,null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","kW","kW","kW"]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E133","v":"Police station"},null,0.52,5366,"2025 App","Public Order and Safety",null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A74","v":100},{"$f":"'Project Info'!B74","v":105},{"$f":"'Project Info'!C74","v":102},{"$f":"'Project Info'!D74","v":76},{"$f":"'Project Info'!E74","v":40},{"$f":"'Project Info'!F74","v":0},{"$f":"'Project Info'!G74","v":0},{"$f":"'Project Info'!H74","v":0},{"$f":"'Project Info'!I74","v":0},{"$f":"'Project Info'!J74","v":0},{"$f":"'Project Info'!K74","v":0},{"$f":"'Project Info'!L74","v":0},{"$f":"$AF$137*$V$9/1000","v":0},{"$f":"$AF$137*$V$10/1000","v":0},{"$f":"AN141-AO141","v":0}]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E134","v":"Post office"},null,0.52,3425,"2025 App","Public Services (non food)",null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A75","v":95},{"$f":"'Project Info'!B75","v":100},{"$f":"'Project Info'!C75","v":95.219272727272724},{"$f":"'Project Info'!D75","v":74.534025272781079},{"$f":"'Project Info'!E75","v":37.923296058061368},{"$f":"'Project Info'!F75","v":0},{"$f":"'Project Info'!G75","v":0},{"$f":"'Project Info'!H75","v":0},{"$f":"'Project Info'!I75","v":0},{"$f":"'Project Info'!J75","v":0},{"$f":"'Project Info'!K75","v":0},{"$f":"'Project Info'!L75","v":0},0,0,{"$f":"AN142-AO142","v":0}]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E135","v":"Religious Worship/Church"},null,0.6,1810,"2025 App",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A76","v":90},{"$f":"'Project Info'!B76","v":95},{"$f":"'Project Info'!C76","v":92.016049160256074},{"$f":"'Project Info'!D76","v":72.911561930607689},{"$f":"'Project Info'!E76","v":36.467095439351091},{"$f":"'Project Info'!F76","v":0},{"$f":"'Project Info'!G76","v":0},{"$f":"'Project Info'!H76","v":0},{"$f":"'Project Info'!I76","v":0},{"$f":"'Project Info'!J76","v":0},{"$f":"'Project Info'!K76","v":0},{"$f":"'Project Info'!L76","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E136","v":"Retail"},null,0.76,4939,"2025 App",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A77","v":85},{"$f":"'Project Info'!B77","v":90},{"$f":"'Project Info'!C77","v":87.457811360655285},{"$f":"'Project Info'!D77","v":70.80538329449476},{"$f":"'Project Info'!E77","v":34.679413213566804},{"$f":"'Project Info'!F77","v":0},{"$f":"'Project Info'!G77","v":0},{"$f":"'Project Info'!H77","v":0},{"$f":"'Project Info'!I77","v":0},{"$f":"'Project Info'!J77","v":0},{"$f":"'Project Info'!K77","v":0},{"$f":"'Project Info'!L77","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E137","v":"Sports arena"},null,0.55000000000000004,{"$f":"L124","v":5468},"2025 App","From Gymnasium",null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A78","v":80},{"$f":"'Project Info'!B78","v":85},{"$f":"'Project Info'!C78","v":82.136788830239965},{"$f":"'Project Info'!D78","v":67.872393622439333},{"$f":"'Project Info'!E78","v":32.296248223809314},{"$f":"'Project Info'!F78","v":0},{"$f":"'Project Info'!G78","v":0},{"$f":"'Project Info'!H78","v":0},{"$f":"'Project Info'!I78","v":0},{"$f":"'Project Info'!J78","v":0},{"$f":"'Project Info'!K78","v":0},{"$f":"'Project Info'!L78","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E138","v":"Storage Facility"},null,{"$f":"K149","v":0.4},3420,"2025 App","From Warehouse - Distribution Center",null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A79","v":75},{"$f":"'Project Info'!B79","v":80},{"$f":"'Project Info'!C79","v":76.988400157585886},{"$f":"'Project Info'!D79","v":65.129261896908645},{"$f":"'Project Info'!E79","v":30.190476812806729},{"$f":"'Project Info'!F79","v":0},{"$f":"'Project Info'!G79","v":0},{"$f":"'Project Info'!H79","v":0},{"$f":"'Project Info'!I79","v":0},{"$f":"'Project Info'!J79","v":0},{"$f":"'Project Info'!K79","v":0},{"$f":"'Project Info'!L79","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E139","v":"Town hall"},null,0.53,3425,"2025 App","Public Services (non food)",null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A80","v":70},{"$f":"'Project Info'!B80","v":75},{"$f":"'Project Info'!C80","v":72.457982050814195},{"$f":"'Project Info'!D80","v":63.604425012889301},{"$f":"'Project Info'!E80","v":29.088683095945193},{"$f":"'Project Info'!F80","v":0},{"$f":"'Project Info'!G80","v":0},{"$f":"'Project Info'!H80","v":0},{"$f":"'Project Info'!I80","v":0},{"$f":"'Project Info'!J80","v":0},{"$f":"'Project Info'!K80","v":0},{"$f":"'Project Info'!L80","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E140","v":"Transportation"},null,0.42,6512,"2025 App","From Warehouse - Distribution Center",null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A81","v":65},{"$f":"'Project Info'!B81","v":70},{"$f":"'Project Info'!C81","v":67.815831070966169},{"$f":"'Project Info'!D81","v":61.631331368130574},{"$f":"'Project Info'!E81","v":27.661514889731574},{"$f":"'Project Info'!F81","v":0},{"$f":"'Project Info'!G81","v":0},{"$f":"'Project Info'!H81","v":0},{"$f":"'Project Info'!I81","v":0},{"$f":"'Project Info'!J81","v":0},{"$f":"'Project Info'!K81","v":0},{"$f":"'Project Info'!L81","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E141","v":"Warehouse - Distribution Center"},null,0.4,6512,"2025 App",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A82","v":60},{"$f":"'Project Info'!B82","v":65},{"$f":"'Project Info'!C82","v":62.535961472271332},{"$f":"'Project Info'!D82","v":57.135476922863582},{"$f":"'Project Info'!E82","v":24.623037157728302},{"$f":"'Project Info'!F82","v":0},{"$f":"'Project Info'!G82","v":0},{"$f":"'Project Info'!H82","v":0},{"$f":"'Project Info'!I82","v":0},{"$f":"'Project Info'!J82","v":0},{"$f":"'Project Info'!K82","v":0},{"$f":"'Project Info'!L82","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E142","v":"Warehouse - Inactive Storage"},null,0.4,2316,"2025 App",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A83","v":55},{"$f":"'Project Info'!B83","v":60},{"$f":"'Project Info'!C83","v":57.125792270740902},{"$f":"'Project Info'!D83","v":52.596971157053673},{"$f":"'Project Info'!E83","v":21.818001539159841},{"$f":"'Project Info'!F83","v":0},{"$f":"'Project Info'!G83","v":0},{"$f":"'Project Info'!H83","v":0},{"$f":"'Project Info'!I83","v":0},{"$f":"'Project Info'!J83","v":0},{"$f":"'Project Info'!K83","v":0},{"$f":"'Project Info'!L83","v":0},0,0,0]
[null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E143","v":"Workshop"},null,0.71,{"$f":"L137","v":2567},"2025 App","From Small Office",null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A84","v":50},{"$f":"'Project Info'!B84","v":55},{"$f":"'Project Info'!C84","v":52.235698854337961},{"$f":"'Project Info'!D84","v":48.022768090099298},{"$f":"'Project Info'!E84","v":19.246640192796217},{"$f":"'Project Info'!F84","v":0},{"$f":"'Project Info'!G84","v":0},{"$f":"'Project Info'!H84","v":0},{"$f":"'Project Info'!I84","v":0},{"$f":"'Project Info'!J84","v":0},{"$f":"'Project Info'!K84","v":0},{"$f":"'Project Info'!L84","v":0},0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A85","v":45},{"$f":"'Project Info'!B85","v":50},{"$f":"'Project Info'!C85","v":47.459170258371508},{"$f":"'Project Info'!D85","v":43.465397050422162},{"$f":"'Project Info'!E85","v":16.894183241713304},{"$f":"'Project Info'!F85","v":0},{"$f":"'Project Info'!G85","v":0},{"$f":"'Project Info'!H85","v":0},{"$f":"'Project Info'!I85","v":0},{"$f":"'Project Info'!J85","v":0},{"$f":"'Project Info'!K85","v":0},{"$f":"'Project Info'!L85","v":0},0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A86","v":40},{"$f":"'Project Info'!B86","v":45},{"$f":"'Project Info'!C86","v":42.677030404888129},{"$f":"'Project Info'!D86","v":38.812544504634097},{"$f":"'Project Info'!E86","v":14.690265649465921},{"$f":"'Project Info'!F86","v":0},{"$f":"'Project Info'!G86","v":0},{"$f":"'Project Info'!H86","v":0},{"$f":"'Project Info'!I86","v":0},{"$f":"'Project Info'!J86","v":0},{"$f":"'Project Info'!K86","v":0},{"$f":"'Project Info'!L86","v":0},0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A87","v":35},{"$f":"'Project Info'!B87","v":40},{"$f":"'Project Info'!C87","v":37.333046773755832},{"$f":"'Project Info'!D87","v":33.904706919479686},{"$f":"'Project Info'!E87","v":12.53841602318813},{"$f":"'Project Info'!F87","v":0},{"$f":"'Project Info'!G87","v":0},{"$f":"'Project Info'!H87","v":0},{"$f":"'Project Info'!I87","v":0},{"$f":"'Project Info'!J87","v":0},{"$f":"'Project Info'!K87","v":0},{"$f":"'Project Info'!L87","v":0},0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A88","v":30},{"$f":"'Project Info'!B88","v":35},{"$f":"'Project Info'!C88","v":32.638179845662044},{"$f":"'Project Info'!D88","v":29.547170928664851},{"$f":"'Project Info'!E88","v":10.728972818165861},{"$f":"'Project Info'!F88","v":0},{"$f":"'Project Info'!G88","v":0},{"$f":"'Project Info'!H88","v":0},{"$f":"'Project Info'!I88","v":0},{"$f":"'Project Info'!J88","v":0},{"$f":"'Project Info'!K88","v":0},{"$f":"'Project Info'!L88","v":0},0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A89","v":25},{"$f":"'Project Info'!B89","v":30},{"$f":"'Project Info'!C89","v":27.529264646850947},{"$f":"'Project Info'!D89","v":24.652717392657845},{"$f":"'Project Info'!E89","v":8.8041305482613303},{"$f":"'Project Info'!F89","v":0},{"$f":"'Project Info'!G89","v":0},{"$f":"'Project Info'!H89","v":0},{"$f":"'Project Info'!I89","v":0},{"$f":"'Project Info'!J89","v":0},{"$f":"'Project Info'!K89","v":0},{"$f":"'Project Info'!L89","v":0},0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A90","v":20},{"$f":"'Project Info'!B90","v":25},{"$f":"'Project Info'!C90","v":22.998111483544687},{"$f":"'Project Info'!D90","v":20.383306659827422},{"$f":"'Project Info'!E90","v":7.246164547543378},{"$f":"'Project Info'!F90","v":0},{"$f":"'Project Info'!G90","v":0},{"$f":"'Project Info'!H90","v":0},{"$f":"'Project Info'!I90","v":0},{"$f":"'Project Info'!J90","v":0},{"$f":"'Project Info'!K90","v":0},{"$f":"'Project Info'!L90","v":0},0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A91","v":15},{"$f":"'Project Info'!B91","v":20},{"$f":"'Project Info'!C91","v":17.808510327474309},{"$f":"'Project Info'!D91","v":15.420865796304254},{"$f":"'Project Info'!E91","v":5.5490484131518292},{"$f":"'Project Info'!F91","v":0},{"$f":"'Project Info'!G91","v":0},{"$f":"'Project Info'!H91","v":0},{"$f":"'Project Info'!I91","v":0},{"$f":"'Project Info'!J91","v":0},{"$f":"'Project Info'!K91","v":0},{"$f":"'Project Info'!L91","v":0},0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A92","v":10},{"$f":"'Project Info'!B92","v":15},{"$f":"'Project Info'!C92","v":12.269931130346862},{"$f":"'Project Info'!D92","v":10.318264913023604},{"$f":"'Project Info'!E92","v":3.9082824916941998},{"$f":"'Project Info'!F92","v":0},{"$f":"'Project Info'!G92","v":0},{"$f":"'Project Info'!H92","v":0},{"$f":"'Project Info'!I92","v":0},{"$f":"'Project Info'!J92","v":0},{"$f":"'Project Info'!K92","v":0},{"$f":"'Project Info'!L92","v":0},0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A93","v":5},{"$f":"'Project Info'!B93","v":10},{"$f":"'Project Info'!C93","v":7.3137581369917548},{"$f":"'Project Info'!D93","v":5.7052382449247707},{"$f":"'Project Info'!E93","v":2.5019418419888937},{"$f":"'Project Info'!F93","v":0},{"$f":"'Project Info'!G93","v":0},{"$f":"'Project Info'!H93","v":0},{"$f":"'Project Info'!I93","v":0},{"$f":"'Project Info'!J93","v":0},{"$f":"'Project Info'!K93","v":0},{"$f":"'Project Info'!L93","v":0},0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A94","v":0},{"$f":"'Project Info'!B94","v":5},{"$f":"'Project Info'!C94","v":2.6119461836144886},{"$f":"'Project Info'!D94","v":1.2699770062067783},{"$f":"'Project Info'!E94","v":1.2046477897733283},{"$f":"'Project Info'!F94","v":8760},{"$f":"'Project Info'!G94","v":2672},{"$f":"'Project Info'!H94","v":3160},{"$f":"'Project Info'!I94","v":1344},{"$f":"'Project Info'!J94","v":1584},{"$f":"'Project Info'!K94","v":88},{"$f":"'Project Info'!L94","v":264},0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A95","v":-5},{"$f":"'Project Info'!B95","v":0},{"$f":"'Project Info'!C95","v":-1.6731398516793925},{"$f":"'Project Info'!D95","v":-2.7083318773557807},{"$f":"'Project Info'!E95","v":7.9391832815876459E-2},{"$f":"'Project Info'!F95","v":0},{"$f":"'Project Info'!G95","v":0},{"$f":"'Project Info'!H95","v":0},{"$f":"'Project Info'!I95","v":0},{"$f":"'Project Info'!J95","v":0},{"$f":"'Project Info'!K95","v":0},{"$f":"'Project Info'!L95","v":0},0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A96","v":-10},{"$f":"'Project Info'!B96","v":-5},{"$f":"'Project Info'!C96","v":-6.5729865085377277},{"$f":"'Project Info'!D96","v":-7.2465935998252222},{"$f":"'Project Info'!E96","v":-1.168423365310433},{"$f":"'Project Info'!F96","v":0},{"$f":"'Project Info'!G96","v":0},{"$f":"'Project Info'!H96","v":0},{"$f":"'Project Info'!I96","v":0},{"$f":"'Project Info'!J96","v":0},{"$f":"'Project Info'!K96","v":0},{"$f":"'Project Info'!L96","v":0},0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!A97","v":-15},{"$f":"'Project Info'!B97","v":-10},{"$f":"'Project Info'!C97","v":-15.32570353422995},{"$f":"'Project Info'!D97","v":-15.707838211108999},{"$f":"'Project Info'!E97","v":-3.4051318156661381},{"$f":"'Project Info'!F97","v":0},{"$f":"'Project Info'!G97","v":0},{"$f":"'Project Info'!H97","v":0},{"$f":"'Project Info'!I97","v":0},{"$f":"'Project Info'!J97","v":0},{"$f":"'Project Info'!K97","v":0},{"$f":"'Project Info'!L97","v":0},0,0,0]

{"sheet":"Exterior Lighting","index":10,"n_rows":130,"n_cols":28,"rows_kept":130,"cut":false,"hidden":true,"merged":[[1,10,5,17],[7,10,13,17],[191,17,197,17],[191,20,197,20],[184,17,190,17],[184,20,190,20]]}
["Complete Savings Summary",null,null,null,null,"Measure Summary",null,null,null,null,"Measure Description"]
["Annual kWh Savings",null,null,{"$f":"R25","v":0},null,null,null,"Value","Unit",null,"This measure considers savings from a high performance EXTERIOR lighting system design with reduced lighting power below the baseline maximum allowable value. \n*The Lighting COMCheck Report should be used to verify the Design Watts. Any alternative approach to estimating design watts must first be approved by the PA."]
["% On Peak",null,null,{"$f":"IF(D2<=0,0,MIN(1,A15+C15))","v":0},null,"Annual Electric Savings",null,{"$f":"R25","v":0},"kWh"]
["Max kW",null,null,{"$f":"R23","v":0},null,"Annual Fuel Savings",null,{"$f":"D7*C28","v":{"$error":"#N/A"}},{"$f":"D20","v":{"$error":"#N/A"}}]
["Summer kW",null,null,0,null,"Incremental","Default Calc",{"$f":"IFERROR($T$69*R23*1000,0)","v":0},"$"]
["Winter kW",null,null,{"$f":"R23","v":0},null,"Cost","Project Specific",null,"$ (Optional)"]
["Annual Fuel Savings (MMBtu)",null,null,0,null,"Estimated Incentive",null,{"$f":"IF(AND($C$24>=0,$C$25>=0),MAX(0,H3)*C24+MAX(0,H4)*C25,\"TBD\")","v":{"$error":"#N/A"}},"$",null,"Notes (Optional)"]
["Incremental Cost (Default Calc)",null,null,{"$f":"H5","v":0}]
["Incremental Cost (for Summary)",null,null,{"$f":"IF(H6>0,H6,D8)","v":0},null,"Project Information Summary"]
["kWh Savings by Peak Period",null,null,null,null,null,"STATE","NH"]
["Winter","Winter","Summer","Summer",null,null,"Program Year",{"$f":"'Project Info'!C19","v":0}]
["On-Peak","Off-Peak","On-Peak","Off-Peak",null,null,"Code IECC Version",{"$f":"MID('Project Info'!C20,1,4)","v":"2018"}]
["kWh","kWh","kWh","kWh",null,null,"Electric PA",{"$f":"'Project Info'!F3","v":0}]
[{"$f":"$H$3*A15","v":0},{"$f":"$H$3*B15","v":0},0,0,null,"*NOTE: Baseline values are automated and cannot be changed."]
[{"$f":"24%*(H3>0)","v":0},{"$f":"57%*(H3>0)","v":0},{"$f":"6%*(H3>0)","v":0},{"$f":"13%*(H3>0)","v":0}]
[null,null,null,null,null,"Table 1: Design Exterior Lighting Inputs",null,null,null,null,null,null,null,null,null,"Savings Calculation"]
["Utility Rates",null,null,null,null,null,null,null,"Manual (Table 3)","COMCheck Report",null,null,null,null,null,null,null,"Tradable","Non-Tradable"]
[null,null,"Rate","Unit",null,null,null,"Design Total Exterior Watts",{"$f":"$AB$26","v":0},null,"< If used, the COMCheck Report should be provided.",null,null,null,null,null,"Baseline Watts Breakdown",{"$f":"SUM(N25:N45)","v":600},{"$f":"SUM(N47:N55)","v":0}]
["Electric",null,{"$f":"'ECM Summary'!$E$31","v":0.1593},"kWh",null,null,null,"Ext Fixtures Annual Run Hours",{"$f":"IF(H10=\"NH\",4345,3672)","v":4345}]
[{"$f":"'ECM Summary'!$C$32","v":0},null,{"$f":"'ECM Summary'!$E$32","v":{"$error":"#N/A"}},{"$f":"'ECM Summary'!$F$32","v":{"$error":"#N/A"}},null,null,null,"(Optional) Lighting Hours Override"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Baseline Total Watts",{"$f":"R18+S18","v":600}]
["Custom Incentive Rates",null,null,null,null,"Table 2: Baseline Lighting Allowance Inputs",null,null,null,null,null,null,null,null,null,null,"Design Total Watts",{"$f":"IF(J18>0,J18,I18)","v":0}]
[null,null,"Rate","Unit",null,null,null,null,null,"Project Lighting Zone",null,"Baseline",null,"Baseline",null,null,"Design kW Reduction",{"$f":"(R21-R22)/1000*(R22>0)","v":0}]
["Electric",null,{"$f":"'ECM Summary'!$J$31","v":0.28000000000000003},"kWh",null,null,null,null,null,"Unit","Qty","Watts per unit",null,"Watts",null,null,"Exterior Lighting Hours",{"$f":"IF(I20>0,I20,I19)","v":4345}]
[{"$f":"'ECM Summary'!$H$32","v":0},null,{"$f":"'ECM Summary'!$J$32","v":0},{"$f":"'ECM Summary'!$K$32","v":{"$error":"#N/A"}},1,"Base Allowance",null,null,null,null,1,{"$f":"OFFSET($K$64,MATCH(E25,$F$65:$F$95),MATCH($K$23,$L$64:$P$64))","v":600},null,{"$f":"L25*K25","v":600},null,null,"Annual kWh Savings",{"$f":"R23*R24","v":0}]
[null,null,null,null,2,"Uncovered Parking Areas",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Design Watts:",{"$f":"SUM(AB30:AB55)","v":0}]
["Fossil Fuel",null,{"$f":"'Project Info'!C21","v":0},null,3,"Parking Areas and Drives",null,null,null,"ft²",null,{"$f":"OFFSET($K$64,MATCH(E27,$F$65:$F$95),MATCH($K$23,$L$64:$P$64))","v":4.02E-2},null,{"$f":"L27*K27","v":0},null,"Table 3: Proposed/Design Exterior Lighting Fixtures"]
["Fuel Conversion",null,{"$f":"LOOKUP(C27,'Project Info'!X102:X104,'Project Info'!Z102:Z104)","v":{"$error":"#N/A"}},null,4,"Building Grounds",null,null,null,null,null,null,null,null,null,"Fixture",null,null,null,null,null,null,null,null,null,"Total Fixture","Fixture Power","Total Design"]
[null,null,null,null,5,"Walkways and ramps less than 10 ft wide",null,null,null,"linear ft",null,{"$f":"OFFSET($K$64,MATCH(E29,$F$65:$F$95),MATCH($K$23,$L$64:$P$64))","v":0.46899999999999997},null,{"$f":"L29*K29","v":0},null,"ID","Manufacturer","Model Number",null,null,null,"Fixture Type (Optional)",null,null,null,"Qty","W/Fixture","Watts"]
[null,null,null,null,6,"Walkways and ramps 10 ft wide or greater, ",null,null,null,"ft²",null,{"$f":"OFFSET($K$64,MATCH(E30,$F$65:$F$95),MATCH($K$23,$L$64:$P$64))","v":9.3800000000000008E-2},null,{"$f":"L30*K30","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"Z30*AA30","v":0}]
[null,null,null,null,7,"           plaza areas, special feature areas",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"Z31*AA31","v":0}]
[null,null,null,null,8,"Dining Areas",null,null,null,"ft²",null,{"$f":"OFFSET($K$64,MATCH(E32,$F$65:$F$95),MATCH($K$23,$L$64:$P$64))","v":0.65},null,{"$f":"L32*K32","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,9,"Stairways",null,null,null,"ft²",null,{"$f":"OFFSET($K$64,MATCH(E33,$F$65:$F$95),MATCH($K$23,$L$64:$P$64))","v":0.67},null,{"$f":"L33*K33","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,10,"Pedestrian Tunnels",null,null,null,"ft²",null,{"$f":"OFFSET($K$64,MATCH(E34,$F$65:$F$95),MATCH($K$23,$L$64:$P$64))","v":0.10050000000000001},null,{"$f":"L34*K34","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,11,"Landscaping",null,null,null,"ft²",null,{"$f":"OFFSET($K$64,MATCH(E35,$F$65:$F$95),MATCH($K$23,$L$64:$P$64))","v":0.04},null,{"$f":"L35*K35","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,12,"Building Entrances and Exits",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,13,"Main Entries",null,null,null,"linear ft",null,{"$f":"OFFSET($K$64,MATCH(E37,$F$65:$F$95),MATCH($K$23,$L$64:$P$64))","v":13.4},null,{"$f":"L37*K37","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,14,"Entry canopies",null,null,null,"ft²",null,{"$f":"OFFSET($K$64,MATCH(E38,$F$65:$F$95),MATCH($K$23,$L$64:$P$64))","v":0.16750000000000001},null,{"$f":"L38*K38","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,15,"Other Doors",null,null,null,"linear ft",null,{"$f":"OFFSET($K$64,MATCH(E39,$F$65:$F$95),MATCH($K$23,$L$64:$P$64))","v":13.4},null,{"$f":"L39*K39","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,16,"Sales Canopies",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,17,"Free-standing and attached",null,null,null,"ft²",null,{"$f":"OFFSET($K$64,MATCH(E41,$F$65:$F$95),MATCH($K$23,$L$64:$P$64))","v":0.40200000000000002},null,{"$f":"L41*K41","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,18,"Outdoor Sales",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,19,"Open areas (including vehicle sales lots)",null,null,null,"ft²",null,{"$f":"OFFSET($K$64,MATCH(E43,$F$65:$F$95),MATCH($K$23,$L$64:$P$64))","v":0.16750000000000001},null,{"$f":"L43*K43","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"Z43*AA43","v":0}]
[null,null,null,null,20,"Street frontage for vehicle sales lots",null,null,null,"linear ft",null,{"$f":"OFFSET($K$64,MATCH(E44,$F$65:$F$95),MATCH($K$23,$L$64:$P$64))","v":6.7},null,{"$f":"L44*K44","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,21,"          in addition to \"open area\" allowance",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,22,"Building Exteriors (Non-Tradable)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,23,"Building facades",null,null,null,"ft²",null,{"$f":"OFFSET($K$64,MATCH(E47,$F$65:$F$95),MATCH($K$23,$L$64:$P$64))","v":5.0250000000000003E-2},null,{"$f":"L47*K47","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,24,"Automated teller machines (ATM)",null,null,null,"Watts",null,{"$f":"OFFSET($K$64,MATCH(E48,$F$65:$F$95),MATCH($K$23,$L$64:$P$64))","v":45},null,{"$f":"L48*K48","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,25,"          and night depositories",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,26,"Uncovered entrances and gatehouse inpection",null,null,null,"ft²",null,{"$f":"OFFSET($K$64,MATCH(E50,$F$65:$F$95),MATCH($K$23,$L$64:$P$64))","v":0.50250000000000006},null,{"$f":"L50*K50","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,27,"          stations at guarded facilities",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,28,"Uncovered loading areas for law enforcement, fire,",null,null,null,"ft²",null,{"$f":"OFFSET($K$64,MATCH(E52,$F$65:$F$95),MATCH($K$23,$L$64:$P$64))","v":0.33500000000000002},null,{"$f":"L52*K52","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,29,"          ambulance and other emergency service vehicles",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"Z53*AA53","v":0}]
[null,null,null,null,30,"Drive-up windows and doors",null,null,null,"Drive-thru Qty",null,{"$f":"OFFSET($K$64,MATCH(E54,$F$65:$F$95),MATCH($K$23,$L$64:$P$64))","v":200},null,{"$f":"L54*K54","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,31,"Parking near 24-hour retail entrances",null,null,null,"Main Entry Qty",null,{"$f":"OFFSET($K$64,MATCH(E55,$F$65:$F$95),MATCH($K$23,$L$64:$P$64))","v":400},null,{"$f":"L55*K55","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"Z55*AA55","v":0}]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,"Code IECC Version",{"$f":"H12","v":"2018"}]
[null,null,null,null,null,null,null,"NH ISP, % of 2015 IECC Values",0.67]
[null,null,null,null,null,null,"Baseline Exterior Lighting Power Allowances",null,null,null,null,"Default Zn 2","Lighting Zone"]
[null,null,null,null,null,null,"Rows in Yellow use 2018 IECC due to better LPD or no category in 2015 IECC",null,null,null,"Unit",0,1,2,3,4]
[null,null,null,null,null,1,"Base Allowance",null,null,null,"Watts",{"$f":"N65","v":600},{"$f":"M100","v":500},{"$f":"N100","v":600},{"$f":"O100","v":750},{"$f":"P100","v":1300}]
[null,null,null,null,null,2,"Uncovered Parking Areas"]
[null,null,null,null,null,3,"Parking Areas and Drives",null,null,null,"W/ft²",{"$f":"N67","v":4.02E-2},{"$f":"$I$62*M102","v":2.6800000000000001E-2},{"$f":"$I$62*N102","v":4.02E-2},{"$f":"$I$62*O102","v":6.7000000000000004E-2},{"$f":"$I$62*P102","v":8.7100000000000011E-2}]
[null,null,null,null,null,4,"Building Grounds",null,null,null,null,null,null,null,null,null,null,null,"Incremental Cost"]
[null,null,null,null,null,5,"Walkways and ramps less than 10 ft wide",null,null,null,"W/linear ft",0.46899999999999997,{"$f":"$I$62*M104","v":0.46899999999999997},0.46899999999999997,0.53600000000000003,0.67,null,null,"LPD $/Watt Saved",5]
[null,null,null,null,null,6,"Walkways and ramps 10 ft wide or greater, ",null,null,null,"W/ft²",9.3800000000000008E-2,9.3800000000000008E-2,9.3800000000000008E-2,0.1072,0.13400000000000001]
[null,null,null,null,null,7,"           plaza areas, special feature areas"]
[null,null,null,null,null,8,"Dining Areas",null,null,null,"W/ft²",0.65,0.65,0.65,0.75,0.95]
[null,null,null,null,null,9,"Stairways",null,null,null,"W/ft²",0.67,{"$f":"$I$62*M108","v":0.50250000000000006},0.67,0.67,0.67]
[null,null,null,null,null,10,"Pedestrian Tunnels",null,null,null,"W/ft²",0.10050000000000001,0.10050000000000001,0.10050000000000001,0.13400000000000001,0.20100000000000001]
[null,null,null,null,null,11,"Landscaping",null,null,null,"W/ft²",0.04,0.03,0.04,0.04,0.04]
[null,null,null,null,null,12,"Building Entrances and Exits"]
[null,null,null,null,null,13,"Main Entries",null,null,null,"W/linear ft",13.4,{"$f":"$I$62*M112","v":13.4},13.4,20.100000000000001,20.100000000000001]
[null,null,null,null,null,14,"Entry canopies",null,null,null,"W/ft²",0.16750000000000001,0.16750000000000001,0.16750000000000001,0.26800000000000002,0.26800000000000002]
[null,null,null,null,null,15,"Other Doors",null,null,null,"W/linear ft",13.4,13.4,13.4,13.4,13.4]
[null,null,null,null,null,16,"Sales Canopies"]
[null,null,null,null,null,17,"Free-standing and attached",null,null,null,"W/ft²",0.40200000000000002,{"$f":"$I$62*M116","v":0.40200000000000002},{"$f":"$I$62*N116","v":0.40200000000000002},{"$f":"$I$62*O116","v":0.53600000000000003},{"$f":"$I$62*P116","v":0.67}]
[null,null,null,null,null,18,"Outdoor Sales"]
[null,null,null,null,null,19,"Open areas (including vehicle sales lots)",null,null,null,"W/ft²",0.16750000000000001,{"$f":"$I$62*M118","v":0.16750000000000001},0.16750000000000001,0.33500000000000002,0.46899999999999997]
[null,null,null,null,null,20,"Street frontage for vehicle sales lots",null,null,null,"W/linear ft",6.7,0,6.7,6.7,20.100000000000001]
[null,null,null,null,null,21,"          in addition to \"open area\" allowance"]
[null,null,null,null,null,22,"Building Exteriors"]
[null,null,null,null,null,23,"Building facades",null,null,null,"W/ft²",5.0250000000000003E-2,{"$f":"$I$62*M122","v":0},{"$f":"$I$62*N122","v":5.0250000000000003E-2},{"$f":"$I$62*O122","v":7.5710000000000013E-2},{"$f":"$I$62*P122","v":0.10050000000000001}]
[null,null,null,null,null,24,"Automated teller machines (ATM)",null,null,null,"Watts",45,45,45,45,45,135,"First"]
[null,null,null,null,null,25,"          and night depositories"]
[null,null,null,null,null,26,"Uncovered entrances and gatehouse inpection",null,null,null,"W/ft²",0.50250000000000006,{"$f":"$I$62*M125","v":0.50250000000000006},{"$f":"$I$62*N125","v":0.50250000000000006},{"$f":"$I$62*O125","v":0.50250000000000006},{"$f":"$I$62*P125","v":0.50250000000000006}]
[null,null,null,null,null,27,"          stations at guarded facilities"]
[null,null,null,null,null,28,"Uncovered loading areas for law enforcement, fire,",null,null,null,"W/ft²",0.33500000000000002,{"$f":"$I$62*M127","v":0.33500000000000002},{"$f":"$I$62*N127","v":0.33500000000000002},{"$f":"$I$62*O127","v":0.33500000000000002},{"$f":"$I$62*P127","v":0.33500000000000002}]
[null,null,null,null,null,29,"          ambulance and other emergency service vehicles"]
[null,null,null,null,null,30,"Drive-up windows and doors",null,null,null,"Drive-thru",200,200,200,200,200]
[null,null,null,null,null,31,"Parking near 24-hour retail entrances",null,null,null,"Entry",400,400,400,400,400]
[]
[]
[null,null,null,null,null,null,"2015 IECC Values",null,null,null,null,null,"Lighting Zone"]
[null,null,null,null,null,null,null,null,null,null,"Unit",null,1,2,3,4]
[null,null,null,null,null,null,"Base Allowance",null,null,null,"Watts",null,500,600,750,1300]
[null,null,null,null,null,null,"Uncovered Parking Areas"]
[null,null,null,null,null,null,"Parking Areas and Drives",null,null,null,"W/ft²",null,0.04,0.06,0.1,0.13]
[null,null,null,null,null,null,"Building Grounds"]
[null,null,null,null,null,null,"Walkways and ramps less than 10 ft wide",null,null,null,"W/linear ft",null,0.7,0.7,0.8,1]
[null,null,null,null,null,null,"Walkways and ramps 10 ft wide or greater, ",null,null,null,"W/ft²",null,0.14000000000000001,0.14000000000000001,0.16,0.2]
[null,null,null,null,null,null,"           plaza areas, special feature areas"]
[null,null,null,null,null,null,"Dining Areas",null,null,null,"W/ft²",null,0.65,0.65,0.75,0.95]
[null,null,null,null,null,null,"Stairways",null,null,null,"W/ft²",null,0.75,1,1,1]
[null,null,null,null,null,null,"Pedestrian Tunnels",null,null,null,"W/ft²",null,0.15,0.15,0.2,0.3]
[null,null,null,null,null,null,"Landscaping",null,null,null,"W/ft²",null,0.03,0.04,0.04,0.04]
[null,null,null,null,null,null,"Building Entrances and Exits"]
[null,null,null,null,null,null,"Main Entries",null,null,null,"W/linear ft",null,20,20,30,30]
[null,null,null,null,null,null,"Entry canopies",null,null,null,"W/ft²",null,0.25,0.25,0.4,0.4]
[null,null,null,null,null,null,"Other Doors",null,null,null,"W/linear ft",null,20,20,20,20]
[null,null,null,null,null,null,"Sales Canopies"]
[null,null,null,null,null,null,"Free-standing and attached",null,null,null,"W/ft²",null,0.6,0.6,0.8,1]
[null,null,null,null,null,null,"Outdoor Sales"]
[null,null,null,null,null,null,"Open areas (including vehicle sales lots)",null,null,null,"W/ft²",null,0.25,0.25,0.5,0.7]
[null,null,null,null,null,null,"Street frontage for vehicle sales lots",null,null,null,"W/linear ft",null,0,10,10,30]
[null,null,null,null,null,null,"          in addition to \"open area\" allowance"]
[null,null,null,null,null,null,"Building Exteriors"]
[null,null,null,null,null,null,"Building facades",null,null,null,"W/ft²",null,0,7.4999999999999997E-2,0.113,0.15]
[null,null,null,null,null,null,"Automated teller machines (ATM)",null,null,null,"Watts",null,90,90,90,90,270,"First"]
[null,null,null,null,null,null,"          and night depositories"]
[null,null,null,null,null,null,"Uncovered entrances and gatehouse inpection",null,null,null,"W/ft²",null,0.75,0.75,0.75,0.75]
[null,null,null,null,null,null,"          stations at guarded facilities"]
[null,null,null,null,null,null,"Uncovered loading areas for law enforcement, fire,",null,null,null,"W/ft²",null,0.5,0.5,0.5,0.5]
[null,null,null,null,null,null,"          ambulance and other emergency service vehicles"]
[null,null,null,null,null,null,"Drive-up windows and doors",null,null,null,"Drive-thru",null,400,400,400,400]
[null,null,null,null,null,null,"Parking near 24-hour retail entrances",null,null,null,"Entry",null,800,800,800,800]

{"sheet":"Unitary HVAC (RTU, AC, HP, VRF)","index":11,"n_rows":190,"n_cols":80,"rows_kept":190,"cut":false,"hidden":true,"merged":[[36,12,36,13],[32,14,32,15],[33,14,33,15],[34,14,34,15],[35,14,35,15],[36,14,36,15],[32,12,32,13],[33,12,33,13],[34,12,34,13],[35,12,35,13],[1,19,11,27],[23,12,23,13],[24,12,24,13],[25,12,25,13],[26,12,26,13],[1,10,8,17],[10,10,13,17],[27,14,27,15],[28,14,28,15],[29,14,29,15],[30,14,30,15],[31,14,31,15],[32,10,32,11],[33,10,33,11],[34,10,34,11],[35,10,35,11],[36,10,36,11],[27,12,27,13],[28,12,28,13],[29,12,29,13],[30,12,30,13],[31,12,31,13],[37,14,37,15],[23,10,23,11],[24,10,24,11],[25,10,25,11],[26,10,26,11],[23,14,23,15],[24,14,24,15],[25,14,25,15],[26,14,26,15],[27,10,27,11],[28,10,28,11],[29,10,29,11],[30,10,30,11],[31,10,31,11],[37,10,37,11],[37,12,37,13]]}
["Savings Summary",null,null,null,null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,null,null,"Notes (Optional)"]
["Annual kWh Savings",null,null,{"$f":"SUM(A14:D14)","v":0},null,null,null,"Value","Unit",null,"This measure considers savings from high performance electrically operated air-to-air and water-to-air unitary cooling/heating equipment with cooling and heating performance that exceeds the minimum requirements of energy code. Equipment analyzed can include the following:\no DX Air Handlers and Rooftop Units\no Unitary Air Conditioners\no Air-to-air Heat Pumps\no Variable Refrigerant Flow Systems\no Small Water-to-Air Heat Pumps <= 135 MBH capacity\n",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Energy Savings Breakdown/Summary",null,null,null,null,null,null,"Mass Save HEAT PUMP Metrics"]
["% On Peak",null,null,{"$f":"IF(D2<=0,0,MIN(1,A15+C15))","v":0},null,"Annual Electric Savings",null,{"$f":"D2","v":0},"kWh",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"kWh Savings",null,null,null,"Quantity of HPs (#)",null,null,{"$f":"SUMPRODUCT(AH24:AH38,AK24:AK38)","v":0}]
["Max kW",null,null,{"$f":"MAX(AY56:AY79,AY86:AY109)","v":0},null,"Annual Fuel Savings",null,{"$f":"D7*C28","v":{"$error":"#N/A"}},{"$f":"D20","v":{"$error":"#N/A"}},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"HVAC/Comfort Systems",null,null,"Cooling","Heating","Total",null,"HP Annual Savings (kWh)",null,null,{"$f":"$AQ$41*H3","v":{"$error":"#DIV/0!"}}]
["Summer kW",null,null,{"$f":"(SUMPRODUCT(R56:R79,AY56:AY79)+SUMPRODUCT(R86:R109,AY86:AY109))/SUM(R56:R79,R86:R109)","v":0},null,"Incremental","Default Calc",{"$f":"$AF$144*($R$39*($AA$39-$AE$39)+$R$40*($AA$40-$AE$40))+$AF$145*($S$39*($AB$39-$AF$39)+$S$40*($AB$40-$AF$40))","v":0},"$",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Occupied Hours",null,null,{"$f":"SUMPRODUCT(AE56:AE79,$L$56:$L$79)","v":0},{"$f":"SUMPRODUCT(AF56:AF79,$L$56:$L$79)","v":0},{"$f":"AG5+AH5","v":0},null,"HP Incremental Cost ($)",null,null,{"$f":"$AQ$41*D9","v":{"$error":"#DIV/0!"}}]
["Winter kW",null,null,{"$f":"(SUMPRODUCT(Q56:Q79,AY56:AY79)+SUMPRODUCT(Q86:Q109,AY86:AY109))/SUM(Q56:Q79,Q86:Q109)","v":0},null,"Cost","Project Specific",null,"$ (Optional)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Unoccupied Hours",null,null,{"$f":"SUMPRODUCT(AE86:AE109,$L$86:$L$109)","v":0},{"$f":"SUMPRODUCT(AF86:AF109,$L$86:$L$109)","v":0},{"$f":"AG6+AH6","v":0},null,"HP Incentive ($)",null,null,{"$f":"$AQ$41*H7","v":{"$error":"#DIV/0!"}}]
["Annual Fuel Savings (MMBtu)",null,null,0,null,"Estimated Incentive",null,{"$f":"IF(AND($C$24>=0,$C$25>=0),MAX(0,H3)*C24+MAX(0,H4)*C25,\"TBD\")","v":{"$error":"#N/A"}},"$",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"HVAC/Comfort Total",null,null,{"$f":"AG5+AG6","v":0},{"$f":"AH5+AH6","v":0},0,null,"HP Summer kW Saved (kW)",null,null,{"$f":"$AQ$41*D5","v":{"$error":"#DIV/0!"}}]
["Incremental Cost (Default Calc)",null,null,{"$f":"$AF$144*($R$39*($AA$39-$AE$39)+$R$40*($AA$40-$AE$40))+$AF$145*($S$39*($AB$39-$AF$39)+$S$40*($AB$40-$AF$40))","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"HP Winter kW Saved (kW)",null,null,{"$f":"$AQ$41*D6","v":{"$error":"#DIV/0!"}}]
["Incremental Cost (for Summary)",null,null,{"$f":"IF(H6>0,H6,D8)","v":0},null,"Project Information Summary",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Constant/IT Load Systems",null,null,"Cooling","Heating","Total"]
["kWh Savings by Peak Period",null,null,null,null,null,"STATE",{"$f":"'Project Info'!C15","v":"NH"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Occupied Hours",null,null,{"$f":"SUMPRODUCT(AU56:AU79,$L$56:$L$79)","v":0},{"$f":"SUMPRODUCT(AV56:AV79,$L$56:$L$79)","v":0},{"$f":"AG10+AH10","v":0}]
["Winter","Winter","Summer","Summer",null,null,"Program Year",{"$f":"'Project Info'!C19","v":0},null,null,"NOTE: Certain equipment types have energy code performanmce requirements for a limited range of capacities. If a Unit Type is entered with a capacity for which there is no code requirement, the tool will return an error.  In this case, the equipment should be removed and analyzed as a User Defined measure.",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Unoccupied Hours",null,null,{"$f":"SUMPRODUCT(AU86:AU109,$L$86:$L$109)","v":0},{"$f":"SUMPRODUCT(AV86:AV109,$L$86:$L$109)","v":0},{"$f":"AG11+AH11","v":0}]
["On-Peak","Off-Peak","On-Peak","Off-Peak",null,null,"Code IECC Version",{"$f":"MID('Project Info'!C20,1,4)","v":"2018"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Constant/IT Load Total",null,null,{"$f":"AG10+AG11","v":0},{"$f":"AH10+AH11","v":0},{"$f":"AG12+AH12","v":0}]
["kWh","kWh","kWh","kWh",null,null,"Electric PA",{"$f":"'Project Info'!F3","v":0}]
[{"$f":"SUMPRODUCT($AY$56:$AY$79,M56:M79)+SUMPRODUCT($AY$86:$AY$109,M86:M109)","v":0},{"$f":"SUMPRODUCT($AY$56:$AY$79,N56:N79)+SUMPRODUCT($AY$86:$AY$109,N86:N109)","v":0},{"$f":"SUMPRODUCT($AY$56:$AY$79,O56:O79)+SUMPRODUCT($AY$86:$AY$109,O86:O109)","v":0},{"$f":"SUMPRODUCT($AY$56:$AY$79,P56:P79)+SUMPRODUCT($AY$86:$AY$109,P86:P109)","v":0},null,null,"Gas PA",{"$f":"'Project Info'!I3","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Unitary Equip Savings",null,null,"Cooling","Heating","Total"]
[{"$f":"ROUND(IF(A14<=0,0,A14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(B14<=0,0,B14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(C14<=0,0,C14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"IF(SUM(A14:D14)=0,0,1-SUM(A15:C15))","v":0},null,"*NOTE: Baseline values are automated and cannot be changed.",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total",null,null,{"$f":"AG7+AG12","v":0},{"$f":"AH7+AH12","v":0},{"$f":"AG15+AH15","v":0}]
[]
["Utility Rates"]
[null,null,"Rate","Unit",null,"Table 1: System Parameters"]
["Electric",null,{"$f":"'ECM Summary'!$E$31","v":0.1593},"kWh",null,null,1,2,3,4,5,null,6,null,7,null,8,9,10,11,12,13,14,15,null,"Baseline vs. Proposed Assumptions Summary"]
[{"$f":"'ECM Summary'!$C$32","v":0},null,{"$f":"'ECM Summary'!$E$32","v":{"$error":"#N/A"}},{"$f":"'ECM Summary'!$F$32","v":{"$error":"#N/A"}},null,null,"Qty of Identical",null,null,null,null,null,null,null,null,null,null,"Outdoor/Condensing Unit",null,"Proposed/Design Performance (AHRI Ratings)",null,null,null,null,null,"Proposed Performance",null,null,null,"Baseline Performance",null,null,null,null,"Proposed"]
[null,null,null,null,null,null,"Units (optional)",null,"Unit","Manufacturer","Condenser",null,"Primary",null,"·Heating·",null,"VRF","Cooling","Heating","Cooling",null,"Heating",null,null,"Heating","Cooling",null,"Heating",null,"Cooling",null,"Heating",null,null,"IEER",null,"Calculation of % Savings from Heat Pumps (for HP Metrics)"]
["Custom Incentive Rates",null,null,null,null,"Line","\"0\" = no units","Unit","Type","& Model","Type",null,"Load Profile",null,"Source",null,"Heat","Capacity","Capacity","Full Load",null,"COP","COP Low Temp",null,"Perf.","Full Load",null,"COP","COP","Full Load",null,"COP","COP","Unit","with",null,"Heat","HP","Cool","Heat","Avg Heating COP",null,"Savings"]
[null,null,"Rate","Unit",null,"#","\"blank\" = 1 unit","Tag/#",null,"(Optional)",null,null,null,null,null,null,"Recovery?","MBH","MBH","EER","IEER/SEER2","(@47°F air-cooled)","(@17°F air-cooled)","HSPF2","Units","EER","IEER/SEER","47°F","17°F","EER","IEER","47°F","17°F","Qty","Limit",null,"Pump?","Heating?","EFLH","EFLH","Base","Proposed","kWh"]
["Electric",null,{"$f":"'ECM Summary'!$J$31","v":0.28000000000000003},"kWh",null,1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(AND(O24=$G$119,S24>0),IF(AND(K24=$I$113,S24<$J$118),$I$119,$J$119),$I$120)","v":"NA"},{"$f":"IF($I24=\"\",\"\",T24)","v":""},{"$f":"IF($I24=\"\",\"\",U24)","v":""},{"$f":"IF($Y24=$I$119,$X24/3.412,IF($Y24=$J$119,V24,\"\"))","v":""},{"$f":"IF($Y24=$I$119,$X24/3.412,IF($Y24=$J$119,IF(AF24=AG24,V24,IF(W24=0,AG24,W24)),\"\"))","v":""},{"$f":"IF($I24=\"\",\"\",MAX(0,OFFSET(IF($H$12=\"2015\",$I$167,$AU$167),MATCH($I24,$F$168:$F$189,0)+MATCH($K24,$H$169:$H$174,0),MATCH($R24,$J$166:$O$166,1))-IF(OR($I24<>$G$115,$R24<$K$167),0,IF($Q24=\"Yes\",0.2,0))))","v":""},{"$f":"IF($I24=\"\",\"\",MAX(0,OFFSET(IF($H$12=\"2015\",$R$167,$BD$167),MATCH($I24,$F$168:$F$189,0)+MATCH($K24,$Q$169:$Q$174,0),MATCH($R24,$S$166:$X$166,1))-IF(OR($I24<>$G$115,$R24<$T$167),0,IF($Q24=\"Yes\",0.2,0))))","v":""},{"$f":"IF($I24=\"\",\"\",MAX(0,OFFSET(IF($H$12=\"2015\",$AA$167,$BM$167),MATCH($I24,$F$168:$F$189,0)+MATCH($K24,$Z$169:$Z$174,0),MATCH($S24,$AB$166:$AG$166,1))))","v":""},{"$f":"IF($I24=\"\",\"\",MAX(0,OFFSET(IF($H$12=\"2015\",$AJ$167,$BV$167),MATCH($I24,$F$168:$F$189,0)+MATCH($K24,$AI$169:$AI$174,0),MATCH($S24,$AK$166:$AP$166,1))))","v":""},{"$f":"IF(I24=\"\",0,IF(G24<>\"\",G24,1))","v":0},{"$f":"IF($I24=\"\",\"\",MIN(U24,$U$122))","v":""},null,{"$f":"1*(OR(I24=$I$43,I24=$I$45))","v":0},{"$f":"1*(O24=$O$42)*(OR(I24=$I$43,I24=$I$45))","v":0},{"$f":"IF(M24=$M$42,$V$118,IF(M24=$M$43,$X$120*8760,0))*(AH24>0)","v":0},{"$f":"$AE$118*AL24","v":0},{"$f":"IF(AL24=0,0,AVERAGE(AF24:AG24))","v":0},{"$f":"IF(AL24=0,0,AVERAGE(AB24:AC24))","v":0},{"$f":"IF(AH24=0,0,R24*AH24*AM24*(1/AE24-1/AA24))+IF(AL24=0,0,S24*AH24*AN24*(1/3.412)*(1/AO24-1/AP24))","v":0}]
[{"$f":"'ECM Summary'!$H$32","v":0},null,{"$f":"'ECM Summary'!$J$32","v":0},{"$f":"'ECM Summary'!$K$32","v":{"$error":"#N/A"}},null,2,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"NA","","",{"$f":"IF($Y25=$I$119,$X25/3.412,IF($Y25=$J$119,V25,\"\"))","v":""},"","","","","",{"$f":"IF(I25=\"\",0,IF(G25>0,G25,1))","v":0},{"$f":"IF($I25=\"\",\"\",MIN(U25,$U$122))","v":""},null,0,{"$f":"1*(O25=$O$42)*(OR(I25=$I$43,I25=$I$45))","v":0},{"$f":"IF(M25=$M$42,$V$118,IF(M25=$M$43,$X$120*8760,0))*(AH25>0)","v":0},{"$f":"$AE$118*AL25","v":0},{"$f":"IF(AL25=0,0,AVERAGE(AF25:AG25))","v":0},{"$f":"IF(AL25=0,0,AVERAGE(AB25:AC25))","v":0},{"$f":"IF(AH25=0,0,R25*AH25*AM25*(1/AE25-1/AA25))+IF(AL25=0,0,S25*AH25*AN25*(1/3.412)*(1/AO25-1/AP25))","v":0}]
[null,null,null,null,null,3,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"NA","","","","","","","","",0,"",null,0,0,0,0,0,0,0]
["Fossil Fuel",null,{"$f":"'Project Info'!C21","v":0},null,null,4,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"NA","","","","","","","","",0,"",null,0,0,0,0,0,0,0]
["Fuel Conversion",null,{"$f":"LOOKUP(C27,'Project Info'!X102:X104,'Project Info'!Z102:Z104)","v":{"$error":"#N/A"}},null,null,5,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"NA","","","","","","","","",0,"",null,0,0,0,0,0,0,0]
[null,null,null,null,null,6,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"NA","","","","","","","","",0,"",null,0,0,0,0,0,0,0]
[null,null,null,null,null,7,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"NA","","","","","","","","",0,"",null,0,0,0,0,0,0,0]
[null,null,null,null,null,8,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"NA","","","","","","","","",0,"",null,0,0,0,0,0,0,0]
[null,null,null,null,null,9,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"NA","","","","","","","","",0,"",null,0,0,0,0,0,0,0]
[null,null,null,null,null,10,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"NA","","","","","","","","",0,"",null,0,0,0,0,0,0,0]
[null,null,null,null,null,11,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"NA","","","","","","","","",0,"",null,0,0,0,0,0,0,0]
[null,null,null,null,null,12,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"NA","","","","","","","","",0,"",null,0,0,0,0,0,0,0]
[null,null,null,null,null,13,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"NA","","","","","","","","",0,"",null,0,0,0,0,0,0,0]
[null,null,null,null,null,14,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"NA","","","","","","","","",0,"",null,0,0,0,0,0,0,0]
[null,null,null,null,null,15,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"NA","","","","","","","","",0,"",null,0,0,0,0,0,0,0]
[null,null,null,null,null,null,"Comfort/HVAC Systems: Total or Weighted Avg.",null,null,null,null,null,null,null,null,null,null,{"$f":"SUMPRODUCT(R24:R38,1*($M$24:$M$38=$M$42),$AH$24:$AH$38)","v":0},{"$f":"SUMPRODUCT(S24:S38,1*($M$24:$M$38=$M$42),1*($O$24:$O$38<>$G$120),$AH$24:$AH$38)","v":0},{"$f":"IF($R39<=0,0,SUMPRODUCT(T24:T38,$R$24:$R$38,1*($M$24:$M$38=$M$42),$AH$24:$AH$38)/$R39)","v":0},{"$f":"IF($R39<=0,0,SUMPRODUCT(U24:U38,$R$24:$R$38,1*($M$24:$M$38=$M$42),$AH$24:$AH$38)/$R39)","v":0},{"$f":"IF($S39<=0,0,SUMPRODUCT(AB24:AB38,$S$24:$S$38,1*($M$24:$M$38=$M$42),1*($O$24:$O$38<>$G$120),$AH$24:$AH$38)/$S39)","v":0},{"$f":"IF($S39<=0,0,SUMPRODUCT(AC24:AC38,$S$24:$S$38,1*($M$24:$M$38=$M$42),1*($O$24:$O$38<>$G$120),$AH$24:$AH$38)/$S39)","v":0},null,null,{"$f":"T39","v":0},0,{"$f":"IF($S39<=0,0,SUMPRODUCT(AB24:AB38,$S$24:$S$38,1*($M$24:$M$38=$M$42),1*($O$24:$O$38<>$G$120),$AH$24:$AH$38)/$S39)","v":0},{"$f":"IF($S39<=0,0,SUMPRODUCT(AC24:AC38,$S$24:$S$38,1*($M$24:$M$38=$M$42),1*($O$24:$O$38<>$G$120),$AH$24:$AH$38)/$S39)","v":0},{"$f":"IF($R39<=0,0,SUMPRODUCT(AD24:AD38,$R$24:$R$38,1*($M$24:$M$38=$M$42),$AH$24:$AH$38)/$R39)","v":0},{"$f":"IF($R39<=0,0,SUMPRODUCT(AE24:AE38,$R$24:$R$38,1*($M$24:$M$38=$M$42),$AH$24:$AH$38)/$R39)","v":0},{"$f":"IF($S39<=0,0,SUMPRODUCT(AF24:AF38,$S$24:$S$38,1*($M$24:$M$38=$M$42),1*($O$24:$O$38<>$G$120),$AH$24:$AH$38)/$S39)","v":0},{"$f":"IF($S39<=0,0,SUMPRODUCT(AG24:AG38,$S$24:$S$38,1*($M$24:$M$38=$M$42),1*($O$24:$O$38<>$G$120),$AH$24:$AH$38)/$S39)","v":0},null,{"$f":"IF($R39<=0,0,SUMPRODUCT(AI24:AI38,$R$24:$R$38,1*($M$24:$M$38=$M$42),$AH$24:$AH$38)/$R39)","v":0},null,null,null,null,null,null,"Total TRM Savings",{"$f":"SUM(AQ24:AQ38)","v":0}]
[null,null,null,null,null,null,"Constant/IT-Elec Room Systems: Total or Weighted Avg.",null,null,null,null,null,null,null,null,null,null,{"$f":"SUMPRODUCT(R24:R38,1*($M$24:$M$38=$M$43),$AH$24:$AH$38)","v":0},{"$f":"SUMPRODUCT(S24:S38,1*($M$24:$M$38=$M$43),1*($O$24:$O$38<>$G$120),$AH$24:$AH$38)","v":0},{"$f":"IF($R40<=0,0,SUMPRODUCT(T24:T38,$R$24:$R$38,1*($M$24:$M$38=$M$43),$AH$24:$AH$38)/$R40)","v":0},{"$f":"IF($R40<=0,0,SUMPRODUCT(U24:U38,$R$24:$R$38,1*($M$24:$M$38=$M$43),$AH$24:$AH$38)/$R40)","v":0},{"$f":"IF($S40<=0,0,SUMPRODUCT(AB24:AB38,$S$24:$S$38,1*($M$24:$M$38=$M$43),1*($O$24:$O$38<>$G$120),$AH$24:$AH$38)/$S40)","v":0},{"$f":"IF($S40<=0,0,SUMPRODUCT(AC24:AC38,$S$24:$S$38,1*($M$24:$M$38=$M$43),1*($O$24:$O$38<>$G$120),$AH$24:$AH$38)/$S40)","v":0},null,null,0,0,{"$f":"IF($S40<=0,0,SUMPRODUCT(AB24:AB38,$S$24:$S$38,1*($M$24:$M$38=$M$43),1*($O$24:$O$38<>$G$120),$AH$24:$AH$38)/$S40)","v":0},{"$f":"IF($S40<=0,0,SUMPRODUCT(AC24:AC38,$S$24:$S$38,1*($M$24:$M$38=$M$43),1*($O$24:$O$38<>$G$120),$AH$24:$AH$38)/$S40)","v":0},{"$f":"IF($R40<=0,0,SUMPRODUCT(AD24:AD38,$R$24:$R$38,1*($M$24:$M$38=$M$43),$AH$24:$AH$38)/$R40)","v":0},{"$f":"IF($R40<=0,0,SUMPRODUCT(AE24:AE38,$R$24:$R$38,1*($M$24:$M$38=$M$43),$AH$24:$AH$38)/$R40)","v":0},{"$f":"IF($S40<=0,0,SUMPRODUCT(AF24:AF38,$S$24:$S$38,1*($M$24:$M$38=$M$43),1*($O$24:$O$38<>$G$120),$AH$24:$AH$38)/$S40)","v":0},{"$f":"IF($S40<=0,0,SUMPRODUCT(AG24:AG38,$S$24:$S$38,1*($M$24:$M$38=$M$43),1*($O$24:$O$38<>$G$120),$AH$24:$AH$38)/$S40)","v":0},null,{"$f":"IF($R40<=0,0,SUMPRODUCT(AI24:AI38,$R$24:$R$38,1*($M$24:$M$38=$M$43),$AH$24:$AH$38)/$R40)","v":0},null,null,null,null,null,null,"TRM Savings from HEAT PUMPS",{"$f":"SUMPRODUCT(AQ24:AQ38,AK24:AK38)","v":0}]
[null,null,null,null,null,null,null,null,"System Types",null,"Condenser Type",null,"Load Profiles",null,"·Heating Source",null,"HR?",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"% Savings from HEAT PUMPS",{"$f":"MIN(1,AQ40/AQ39)","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,{"$f":"G112","v":"Air Conditioner"},null,{"$f":"I112","v":"Air Cooled"},null,"HVAC/Comfort",null,{"$f":"G119","v":"Heat Pump"},null,"No"]
[null,null,null,null,null,null,null,null,{"$f":"G113","v":"Heat Pump"},null,{"$f":"J112","v":"Water Cooled"},null,"Constant/IT-Elec Rooms",null,{"$f":"Other_None","v":"Other/None"},null,"Yes"]
[null,null,null,null,null,null,null,null,{"$f":"G114","v":"VRF AC Only"},null,{"$f":"K112","v":"Evap Cooled"}]
[null,null,null,null,null,null,null,null,{"$f":"G115","v":"VRF Heat Pump"},null,{"$f":"J113","v":"Water Loop (HP)"}]
[null,null,null,null,null,null,null,null,null,null,{"$f":"K113","v":"Ground Water (HP)"}]
[null,null,null,null,null,null,null,null,null,null,{"$f":"L113","v":"Ground Loop (HP)"}]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Load Profile",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Load Profile"]
[null,null,null,null,null,null,"Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown",null,null,null,null,null,null,"Comfort/HVAC",null,null,null,"Cooling Demand",null,null,null,"Heating Demand",null,null,null,"Demand Savings",null,null,null,"Constant/IT/Elec",null,null,null,"Cooling Demand",null,null,null,"Heating Demand",null,null,null,"Demand Savings",null,null,null,"Overall"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Cooling","Cooling","Heating","Heating","Base","Proposed","Base","Design","Base","Proposed","Base","Design","Cooling","Heating","Total",null,"Cooling","Cooling","Heating","Heating","Base","Proposed","Base","Design","Base","Proposed","Base","Design","Cooling","Heating","Total",null,"Demand"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Load","Load","Load","Load","Perf","Perf","Demand","Demand","Perf","Perf","Demand","Demand","Savings","Savings","Savings",null,"Load","Load","Load","Load","Perf","Perf","Demand","Demand","Perf","Perf","Demand","Demand","Savings","Savings","Savings",null,"Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","%","MBH","%","MBH","EER","EER","kW","kW","COP","COP","kW","kW","kW","kW","kW",null,"%","MBH","%","MBH","EER","EER","kW","kW","COP","COP","kW","kW","kW","kW","kW",null,"kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A44","v":100},{"$f":"'Project Info'!B44","v":105},{"$f":"'Project Info'!C44","v":102},{"$f":"'Project Info'!D44","v":76},{"$f":"'Project Info'!E44","v":40},{"$f":"'Project Info'!F44","v":0},{"$f":"'Project Info'!G44","v":0},{"$f":"'Project Info'!H44","v":0},{"$f":"'Project Info'!I44","v":0},{"$f":"'Project Info'!J44","v":0},{"$f":"'Project Info'!K44","v":0},{"$f":"'Project Info'!L44","v":0},{"$f":"MAX(0,MIN(1,TREND($U$116:$V$116,$S$116:$T$116,$I56)*$W$111))*($I56>=$T$116)","v":0.96899999999999986},{"$f":"$R$39*S56","v":0},{"$f":"MAX(0,MIN(1,TREND($AD$116:$AE$116,$AB$116:$AC$116,$I56)*$W$111))*($I56<=$AB$116)","v":0},{"$f":"$S$39*U56","v":0},{"$f":"OFFSET($G$137,MATCH($I56,$G$138:$G$148,-1),MATCH(S56,$H$137:$L$137,-1))*(S56>0)","v":0},{"$f":"OFFSET($G$150,MATCH($I56,$G$151:$G$161,-1),MATCH(S56,$H$150:$L$150,-1))*(S56>0)","v":0},{"$f":"IF(T56>0,T56/W56,0)","v":0},{"$f":"IF(T56>0,T56/X56,0)","v":0},{"$f":"MIN($AB$134,TREND($AB$134:$AC$134,$AB$133:$AC$133,$I56))*(U56>0)","v":0},{"$f":"MIN($AB$135,TREND($AB$135:$AC$135,$AB$133:$AC$133,$I56))*(U56>0)","v":0},{"$f":"IF(V56>0,V56/AA56/3.412,0)","v":0},{"$f":"IF(V56>0,V56/AB56/3.412,0)","v":0},{"$f":"Y56-Z56","v":0},{"$f":"AC56-AD56","v":0},{"$f":"AE56+AF56","v":0},null,{"$f":"$X$120","v":0.25},{"$f":"$R$40*AI56","v":0},{"$f":"$Y$120","v":0},{"$f":"$S$40*AK56","v":0},{"$f":"OFFSET($Q$137,MATCH($I56,$Q$138:$Q$148,-1),MATCH(AI56,$R$137:$V$137,-1))*(AI56>0)","v":0},{"$f":"OFFSET($Q$150,MATCH($I56,$Q$151:$Q$161,-1),MATCH(AI56,$R$150:$V$150,-1))*(AI56>0)","v":0},{"$f":"IF(AJ56>0,AJ56/AM56,0)","v":0},{"$f":"IF(AJ56>0,AJ56/AN56,0)","v":0},{"$f":"MIN($AB$134,TREND($AB$134:$AC$134,$AB$133:$AC$133,$I56))*(AK56>0)","v":0},{"$f":"MIN($AB$135,TREND($AB$135:$AC$135,$AB$133:$AC$133,$I56))*(AK56>0)","v":0},{"$f":"IF(AL56>0,AL56/AQ56/3.412,0)","v":0},{"$f":"IF(AL56>0,AL56/AR56/3.412,0)","v":0},{"$f":"AO56-AP56","v":0},{"$f":"AS56-AT56","v":0},{"$f":"AU56+AV56","v":0},null,{"$f":"AG56+AW56","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A45","v":95},{"$f":"'Project Info'!B45","v":100},{"$f":"'Project Info'!C45","v":95.219272727272724},{"$f":"'Project Info'!D45","v":74.534025272781079},{"$f":"'Project Info'!E45","v":37.923296058061368},{"$f":"'Project Info'!F45","v":0},{"$f":"'Project Info'!G45","v":0},{"$f":"'Project Info'!H45","v":0},{"$f":"'Project Info'!I45","v":0},{"$f":"'Project Info'!J45","v":0},{"$f":"'Project Info'!K45","v":0},{"$f":"'Project Info'!L45","v":0},0.85372763636363624,0,{"$f":"MAX(0,MIN(1,TREND($AD$116:$AE$116,$AB$116:$AC$116,$I57)*$W$111))*($I57<=$AB$116)","v":0},0,0,0,{"$f":"IF(T57>0,T57/W57,0)","v":0},{"$f":"IF(T57>0,T57/X57,0)","v":0},0,0,{"$f":"IF(V57>0,V57/AA57/3.412,0)","v":0},{"$f":"IF(V57>0,V57/AB57/3.412,0)","v":0},{"$f":"Y57-Z57","v":0},{"$f":"AC57-AD57","v":0},{"$f":"AE57+AF57","v":0},null,{"$f":"$X$120","v":0.25},0,{"$f":"$Y$120","v":0},0,0,0,{"$f":"IF(AJ57>0,AJ57/AM57,0)","v":0},{"$f":"IF(AJ57>0,AJ57/AN57,0)","v":0},0,0,{"$f":"IF(AL57>0,AL57/AQ57/3.412,0)","v":0},{"$f":"IF(AL57>0,AL57/AR57/3.412,0)","v":0},{"$f":"AO57-AP57","v":0},{"$f":"AS57-AT57","v":0},{"$f":"AU57+AV57","v":0},null,{"$f":"AG57+AW57","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A46","v":90},{"$f":"'Project Info'!B46","v":95},{"$f":"'Project Info'!C46","v":92.016049160256074},{"$f":"'Project Info'!D46","v":72.911561930607689},{"$f":"'Project Info'!E46","v":36.467095439351091},{"$f":"'Project Info'!F46","v":0},{"$f":"'Project Info'!G46","v":0},{"$f":"'Project Info'!H46","v":0},{"$f":"'Project Info'!I46","v":0},{"$f":"'Project Info'!J46","v":0},{"$f":"'Project Info'!K46","v":0},{"$f":"'Project Info'!L46","v":0},0.79927283572435337,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A47","v":85},{"$f":"'Project Info'!B47","v":90},{"$f":"'Project Info'!C47","v":87.457811360655285},{"$f":"'Project Info'!D47","v":70.80538329449476},{"$f":"'Project Info'!E47","v":34.679413213566804},{"$f":"'Project Info'!F47","v":0},{"$f":"'Project Info'!G47","v":0},{"$f":"'Project Info'!H47","v":0},{"$f":"'Project Info'!I47","v":0},{"$f":"'Project Info'!J47","v":0},{"$f":"'Project Info'!K47","v":0},{"$f":"'Project Info'!L47","v":0},0.7217827931311398,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A48","v":80},{"$f":"'Project Info'!B48","v":85},{"$f":"'Project Info'!C48","v":82.136788830239965},{"$f":"'Project Info'!D48","v":67.872393622439333},{"$f":"'Project Info'!E48","v":32.296248223809314},{"$f":"'Project Info'!F48","v":0},{"$f":"'Project Info'!G48","v":0},{"$f":"'Project Info'!H48","v":0},{"$f":"'Project Info'!I48","v":0},{"$f":"'Project Info'!J48","v":0},{"$f":"'Project Info'!K48","v":0},{"$f":"'Project Info'!L48","v":0},0.63132541011407939,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A49","v":75},{"$f":"'Project Info'!B49","v":80},{"$f":"'Project Info'!C49","v":76.988400157585886},{"$f":"'Project Info'!D49","v":65.129261896908645},{"$f":"'Project Info'!E49","v":30.190476812806729},{"$f":"'Project Info'!F49","v":0},{"$f":"'Project Info'!G49","v":0},{"$f":"'Project Info'!H49","v":0},{"$f":"'Project Info'!I49","v":0},{"$f":"'Project Info'!J49","v":0},{"$f":"'Project Info'!K49","v":0},{"$f":"'Project Info'!L49","v":0},0.5438028026789602,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A50","v":70},{"$f":"'Project Info'!B50","v":75},{"$f":"'Project Info'!C50","v":72.457982050814195},{"$f":"'Project Info'!D50","v":63.604425012889301},{"$f":"'Project Info'!E50","v":29.088683095945193},{"$f":"'Project Info'!F50","v":0},{"$f":"'Project Info'!G50","v":0},{"$f":"'Project Info'!H50","v":0},{"$f":"'Project Info'!I50","v":0},{"$f":"'Project Info'!J50","v":0},{"$f":"'Project Info'!K50","v":0},{"$f":"'Project Info'!L50","v":0},0.46678569486384142,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A51","v":65},{"$f":"'Project Info'!B51","v":70},{"$f":"'Project Info'!C51","v":67.815831070966169},{"$f":"'Project Info'!D51","v":61.631331368130574},{"$f":"'Project Info'!E51","v":27.661514889731574},{"$f":"'Project Info'!F51","v":0},{"$f":"'Project Info'!G51","v":0},{"$f":"'Project Info'!H51","v":0},{"$f":"'Project Info'!I51","v":0},{"$f":"'Project Info'!J51","v":0},{"$f":"'Project Info'!K51","v":0},{"$f":"'Project Info'!L51","v":0},0.38786912820642494,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A52","v":60},{"$f":"'Project Info'!B52","v":65},{"$f":"'Project Info'!C52","v":62.535961472271332},{"$f":"'Project Info'!D52","v":57.135476922863582},{"$f":"'Project Info'!E52","v":24.623037157728302},{"$f":"'Project Info'!F52","v":0},{"$f":"'Project Info'!G52","v":0},{"$f":"'Project Info'!H52","v":0},{"$f":"'Project Info'!I52","v":0},{"$f":"'Project Info'!J52","v":0},{"$f":"'Project Info'!K52","v":0},{"$f":"'Project Info'!L52","v":0},0.29811134502861264,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A53","v":55},{"$f":"'Project Info'!B53","v":60},{"$f":"'Project Info'!C53","v":57.125792270740902},{"$f":"'Project Info'!D53","v":52.596971157053673},{"$f":"'Project Info'!E53","v":21.818001539159841},{"$f":"'Project Info'!F53","v":0},{"$f":"'Project Info'!G53","v":0},{"$f":"'Project Info'!H53","v":0},{"$f":"'Project Info'!I53","v":0},{"$f":"'Project Info'!J53","v":0},{"$f":"'Project Info'!K53","v":0},{"$f":"'Project Info'!L53","v":0},0.20613846860259546,0,0.12164614854805356,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A54","v":50},{"$f":"'Project Info'!B54","v":55},{"$f":"'Project Info'!C54","v":52.235698854337961},{"$f":"'Project Info'!D54","v":48.022768090099298},{"$f":"'Project Info'!E54","v":19.246640192796217},{"$f":"'Project Info'!F54","v":0},{"$f":"'Project Info'!G54","v":0},{"$f":"'Project Info'!H54","v":0},{"$f":"'Project Info'!I54","v":0},{"$f":"'Project Info'!J54","v":0},{"$f":"'Project Info'!K54","v":0},{"$f":"'Project Info'!L54","v":0},0.12300688052374546,0,0.18399483960719104,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A55","v":45},{"$f":"'Project Info'!B55","v":50},{"$f":"'Project Info'!C55","v":47.459170258371508},{"$f":"'Project Info'!D55","v":43.465397050422162},{"$f":"'Project Info'!E55","v":16.894183241713304},{"$f":"'Project Info'!F55","v":0},{"$f":"'Project Info'!G55","v":0},{"$f":"'Project Info'!H55","v":0},{"$f":"'Project Info'!I55","v":0},{"$f":"'Project Info'!J55","v":0},{"$f":"'Project Info'!K55","v":0},{"$f":"'Project Info'!L55","v":0},0,0,0.24489557920576333,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A56","v":40},{"$f":"'Project Info'!B56","v":45},{"$f":"'Project Info'!C56","v":42.677030404888129},{"$f":"'Project Info'!D56","v":38.812544504634097},{"$f":"'Project Info'!E56","v":14.690265649465921},{"$f":"'Project Info'!F56","v":0},{"$f":"'Project Info'!G56","v":0},{"$f":"'Project Info'!H56","v":0},{"$f":"'Project Info'!I56","v":0},{"$f":"'Project Info'!J56","v":0},{"$f":"'Project Info'!K56","v":0},{"$f":"'Project Info'!L56","v":0},0,0,0.30586786233767638,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A57","v":35},{"$f":"'Project Info'!B57","v":40},{"$f":"'Project Info'!C57","v":37.333046773755832},{"$f":"'Project Info'!D57","v":33.904706919479686},{"$f":"'Project Info'!E57","v":12.53841602318813},{"$f":"'Project Info'!F57","v":0},{"$f":"'Project Info'!G57","v":0},{"$f":"'Project Info'!H57","v":0},{"$f":"'Project Info'!I57","v":0},{"$f":"'Project Info'!J57","v":0},{"$f":"'Project Info'!K57","v":0},{"$f":"'Project Info'!L57","v":0},0,0,0.37400365363461313,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A58","v":30},{"$f":"'Project Info'!B58","v":35},{"$f":"'Project Info'!C58","v":32.638179845662044},{"$f":"'Project Info'!D58","v":29.547170928664851},{"$f":"'Project Info'!E58","v":10.728972818165861},{"$f":"'Project Info'!F58","v":0},{"$f":"'Project Info'!G58","v":0},{"$f":"'Project Info'!H58","v":0},{"$f":"'Project Info'!I58","v":0},{"$f":"'Project Info'!J58","v":0},{"$f":"'Project Info'!K58","v":0},{"$f":"'Project Info'!L58","v":0},0,0,0.43386320696780895,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A59","v":25},{"$f":"'Project Info'!B59","v":30},{"$f":"'Project Info'!C59","v":27.529264646850947},{"$f":"'Project Info'!D59","v":24.652717392657845},{"$f":"'Project Info'!E59","v":8.8041305482613303},{"$f":"'Project Info'!F59","v":0},{"$f":"'Project Info'!G59","v":0},{"$f":"'Project Info'!H59","v":0},{"$f":"'Project Info'!I59","v":0},{"$f":"'Project Info'!J59","v":0},{"$f":"'Project Info'!K59","v":0},{"$f":"'Project Info'!L59","v":0},0,0,0.49900187575265048,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A60","v":20},{"$f":"'Project Info'!B60","v":25},{"$f":"'Project Info'!C60","v":22.998111483544687},{"$f":"'Project Info'!D60","v":20.383306659827422},{"$f":"'Project Info'!E60","v":7.246164547543378},{"$f":"'Project Info'!F60","v":0},{"$f":"'Project Info'!G60","v":0},{"$f":"'Project Info'!H60","v":0},{"$f":"'Project Info'!I60","v":0},{"$f":"'Project Info'!J60","v":0},{"$f":"'Project Info'!K60","v":0},{"$f":"'Project Info'!L60","v":0},0,0,0.55677407858480521,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A61","v":15},{"$f":"'Project Info'!B61","v":20},{"$f":"'Project Info'!C61","v":17.808510327474309},{"$f":"'Project Info'!D61","v":15.420865796304254},{"$f":"'Project Info'!E61","v":5.5490484131518292},{"$f":"'Project Info'!F61","v":0},{"$f":"'Project Info'!G61","v":0},{"$f":"'Project Info'!H61","v":0},{"$f":"'Project Info'!I61","v":0},{"$f":"'Project Info'!J61","v":0},{"$f":"'Project Info'!K61","v":0},{"$f":"'Project Info'!L61","v":0},0,0,0.6229414933247025,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A62","v":10},{"$f":"'Project Info'!B62","v":15},{"$f":"'Project Info'!C62","v":12.269931130346862},{"$f":"'Project Info'!D62","v":10.318264913023604},{"$f":"'Project Info'!E62","v":3.9082824916941998},{"$f":"'Project Info'!F62","v":0},{"$f":"'Project Info'!G62","v":0},{"$f":"'Project Info'!H62","v":0},{"$f":"'Project Info'!I62","v":0},{"$f":"'Project Info'!J62","v":0},{"$f":"'Project Info'!K62","v":0},{"$f":"'Project Info'!L62","v":0},0,0,0.69355837808807752,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A63","v":5},{"$f":"'Project Info'!B63","v":10},{"$f":"'Project Info'!C63","v":7.3137581369917548},{"$f":"'Project Info'!D63","v":5.7052382449247707},{"$f":"'Project Info'!E63","v":2.5019418419888937},{"$f":"'Project Info'!F63","v":0},{"$f":"'Project Info'!G63","v":0},{"$f":"'Project Info'!H63","v":0},{"$f":"'Project Info'!I63","v":0},{"$f":"'Project Info'!J63","v":0},{"$f":"'Project Info'!K63","v":0},{"$f":"'Project Info'!L63","v":0},0,0,0.7567495837533551,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A64","v":0},{"$f":"'Project Info'!B64","v":5},{"$f":"'Project Info'!C64","v":2.6119461836144886},{"$f":"'Project Info'!D64","v":1.2699770062067783},{"$f":"'Project Info'!E64","v":1.2046477897733283},{"$f":"'Project Info'!F64","v":0},{"$f":"'Project Info'!G64","v":0},{"$f":"'Project Info'!H64","v":0},{"$f":"'Project Info'!I64","v":0},{"$f":"'Project Info'!J64","v":0},{"$f":"'Project Info'!K64","v":0},{"$f":"'Project Info'!L64","v":0},0,0,0.81669768615891525,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A65","v":-5},{"$f":"'Project Info'!B65","v":0},{"$f":"'Project Info'!C65","v":-1.6731398516793925},{"$f":"'Project Info'!D65","v":-2.7083318773557807},{"$f":"'Project Info'!E65","v":7.9391832815876459E-2},{"$f":"'Project Info'!F65","v":0},{"$f":"'Project Info'!G65","v":0},{"$f":"'Project Info'!H65","v":0},{"$f":"'Project Info'!I65","v":0},{"$f":"'Project Info'!J65","v":0},{"$f":"'Project Info'!K65","v":0},{"$f":"'Project Info'!L65","v":0},0,0,0.87133253310891234,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A66","v":-10},{"$f":"'Project Info'!B66","v":-5},{"$f":"'Project Info'!C66","v":-6.5729865085377277},{"$f":"'Project Info'!D66","v":-7.2465935998252222},{"$f":"'Project Info'!E66","v":-1.168423365310433},{"$f":"'Project Info'!F66","v":0},{"$f":"'Project Info'!G66","v":0},{"$f":"'Project Info'!H66","v":0},{"$f":"'Project Info'!I66","v":0},{"$f":"'Project Info'!J66","v":0},{"$f":"'Project Info'!K66","v":0},{"$f":"'Project Info'!L66","v":0},0,0,0.93380557798385599,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A67","v":-15},{"$f":"'Project Info'!B67","v":-10},{"$f":"'Project Info'!C67","v":-15.32570353422995},{"$f":"'Project Info'!D67","v":-15.707838211108999},{"$f":"'Project Info'!E67","v":-3.4051318156661381},{"$f":"'Project Info'!F67","v":0},{"$f":"'Project Info'!G67","v":0},{"$f":"'Project Info'!H67","v":0},{"$f":"'Project Info'!I67","v":0},{"$f":"'Project Info'!J67","v":0},{"$f":"'Project Info'!K67","v":0},{"$f":"'Project Info'!L67","v":0},0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Load Profile",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Load Profile"]
[null,null,null,null,null,null,"Unoccupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown",null,null,null,null,null,null,"Comfort/HVAC",null,null,null,"Cooling Demand",null,null,null,"Heating Demand",null,null,null,"Demand Savings",null,null,null,"Constant/IT/Elec",null,null,null,"Cooling Demand",null,null,null,"Heating Demand",null,null,null,"Demand Savings",null,null,null,"Overall"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Cooling","Cooling","Heating","Heating","Base","Proposed","Base","Design","Base","Proposed","Base","Design","Cooling","Heating","Total",null,"Cooling","Cooling","Heating","Heating","Base","Proposed","Base","Design","Base","Proposed","Base","Design","Cooling","Heating","Total",null,"Demand"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Load","Load","Load","Load","Perf","Perf","Demand","Demand","Perf","Perf","Demand","Demand","Savings","Savings","Savings",null,"Load","Load","Load","Load","Perf","Perf","Demand","Demand","Perf","Perf","Demand","Demand","Savings","Savings","Savings",null,"Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","%","MBH","%","MBH","EER","EER","kW","kW","COP","COP","kW","kW","kW","kW","kW",null,"%","MBH","%","MBH","EER","EER","kW","kW","COP","COP","kW","kW","kW","kW","kW",null,"kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A74","v":100},{"$f":"'Project Info'!B74","v":105},{"$f":"'Project Info'!C74","v":102},{"$f":"'Project Info'!D74","v":76},{"$f":"'Project Info'!E74","v":40},{"$f":"'Project Info'!F74","v":0},{"$f":"'Project Info'!G74","v":0},{"$f":"'Project Info'!H74","v":0},{"$f":"'Project Info'!I74","v":0},{"$f":"'Project Info'!J74","v":0},{"$f":"'Project Info'!K74","v":0},{"$f":"'Project Info'!L74","v":0},{"$f":"MAX(0,MIN(1,TREND($Y$116:$Z$116,$W$116:$X$116,$I86)))*($I86>=$X$116)","v":0.49799999999999989},{"$f":"$R$39*S86","v":0},{"$f":"MAX(0,MIN(1,TREND($AH$116:$AI$116,$AF$116:$AG$116,$I86)))*($I86<=$AF$116)","v":0},{"$f":"$S$39*U86","v":0},{"$f":"OFFSET($G$137,MATCH($I86,$G$138:$G$148,-1),MATCH(S86,$H$137:$L$137,-1))*(S86>0)","v":0},{"$f":"OFFSET($G$150,MATCH($I86,$G$151:$G$161,-1),MATCH(S86,$H$150:$L$150,-1))*(S86>0)","v":0},{"$f":"IF(T86>0,T86/W86,0)","v":0},{"$f":"IF(T86>0,T86/X86,0)","v":0},{"$f":"MIN($AB$134,TREND($AB$134:$AC$134,$AB$133:$AC$133,$I86))*(U86>0)","v":0},{"$f":"MIN($AB$135,TREND($AB$135:$AC$135,$AB$133:$AC$133,$I86))*(U86>0)","v":0},{"$f":"IF(V86>0,V86/AA86/3.412,0)","v":0},{"$f":"IF(V86>0,V86/AB86/3.412,0)","v":0},{"$f":"Y86-Z86","v":0},{"$f":"AC86-AD86","v":0},{"$f":"AE86+AF86","v":0},null,{"$f":"$X$120","v":0.25},{"$f":"$R$40*AI86","v":0},{"$f":"$Y$120","v":0},{"$f":"$S$40*AK86","v":0},{"$f":"OFFSET($Q$137,MATCH($I86,$Q$138:$Q$148,-1),MATCH(AI86,$R$137:$V$137,-1))*(AI86>0)","v":0},{"$f":"OFFSET($Q$150,MATCH($I86,$Q$151:$Q$161,-1),MATCH(AI86,$R$150:$V$150,-1))*(AI86>0)","v":0},{"$f":"IF(AJ86>0,AJ86/AM86,0)","v":0},{"$f":"IF(AJ86>0,AJ86/AN86,0)","v":0},{"$f":"MIN($AB$134,TREND($AB$134:$AC$134,$AB$133:$AC$133,$I86))*(AK86>0)","v":0},{"$f":"MIN($AB$135,TREND($AB$135:$AC$135,$AB$133:$AC$133,$I86))*(AK86>0)","v":0},{"$f":"IF(AL86>0,AL86/AQ86/3.412,0)","v":0},{"$f":"IF(AL86>0,AL86/AR86/3.412,0)","v":0},{"$f":"AO86-AP86","v":0},{"$f":"AS86-AT86","v":0},{"$f":"AU86+AV86","v":0},null,{"$f":"AG86+AW86","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A75","v":95},{"$f":"'Project Info'!B75","v":100},{"$f":"'Project Info'!C75","v":95.219272727272724},{"$f":"'Project Info'!D75","v":74.534025272781079},{"$f":"'Project Info'!E75","v":37.923296058061368},{"$f":"'Project Info'!F75","v":0},{"$f":"'Project Info'!G75","v":0},{"$f":"'Project Info'!H75","v":0},{"$f":"'Project Info'!I75","v":0},{"$f":"'Project Info'!J75","v":0},{"$f":"'Project Info'!K75","v":0},{"$f":"'Project Info'!L75","v":0},{"$f":"MAX(0,MIN(1,TREND($Y$116:$Z$116,$W$116:$X$116,$I87)))*($I87>=$X$116)","v":0.40306981818181808},0,{"$f":"MAX(0,MIN(1,TREND($AH$116:$AI$116,$AF$116:$AG$116,$I87)))*($I87<=$AF$116)","v":0},0,0,0,{"$f":"IF(T87>0,T87/W87,0)","v":0},{"$f":"IF(T87>0,T87/X87,0)","v":0},0,0,{"$f":"IF(V87>0,V87/AA87/3.412,0)","v":0},{"$f":"IF(V87>0,V87/AB87/3.412,0)","v":0},{"$f":"Y87-Z87","v":0},{"$f":"AC87-AD87","v":0},{"$f":"AE87+AF87","v":0},null,{"$f":"$X$120","v":0.25},0,{"$f":"$Y$120","v":0},0,0,0,{"$f":"IF(AJ87>0,AJ87/AM87,0)","v":0},{"$f":"IF(AJ87>0,AJ87/AN87,0)","v":0},0,0,{"$f":"IF(AL87>0,AL87/AQ87/3.412,0)","v":0},{"$f":"IF(AL87>0,AL87/AR87/3.412,0)","v":0},{"$f":"AO87-AP87","v":0},{"$f":"AS87-AT87","v":0},{"$f":"AU87+AV87","v":0},null,{"$f":"AG87+AW87","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A76","v":90},{"$f":"'Project Info'!B76","v":95},{"$f":"'Project Info'!C76","v":92.016049160256074},{"$f":"'Project Info'!D76","v":72.911561930607689},{"$f":"'Project Info'!E76","v":36.467095439351091},{"$f":"'Project Info'!F76","v":0},{"$f":"'Project Info'!G76","v":0},{"$f":"'Project Info'!H76","v":0},{"$f":"'Project Info'!I76","v":0},{"$f":"'Project Info'!J76","v":0},{"$f":"'Project Info'!K76","v":0},{"$f":"'Project Info'!L76","v":0},0.358224688243585,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A77","v":85},{"$f":"'Project Info'!B77","v":90},{"$f":"'Project Info'!C77","v":87.457811360655285},{"$f":"'Project Info'!D77","v":70.80538329449476},{"$f":"'Project Info'!E77","v":34.679413213566804},{"$f":"'Project Info'!F77","v":0},{"$f":"'Project Info'!G77","v":0},{"$f":"'Project Info'!H77","v":0},{"$f":"'Project Info'!I77","v":0},{"$f":"'Project Info'!J77","v":0},{"$f":"'Project Info'!K77","v":0},{"$f":"'Project Info'!L77","v":0},0.29440935904917398,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A78","v":80},{"$f":"'Project Info'!B78","v":85},{"$f":"'Project Info'!C78","v":82.136788830239965},{"$f":"'Project Info'!D78","v":67.872393622439333},{"$f":"'Project Info'!E78","v":32.296248223809314},{"$f":"'Project Info'!F78","v":0},{"$f":"'Project Info'!G78","v":0},{"$f":"'Project Info'!H78","v":0},{"$f":"'Project Info'!I78","v":0},{"$f":"'Project Info'!J78","v":0},{"$f":"'Project Info'!K78","v":0},{"$f":"'Project Info'!L78","v":0},0.21991504362335956,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A79","v":75},{"$f":"'Project Info'!B79","v":80},{"$f":"'Project Info'!C79","v":76.988400157585886},{"$f":"'Project Info'!D79","v":65.129261896908645},{"$f":"'Project Info'!E79","v":30.190476812806729},{"$f":"'Project Info'!F79","v":0},{"$f":"'Project Info'!G79","v":0},{"$f":"'Project Info'!H79","v":0},{"$f":"'Project Info'!I79","v":0},{"$f":"'Project Info'!J79","v":0},{"$f":"'Project Info'!K79","v":0},{"$f":"'Project Info'!L79","v":0},0.14783760220620235,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A80","v":70},{"$f":"'Project Info'!B80","v":75},{"$f":"'Project Info'!C80","v":72.457982050814195},{"$f":"'Project Info'!D80","v":63.604425012889301},{"$f":"'Project Info'!E80","v":29.088683095945193},{"$f":"'Project Info'!F80","v":0},{"$f":"'Project Info'!G80","v":0},{"$f":"'Project Info'!H80","v":0},{"$f":"'Project Info'!I80","v":0},{"$f":"'Project Info'!J80","v":0},{"$f":"'Project Info'!K80","v":0},{"$f":"'Project Info'!L80","v":0},8.4411748711398782E-2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A81","v":65},{"$f":"'Project Info'!B81","v":70},{"$f":"'Project Info'!C81","v":67.815831070966169},{"$f":"'Project Info'!D81","v":61.631331368130574},{"$f":"'Project Info'!E81","v":27.661514889731574},{"$f":"'Project Info'!F81","v":0},{"$f":"'Project Info'!G81","v":0},{"$f":"'Project Info'!H81","v":0},{"$f":"'Project Info'!I81","v":0},{"$f":"'Project Info'!J81","v":0},{"$f":"'Project Info'!K81","v":0},{"$f":"'Project Info'!L81","v":0},0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A82","v":60},{"$f":"'Project Info'!B82","v":65},{"$f":"'Project Info'!C82","v":62.535961472271332},{"$f":"'Project Info'!D82","v":57.135476922863582},{"$f":"'Project Info'!E82","v":24.623037157728302},{"$f":"'Project Info'!F82","v":0},{"$f":"'Project Info'!G82","v":0},{"$f":"'Project Info'!H82","v":0},{"$f":"'Project Info'!I82","v":0},{"$f":"'Project Info'!J82","v":0},{"$f":"'Project Info'!K82","v":0},{"$f":"'Project Info'!L82","v":0},0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A83","v":55},{"$f":"'Project Info'!B83","v":60},{"$f":"'Project Info'!C83","v":57.125792270740902},{"$f":"'Project Info'!D83","v":52.596971157053673},{"$f":"'Project Info'!E83","v":21.818001539159841},{"$f":"'Project Info'!F83","v":0},{"$f":"'Project Info'!G83","v":0},{"$f":"'Project Info'!H83","v":0},{"$f":"'Project Info'!I83","v":0},{"$f":"'Project Info'!J83","v":0},{"$f":"'Project Info'!K83","v":0},{"$f":"'Project Info'!L83","v":0},0,0,2.3951731077159255E-2,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A84","v":50},{"$f":"'Project Info'!B84","v":55},{"$f":"'Project Info'!C84","v":52.235698854337961},{"$f":"'Project Info'!D84","v":48.022768090099298},{"$f":"'Project Info'!E84","v":19.246640192796217},{"$f":"'Project Info'!F84","v":0},{"$f":"'Project Info'!G84","v":0},{"$f":"'Project Info'!H84","v":0},{"$f":"'Project Info'!I84","v":0},{"$f":"'Project Info'!J84","v":0},{"$f":"'Project Info'!K84","v":0},{"$f":"'Project Info'!L84","v":0},0,0,6.4702509547183706E-2,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A85","v":45},{"$f":"'Project Info'!B85","v":50},{"$f":"'Project Info'!C85","v":47.459170258371508},{"$f":"'Project Info'!D85","v":43.465397050422162},{"$f":"'Project Info'!E85","v":16.894183241713304},{"$f":"'Project Info'!F85","v":0},{"$f":"'Project Info'!G85","v":0},{"$f":"'Project Info'!H85","v":0},{"$f":"'Project Info'!I85","v":0},{"$f":"'Project Info'!J85","v":0},{"$f":"'Project Info'!K85","v":0},{"$f":"'Project Info'!L85","v":0},0,0,0.1045069145135708,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A86","v":40},{"$f":"'Project Info'!B86","v":45},{"$f":"'Project Info'!C86","v":42.677030404888129},{"$f":"'Project Info'!D86","v":38.812544504634097},{"$f":"'Project Info'!E86","v":14.690265649465921},{"$f":"'Project Info'!F86","v":0},{"$f":"'Project Info'!G86","v":0},{"$f":"'Project Info'!H86","v":0},{"$f":"'Project Info'!I86","v":0},{"$f":"'Project Info'!J86","v":0},{"$f":"'Project Info'!K86","v":0},{"$f":"'Project Info'!L86","v":0},0,0,0.14435807995926564,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A87","v":35},{"$f":"'Project Info'!B87","v":40},{"$f":"'Project Info'!C87","v":37.333046773755832},{"$f":"'Project Info'!D87","v":33.904706919479686},{"$f":"'Project Info'!E87","v":12.53841602318813},{"$f":"'Project Info'!F87","v":0},{"$f":"'Project Info'!G87","v":0},{"$f":"'Project Info'!H87","v":0},{"$f":"'Project Info'!I87","v":0},{"$f":"'Project Info'!J87","v":0},{"$f":"'Project Info'!K87","v":0},{"$f":"'Project Info'!L87","v":0},0,0,0.18889127688536811,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A88","v":30},{"$f":"'Project Info'!B88","v":35},{"$f":"'Project Info'!C88","v":32.638179845662044},{"$f":"'Project Info'!D88","v":29.547170928664851},{"$f":"'Project Info'!E88","v":10.728972818165861},{"$f":"'Project Info'!F88","v":0},{"$f":"'Project Info'!G88","v":0},{"$f":"'Project Info'!H88","v":0},{"$f":"'Project Info'!I88","v":0},{"$f":"'Project Info'!J88","v":0},{"$f":"'Project Info'!K88","v":0},{"$f":"'Project Info'!L88","v":0},0,0,0.22801516795281629,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A89","v":25},{"$f":"'Project Info'!B89","v":30},{"$f":"'Project Info'!C89","v":27.529264646850947},{"$f":"'Project Info'!D89","v":24.652717392657845},{"$f":"'Project Info'!E89","v":8.8041305482613303},{"$f":"'Project Info'!F89","v":0},{"$f":"'Project Info'!G89","v":0},{"$f":"'Project Info'!H89","v":0},{"$f":"'Project Info'!I89","v":0},{"$f":"'Project Info'!J89","v":0},{"$f":"'Project Info'!K89","v":0},{"$f":"'Project Info'!L89","v":0},0,0,0.27058946127624206,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A90","v":20},{"$f":"'Project Info'!B90","v":25},{"$f":"'Project Info'!C90","v":22.998111483544687},{"$f":"'Project Info'!D90","v":20.383306659827422},{"$f":"'Project Info'!E90","v":7.246164547543378},{"$f":"'Project Info'!F90","v":0},{"$f":"'Project Info'!G90","v":0},{"$f":"'Project Info'!H90","v":0},{"$f":"'Project Info'!I90","v":0},{"$f":"'Project Info'!J90","v":0},{"$f":"'Project Info'!K90","v":0},{"$f":"'Project Info'!L90","v":0},0,0,0.30834907097046094,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A91","v":15},{"$f":"'Project Info'!B91","v":20},{"$f":"'Project Info'!C91","v":17.808510327474309},{"$f":"'Project Info'!D91","v":15.420865796304254},{"$f":"'Project Info'!E91","v":5.5490484131518292},{"$f":"'Project Info'!F91","v":0},{"$f":"'Project Info'!G91","v":0},{"$f":"'Project Info'!H91","v":0},{"$f":"'Project Info'!I91","v":0},{"$f":"'Project Info'!J91","v":0},{"$f":"'Project Info'!K91","v":0},{"$f":"'Project Info'!L91","v":0},0,0,0.35159574727104737,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A92","v":10},{"$f":"'Project Info'!B92","v":15},{"$f":"'Project Info'!C92","v":12.269931130346862},{"$f":"'Project Info'!D92","v":10.318264913023604},{"$f":"'Project Info'!E92","v":3.9082824916941998},{"$f":"'Project Info'!F92","v":0},{"$f":"'Project Info'!G92","v":0},{"$f":"'Project Info'!H92","v":0},{"$f":"'Project Info'!I92","v":0},{"$f":"'Project Info'!J92","v":0},{"$f":"'Project Info'!K92","v":0},{"$f":"'Project Info'!L92","v":0},0,0,0.39775057391377611,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A93","v":5},{"$f":"'Project Info'!B93","v":10},{"$f":"'Project Info'!C93","v":7.3137581369917548},{"$f":"'Project Info'!D93","v":5.7052382449247707},{"$f":"'Project Info'!E93","v":2.5019418419888937},{"$f":"'Project Info'!F93","v":0},{"$f":"'Project Info'!G93","v":0},{"$f":"'Project Info'!H93","v":0},{"$f":"'Project Info'!I93","v":0},{"$f":"'Project Info'!J93","v":0},{"$f":"'Project Info'!K93","v":0},{"$f":"'Project Info'!L93","v":0},0,0,0.43905201552506862,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A94","v":0},{"$f":"'Project Info'!B94","v":5},{"$f":"'Project Info'!C94","v":2.6119461836144886},{"$f":"'Project Info'!D94","v":1.2699770062067783},{"$f":"'Project Info'!E94","v":1.2046477897733283},{"$f":"'Project Info'!F94","v":8760},{"$f":"'Project Info'!G94","v":2672},{"$f":"'Project Info'!H94","v":3160},{"$f":"'Project Info'!I94","v":1344},{"$f":"'Project Info'!J94","v":1584},{"$f":"'Project Info'!K94","v":88},{"$f":"'Project Info'!L94","v":264},0,0,0.47823378180321252,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A95","v":-5},{"$f":"'Project Info'!B95","v":0},{"$f":"'Project Info'!C95","v":-1.6731398516793925},{"$f":"'Project Info'!D95","v":-2.7083318773557807},{"$f":"'Project Info'!E95","v":7.9391832815876459E-2},{"$f":"'Project Info'!F95","v":0},{"$f":"'Project Info'!G95","v":0},{"$f":"'Project Info'!H95","v":0},{"$f":"'Project Info'!I95","v":0},{"$f":"'Project Info'!J95","v":0},{"$f":"'Project Info'!K95","v":0},{"$f":"'Project Info'!L95","v":0},0,0,0.51394283209732816,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A96","v":-10},{"$f":"'Project Info'!B96","v":-5},{"$f":"'Project Info'!C96","v":-6.5729865085377277},{"$f":"'Project Info'!D96","v":-7.2465935998252222},{"$f":"'Project Info'!E96","v":-1.168423365310433},{"$f":"'Project Info'!F96","v":0},{"$f":"'Project Info'!G96","v":0},{"$f":"'Project Info'!H96","v":0},{"$f":"'Project Info'!I96","v":0},{"$f":"'Project Info'!J96","v":0},{"$f":"'Project Info'!K96","v":0},{"$f":"'Project Info'!L96","v":0},0,0,0.55477488757114757,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A97","v":-15},{"$f":"'Project Info'!B97","v":-10},{"$f":"'Project Info'!C97","v":-15.32570353422995},{"$f":"'Project Info'!D97","v":-15.707838211108999},{"$f":"'Project Info'!E97","v":-3.4051318156661381},{"$f":"'Project Info'!F97","v":0},{"$f":"'Project Info'!G97","v":0},{"$f":"'Project Info'!H97","v":0},{"$f":"'Project Info'!I97","v":0},{"$f":"'Project Info'!J97","v":0},{"$f":"'Project Info'!K97","v":0},{"$f":"'Project Info'!L97","v":0},0,0,0.62771419611858281,0,0,0,0,0,0,0,0,0,0,0,0,null,0.25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0]
[]
[null,null,null,null,null,null,"System Types",null,"Condenser Type",null,null,null,null,null,null,null,null,null,"HVAC Peak Load as % of Max Operating Capacity",null,null,null,0.85]
[null,null,null,null,null,null,"Air Conditioner",null,"Air Cooled","Water Cooled","Evap Cooled",null,null,null,null,null,null,null,"Estimated Cooling Load Profile",null,null,null,null,null,null,null,null,"Estimated Heating Load Profile"]
[null,null,null,null,null,null,"Heat Pump",null,"Air Cooled","Water Loop (HP)","Ground Water (HP)","Ground Loop (HP)",null,null,null,null,null,null,"Occupied Profile",null,null,null,"Unocc Profile",null,null,null,null,"Occupied Profile",null,null,null,"Unocc Profile"]
[null,null,null,null,null,null,"VRF AC Only",null,"Air Cooled",null,null,null,null,null,null,null,null,null,"Max OAT","Min OAT","% Load @","%Load @","Max OAT","Min OAT","% Load @","%Load @",null,"Max OAT","Min OAT","% Load @","%Load @","Max OAT","Min OAT","% Load @","%Load @"]
[null,null,null,null,null,null,"VRF Heat Pump",null,"Air Cooled","Water Cooled","Ground Water (HP)","Ground Loop (HP)",null,null,null,null,null,null,"°F","°F","Max OAT","Min OAT","°F","°F","Max OAT","Min OAT",null,"°F","°F","Max OAT","Min OAT","°F","°F","Max OAT","Min OAT"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'High Efficiency Chillers'!I94","v":95},{"$f":"'High Efficiency Chillers'!J94","v":50},{"$f":"'High Efficiency Chillers'!K94","v":1},{"$f":"'High Efficiency Chillers'!L94","v":0.1},{"$f":"'High Efficiency Chillers'!M94","v":95},{"$f":"'High Efficiency Chillers'!N94","v":70},{"$f":"'High Efficiency Chillers'!O94","v":0.4},{"$f":"'High Efficiency Chillers'!P94","v":0.05},null,{"$f":"'Condensing Boilers'!L94","v":60},{"$f":"'Condensing Boilers'!M94","v":0},{"$f":"'Condensing Boilers'!N94","v":0.1},{"$f":"'Condensing Boilers'!O94","v":1},{"$f":"'Condensing Boilers'!P94","v":60},{"$f":"'Condensing Boilers'!Q94","v":0},{"$f":"'Condensing Boilers'!R94","v":0},{"$f":"'Condensing Boilers'!S94","v":0.5}]
[null,null,null,null,null,null,null,null,"Perf. Unit",null,null,null,null,null,null,null,null,null,95,55,{"$f":"U116*$R$39","v":0},{"$f":"V116*$R$39","v":0},95,65,{"$f":"Y116*$R$39","v":0},{"$f":"Z116*$R$39","v":0},null,55,5,{"$f":"AD116*$S$39","v":0},{"$f":"AE116*$S$39","v":0},55,5,{"$f":"AH116*$S$39","v":0},{"$f":"AI116*$S$39","v":0}]
[null,null,null,null,null,null,"Heating System Type",null,0,65,null,null,null,null,null,null,null,null,"Bin Model EFLH Cooling",null,null,{"$f":"SUMPRODUCT(S56:S79,L56:L79)+SUMPRODUCT(S86:S109,L86:L109)","v":0},null,null,null,null,null,"Bin Model EFLH Heatling",null,null,{"$f":"SUMPRODUCT(U56:U79,L56:L79)+SUMPRODUCT(U86:U109,L86:L109)","v":4189.3279285961416}]
[null,null,null,null,null,null,"Heat Pump",null,"HSPF","COP",null,null,null,null,null,null,null,null,null,null,null,null,null,"Cooling","Heating"]
[null,null,null,null,null,null,"Other/None",null,"NA","NA",null,null,null,null,null,null,null,null,"Constant/IT-Elec Rooms Average 24/7 % Load",null,null,null,null,0.25,0]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"IEER Limit for Calculations",null,25]
[]
[]
[null,null,null,null,null,null,"OAT Perf. Impact",null,5.0000000000000001E-3,"% improvement per °F OAT reduction"]
[]
[null,null,null,null,null,null,null,null,0.75,0.5,0.25]
[null,null,null,null,null,null,"PL EER Factors",null,0.96875,1.0498263888888888,1.0941840277777777]
[]
[null,null,null,null,null,null,null,"HVAC Systems - Part Load Cooling Performance",null,null,null,null,null,null,null,null,null,"HVAC Load Profile -Part Load Cooling Performance",null,null,null,null,null,null,null,null,"HVAC Load Profile"]
[null,null,null,null,null,null,null,0.02,0.61699999999999999,0.23799999999999999,0.125,null,null,"IEER",null,null,null,0.02,0.61699999999999999,0.23799999999999999,0.125,null,null,"IEER",null,null,"Heating Performance - COP vs. OAT°F"]
[null,null,null,null,null,null,null,1,0.75,0.5,0.25,-0.01,"IEER","Calculated",null,null,null,1,0.75,0.5,0.25,-0.01,"IEER","Calculated",null,null,null,"OAT (°F)"]
[null,null,null,null,null,null,"Base",{"$f":"$AD$39","v":0},{"$f":"IF(OR(H133=\"\",H133=0),0,($M133/$H133)*I$128*$H133)","v":0},{"$f":"IF(OR(H133=0,H133=\"\"),0,($M133/$H133)*J$128*$H133)","v":0},{"$f":"IF(OR(H133=0,H133=\"\"),0,($M133/$H133)*K$128*$H133)","v":0},{"$f":"K133*0.75","v":0},{"$f":"$AE$39","v":0},{"$f":"SUMPRODUCT(H133:K133,$H$131:$K$131)","v":0},{"$f":"1-N133/M133","v":{"$error":"#DIV/0!"}},null,"Base",{"$f":"$AD$40","v":0},{"$f":"IF(R133=0,0,($W133/$R133)*I$128*$R133)","v":0},0,0,{"$f":"U133*0.75","v":0},{"$f":"$AE$40","v":0},{"$f":"SUMPRODUCT(R133:U133,$H$131:$K$131)","v":0},{"$f":"1-X133/W133","v":{"$error":"#DIV/0!"}},null,null,47,17]
[null,null,null,null,null,null,"Proposed",{"$f":"$Z$39","v":0},{"$f":"IF(OR(H134=0,H134=\"\"),0,($M134/$H134)*I$128*$H134)","v":0},{"$f":"IF(OR(H134=0,H134=\"\"),0,($M134/$H134)*J$128*$H134)","v":0},{"$f":"IF(OR(H134=0,H134=\"\"),0,($M134/$H134)*K$128*$H134)","v":0},{"$f":"K134*0.75","v":0},{"$f":"$AI$39","v":0},{"$f":"SUMPRODUCT(H134:K134,$H$131:$K$131)","v":0},{"$f":"1-N134/M134","v":{"$error":"#DIV/0!"}},null,"Proposed",{"$f":"$Z$40","v":0},0,0,0,{"$f":"U134*0.75","v":0},{"$f":"$AI$40","v":0},{"$f":"SUMPRODUCT(R134:U134,$H$131:$K$131)","v":0},{"$f":"1-X134/W134","v":{"$error":"#DIV/0!"}},null,"Base",{"$f":"AF39","v":0},{"$f":"AG39","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Proposed",{"$f":"AB39","v":0},{"$f":"AC39","v":0}]
[null,null,null,null,null,null,"HVAC Systems - Baseline Cooling Performance Table",null,null,null,null,null,null,null,null,null,"Constant/IT-Elec Room Systems - Baseline Cooling Performance Table"]
[null,null,null,null,null,null,"OAT",1,0.75,0.5,0.25,-0.01,null,null,null,null,"OAT",1,0.75,0.5,0.25,-0.01,null,null,null,null,"Incremental Cost Data"]
[null,null,null,null,null,null,105,{"$f":"H139","v":0},{"$f":"I139","v":0},{"$f":"J139","v":0},{"$f":"K139","v":0},{"$f":"L139","v":0},null,null,null,null,105,{"$f":"R139","v":0},{"$f":"S139","v":0},{"$f":"T139","v":0},{"$f":"U139","v":0},{"$f":"V139","v":0},null,null,null,null,"from eComfort.com"]
[null,null,null,null,null,null,95,{"$f":"H133","v":0},{"$f":"$I$142/(1-($G$142-$G139)*$I$125)","v":0},{"$f":"$J$144/(1-($G$144-$G139)*$I$125)","v":0},{"$f":"$K$145/(1-($G$145-$G139)*$I$125)","v":0},{"$f":"K139","v":0},null,null,null,null,95,{"$f":"R133","v":0},{"$f":"$S$142/(1-($Q$142-$Q139)*$I$125)","v":0},{"$f":"$T$144/(1-($Q$144-$Q139)*$I$125)","v":0},{"$f":"$U$145/(1-($Q$145-$Q139)*$I$125)","v":0},{"$f":"U139","v":0}]
[null,null,null,null,null,null,90,{"$f":"$H$139/(1-($G$139-$G140)*$I$125)","v":0},{"$f":"$I$142/(1-($G$142-$G140)*$I$125)","v":0},{"$f":"$J$144/(1-($G$144-$G140)*$I$125)","v":0},0,0,null,null,null,null,90,{"$f":"$R$139/(1-($Q$139-$Q140)*$I$125)","v":0},{"$f":"$S$142/(1-($Q$142-$Q140)*$I$125)","v":0},{"$f":"$T$144/(1-($Q$144-$Q140)*$I$125)","v":0},0,0,null,null,null,null,"Packged Heat Pump"]
[null,null,null,null,null,null,85,0,{"$f":"$I$142/(1-($G$142-$G141)*$I$125)","v":0},{"$f":"$J$144/(1-($G$144-$G141)*$I$125)","v":0},0,0,null,null,null,null,85,0,{"$f":"$S$142/(1-($Q$142-$Q141)*$I$125)","v":0},{"$f":"$T$144/(1-($Q$144-$Q141)*$I$125)","v":0},0,0,null,null,null,null,"Cooling Cap",60,"MBH"]
[null,null,null,null,null,null,80,0,{"$f":"I133","v":0},{"$f":"$J$144/(1-($G$144-$G142)*$I$125)","v":0},0,0,null,null,null,null,80,0,{"$f":"S133","v":0},{"$f":"$T$144/(1-($Q$144-$Q142)*$I$125)","v":0},0,0,null,null,null,null,"Heating Cap",57,"MBH"]
[null,null,null,null,null,null,75,0,{"$f":"$I$142/(1-($G$142-$G143)*$I$125)","v":0},{"$f":"$J$144/(1-($G$144-$G143)*$I$125)","v":0},0,0,null,null,null,null,75,0,{"$f":"$S$142/(1-($Q$142-$Q143)*$I$125)","v":0},{"$f":"$T$144/(1-($Q$144-$Q143)*$I$125)","v":0},0,0]
[null,null,null,null,null,null,70,0,{"$f":"$I$142/(1-($G$142-$G144)*$I$125)","v":0},{"$f":"J133","v":0},0,0,null,null,null,null,70,0,{"$f":"$S$142/(1-($Q$142-$Q144)*$I$125)","v":0},{"$f":"T133","v":0},0,0,null,null,null,null,"SEER","$",null,"Est Cost/SEER/MBH",null,{"$f":"(AB146-AB145)/(AA146-AA145)/AB141","v":8.2249999999999996}]
[null,null,null,null,null,null,65,0,{"$f":"$I$142/(1-($G$142-$G145)*$I$125)","v":0},{"$f":"$J$144/(1-($G$144-$G145)*$I$125)","v":0},{"$f":"K133","v":0},0,"< Min Cond Temp",null,null,null,65,0,{"$f":"$S$142/(1-($Q$142-$Q145)*$I$125)","v":0},{"$f":"$T$144/(1-($Q$144-$Q145)*$I$125)","v":0},{"$f":"U133","v":0},0,"< Min Cond Temp",null,null,null,14,3275,null,"Est Cost/HSPF/MBH",null,{"$f":"(AB150-AB149)/(AA150-AA149)/AB142","v":44.298245614035245}]
[null,null,null,null,null,null,60,{"$f":"H145","v":0},{"$f":"I145","v":0},0,0,0,null,null,null,null,60,{"$f":"R145","v":0},0,0,0,0,null,null,null,null,16,4262]
[null,null,null,null,null,null,55,{"$f":"H146","v":0},0,0,0,0,null,null,null,null,55,0,0,0,0,0]
[null,null,null,null,null,null,-20,{"$f":"H147","v":0},{"$f":"I147","v":0},{"$f":"J147","v":0},{"$f":"K147","v":0},{"$f":"L147","v":0},null,null,null,null,-20,0,0,0,0,0,null,null,null,null,"HSPF","$"]
[null,null,null,null,null,null,"HVAC Systems - Proposed Cooling Performance Table",null,null,null,null,null,null,null,null,null,"Constant/IT-Elec Room Systems - Proposed Cooling Performance Table",null,null,null,null,null,null,null,null,null,8,4450]
[null,null,null,null,null,null,"OAT",1,0.75,0.5,0.25,-0.01,null,null,null,null,"OAT",1,0.75,0.5,0.25,-0.01,null,null,null,null,8.1999999999999993,4955]
[null,null,null,null,null,null,105,{"$f":"H152","v":0},{"$f":"I152","v":0},{"$f":"J152","v":0},{"$f":"K152","v":0},{"$f":"L152","v":0},null,null,null,null,105,{"$f":"R152","v":0},{"$f":"S152","v":0},{"$f":"T152","v":0},{"$f":"U152","v":0},{"$f":"V152","v":0}]
[null,null,null,null,null,null,95,{"$f":"H134","v":0},{"$f":"$I$155/(1-($G$155-$G152)*$I$125)","v":0},{"$f":"$J$157/(1-($G$157-$G152)*$I$125)","v":0},{"$f":"$K$158/(1-($G$158-$G152)*$I$125)","v":0},{"$f":"K152","v":0},null,null,null,null,95,{"$f":"R134","v":0},{"$f":"$S$155/(1-($Q$155-$Q152)*$I$125)","v":0},{"$f":"$T$157/(1-($Q$157-$Q152)*$I$125)","v":0},{"$f":"$U$158/(1-($Q$158-$Q152)*$I$125)","v":0},{"$f":"U152","v":0}]
[null,null,null,null,null,null,90,{"$f":"$H$152/(1-($G$152-$G153)*$I$125)","v":0},{"$f":"$I$155/(1-($G$155-$G153)*$I$125)","v":0},{"$f":"$J$157/(1-($G$157-$G153)*$I$125)","v":0},0,{"$f":"K153","v":0},null,null,null,null,90,{"$f":"$R$152/(1-($Q$152-$Q153)*$I$125)","v":0},{"$f":"$S$155/(1-($Q$155-$Q153)*$I$125)","v":0},{"$f":"$T$157/(1-($Q$157-$Q153)*$I$125)","v":0},0,{"$f":"U153","v":0}]
[null,null,null,null,null,null,85,0,{"$f":"$I$155/(1-($G$155-$G154)*$I$125)","v":0},{"$f":"$J$157/(1-($G$157-$G154)*$I$125)","v":0},0,0,null,null,null,null,85,0,{"$f":"$S$155/(1-($Q$155-$Q154)*$I$125)","v":0},{"$f":"$T$157/(1-($Q$157-$Q154)*$I$125)","v":0},0,0]
[null,null,null,null,null,null,80,0,{"$f":"I134","v":0},{"$f":"$J$157/(1-($G$157-$G155)*$I$125)","v":0},0,0,null,null,null,null,80,0,{"$f":"S134","v":0},{"$f":"$T$157/(1-($Q$157-$Q155)*$I$125)","v":0},0,0]
[null,null,null,null,null,null,75,0,{"$f":"$I$155/(1-($G$155-$G156)*$I$125)","v":0},{"$f":"$J$157/(1-($G$157-$G156)*$I$125)","v":0},0,0,null,null,null,null,75,0,{"$f":"$S$155/(1-($Q$155-$Q156)*$I$125)","v":0},{"$f":"$T$157/(1-($Q$157-$Q156)*$I$125)","v":0},0,0]
[null,null,null,null,null,null,70,0,{"$f":"$I$155/(1-($G$155-$G157)*$I$125)","v":0},{"$f":"J134","v":0},0,0,null,null,null,null,70,0,{"$f":"$S$155/(1-($Q$155-$Q157)*$I$125)","v":0},{"$f":"T134","v":0},0,0]
[null,null,null,null,null,null,65,0,{"$f":"$I$155/(1-($G$155-$G158)*$I$125)","v":0},{"$f":"$J$157/(1-($G$157-$G158)*$I$125)","v":0},{"$f":"K134","v":0},0,"< Min Cond Temp",null,null,null,65,0,{"$f":"$S$155/(1-($Q$155-$Q158)*$I$125)","v":0},{"$f":"$T$157/(1-($Q$157-$Q158)*$I$125)","v":0},{"$f":"U134","v":0},0,"< Min Cond Temp"]
[null,null,null,null,null,null,60,{"$f":"H158","v":0},{"$f":"I158","v":0},0,0,0,null,null,null,null,60,{"$f":"R158","v":0},0,0,0,0]
[null,null,null,null,null,null,55,{"$f":"H159","v":0},0,0,0,0,null,null,null,null,55,0,0,0,0,0]
[null,null,null,null,null,null,-20,{"$f":"H160","v":0},0,0,0,0,null,null,null,null,-20,0,0,0,0,0]
[]
[null,null,null,"** Using AC values fo electric heat or no heat)"]
[null,null,null,null,null,2015,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2018]
[null,null,null,null,null,null,null,"Baseline EER",null,null,null,null,null,null,null,null,"Baseline IEER",null,null,null,null,null,null,null,null,"Baseline COP 47",null,null,null,null,null,null,null,null,"Baseline COP 17",null,null,null,null,null,null,null,null,null,null,"Baseline EER",null,null,null,null,null,null,null,null,"Baseline IEER",null,null,null,null,null,null,null,null,"Baseline COP 47",null,null,null,null,null,null,null,null,"Baseline COP 17"]
[null,null,null,null,null,null,null,null,"MBH ≥",0,17,65,135,240,760,null,null,"MBH ≥",0,17,65,135,240,760,null,null,"MBH ≥",0,17,65,135,240,760,null,null,"MBH ≥",0,17,65,135,240,760,null,null,null,null,"MBH ≥",0,17,65,135,240,760,null,null,"MBH ≥",0,17,65,135,240,760,null,null,"MBH ≥",0,17,65,135,240,760,null,null,"MBH ≥",0,17,65,135,240,760]
[null,null,null,null,null,null,null,null,"MBH <",17,65,135,240,760,10000,null,null,"MBH <",17,65,135,240,760,10000,null,null,"MBH <",17,65,135,240,760,10000,null,null,"MBH <",17,65,135,240,760,10000,null,null,null,null,"MBH <",17,65,135,240,760,10000,null,null,"MBH <",17,65,135,240,760,10000,null,null,"MBH <",17,65,135,240,760,10000,null,null,"MBH <",17,65,135,240,760,10000]
[null,null,null,null,null,{"$f":"$G$112","v":"Air Conditioner"},null,"AC - Cooling Only",null,null,null,null,null,null,null,null,"AC - Cooling Only",null,null,null,null,null,null,null,null,"AC - Cooling Only",null,null,null,null,null,null,null,null,"AC - Cooling Only",null,null,null,null,null,null,null,null,{"$f":"$G$112","v":"Air Conditioner"},null,"AC - Cooling Only",null,null,null,null,null,null,null,null,"AC - Cooling Only",null,null,null,null,null,null,null,null,"AC - Cooling Only",null,null,null,null,null,null,null,null,"AC - Cooling Only"]
[null,null,null,null,null,"Air Cooled",null,"Air Cooled",null,{"$f":"K169","v":11.049999999999999},{"$f":"0.85*T169","v":11.049999999999999},11.2,11,10,9.6999999999999993,null,"Air Cooled",null,{"$f":"T169","v":13},13,12.8,12.4,11.6,11.2,null,"Air Cooled",null,0,0,0,0,0,0,null,"Air Cooled",null,0,0,0,0,0,0,null,null,null,"Air Cooled",null,13,13,11.2,11,10,9.6999999999999993,null,"Air Cooled",null,{"$f":"BF169","v":13},13,14.6,14,13,13,null,"Air Cooled",null,0,0,0,0,0,0,null,"Air Cooled",null,0,0,0,0,0,0]
[null,null,null,null,null,"Water Cooled",null,"Water Cooled",null,{"$f":"K170","v":12.1},12.1,12.1,12.5,12.4,12.2,null,"Water Cooled",null,{"$f":"T170","v":12.3},12.3,13.9,13.9,13.6,13.5,null,"Water Cooled",null,0,0,0,0,0,0,null,"Water Cooled",null,0,0,0,0,0,0,null,null,null,"Water Cooled",null,{"$f":"AW170","v":12.1},12.1,12.1,12.5,12.4,12.2,null,"Water Cooled",null,{"$f":"BF170","v":12.3},12.3,13.9,13.9,13.6,13.5,null,"Water Cooled",null,0,0,0,0,0,0,null,"Water Cooled",null,0,0,0,0,0,0]
[null,null,null,null,null,"Evap Cooled",null,"Evap Cooled",null,{"$f":"K171","v":12.1},12.1,12.1,12,11.9,11.7,null,"Evap Cooled",null,{"$f":"T171","v":12.3},12.3,12.3,12.2,12.1,11.9,null,"Evap Cooled",null,0,0,0,0,0,0,null,"Evap Cooled",null,0,0,0,0,0,0,null,null,null,"Evap Cooled",null,{"$f":"AW171","v":12.1},12.1,12.1,12,11.9,11.7,null,"Evap Cooled",null,{"$f":"BF171","v":12.3},12.3,12.3,12.2,12.1,11.9,null,"Evap Cooled",null,0,0,0,0,0,0,null,"Evap Cooled",null,0,0,0,0,0,0]
[null,null,null,null,null,null,null,"Water Loop (HP)",null,0,0,0,0,0,0,null,"Water Loop (HP)",null,0,0,0,0,0,0,null,"Water Loop (HP)",null,0,0,0,0,0,0,null,"Water Loop (HP)",null,0,0,0,0,0,0,null,null,null,"Water Loop (HP)",null,0,0,0,0,0,0,null,"Water Loop (HP)",null,0,0,0,0,0,0,null,"Water Loop (HP)",null,0,0,0,0,0,0,null,"Water Loop (HP)",null,0,0,0,0,0,0]
[null,null,null,null,null,null,null,"Ground Water (HP)",null,0,0,0,0,0,0,null,"Ground Water (HP)",null,0,0,0,0,0,0,null,"Ground Water (HP)",null,0,0,0,0,0,0,null,"Ground Water (HP)",null,0,0,0,0,0,0,null,null,null,"Ground Water (HP)",null,0,0,0,0,0,0,null,"Ground Water (HP)",null,0,0,0,0,0,0,null,"Ground Water (HP)",null,0,0,0,0,0,0,null,"Ground Water (HP)",null,0,0,0,0,0,0]
[null,null,null,null,null,null,null,"Ground Loop (HP)",null,0,0,0,0,0,0,null,"Ground Loop (HP)",null,0,0,0,0,0,0,null,"Ground Loop (HP)",null,0,0,0,0,0,0,null,"Ground Loop (HP)",null,0,0,0,0,0,0,null,null,null,"Ground Loop (HP)",null,0,0,0,0,0,0,null,"Ground Loop (HP)",null,0,0,0,0,0,0,null,"Ground Loop (HP)",null,0,0,0,0,0,0,null,"Ground Loop (HP)",null,0,0,0,0,0,0]
[null,null,null,null,null,{"$f":"$G$113","v":"Heat Pump"},null,"AC - Cooling Only",null,null,null,null,null,null,null,null,"AC - Cooling Only",null,null,null,null,null,null,null,null,"AC - Cooling Only",null,null,null,null,null,null,null,null,"AC - Cooling Only",null,null,null,null,null,null,null,null,{"$f":"$G$113","v":"Heat Pump"},null,"AC - Cooling Only",null,null,null,null,null,null,null,null,"AC - Cooling Only",null,null,null,null,null,null,null,null,"AC - Cooling Only",null,null,null,null,null,null,null,null,"AC - Cooling Only"]
[null,null,null,null,null,"Air Cooled",null,"Air Cooled",null,{"$f":"K176","v":11.9},{"$f":"0.85*T176","v":11.9},11,10.6,9.5,9.5,null,"Air Cooled",null,{"$f":"T176","v":14},14,12,11.6,10.6,10.6,null,"Air Cooled",null,{"$f":"8.2/3.412","v":2.4032825322391558},{"$f":"8.2/3.412","v":2.4032825322391558},3.3,3.2,3.2,3.2,null,"Air Cooled",null,{"$f":"8.2/3.412","v":2.4032825322391558},{"$f":"8.2/3.412","v":2.4032825322391558},2.25,2.0499999999999998,2.0499999999999998,2.0499999999999998,null,null,null,"Air Cooled",null,11.5,11.5,11,10.6,9.5,9.5,null,"Air Cooled",null,14.3,14.3,14.1,13.5,12.5,12.5,null,"Air Cooled",null,{"$f":"7.5/3.412","v":2.1981242672919108},{"$f":"7.5/3.412","v":2.1981242672919108},3.3,3.2,3.2,3.2,null,"Air Cooled",null,{"$f":"7.5/3.412","v":2.1981242672919108},{"$f":"7.5/3.412","v":2.1981242672919108},2.25,2.0499999999999998,2.0499999999999998,2.0499999999999998]
[null,null,null,null,null,"Water Loop (HP)",null,"Water Cooled",null,0,0,0,0,0,0,null,"Water Cooled",null,0,0,0,0,0,0,null,"Water Cooled",null,0,0,0,0,0,0,null,"Water Cooled",null,0,0,0,0,0,0,null,null,null,"Water Cooled",null,0,0,0,0,0,0,null,"Water Cooled",null,0,0,0,0,0,0,null,"Water Cooled",null,0,0,0,0,0,0,null,"Water Cooled",null,0,0,0,0,0,0]
[null,null,null,null,null,"Ground Water (HP)",null,"Evap Cooled",null,0,0,0,0,0,0,null,"Evap Cooled",null,0,0,0,0,0,0,null,"Evap Cooled",null,0,0,0,0,0,0,null,"Evap Cooled",null,0,0,0,0,0,0,null,null,null,"Evap Cooled",null,0,0,0,0,0,0,null,"Evap Cooled",null,0,0,0,0,0,0,null,"Evap Cooled",null,0,0,0,0,0,0,null,"Evap Cooled",null,0,0,0,0,0,0]
[null,null,null,null,null,"Ground Loop (HP)",null,"Water Loop (HP)",null,12.2,13,13,0,0,0,null,"Water Loop (HP)",null,12.2,13,13,0,0,0,null,"Water Loop (HP)",null,4.3,4.3,4.3,0,0,0,null,"Water Loop (HP)",null,4.3,4.3,4.3,0,0,0,null,null,null,"Water Loop (HP)",null,12.2,13,13,0,0,0,null,"Water Loop (HP)",null,12.2,13,13,0,0,0,null,"Water Loop (HP)",null,4.3,4.3,4.3,0,0,0,null,"Water Loop (HP)",null,4.3,4.3,4.3,0,0,0]
[null,null,null,null,null,null,null,"Ground Water (HP)",null,18,18,18,0,0,0,null,"Ground Water (HP)",null,18,18,18,0,0,0,null,"Ground Water (HP)",null,3.7,3.7,3.7,0,0,0,null,"Ground Water (HP)",null,3.7,3.7,3.7,0,0,0,null,null,null,"Ground Water (HP)",null,18,18,18,0,0,0,null,"Ground Water (HP)",null,18,18,18,0,0,0,null,"Ground Water (HP)",null,3.7,3.7,3.7,0,0,0,null,"Ground Water (HP)",null,3.7,3.7,3.7,0,0,0]
[null,null,null,null,null,null,null,"Ground Loop (HP)",null,14.1,14.1,14.1,"N/A","N/A","N/A",null,"Ground Loop (HP)",null,14.1,14.1,14.1,"N/A","N/A","N/A",null,"Ground Loop (HP)",null,3.2,3.2,3.2,"N/A","N/A","N/A",null,"Ground Loop (HP)",null,3.2,3.2,3.2,"N/A","N/A","N/A",null,null,null,"Ground Loop (HP)",null,14.1,14.1,14.1,"N/A","N/A","N/A",null,"Ground Loop (HP)",null,14.1,14.1,14.1,"N/A","N/A","N/A",null,"Ground Loop (HP)",null,3.2,3.2,3.2,"N/A","N/A","N/A",null,"Ground Loop (HP)",null,3.2,3.2,3.2,"N/A","N/A","N/A"]
[null,null,null,null,null,{"$f":"$G$115","v":"VRF Heat Pump"},null,"AC - Cooling Only",null,{"$f":"K182","v":11.049999999999999},{"$f":"0.85*T182","v":11.049999999999999},11.2,11,10,10,null,"AC - Cooling Only",null,{"$f":"T182","v":13},13,15.5,14.9,13.9,13.9,null,"AC - Cooling Only",null,{"$f":"AC182","v":0},0,0,0,0,0,null,"AC - Cooling Only",null,{"$f":"AL182","v":0},0,0,0,0,0,null,{"$f":"$G$115","v":"VRF Heat Pump"},null,"AC - Cooling Only",null,{"$f":"0.75*BE182","v":10.725000000000001},{"$f":"0.75*BF182","v":10.725000000000001},11.2,11,10,10,null,"AC - Cooling Only",null,14.3,14.3,15.5,14.9,13.9,13.9,null,"AC - Cooling Only",null,0,0,0,0,0,0,null,"AC - Cooling Only",null,0,0,0,0,0,0]
[null,null,null,null,null,"Air Cooled",null,"Air Cooled",null,{"$f":"K183","v":11.1},11.1,11,10.6,9.5,9.5,null,"Air Cooled",null,{"$f":"T183","v":13},13,14.6,13.9,12.7,12.7,null,"Air Cooled",null,{"$f":"AC183","v":2.2567409144196953},{"$f":"7.7/3.412","v":2.2567409144196953},3.3,3.2,3.2,3.2,null,"Air Cooled",null,{"$f":"AL183","v":2.2567409144196953},{"$f":"7.7/3.412","v":2.2567409144196953},2.25,2.0499999999999998,2.0499999999999998,2.0499999999999998,null,null,null,"Air Cooled",null,{"$f":"0.75*BE183","v":10.725000000000001},10.725000000000001,10.95,10.6,9.5249999999999986,9.5249999999999986,null,"Air Cooled",null,14.3,14.3,14.6,13.9,12.7,12.7,null,"Air Cooled",null,{"$f":"7.5/3.412","v":2.1981242672919108},{"$f":"7.5/3.412","v":2.1981242672919108},3.3,3.2,3.2,3.2,null,"Air Cooled",null,{"$f":"7.5/3.412","v":2.1981242672919108},{"$f":"7.5/3.412","v":2.1981242672919108},2.25,2.0499999999999998,2.0499999999999998,2.0499999999999998]
[null,null,null,null,null,"Water Loop (HP)",null,"Water Cooled",null,12,12,12,10,10,10,null,"Water Cooled",null,12,{"$f":"K184","v":12},{"$f":"L184","v":12},{"$f":"M184","v":10},{"$f":"N184","v":10},{"$f":"O184","v":10},null,"Water Cooled",null,4.2,4.2,4.2,3.9,3.9,3.9,null,"Water Cooled",null,4.2,4.2,4.2,3.9,3.9,3.9,null,null,null,"Water Cooled",null,12,12,12,10,10,10,null,"Water Cooled",null,16,16,16,14,12,12,null,"Water Cooled",null,4.3,4.3,4.3,4,3.9,3.9,null,"Water Cooled",null,4.3,4.3,4.3,4,3.9,3.9]
[null,null,null,null,null,"Ground Water (HP)",null,"Evap Cooled",null,0,0,0,0,0,0,null,"Evap Cooled",null,0,0,0,0,0,0,null,"Evap Cooled",null,0,0,0,0,0,0,null,"Evap Cooled",null,0,0,0,0,0,0,null,null,null,"Evap Cooled",null,0,0,0,0,0,0,null,"Evap Cooled",null,0,0,0,0,0,0,null,"Evap Cooled",null,0,0,0,0,0,0,null,"Evap Cooled",null,0,0,0,0,0,0]
[null,null,null,null,null,"Ground Loop (HP)",null,"Water Loop (HP)",null,0,0,0,0,0,0,null,"Water Loop (HP)",null,0,0,0,0,0,0,null,"Water Loop (HP)",null,0,0,0,0,0,0,null,"Water Loop (HP)",null,0,0,0,0,0,0,null,null,null,"Water Loop (HP)",null,0,0,0,0,0,0,null,"Water Loop (HP)",null,0,0,0,0,0,0,null,"Water Loop (HP)",null,0,0,0,0,0,0,null,"Water Loop (HP)",null,0,0,0,0,0,0]
[null,null,null,null,null,null,null,"Ground Water (HP)",null,16.2,16.2,16.2,13.8,13.8,13.8,null,"Ground Water (HP)",null,16.2,{"$f":"K187","v":16.2},16.2,13.8,13.8,13.8,null,"Ground Water (HP)",null,3.6,3.6,3.6,3.3,3.3,3.3,null,"Ground Water (HP)",null,3.6,3.6,3.6,3.3,3.3,3.3,null,null,null,"Ground Water (HP)",null,16.2,16.2,16.2,13.8,13.8,13.8,null,"Ground Water (HP)",null,16.2,16.2,16.2,13.8,13.8,13.8,null,"Ground Water (HP)",null,3.6,3.6,3.6,3.3,3.3,3.3,null,"Ground Water (HP)",null,3.6,3.6,3.6,3.3,3.3,3.3]
[null,null,null,null,null,null,null,"Ground Loop (HP)",null,13.4,13.4,13.4,11,11,11,null,"Ground Loop (HP)",null,13.4,13.4,13.4,11,11,11,null,"Ground Loop (HP)",null,3.1,3.1,3.1,2.8,2.8,2.8,null,"Ground Loop (HP)",null,3.1,3.1,3.1,2.8,2.8,2.8,null,null,null,"Ground Loop (HP)",null,13.4,13.4,13.4,11,11,11,null,"Ground Loop (HP)",null,13.4,13.4,13.4,11,11,11,null,"Ground Loop (HP)",null,3.1,3.1,3.1,2.8,2.8,2.8,null,"Ground Loop (HP)",null,3.1,3.1,3.1,2.8,2.8,2.8]
[null,null,null,null,null,{"$f":"$G$114","v":"VRF AC Only"},null,"AC - Cooling Only",null,{"$f":"K189","v":11.049999999999999},{"$f":"0.85*T189","v":11.049999999999999},11.2,11,10,10,null,"AC - Cooling Only",null,{"$f":"T189","v":13},13,13.1,12.9,11.6,11.6,null,"AC - Cooling Only",null,0,0,0,0,0,0,null,"AC - Cooling Only",null,0,0,0,0,0,0,null,{"$f":"$G$114","v":"VRF AC Only"},null,"AC - Cooling Only",null,{"$f":"0.75*BE189","v":10.725000000000001},{"$f":"0.75*BF189","v":10.725000000000001},11.2,11,10,10,null,"AC - Cooling Only",null,14.3,14.3,15.5,14.9,13.9,13.9,null,"AC - Cooling Only",null,0,0,0,0,0,0,null,"AC - Cooling Only",null,0,0,0,0,0,0]
[null,null,null,null,null,"Air Cooled",null,"Air Cooled",null,{"$f":"K190","v":11.3},11.3,11.2,11,10,10,null,"Air Cooled",null,{"$f":"T190","v":13},13,13.1,12.9,11.6,11.6,null,"Air Cooled",null,0,0,0,0,0,0,null,"Air Cooled",null,0,0,0,0,0,0,null,null,null,"Air Cooled",null,{"$f":"0.75*BE190","v":10.725000000000001},10.725000000000001,11.2,11,10,10,null,"Air Cooled",null,14.3,14.3,15.5,14.9,13.9,13.9,null,"Air Cooled",null,0,0,0,0,0,0,null,"Air Cooled",null,0,0,0,0,0,0]

{"sheet":"High Efficiency Chillers","index":12,"n_rows":143,"n_cols":51,"rows_kept":143,"cut":false,"hidden":true,"merged":[[24,13,24,14],[24,15,24,16],[1,19,11,27],[18,13,18,14],[15,13,15,14],[15,15,15,16],[18,15,18,16],[1,10,4,17]]}
["Savings Summary",null,null,null,null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,null,null,"Notes (Optional)"]
["Annual kWh Savings",null,null,{"$f":"SUM(A14:D14)","v":0},null,null,null,"Value","Unit",null,"This measure considers savings from installing high performance chillers that exceed the energy code requirements."]
["% On Peak",null,null,{"$f":"IF(D2<=0,0,MIN(1,A15+C15))","v":0},null,"Annual Electric Savings",null,{"$f":"D2","v":0},"kWh"]
["Max kW",null,null,{"$f":"MAX(AB35:AB58,AB65:AB88)","v":0},null,"Annual Fuel Savings",null,{"$f":"D7*C28","v":{"$error":"#N/A"}},{"$f":"D20","v":{"$error":"#N/A"}}]
["Summer kW",null,null,{"$f":"(SUMPRODUCT(R35:R58,AB35:AB58)+SUMPRODUCT(R65:R88,AB65:AB88))/SUM(R35:R58,R65:R88)","v":0},null,"Incremental","Default Calc",{"$f":"SUM($AY$102:$AY$103)","v":0},"$"]
["Winter kW",null,null,{"$f":"(SUMPRODUCT(Q35:Q58,AB35:AB58)+SUMPRODUCT(Q65:Q88,AB65:AB88))/SUM(Q35:Q58,Q65:Q88)","v":0},null,"Cost","Project Specific",null,"$ (Optional)"]
["Annual Fuel Savings (MMBtu)",null,null,{"$f":"(SUMPRODUCT($L$35:$L$58,AA35:AA58)+SUMPRODUCT($L$65:$L$88,AA65:AA88))/1000","v":0},null,"Estimated Incentive",null,{"$f":"IF(AND($C$24>=0,$C$25>=0),MAX(0,H3)*C24+MAX(0,H4)*C25,\"TBD\")","v":{"$error":"#N/A"}},"$"]
["Incremental Cost (Default Calc)",null,null,{"$f":"SUM($AY$102:$AY$103)","v":0}]
["Incremental Cost (for Summary)",null,null,{"$f":"IF(H6>0,H6,D8)","v":0},null,"Project Information Summary"]
["kWh Savings by Peak Period",null,null,null,null,null,"STATE",{"$f":"'Project Info'!C15","v":"NH"}]
["Winter","Winter","Summer","Summer",null,null,"Program Year",{"$f":"'Project Info'!C19","v":0}]
["On-Peak","Off-Peak","On-Peak","Off-Peak",null,null,"Code IECC Version",{"$f":"MID('Project Info'!C20,1,4)","v":"2018"}]
["kWh","kWh","kWh","kWh",null,null,"Electric PA",{"$f":"'Project Info'!F3","v":0}]
[{"$f":"SUMPRODUCT($AN$35:$AN$58,M35:M58)+SUMPRODUCT($AN$65:$AN$88,M65:M88)","v":0},{"$f":"SUMPRODUCT($AN$35:$AN$58,N35:N58)+SUMPRODUCT($AN$65:$AN$88,N65:N88)","v":0},{"$f":"SUMPRODUCT($AN$35:$AN$58,O35:O58)+SUMPRODUCT($AN$65:$AN$88,O65:O88)","v":0},{"$f":"SUMPRODUCT($AN$35:$AN$58,P35:P58)+SUMPRODUCT($AN$65:$AN$88,P65:P88)","v":0},null,null,"Gas PA",{"$f":"'Project Info'!I3","v":0},null,null,"Table 1: Chiller Plant Parameters",null,null,null,null,"Optional: System 2",null,null,"Baseline vs. Proposed Assumptions Summary"]
[{"$f":"ROUND(IF(A14<=0,0,A14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(B14<=0,0,B14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(C14<=0,0,C14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"IF(SUM(A14:D14)=0,0,1-SUM(A15:C15))","v":0},null,"*NOTE: Baseline values are automated and cannot be changed.",null,null,null,null,null,null,null,"System 1",null,"Include?",null,null,null,"Capacity","Perf.","Baseline Performance",null,"Proposed Performance",null,"EFLH"]
[null,null,null,null,null,null,null,null,null,null,"System Load Profile",null,null,null,null,null,null,null,null,"tons/chiller","Unit","FL","IEER/IPLV","FL","IEER/IPLV","Cooling"]
["Utility Rates",null,null,null,null,null,null,null,null,null,"Chiller Quantity",null,null,null,null,null,null,null,"System 1",{"$f":"N18","v":0},{"$f":"O20","v":"kW/ton"},{"$f":"IF(U17=\"EER\",S102,R102)","v":0.75},{"$f":"IF(U17=\"EER\",U102,T102)","v":0.6},{"$f":"IF(U17=\"EER\",O102,N102)","v":0},{"$f":"IF(U17=\"EER\",Q102,P102)","v":0},{"$f":"IF(ISERROR(AH102)=TRUE,0,AH102)","v":0}]
[null,null,"Rate","Unit",null,null,null,null,null,null,"Capacity, per Chiller (tons)",null,null,null,"tons",null,"tons",null,"System 2",{"$f":"IF(Q15=\"No\", \"NA\",P18)","v":0},{"$f":"IF(Q15=\"No\", \"NA\", Q20)","v":"kW/ton"},{"$f":"IF(Q15=\"No\", \"NA\", IF(U18=\"EER\",S103,R103))","v":0.75},{"$f":"IF(Q15=\"No\", \"NA\", IF(U18=\"EER\",U103,T103))","v":0.6},{"$f":"IF(Q15=\"No\", \"NA\", IF(U18=\"EER\",O103,N103))","v":0},{"$f":"IF(Q15=\"No\", \"NA\", IF(U18=\"EER\",Q103,P103))","v":0},{"$f":"IF(ISERROR(AH103)=TRUE,0,AH103)","v":0}]
["Electric",null,{"$f":"'ECM Summary'!$E$31","v":0.1593},"kWh",null,null,null,null,null,null,"Chiller Type"]
[{"$f":"'ECM Summary'!$C$32","v":0},null,{"$f":"'ECM Summary'!$E$32","v":{"$error":"#N/A"}},{"$f":"'ECM Summary'!$F$32","v":{"$error":"#N/A"}},null,null,null,null,null,null,"AHRI Full Load Performance",null,null,null,{"$f":"IF(N19=\"Air-Cooled\", \"EER\", \"kW/ton\")","v":"kW/ton"},null,{"$f":"IF(P19=\"Air-Cooled\", \"EER\", \"kW/ton\")","v":"kW/ton"}]
[null,null,null,null,null,null,null,null,null,null,"AHRI Part Load Performance, IEER/IPLV",null,null,null,{"$f":"IF(N19=\"Air-Cooled\", \"IEER\", \"kW/ton (IPLV)\")","v":"kW/ton (IPLV)"},null,{"$f":"IF(P19=\"Air-Cooled\", \"IEER\", \"kW/ton (IPLV)\")","v":"kW/ton (IPLV)"}]
["Custom Incentive Rates",null,null,null,null,null,null,null,null,null,"Max # of Operating Chillers",null,null,null,{"$f":"MAX(1,N17-1)","v":1},null,{"$f":"MAX(1,P17-1)","v":1}]
[null,null,"Rate","Unit",null,null,null,null,null,null,"Peak Load % of Max Operating Capacity",null,null,null,0.85,null,0.85]
["Electric",null,{"$f":"'ECM Summary'!$J$31","v":0.28000000000000003},"kWh",null,null,null,null,null,null,"Incentive (Custom)",null,null,null,{"$f":"$AX$102","v":0},null,{"$f":"$AX$103","v":0}]
[{"$f":"'ECM Summary'!$H$32","v":0},null,{"$f":"'ECM Summary'!$J$32","v":0},{"$f":"'ECM Summary'!$K$32","v":{"$error":"#N/A"}},null,null,null,null,null,null,"Manufacturer & Model (Optional)"]
[]
["Fossil Fuel",null,{"$f":"'Project Info'!C21","v":0}]
["Fuel Conversion",null,{"$f":"LOOKUP(C27,'Project Info'!X102:X104,'Project Info'!Z102:Z104)","v":{"$error":"#N/A"}}]
[]
[]
[null,null,null,null,null,null,"Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown",null,null,null,null,null,null,"System 1 Analysis",null,null,null,null,null,null,null,null,null,"System 2 Analysis",null,null,null,null,null,null,null,null,null,"Total Combined"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Cooling","Qty","Per Unit","Avg.","Base","Proposed","Base","Design","Demand","Demand","Cooling","Qty","Per Unit","Avg.","Base","Proposed","Base","Design","Demand","Demand","Demand"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Load","Running","Load","Part Load","Perf","Perf","Demand","Demand","Savings","Savings","Load","Running","Load","Part Load","Perf","Perf","Demand","Demand","Savings","Savings","Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","tons","Chillers","tons","%","kW/ton","kW/ton","kW","kW","MBH","kW","tons","Chillers","tons","%","kW/ton","kW/ton","kW","kW","MBH","kW","MBH","kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A44","v":100},{"$f":"'Project Info'!B44","v":105},{"$f":"'Project Info'!C44","v":102},{"$f":"'Project Info'!D44","v":76},{"$f":"'Project Info'!E44","v":40},{"$f":"'Project Info'!F44","v":0},{"$f":"'Project Info'!G44","v":0},{"$f":"'Project Info'!H44","v":0},{"$f":"'Project Info'!I44","v":0},{"$f":"'Project Info'!J44","v":0},{"$f":"'Project Info'!K44","v":0},{"$f":"'Project Info'!L44","v":0},{"$f":"$L$102*$M$102*MAX(0,TREND($AB$102:$AC$102,$Z$102:$AA$102,$I35))*($I35>=$AA$102)","v":0},{"$f":"IF($M$102=0,0,MIN($L$102,ROUNDUP(S35/$M$102,0)))","v":0},{"$f":"IF(S35>0,S35/T35,0)","v":0},{"$f":"IF($M$102=0,0,MIN(1,U35/$M$102))","v":0},{"$f":"OFFSET($Z$118,MATCH($I35,$Z$119:$Z$129,-1),MATCH($V35,$AA$118:$AE$118,-1))","v":0.67764705882352927},{"$f":"OFFSET($Z$132,MATCH(I35,$Z$133:$Z$143,-1),MATCH($V35,$AA$132:$AE$132,-1))","v":0},{"$f":"W35*S35","v":0},{"$f":"S35*X35","v":0},0,{"$f":"Y35-Z35","v":0},{"$f":"$L$103*$M$103*MAX(0,TREND($AB$103:$AC$103,$Z$103:$AA$103,$I35))*($I35>=$AA$103)","v":0},{"$f":"IF($M$103=0,0,MIN($L$103,ROUNDUP(AC35/$M$103,0)))","v":0},{"$f":"IF(AC35>0,AC35/AD35,0)","v":0},{"$f":"IF($M$103=0,0,MIN(1,AE35/$M$103))","v":0},{"$f":"OFFSET($AH$118,MATCH($I35,$AH$119:$AH$129,-1),MATCH($AF35,$AI$118:$AM$118,-1))","v":0.67764705882352927},{"$f":"OFFSET($AH$132,MATCH(I35,$AH$133:$AH$143,-1),MATCH($AF35,$AI$132:$AM$132,-1))","v":0},{"$f":"AG35*AC35","v":0},{"$f":"AC35*AH35","v":0},0,{"$f":"AI35-AJ35","v":0},{"$f":"AA35+AK35","v":0},{"$f":"AB35+AL35","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A45","v":95},{"$f":"'Project Info'!B45","v":100},{"$f":"'Project Info'!C45","v":95.219272727272724},{"$f":"'Project Info'!D45","v":74.534025272781079},{"$f":"'Project Info'!E45","v":37.923296058061368},{"$f":"'Project Info'!F45","v":0},{"$f":"'Project Info'!G45","v":0},{"$f":"'Project Info'!H45","v":0},{"$f":"'Project Info'!I45","v":0},{"$f":"'Project Info'!J45","v":0},{"$f":"'Project Info'!K45","v":0},{"$f":"'Project Info'!L45","v":0},{"$f":"$L$102*$M$102*MAX(0,TREND($AB$102:$AC$102,$Z$102:$AA$102,$I36))*($I36>=$AA$102)","v":0},{"$f":"IF($M$102=0,0,MIN($L$102,ROUNDUP(S36/$M$102,0)))","v":0},{"$f":"IF(S36>0,S36/T36,0)","v":0},{"$f":"IF($M$102=0,0,MIN(1,U36/$M$102))","v":0},{"$f":"OFFSET($Z$118,MATCH(I36,$Z$119:$Z$129,-1),MATCH($V36,$AA$118:$AE$118,-1))","v":0.67764705882352927},0,0,0,0,{"$f":"Y36-Z36","v":0},{"$f":"$L$103*$M$103*MAX(0,TREND($AB$103:$AC$103,$Z$103:$AA$103,$I36))*($I36>=$AA$103)","v":0},{"$f":"IF($M$103=0,0,MIN($L$103,ROUNDUP(AC36/$M$103,0)))","v":0},{"$f":"IF(AC36>0,AC36/AD36,0)","v":0},{"$f":"IF($M$103=0,0,MIN(1,AE36/$M$103))","v":0},{"$f":"OFFSET($AH$118,MATCH($I36,$AH$119:$AH$129,-1),MATCH($AF36,$AI$118:$AM$118,-1))","v":0.67764705882352927},{"$f":"OFFSET($AH$132,MATCH(I36,$AH$133:$AH$143,-1),MATCH($AF36,$AI$132:$AM$132,-1))","v":0},{"$f":"AG36*AC36","v":0},{"$f":"AC36*AH36","v":0},0,{"$f":"AI36-AJ36","v":0},{"$f":"AA36+AK36","v":0},{"$f":"AB36+AL36","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A46","v":90},{"$f":"'Project Info'!B46","v":95},{"$f":"'Project Info'!C46","v":92.016049160256074},{"$f":"'Project Info'!D46","v":72.911561930607689},{"$f":"'Project Info'!E46","v":36.467095439351091},{"$f":"'Project Info'!F46","v":0},{"$f":"'Project Info'!G46","v":0},{"$f":"'Project Info'!H46","v":0},{"$f":"'Project Info'!I46","v":0},{"$f":"'Project Info'!J46","v":0},{"$f":"'Project Info'!K46","v":0},{"$f":"'Project Info'!L46","v":0},0,0,0,0,0.67764705882352927,0,0,0,0,0,0,0,0,0,0.67764705882352927,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A47","v":85},{"$f":"'Project Info'!B47","v":90},{"$f":"'Project Info'!C47","v":87.457811360655285},{"$f":"'Project Info'!D47","v":70.80538329449476},{"$f":"'Project Info'!E47","v":34.679413213566804},{"$f":"'Project Info'!F47","v":0},{"$f":"'Project Info'!G47","v":0},{"$f":"'Project Info'!H47","v":0},{"$f":"'Project Info'!I47","v":0},{"$f":"'Project Info'!J47","v":0},{"$f":"'Project Info'!K47","v":0},{"$f":"'Project Info'!L47","v":0},0,0,0,0,0.66352941176470581,0,0,0,0,0,0,0,0,0,0.66352941176470581,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A48","v":80},{"$f":"'Project Info'!B48","v":85},{"$f":"'Project Info'!C48","v":82.136788830239965},{"$f":"'Project Info'!D48","v":67.872393622439333},{"$f":"'Project Info'!E48","v":32.296248223809314},{"$f":"'Project Info'!F48","v":0},{"$f":"'Project Info'!G48","v":0},{"$f":"'Project Info'!H48","v":0},{"$f":"'Project Info'!I48","v":0},{"$f":"'Project Info'!J48","v":0},{"$f":"'Project Info'!K48","v":0},{"$f":"'Project Info'!L48","v":0},0,0,0,0,0.64941176470588213,0,0,0,0,0,0,0,0,0,0.64941176470588213,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A49","v":75},{"$f":"'Project Info'!B49","v":80},{"$f":"'Project Info'!C49","v":76.988400157585886},{"$f":"'Project Info'!D49","v":65.129261896908645},{"$f":"'Project Info'!E49","v":30.190476812806729},{"$f":"'Project Info'!F49","v":0},{"$f":"'Project Info'!G49","v":0},{"$f":"'Project Info'!H49","v":0},{"$f":"'Project Info'!I49","v":0},{"$f":"'Project Info'!J49","v":0},{"$f":"'Project Info'!K49","v":0},{"$f":"'Project Info'!L49","v":0},0,0,0,0,0.63529411764705868,0,0,0,0,0,0,0,0,0,0.63529411764705868,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A50","v":70},{"$f":"'Project Info'!B50","v":75},{"$f":"'Project Info'!C50","v":72.457982050814195},{"$f":"'Project Info'!D50","v":63.604425012889301},{"$f":"'Project Info'!E50","v":29.088683095945193},{"$f":"'Project Info'!F50","v":0},{"$f":"'Project Info'!G50","v":0},{"$f":"'Project Info'!H50","v":0},{"$f":"'Project Info'!I50","v":0},{"$f":"'Project Info'!J50","v":0},{"$f":"'Project Info'!K50","v":0},{"$f":"'Project Info'!L50","v":0},0,0,0,0,0.62117647058823522,0,0,0,0,0,0,0,0,0,0.62117647058823522,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A51","v":65},{"$f":"'Project Info'!B51","v":70},{"$f":"'Project Info'!C51","v":67.815831070966169},{"$f":"'Project Info'!D51","v":61.631331368130574},{"$f":"'Project Info'!E51","v":27.661514889731574},{"$f":"'Project Info'!F51","v":0},{"$f":"'Project Info'!G51","v":0},{"$f":"'Project Info'!H51","v":0},{"$f":"'Project Info'!I51","v":0},{"$f":"'Project Info'!J51","v":0},{"$f":"'Project Info'!K51","v":0},{"$f":"'Project Info'!L51","v":0},0,0,0,0,0.60705882352941165,0,0,0,0,0,0,0,0,0,0.60705882352941165,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A52","v":60},{"$f":"'Project Info'!B52","v":65},{"$f":"'Project Info'!C52","v":62.535961472271332},{"$f":"'Project Info'!D52","v":57.135476922863582},{"$f":"'Project Info'!E52","v":24.623037157728302},{"$f":"'Project Info'!F52","v":0},{"$f":"'Project Info'!G52","v":0},{"$f":"'Project Info'!H52","v":0},{"$f":"'Project Info'!I52","v":0},{"$f":"'Project Info'!J52","v":0},{"$f":"'Project Info'!K52","v":0},{"$f":"'Project Info'!L52","v":0},0,0,0,0,0.59294117647058808,0,0,0,0,0,0,0,0,0,0.59294117647058808,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A53","v":55},{"$f":"'Project Info'!B53","v":60},{"$f":"'Project Info'!C53","v":57.125792270740902},{"$f":"'Project Info'!D53","v":52.596971157053673},{"$f":"'Project Info'!E53","v":21.818001539159841},{"$f":"'Project Info'!F53","v":0},{"$f":"'Project Info'!G53","v":0},{"$f":"'Project Info'!H53","v":0},{"$f":"'Project Info'!I53","v":0},{"$f":"'Project Info'!J53","v":0},{"$f":"'Project Info'!K53","v":0},{"$f":"'Project Info'!L53","v":0},0,0,0,0,0.57882352941176451,0,0,0,0,0,0,0,0,0,0.57882352941176451,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A54","v":50},{"$f":"'Project Info'!B54","v":55},{"$f":"'Project Info'!C54","v":52.235698854337961},{"$f":"'Project Info'!D54","v":48.022768090099298},{"$f":"'Project Info'!E54","v":19.246640192796217},{"$f":"'Project Info'!F54","v":0},{"$f":"'Project Info'!G54","v":0},{"$f":"'Project Info'!H54","v":0},{"$f":"'Project Info'!I54","v":0},{"$f":"'Project Info'!J54","v":0},{"$f":"'Project Info'!K54","v":0},{"$f":"'Project Info'!L54","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A55","v":45},{"$f":"'Project Info'!B55","v":50},{"$f":"'Project Info'!C55","v":47.459170258371508},{"$f":"'Project Info'!D55","v":43.465397050422162},{"$f":"'Project Info'!E55","v":16.894183241713304},{"$f":"'Project Info'!F55","v":0},{"$f":"'Project Info'!G55","v":0},{"$f":"'Project Info'!H55","v":0},{"$f":"'Project Info'!I55","v":0},{"$f":"'Project Info'!J55","v":0},{"$f":"'Project Info'!K55","v":0},{"$f":"'Project Info'!L55","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A56","v":40},{"$f":"'Project Info'!B56","v":45},{"$f":"'Project Info'!C56","v":42.677030404888129},{"$f":"'Project Info'!D56","v":38.812544504634097},{"$f":"'Project Info'!E56","v":14.690265649465921},{"$f":"'Project Info'!F56","v":0},{"$f":"'Project Info'!G56","v":0},{"$f":"'Project Info'!H56","v":0},{"$f":"'Project Info'!I56","v":0},{"$f":"'Project Info'!J56","v":0},{"$f":"'Project Info'!K56","v":0},{"$f":"'Project Info'!L56","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A57","v":35},{"$f":"'Project Info'!B57","v":40},{"$f":"'Project Info'!C57","v":37.333046773755832},{"$f":"'Project Info'!D57","v":33.904706919479686},{"$f":"'Project Info'!E57","v":12.53841602318813},{"$f":"'Project Info'!F57","v":0},{"$f":"'Project Info'!G57","v":0},{"$f":"'Project Info'!H57","v":0},{"$f":"'Project Info'!I57","v":0},{"$f":"'Project Info'!J57","v":0},{"$f":"'Project Info'!K57","v":0},{"$f":"'Project Info'!L57","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A58","v":30},{"$f":"'Project Info'!B58","v":35},{"$f":"'Project Info'!C58","v":32.638179845662044},{"$f":"'Project Info'!D58","v":29.547170928664851},{"$f":"'Project Info'!E58","v":10.728972818165861},{"$f":"'Project Info'!F58","v":0},{"$f":"'Project Info'!G58","v":0},{"$f":"'Project Info'!H58","v":0},{"$f":"'Project Info'!I58","v":0},{"$f":"'Project Info'!J58","v":0},{"$f":"'Project Info'!K58","v":0},{"$f":"'Project Info'!L58","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A59","v":25},{"$f":"'Project Info'!B59","v":30},{"$f":"'Project Info'!C59","v":27.529264646850947},{"$f":"'Project Info'!D59","v":24.652717392657845},{"$f":"'Project Info'!E59","v":8.8041305482613303},{"$f":"'Project Info'!F59","v":0},{"$f":"'Project Info'!G59","v":0},{"$f":"'Project Info'!H59","v":0},{"$f":"'Project Info'!I59","v":0},{"$f":"'Project Info'!J59","v":0},{"$f":"'Project Info'!K59","v":0},{"$f":"'Project Info'!L59","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A60","v":20},{"$f":"'Project Info'!B60","v":25},{"$f":"'Project Info'!C60","v":22.998111483544687},{"$f":"'Project Info'!D60","v":20.383306659827422},{"$f":"'Project Info'!E60","v":7.246164547543378},{"$f":"'Project Info'!F60","v":0},{"$f":"'Project Info'!G60","v":0},{"$f":"'Project Info'!H60","v":0},{"$f":"'Project Info'!I60","v":0},{"$f":"'Project Info'!J60","v":0},{"$f":"'Project Info'!K60","v":0},{"$f":"'Project Info'!L60","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A61","v":15},{"$f":"'Project Info'!B61","v":20},{"$f":"'Project Info'!C61","v":17.808510327474309},{"$f":"'Project Info'!D61","v":15.420865796304254},{"$f":"'Project Info'!E61","v":5.5490484131518292},{"$f":"'Project Info'!F61","v":0},{"$f":"'Project Info'!G61","v":0},{"$f":"'Project Info'!H61","v":0},{"$f":"'Project Info'!I61","v":0},{"$f":"'Project Info'!J61","v":0},{"$f":"'Project Info'!K61","v":0},{"$f":"'Project Info'!L61","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A62","v":10},{"$f":"'Project Info'!B62","v":15},{"$f":"'Project Info'!C62","v":12.269931130346862},{"$f":"'Project Info'!D62","v":10.318264913023604},{"$f":"'Project Info'!E62","v":3.9082824916941998},{"$f":"'Project Info'!F62","v":0},{"$f":"'Project Info'!G62","v":0},{"$f":"'Project Info'!H62","v":0},{"$f":"'Project Info'!I62","v":0},{"$f":"'Project Info'!J62","v":0},{"$f":"'Project Info'!K62","v":0},{"$f":"'Project Info'!L62","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A63","v":5},{"$f":"'Project Info'!B63","v":10},{"$f":"'Project Info'!C63","v":7.3137581369917548},{"$f":"'Project Info'!D63","v":5.7052382449247707},{"$f":"'Project Info'!E63","v":2.5019418419888937},{"$f":"'Project Info'!F63","v":0},{"$f":"'Project Info'!G63","v":0},{"$f":"'Project Info'!H63","v":0},{"$f":"'Project Info'!I63","v":0},{"$f":"'Project Info'!J63","v":0},{"$f":"'Project Info'!K63","v":0},{"$f":"'Project Info'!L63","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A64","v":0},{"$f":"'Project Info'!B64","v":5},{"$f":"'Project Info'!C64","v":2.6119461836144886},{"$f":"'Project Info'!D64","v":1.2699770062067783},{"$f":"'Project Info'!E64","v":1.2046477897733283},{"$f":"'Project Info'!F64","v":0},{"$f":"'Project Info'!G64","v":0},{"$f":"'Project Info'!H64","v":0},{"$f":"'Project Info'!I64","v":0},{"$f":"'Project Info'!J64","v":0},{"$f":"'Project Info'!K64","v":0},{"$f":"'Project Info'!L64","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A65","v":-5},{"$f":"'Project Info'!B65","v":0},{"$f":"'Project Info'!C65","v":-1.6731398516793925},{"$f":"'Project Info'!D65","v":-2.7083318773557807},{"$f":"'Project Info'!E65","v":7.9391832815876459E-2},{"$f":"'Project Info'!F65","v":0},{"$f":"'Project Info'!G65","v":0},{"$f":"'Project Info'!H65","v":0},{"$f":"'Project Info'!I65","v":0},{"$f":"'Project Info'!J65","v":0},{"$f":"'Project Info'!K65","v":0},{"$f":"'Project Info'!L65","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A66","v":-10},{"$f":"'Project Info'!B66","v":-5},{"$f":"'Project Info'!C66","v":-6.5729865085377277},{"$f":"'Project Info'!D66","v":-7.2465935998252222},{"$f":"'Project Info'!E66","v":-1.168423365310433},{"$f":"'Project Info'!F66","v":0},{"$f":"'Project Info'!G66","v":0},{"$f":"'Project Info'!H66","v":0},{"$f":"'Project Info'!I66","v":0},{"$f":"'Project Info'!J66","v":0},{"$f":"'Project Info'!K66","v":0},{"$f":"'Project Info'!L66","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A67","v":-15},{"$f":"'Project Info'!B67","v":-10},{"$f":"'Project Info'!C67","v":-15.32570353422995},{"$f":"'Project Info'!D67","v":-15.707838211108999},{"$f":"'Project Info'!E67","v":-3.4051318156661381},{"$f":"'Project Info'!F67","v":0},{"$f":"'Project Info'!G67","v":0},{"$f":"'Project Info'!H67","v":0},{"$f":"'Project Info'!I67","v":0},{"$f":"'Project Info'!J67","v":0},{"$f":"'Project Info'!K67","v":0},{"$f":"'Project Info'!L67","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[]
[]
[null,null,null,null,null,null,"Unoccupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown",null,null,null,null,null,null,"System 1 Analysis",null,null,null,null,null,null,null,null,null,"System 2 Analysis",null,null,null,null,null,null,null,null,null,"Total Combined"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Cooling","Qty","Per Unit","Avg.","Base","Proposed","Base","Design","Demand","Demand","Cooling","Qty","Per Unit","Avg.","Base","Proposed","Base","Design","Demand","Demand","Demand"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Load","Running","Load","Part Load","Perf","Perf","Demand","Demand","Savings","Savings","Load","Running","Load","Part Load","Perf","Perf","Demand","Demand","Savings","Savings","Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","tons","Chillers","tons","%","kW/ton","kW/ton","kW","kW","MBH","kW","tons","Chillers","tons","%","kW/ton","kW/ton","kW","kW","MBH","kW","MBH","kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A74","v":100},{"$f":"'Project Info'!B74","v":105},{"$f":"'Project Info'!C74","v":102},{"$f":"'Project Info'!D74","v":76},{"$f":"'Project Info'!E74","v":40},{"$f":"'Project Info'!F74","v":0},{"$f":"'Project Info'!G74","v":0},{"$f":"'Project Info'!H74","v":0},{"$f":"'Project Info'!I74","v":0},{"$f":"'Project Info'!J74","v":0},{"$f":"'Project Info'!K74","v":0},{"$f":"'Project Info'!L74","v":0},{"$f":"$L$102*$M$102*MAX(0,TREND($AF$102:$AG$102,$AD$102:$AE$102,I65))*($I65>=$AE$102)","v":0},{"$f":"IF($M$102=0,0,MIN($L$102,ROUNDUP(S65/$M$102,0)))","v":0},{"$f":"IF(S65>0,S65/T65,0)","v":0},{"$f":"IF($M$102=0,0,MIN(1,U65/$M$102))","v":0},{"$f":"OFFSET($Z$118,MATCH(I65,$Z$119:$Z$129,-1),MATCH($V65,$AA$118:$AE$118,-1))","v":0.67764705882352927},{"$f":"OFFSET($Z$132,MATCH(I65,$Z$133:$Z$143,-1),MATCH($V65,$AA$132:$AE$132,-1))","v":0},{"$f":"W65*S65","v":0},{"$f":"S65*X65","v":0},0,{"$f":"Y65-Z65","v":0},{"$f":"$L$103*$M$103*MAX(0,TREND($AF$103:$AG$103,$AD$103:$AE$103,$I65))*($I65>=$AE$103)","v":0},{"$f":"IF($M$103=0,0,MIN($L$103,ROUNDUP(AC65/$M$103,0)))","v":0},{"$f":"IF(AC65>0,AC65/AD65,0)","v":0},{"$f":"IF($M$103=0,0,MIN(1,AE65/$M$103))","v":0},{"$f":"OFFSET($AH$118,MATCH($I65,$AH$119:$AH$129,-1),MATCH($AF65,$AI$118:$AM$118,-1))","v":0.67764705882352927},{"$f":"OFFSET($AH$132,MATCH(I65,$AH$133:$AH$143,-1),MATCH($AF65,$AI$132:$AM$132,-1))","v":0},{"$f":"AG65*AC65","v":0},{"$f":"AC65*AH65","v":0},0,{"$f":"AI65-AJ65","v":0},{"$f":"AA65+AK65","v":0},{"$f":"AB65+AL65","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A75","v":95},{"$f":"'Project Info'!B75","v":100},{"$f":"'Project Info'!C75","v":95.219272727272724},{"$f":"'Project Info'!D75","v":74.534025272781079},{"$f":"'Project Info'!E75","v":37.923296058061368},{"$f":"'Project Info'!F75","v":0},{"$f":"'Project Info'!G75","v":0},{"$f":"'Project Info'!H75","v":0},{"$f":"'Project Info'!I75","v":0},{"$f":"'Project Info'!J75","v":0},{"$f":"'Project Info'!K75","v":0},{"$f":"'Project Info'!L75","v":0},{"$f":"$L$102*$M$102*MAX(0,TREND($AF$102:$AG$102,$AD$102:$AE$102,I66))*($I66>=$AE$102)","v":0},{"$f":"IF($M$102=0,0,MIN($L$102,ROUNDUP(S66/$M$102,0)))","v":0},{"$f":"IF(S66>0,S66/T66,0)","v":0},{"$f":"IF($M$102=0,0,MIN(1,U66/$M$102))","v":0},0.67764705882352927,0,0,0,0,{"$f":"Y66-Z66","v":0},{"$f":"$L$103*$M$103*MAX(0,TREND($AF$103:$AG$103,$AD$103:$AE$103,$I66))*($I66>=$AE$103)","v":0},{"$f":"IF($M$103=0,0,MIN($L$103,ROUNDUP(AC66/$M$103,0)))","v":0},{"$f":"IF(AC66>0,AC66/AD66,0)","v":0},{"$f":"IF($M$103=0,0,MIN(1,AE66/$M$103))","v":0},{"$f":"OFFSET($AH$118,MATCH($I66,$AH$119:$AH$129,-1),MATCH($AF66,$AI$118:$AM$118,-1))","v":0.67764705882352927},{"$f":"OFFSET($AH$132,MATCH(I66,$AH$133:$AH$143,-1),MATCH($AF66,$AI$132:$AM$132,-1))","v":0},0,0,0,{"$f":"AI66-AJ66","v":0},{"$f":"AA66+AK66","v":0},{"$f":"AB66+AL66","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A76","v":90},{"$f":"'Project Info'!B76","v":95},{"$f":"'Project Info'!C76","v":92.016049160256074},{"$f":"'Project Info'!D76","v":72.911561930607689},{"$f":"'Project Info'!E76","v":36.467095439351091},{"$f":"'Project Info'!F76","v":0},{"$f":"'Project Info'!G76","v":0},{"$f":"'Project Info'!H76","v":0},{"$f":"'Project Info'!I76","v":0},{"$f":"'Project Info'!J76","v":0},{"$f":"'Project Info'!K76","v":0},{"$f":"'Project Info'!L76","v":0},0,0,0,0,0.67764705882352927,0,0,0,0,0,0,0,0,0,0.67764705882352927,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A77","v":85},{"$f":"'Project Info'!B77","v":90},{"$f":"'Project Info'!C77","v":87.457811360655285},{"$f":"'Project Info'!D77","v":70.80538329449476},{"$f":"'Project Info'!E77","v":34.679413213566804},{"$f":"'Project Info'!F77","v":0},{"$f":"'Project Info'!G77","v":0},{"$f":"'Project Info'!H77","v":0},{"$f":"'Project Info'!I77","v":0},{"$f":"'Project Info'!J77","v":0},{"$f":"'Project Info'!K77","v":0},{"$f":"'Project Info'!L77","v":0},0,0,0,0,0.66352941176470581,0,0,0,0,0,0,0,0,0,0.66352941176470581,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A78","v":80},{"$f":"'Project Info'!B78","v":85},{"$f":"'Project Info'!C78","v":82.136788830239965},{"$f":"'Project Info'!D78","v":67.872393622439333},{"$f":"'Project Info'!E78","v":32.296248223809314},{"$f":"'Project Info'!F78","v":0},{"$f":"'Project Info'!G78","v":0},{"$f":"'Project Info'!H78","v":0},{"$f":"'Project Info'!I78","v":0},{"$f":"'Project Info'!J78","v":0},{"$f":"'Project Info'!K78","v":0},{"$f":"'Project Info'!L78","v":0},0,0,0,0,0.64941176470588213,0,0,0,0,0,0,0,0,0,0.64941176470588213,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A79","v":75},{"$f":"'Project Info'!B79","v":80},{"$f":"'Project Info'!C79","v":76.988400157585886},{"$f":"'Project Info'!D79","v":65.129261896908645},{"$f":"'Project Info'!E79","v":30.190476812806729},{"$f":"'Project Info'!F79","v":0},{"$f":"'Project Info'!G79","v":0},{"$f":"'Project Info'!H79","v":0},{"$f":"'Project Info'!I79","v":0},{"$f":"'Project Info'!J79","v":0},{"$f":"'Project Info'!K79","v":0},{"$f":"'Project Info'!L79","v":0},0,0,0,0,0.63529411764705868,0,0,0,0,0,0,0,0,0,0.63529411764705868,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A80","v":70},{"$f":"'Project Info'!B80","v":75},{"$f":"'Project Info'!C80","v":72.457982050814195},{"$f":"'Project Info'!D80","v":63.604425012889301},{"$f":"'Project Info'!E80","v":29.088683095945193},{"$f":"'Project Info'!F80","v":0},{"$f":"'Project Info'!G80","v":0},{"$f":"'Project Info'!H80","v":0},{"$f":"'Project Info'!I80","v":0},{"$f":"'Project Info'!J80","v":0},{"$f":"'Project Info'!K80","v":0},{"$f":"'Project Info'!L80","v":0},0,0,0,0,0.62117647058823522,0,0,0,0,0,0,0,0,0,0.62117647058823522,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A81","v":65},{"$f":"'Project Info'!B81","v":70},{"$f":"'Project Info'!C81","v":67.815831070966169},{"$f":"'Project Info'!D81","v":61.631331368130574},{"$f":"'Project Info'!E81","v":27.661514889731574},{"$f":"'Project Info'!F81","v":0},{"$f":"'Project Info'!G81","v":0},{"$f":"'Project Info'!H81","v":0},{"$f":"'Project Info'!I81","v":0},{"$f":"'Project Info'!J81","v":0},{"$f":"'Project Info'!K81","v":0},{"$f":"'Project Info'!L81","v":0},0,0,0,0,0.60705882352941165,0,0,0,0,0,0,0,0,0,0.60705882352941165,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A82","v":60},{"$f":"'Project Info'!B82","v":65},{"$f":"'Project Info'!C82","v":62.535961472271332},{"$f":"'Project Info'!D82","v":57.135476922863582},{"$f":"'Project Info'!E82","v":24.623037157728302},{"$f":"'Project Info'!F82","v":0},{"$f":"'Project Info'!G82","v":0},{"$f":"'Project Info'!H82","v":0},{"$f":"'Project Info'!I82","v":0},{"$f":"'Project Info'!J82","v":0},{"$f":"'Project Info'!K82","v":0},{"$f":"'Project Info'!L82","v":0},0,0,0,0,0.59294117647058808,0,0,0,0,0,0,0,0,0,0.59294117647058808,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A83","v":55},{"$f":"'Project Info'!B83","v":60},{"$f":"'Project Info'!C83","v":57.125792270740902},{"$f":"'Project Info'!D83","v":52.596971157053673},{"$f":"'Project Info'!E83","v":21.818001539159841},{"$f":"'Project Info'!F83","v":0},{"$f":"'Project Info'!G83","v":0},{"$f":"'Project Info'!H83","v":0},{"$f":"'Project Info'!I83","v":0},{"$f":"'Project Info'!J83","v":0},{"$f":"'Project Info'!K83","v":0},{"$f":"'Project Info'!L83","v":0},0,0,0,0,0.57882352941176451,0,0,0,0,0,0,0,0,0,0.57882352941176451,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A84","v":50},{"$f":"'Project Info'!B84","v":55},{"$f":"'Project Info'!C84","v":52.235698854337961},{"$f":"'Project Info'!D84","v":48.022768090099298},{"$f":"'Project Info'!E84","v":19.246640192796217},{"$f":"'Project Info'!F84","v":0},{"$f":"'Project Info'!G84","v":0},{"$f":"'Project Info'!H84","v":0},{"$f":"'Project Info'!I84","v":0},{"$f":"'Project Info'!J84","v":0},{"$f":"'Project Info'!K84","v":0},{"$f":"'Project Info'!L84","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A85","v":45},{"$f":"'Project Info'!B85","v":50},{"$f":"'Project Info'!C85","v":47.459170258371508},{"$f":"'Project Info'!D85","v":43.465397050422162},{"$f":"'Project Info'!E85","v":16.894183241713304},{"$f":"'Project Info'!F85","v":0},{"$f":"'Project Info'!G85","v":0},{"$f":"'Project Info'!H85","v":0},{"$f":"'Project Info'!I85","v":0},{"$f":"'Project Info'!J85","v":0},{"$f":"'Project Info'!K85","v":0},{"$f":"'Project Info'!L85","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A86","v":40},{"$f":"'Project Info'!B86","v":45},{"$f":"'Project Info'!C86","v":42.677030404888129},{"$f":"'Project Info'!D86","v":38.812544504634097},{"$f":"'Project Info'!E86","v":14.690265649465921},{"$f":"'Project Info'!F86","v":0},{"$f":"'Project Info'!G86","v":0},{"$f":"'Project Info'!H86","v":0},{"$f":"'Project Info'!I86","v":0},{"$f":"'Project Info'!J86","v":0},{"$f":"'Project Info'!K86","v":0},{"$f":"'Project Info'!L86","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A87","v":35},{"$f":"'Project Info'!B87","v":40},{"$f":"'Project Info'!C87","v":37.333046773755832},{"$f":"'Project Info'!D87","v":33.904706919479686},{"$f":"'Project Info'!E87","v":12.53841602318813},{"$f":"'Project Info'!F87","v":0},{"$f":"'Project Info'!G87","v":0},{"$f":"'Project Info'!H87","v":0},{"$f":"'Project Info'!I87","v":0},{"$f":"'Project Info'!J87","v":0},{"$f":"'Project Info'!K87","v":0},{"$f":"'Project Info'!L87","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A88","v":30},{"$f":"'Project Info'!B88","v":35},{"$f":"'Project Info'!C88","v":32.638179845662044},{"$f":"'Project Info'!D88","v":29.547170928664851},{"$f":"'Project Info'!E88","v":10.728972818165861},{"$f":"'Project Info'!F88","v":0},{"$f":"'Project Info'!G88","v":0},{"$f":"'Project Info'!H88","v":0},{"$f":"'Project Info'!I88","v":0},{"$f":"'Project Info'!J88","v":0},{"$f":"'Project Info'!K88","v":0},{"$f":"'Project Info'!L88","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A89","v":25},{"$f":"'Project Info'!B89","v":30},{"$f":"'Project Info'!C89","v":27.529264646850947},{"$f":"'Project Info'!D89","v":24.652717392657845},{"$f":"'Project Info'!E89","v":8.8041305482613303},{"$f":"'Project Info'!F89","v":0},{"$f":"'Project Info'!G89","v":0},{"$f":"'Project Info'!H89","v":0},{"$f":"'Project Info'!I89","v":0},{"$f":"'Project Info'!J89","v":0},{"$f":"'Project Info'!K89","v":0},{"$f":"'Project Info'!L89","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A90","v":20},{"$f":"'Project Info'!B90","v":25},{"$f":"'Project Info'!C90","v":22.998111483544687},{"$f":"'Project Info'!D90","v":20.383306659827422},{"$f":"'Project Info'!E90","v":7.246164547543378},{"$f":"'Project Info'!F90","v":0},{"$f":"'Project Info'!G90","v":0},{"$f":"'Project Info'!H90","v":0},{"$f":"'Project Info'!I90","v":0},{"$f":"'Project Info'!J90","v":0},{"$f":"'Project Info'!K90","v":0},{"$f":"'Project Info'!L90","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A91","v":15},{"$f":"'Project Info'!B91","v":20},{"$f":"'Project Info'!C91","v":17.808510327474309},{"$f":"'Project Info'!D91","v":15.420865796304254},{"$f":"'Project Info'!E91","v":5.5490484131518292},{"$f":"'Project Info'!F91","v":0},{"$f":"'Project Info'!G91","v":0},{"$f":"'Project Info'!H91","v":0},{"$f":"'Project Info'!I91","v":0},{"$f":"'Project Info'!J91","v":0},{"$f":"'Project Info'!K91","v":0},{"$f":"'Project Info'!L91","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A92","v":10},{"$f":"'Project Info'!B92","v":15},{"$f":"'Project Info'!C92","v":12.269931130346862},{"$f":"'Project Info'!D92","v":10.318264913023604},{"$f":"'Project Info'!E92","v":3.9082824916941998},{"$f":"'Project Info'!F92","v":0},{"$f":"'Project Info'!G92","v":0},{"$f":"'Project Info'!H92","v":0},{"$f":"'Project Info'!I92","v":0},{"$f":"'Project Info'!J92","v":0},{"$f":"'Project Info'!K92","v":0},{"$f":"'Project Info'!L92","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A93","v":5},{"$f":"'Project Info'!B93","v":10},{"$f":"'Project Info'!C93","v":7.3137581369917548},{"$f":"'Project Info'!D93","v":5.7052382449247707},{"$f":"'Project Info'!E93","v":2.5019418419888937},{"$f":"'Project Info'!F93","v":0},{"$f":"'Project Info'!G93","v":0},{"$f":"'Project Info'!H93","v":0},{"$f":"'Project Info'!I93","v":0},{"$f":"'Project Info'!J93","v":0},{"$f":"'Project Info'!K93","v":0},{"$f":"'Project Info'!L93","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A94","v":0},{"$f":"'Project Info'!B94","v":5},{"$f":"'Project Info'!C94","v":2.6119461836144886},{"$f":"'Project Info'!D94","v":1.2699770062067783},{"$f":"'Project Info'!E94","v":1.2046477897733283},{"$f":"'Project Info'!F94","v":8760},{"$f":"'Project Info'!G94","v":2672},{"$f":"'Project Info'!H94","v":3160},{"$f":"'Project Info'!I94","v":1344},{"$f":"'Project Info'!J94","v":1584},{"$f":"'Project Info'!K94","v":88},{"$f":"'Project Info'!L94","v":264},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A95","v":-5},{"$f":"'Project Info'!B95","v":0},{"$f":"'Project Info'!C95","v":-1.6731398516793925},{"$f":"'Project Info'!D95","v":-2.7083318773557807},{"$f":"'Project Info'!E95","v":7.9391832815876459E-2},{"$f":"'Project Info'!F95","v":0},{"$f":"'Project Info'!G95","v":0},{"$f":"'Project Info'!H95","v":0},{"$f":"'Project Info'!I95","v":0},{"$f":"'Project Info'!J95","v":0},{"$f":"'Project Info'!K95","v":0},{"$f":"'Project Info'!L95","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A96","v":-10},{"$f":"'Project Info'!B96","v":-5},{"$f":"'Project Info'!C96","v":-6.5729865085377277},{"$f":"'Project Info'!D96","v":-7.2465935998252222},{"$f":"'Project Info'!E96","v":-1.168423365310433},{"$f":"'Project Info'!F96","v":0},{"$f":"'Project Info'!G96","v":0},{"$f":"'Project Info'!H96","v":0},{"$f":"'Project Info'!I96","v":0},{"$f":"'Project Info'!J96","v":0},{"$f":"'Project Info'!K96","v":0},{"$f":"'Project Info'!L96","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A97","v":-15},{"$f":"'Project Info'!B97","v":-10},{"$f":"'Project Info'!C97","v":-15.32570353422995},{"$f":"'Project Info'!D97","v":-15.707838211108999},{"$f":"'Project Info'!E97","v":-3.4051318156661381},{"$f":"'Project Info'!F97","v":0},{"$f":"'Project Info'!G97","v":0},{"$f":"'Project Info'!H97","v":0},{"$f":"'Project Info'!I97","v":0},{"$f":"'Project Info'!J97","v":0},{"$f":"'Project Info'!K97","v":0},{"$f":"'Project Info'!L97","v":0},0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0,0,0,0.56470588235294106,0,0,0,0,0,0,0]
[]
[null,null,null,null,null,null,"Cooling Load Profiles - Assumptions"]
[null,null,null,null,null,null,null,null,"Occupied Profile",null,null,null,"Unocc Profile"]
[null,null,null,null,null,null,null,null,"Max OAT","Min OAT","% Load @","%Load @","Max OAT","Min OAT","% Load @","%Load @"]
[null,null,null,null,null,null,"System Load Profile",null,"°F","°F","Max OAT","Min OAT","°F","°F","Max OAT","Min OAT"]
[null,null,null,null,null,null,"1-HVAC/Comfort",null,95,50,1,0.1,95,70,0.4,0.05]
[null,null,null,null,null,null,"2-Constant/Process",null,110,-10,1,1,110,-10,1,1]
[null,null,null,null,null,null,0]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Baseline Code IECC Version",null,null,{"$f":"_xlfn.NUMBERVALUE(MID('Project Info'!C20,1,4))","v":2018},null,null,null,null,"Chiller Plant Load Profile"]
[null,null,null,null,null,null,"Chiller System Parameters",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Occupied Profile",null,null,null,"Unocc Profile",null,null,null,null,"Perf Eligibility Thresholds",null,null,null,null,"Prescriptive Incentive",null,null,null,null,null,null,null,null,"Annual","Custom","Incr."]
[null,null,null,null,null,null,null,null,null,null,"Chiller","Max Chillers","Per Chiller","Proposed Full Load Perf",null,"Proposed Part Load Perf",null,"Base Full Load Perf",null,"Base Part Load Perf",null,"Peak Plant Load",null,null,null,"Max OAT","Min OAT","% Load @","%Load @","Max OAT","Min OAT","% Load @","%Load @","Cooling","FL","IPLV","FL","IPLV","Eligible","Base","Perf","Perf","Perf","Perf","Base","Perf","Incentive","Total","Savings","Incentive","Cost"]
[null,null,null,null,null,null,null,"Included?","Chiller Type",null,"Quantity","Operating","tons","kW/ton","EER","kW/ton","IEER","kW/ton","EER","kW/ton","IEER","%","MBH","System Load Profile",null,"°F","°F","Max OAT","Min OAT","°F","°F","Max OAT","Min OAT","EFLH","kW/ton","kW/ton","EER","EER","?","Rate","Rate","Unit","Incr.","delta","$","$","per Unit","Incentive","kWh","$","$"]
[null,null,null,null,null,null,"System 1",1,{"$f":"N19","v":0},null,{"$f":"N17","v":0},{"$f":"IF($N$22=\"\",$O$22,$N$22)","v":1},{"$f":"N18","v":0},{"$f":"IF($O$20=\"EER\",12/$N$20,$N$20)","v":0},{"$f":"IF($O$20=\"EER\",$N$20,12/$N$20)","v":{"$error":"#DIV/0!"}},{"$f":"IF($O$21=\"IEER\",12/$N$21,$N$21)","v":0},{"$f":"IF($O$21=\"IEER\",$N$21,12/$N$21)","v":{"$error":"#DIV/0!"}},{"$f":"IF(N19=G110,OFFSET($J$120,MATCH($N$18,$J$121:$J$122,-1),MATCH($U$98,$K$120:$L$120,0)),IF(N19=G111,OFFSET($J$126,MATCH($N$18,$J$127:$J$131,-1),MATCH($U$98,$K$126:$L$126,0)),OFFSET($J$135,MATCH($N$18,$J$136:$J$140,-1),MATCH($U$98,$K$135:$L$135,0))))","v":0.75},{"$f":"12/R102","v":16},{"$f":"IF(N19=G110,OFFSET($N$120,MATCH($N$18,$N$121:$N$122,-1),MATCH($U$98,$O$120:$P$120,0)),IF(N19=G111,OFFSET($N$126,MATCH($N$18,$N$127:$N$131,-1),MATCH($U$98,$O$126:$P$126,0)),OFFSET($N$135,MATCH($N$18,$N$136:$N$140,-1),MATCH($U$98,$O$135:$P$135,0))))","v":0.6},{"$f":"12/T102","v":20},{"$f":"IF(N23=\"\",O23,N23)","v":0.85},{"$f":"L102*M102*V102","v":0},{"$f":"N16","v":0},null,{"$f":"LOOKUP($X102,$G$94:$G$96,$I$94:$I$96)","v":0},{"$f":"LOOKUP($X102,$G$94:$G$96,$J$94:$J$96)","v":0},{"$f":"V102*LOOKUP($X102,$G$94:$G$96,$K$94:$K$96)","v":0},{"$f":"V102*LOOKUP($X102,$G$94:$G$96,$L$94:$L$96)","v":0},{"$f":"LOOKUP($X102,$G$94:$G$96,$M$94:$M$96)","v":0},{"$f":"LOOKUP($X102,$G$94:$G$96,$N$94:$N$96)","v":0},{"$f":"V102*LOOKUP($X102,$G$94:$G$96,$O$94:$O$96)","v":0},{"$f":"V102*LOOKUP($X102,$G$94:$G$96,$P$94:$P$96)","v":0},{"$f":"(SUMPRODUCT($L$35:$L$58,S35:S58)+SUMPRODUCT($L$65:$L$88,S65:S88))/(L102*M102)","v":{"$error":"#DIV/0!"}},{"$f":"IF($N$19=$G$110,OFFSET($S$120,MATCH($N$18,R121:R122,-1),0),IF($N$19=$G$111,OFFSET($S$126,MATCH($N$18,R127:R131,-1),0),OFFSET($S$135,MATCH($N$18,R136:R140,-1),0)))","v":0},{"$f":"IF($N$19=$G$110,OFFSET($T$120,MATCH($N$18,R121:R122,-1),0),IF($N$19=$G$111,OFFSET($T$126,MATCH($N$18,R127:R131,-1),0),OFFSET($T$135,MATCH($N$18,R136:R140,-1),0)))","v":0},{"$f":"12/AI102","v":{"$error":"#DIV/0!"}},{"$f":"12/AJ102","v":{"$error":"#DIV/0!"}},{"$f":"1*OR($N$102<=$AI$102,$P$102<=$AJ$102)","v":1},{"$f":"IF($N$19=$G$110,OFFSET($U$120,MATCH($N$18,R121:R122,-1),0),IF($N$19=$G$111,OFFSET($U$126,MATCH($N$18,R127:R131,-1),0),OFFSET($U$135,MATCH($N$18,R136:R140,-1),0)))","v":0},{"$f":"IF($N$19=$G$110,OFFSET($V$120,MATCH($N$18,R121:R122,-1),0),IF($N$19=$G$111,OFFSET($V$126,MATCH($N$18,R127:R131,-1),0),OFFSET($V$135,MATCH($N$18,R136:R140,-1),0)))","v":0},{"$f":"$O$20","v":"kW/ton"},{"$f":"IF(AP102=\"EER\", 0.1, 0.01)","v":0.01},{"$f":"MAX(0,IF(AP102=\"EER\",Q102-AL102,AJ102-P102))/AQ102","v":0},{"$f":"AN102*M102*AM102","v":0},{"$f":"MIN(3*AS102,AR102*AO102*M102)*AM102","v":0},{"$f":"AS102+AT102","v":0},{"$f":"AU102*1","v":0},{"$f":"SUMPRODUCT($L$35:$L$58,AB35:AB58)+SUMPRODUCT($L$65:$L$88,AB65:AB88)","v":0},{"$f":"AW102*$C$24","v":0},{"$f":"IF(OR(H102=0,I102=0),0,LOOKUP(I102,$AF$108:$AF$110,$AH$108:$AH$110)*(T102-P102)*M102*K102)","v":0}]
[null,null,null,null,null,null,"System 2",{"$f":"1*(Q15=\"Yes\")","v":0},{"$f":"P19","v":0},null,{"$f":"P17*H103","v":0},{"$f":"IF($P$22=\"\",$Q$22,$P$22)*H103","v":0},{"$f":"P18*H103","v":0},{"$f":"IF($Q$20=\"EER\",12/$P$20,$P$20)","v":0},{"$f":"IF($Q$20=\"EER\",$P$20,12/$P$20)","v":{"$error":"#DIV/0!"}},{"$f":"IF($Q$21=\"IEER\",12/$P$21,$P$21)","v":0},{"$f":"IF($Q$21=\"IEER\",$P$21,12/$P$21)","v":{"$error":"#DIV/0!"}},{"$f":"IF(P19=G110,OFFSET($J$120,MATCH($P$18,$J$121:$J$122,-1),MATCH($U$98,$K$120:$L$120,0)),IF(P19=G111,OFFSET($J$126,MATCH($P$18,$J$127:$J$131,-1),MATCH($U$98,$K$126:$L$126,0)),OFFSET($J$135,MATCH($P$18,$J$136:$J$140,-1),MATCH($U$98,$K$135:$L$135,0))))","v":0.75},{"$f":"12/R103","v":16},{"$f":"IF(P19=G110,OFFSET($N$120,MATCH($P$18,$N$121:$N$122,-1),MATCH($U$98,$O$120:$P$120,0)),IF(P19=G111,OFFSET($N$126,MATCH($P$18,$N$127:$N$131,-1),MATCH($U$98,$O$126:$P$126,0)),OFFSET($N$135,MATCH($P$18,$N$136:$N$140,-1),MATCH($U$98,$O$135:$P$135,0))))","v":0.6},{"$f":"12/T103","v":20},{"$f":"IF(P23=\"\",Q23,P23)","v":0.85},{"$f":"L103*M103*V103","v":0},{"$f":"P16","v":0},null,{"$f":"LOOKUP($X103,$G$94:$G$96,$I$94:$I$96)","v":0},{"$f":"LOOKUP($X103,$G$94:$G$96,$J$94:$J$96)","v":0},{"$f":"V103*LOOKUP($X103,$G$94:$G$96,$K$94:$K$96)","v":0},{"$f":"V103*LOOKUP($X103,$G$94:$G$96,$L$94:$L$96)","v":0},{"$f":"LOOKUP($X103,$G$94:$G$96,$M$94:$M$96)","v":0},{"$f":"LOOKUP($X103,$G$94:$G$96,$N$94:$N$96)","v":0},{"$f":"V103*LOOKUP($X103,$G$94:$G$96,$O$94:$O$96)","v":0},{"$f":"V103*LOOKUP($X103,$G$94:$G$96,$P$94:$P$96)","v":0},{"$f":"(SUMPRODUCT($L$35:$L$58,AC35:AC58)+SUMPRODUCT($L$65:$L$88,AC65:AC88))/(L103*M103)","v":{"$error":"#DIV/0!"}},{"$f":"IF($P$19=$G$110,OFFSET($S$120,MATCH($P$18,R121:R122,-1),0),IF($P$19=$G$111,OFFSET($S$126,MATCH($P$18,R127:R131,-1),0),OFFSET($S$135,MATCH($P$18,R136:R140,-1),0)))","v":0},{"$f":"IF($P$19=$G$110,OFFSET($T$120,MATCH($P$18,R121:R122,-1),0),IF($P$19=$G$111,OFFSET($T$126,MATCH($P$18,R127:R131,-1),0),OFFSET($T$135,MATCH($P$18,R136:R140,-1),0)))","v":0},{"$f":"12/AI103","v":{"$error":"#DIV/0!"}},{"$f":"12/AJ103","v":{"$error":"#DIV/0!"}},{"$f":"1*OR($N$103<=$AI$103,$P$103<=$AJ$103)","v":1},{"$f":"IF($P$19=$G$110,OFFSET($U$120,MATCH($P$18,R121:R122,-1),0),IF($P$19=$G$111,OFFSET($U$126,MATCH($P$18,R127:R131,-1),0),OFFSET($U$135,MATCH($P$18,R136:R140,-1),0)))","v":0},{"$f":"IF($P$19=$G$110,OFFSET($V$120,MATCH($P$18,R121:R122,-1),0),IF($P$19=$G$111,OFFSET($V$126,MATCH($P$18,R127:R131,-1),0),OFFSET($V$135,MATCH($P$18,R136:R140,-1),0)))","v":0},{"$f":"$Q$20","v":"kW/ton"},{"$f":"IF(AP103=\"EER\", 0.1, 0.01)","v":0.01},{"$f":"MAX(0,IF(AP103=\"EER\",Q103-AL103,AJ103-P103))/AQ103","v":0},{"$f":"AN103*M103*AM103","v":0},{"$f":"MIN(3*AS103,AR103*AO103*M103)*AM103","v":0},{"$f":"AS103+AT103","v":0},{"$f":"AU103*1","v":0},{"$f":"SUMPRODUCT($L$35:$L$58,AL35:AL58)+SUMPRODUCT($L$65:$L$88,AL65:AL88)","v":0},{"$f":"AW103*$C$24","v":0},{"$f":"IF(OR(H103=0,I103=0),0,LOOKUP(I103,$AF$108:$AF$110,$AH$108:$AH$110)*(T103-P103)*M103*K103)","v":0}]
[]
[null,null,null,null,null,null,"Include Optional System?"]
[null,null,null,null,null,null,"No",null,null,null,"System 1 - Part Load Cooling Performance Assumptions",null,null,null,null,null,null,null,"System 2 - Part Load Cooling Performance Assumptions",null,null,null,null,null,null,null,null,null,null,null,null,"Incremental Costs"]
[null,null,null,null,null,null,"Yes",null,null,"Line",0.01,0.42,0.45,0.12,null,"IPLV/",null,"Line",0.01,0.42,0.45,0.12,null,"IPLV/",null,null,null,null,null,null,null,null,null,"$/deltaIPLV/ton"]
[null,null,null,null,null,null,null,null,null,"#",1,0.75,0.5,0.25,-0.01,"IEER",null,"#",1,0.75,0.5,0.25,-0.01,"IEER",null,null,null,null,null,null,null,"Air-Cooled",null,{"$f":"20000/0.25/180","v":444.44444444444446}]
[null,null,null,null,null,null,"Condenser/Chiller Types",null,null,"Base",{"$f":"$R$102","v":0.75},{"$f":"IF(K109=0,0,($P109/$K109)*L$112*$K109)","v":0.62950819672131142},0.58181818181818179,0.56470588235294106,{"$f":"N109*1.5","v":0.84705882352941164},{"$f":"$T$102","v":0.6},null,"Base",{"$f":"$R$103","v":0.75},{"$f":"IF(S109=0,0,($X109/$S109)*L$112*$S109)","v":0.62950819672131142},0.58181818181818179,0.56470588235294106,{"$f":"V109*1.5","v":0.84705882352941164},{"$f":"$T$103","v":0.6},null,null,null,null,null,null,null,"Water-Cooled Centrifugal",null,{"$f":"50000/(0.38-0.315)/800","v":961.53846153846155}]
[null,null,null,null,null,null,"Air-Cooled",null,null,"Proposed",{"$f":"IF($O$20=\"EER\",12/$N$20,$N$20)","v":0},0,0,0,{"$f":"N110*1.5","v":0},{"$f":"IF($O$21=\"IEER\",12/$N$21,$N$21)","v":0},null,"Proposed",{"$f":"IF($Q$20=\"EER\",12/$P$20,$P$20)","v":0},0,0,0,{"$f":"V110*1.5","v":0},{"$f":"IF($Q$21=\"IEER\",12/$P$21,$P$21)","v":0},null,"Peak Plant Load @ 95°F OAT",null,null,null,null,null,"Water-Cooled Non-Centrifugal",null,{"$f":"50000/(0.38-0.315)/800","v":961.53846153846155}]
[null,null,null,null,null,null,"Water-Cooled Centrifugal",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Peak Load Factor%",null,{"$f":"IF($N$23=\"\",$O$23,$N$23)","v":0.85}]
[null,null,null,null,null,null,"Water-Cooled Non-Centrifugal",null,null,"PL kW/ton Factors",null,1.0491803278688525,0.96969696969696983,0.94117647058823528,null,null,null,null,null,null,null,null,null,null,null,"Peak Plant tons",null,{"$f":"AB111*IF($N$22=\"\",$O$22,$N$22)*$N$18","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,0.75,0.5,0.25,null,null,null,null,null,null,null,null,null,null,null,"Peak Plant MBH",null,{"$f":"AB112*12","v":0}]
[null,null,null,null,null,null,"Water-cooled Chiller Types"]
[null,null,null,null,null,null,"Centrifugal",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Non VSD OAT Perf. Impact",null,5.0000000000000001E-3,"% improvement per °F OAT reduction"]
[null,null,null,null,null,null,"Other",null,null,"BASELINE CHILLER PERFORMANCE",null,null,null,"BASELINE CHILLER PERFORMANCE",null,null,null,null,null,null,null,null,null,null,null,"VSD OAT Perf Impact",null,5.0000000000000001E-3,"% improvement per °F OAT reduction"]
[null,null,null,null,null,null,null,null,null,"Full Load Performance",null,null,null,"Part Load Performance",null,null,null,"PRESCRIPTIVE INCENTIVE RATES",null,null,null,null,null,null,null,"Baseline Chiller Performance Table - System 1",null,null,null,null,null,null,null,"Baseline Chiller Performance Table - System 2"]
[null,null,null,null,null,null,"Incentive Type Options",null,null,"Air-Cooled",null,null,null,"Air-Cooled",null,null,null,"Air-Cooled",null,null,null,null,null,null,null,"OAT",1,0.75,0.5,0.25,-0.01,null,null,"OAT",1,0.75,0.5,0.25,-0.01]
[null,null,null,null,null,null,"Custom",null,null,null,"FL","FL",null,null,"IPLV","IPLV",null,null,"Max","Max","Base","Perf",null,null,null,105,{"$f":"AA120","v":0.75},{"$f":"AB120","v":0.6767213114754097},{"$f":"AC120","v":0.66909090909090896},{"$f":"AD120","v":0.67764705882352927},{"$f":"AE120","v":0.67764705882352927},null,null,105,{"$f":"AI120","v":0.75},{"$f":"AJ120","v":0.6767213114754097},{"$f":"AK120","v":0.66909090909090896},{"$f":"AL120","v":0.67764705882352927},{"$f":"AM120","v":0.67764705882352927}]
[null,null,null,null,null,null,"Prescriptive",null,null,"Max tons",2015,2018,null,"Max tons",2015,2018,null,"Max tons","FL","IPLV","$/ton","Rate",null,null,null,95,{"$f":"K109","v":0.75},{"$f":"$AB$123*(1-($Z$123-$Z120)*$AB$115)","v":0.6767213114754097},{"$f":"$AC$126*(1-($Z$126-$Z120)*$AB$115)","v":0.66909090909090896},{"$f":"$AD$128*(1-($Z$128-$Z120)*$AB$115)","v":0.67764705882352927},{"$f":"AD120","v":0.67764705882352927},null,null,95,{"$f":"S109","v":0.75},{"$f":"$AJ$123*(1-($AH$123-$AH120)*$AB$115)","v":0.6767213114754097},{"$f":"$AK$126*(1-($AH$126-$AH120)*$AB$115)","v":0.66909090909090896},{"$f":"$AL$128*(1-($AH$128-$AH120)*$AB$115)","v":0.67764705882352927},{"$f":"AL120","v":0.67764705882352927}]
[null,null,null,null,null,null,null,null,null,10000,{"$f":"12/10.1","v":1.1881188118811881},{"$f":"12/10.1","v":1.1881188118811881},null,10000,{"$f":"12/14","v":0.8571428571428571},{"$f":"12/14","v":0.8571428571428571},null,10000,{"$f":"12/10.61","v":1.1310084825636193},{"$f":"12/16.91","v":0.70963926670609101},32,4,null,null,null,90,{"$f":"$AA$120*(1-($Z$120-$Z121)*$AB$115)","v":0.73124999999999996},{"$f":"$AB$123*(1-($Z$123-$Z121)*$AB$115)","v":0.66098360655737698},0.65454545454545454,0.66352941176470581,{"$f":"AD121","v":0.66352941176470581},null,null,90,{"$f":"$AI$120*(1-($AH$120-$AH121)*$AB$115)","v":0.73124999999999996},{"$f":"$AJ$123*(1-($AH$123-$AH121)*$AB$115)","v":0.66098360655737698},{"$f":"$AK$126*(1-($AH$126-$AH121)*$AB$115)","v":0.65454545454545454},{"$f":"$AL$128*(1-($AH$128-$AH121)*$AB$115)","v":0.66352941176470581},{"$f":"AL121","v":0.66352941176470581}]
[null,null,null,null,null,null,null,null,null,149.99,{"$f":"12/10.1","v":1.1881188118811881},{"$f":"12/10.1","v":1.1881188118811881},null,149.99,{"$f":"12/13.7","v":0.87591240875912413},{"$f":"12/13.7","v":0.87591240875912413},null,149.99,{"$f":"12/10.61","v":1.1310084825636193},{"$f":"12/16.59","v":0.72332730560578662},30,2.2000000000000002,null,null,null,85,0.71249999999999991,{"$f":"$AB$123*(1-($Z$123-$Z122)*$AB$115)","v":0.64524590163934414},0.64,0.64941176470588213,0.64941176470588213,null,null,85,{"$f":"$AI$120*(1-($AH$120-$AH122)*$AB$115)","v":0.71249999999999991},0.64524590163934414,0.64,0.64941176470588213,0.64941176470588213]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,80,0.69375000000000009,{"$f":"L109","v":0.62950819672131142},0.62545454545454537,0.63529411764705868,0.63529411764705868,null,null,80,0.69375000000000009,{"$f":"T109","v":0.62950819672131142},0.62545454545454537,0.63529411764705868,0.63529411764705868]
[null,null,null,null,null,null,null,null,null,"Water-Cooled Centrifugal",null,null,null,"Water-Cooled Centrifugal",null,null,null,"Water-Cooled Centrifugal",null,null,null,null,null,null,null,75,0.67500000000000004,{"$f":"$AB$123*(1-($Z$123-$Z124)*$AB$115)","v":0.61377049180327858},0.61090909090909096,0.62117647058823522,0.62117647058823522,null,null,75,0.67500000000000004,0.61377049180327858,0.61090909090909096,0.62117647058823522,0.62117647058823522]
[null,null,null,null,null,null,null,null,null,null,"FL","FL",null,null,"IPLV","IPLV",null,null,"Max","Max","Base","Perf",null,null,null,70,0.65625,{"$f":"$AB$123*(1-($Z$123-$Z125)*$AB$115)","v":0.59803278688524586},0.59636363636363632,0.60705882352941165,0.60705882352941165,null,null,70,0.65625,0.59803278688524586,0.59636363636363632,0.60705882352941165,0.60705882352941165]
[null,null,null,null,null,null,null,null,null,"Max tons",2015,2018,null,"Max tons",2015,2018,null,"Max tons","FL","IPLV","$/ton","Rate",null,null,null,65,0.63749999999999996,{"$f":"$AB$123*(1-($Z$123-$Z126)*$AB$115)","v":0.58229508196721314},{"$f":"M109","v":0.58181818181818179},0.59294117647058808,0.59294117647058808,null,null,65,0.63749999999999996,0.58229508196721314,{"$f":"U109","v":0.58181818181818179},0.59294117647058808,0.59294117647058808]
[null,null,null,null,null,null,null,null,null,10000,0.56000000000000005,0.56000000000000005,null,10000,0.5,0.5,null,10000,0.53200000000000003,0.36099999999999999,20,4,null,null,null,60,0.61874999999999991,{"$f":"$AB$123*(1-($Z$123-$Z127)*$AB$115)","v":0.5665573770491803},{"$f":"$AC$126*(1-($Z$126-$Z127)*$AB$115)","v":0.56727272727272726},0.57882352941176451,0.57882352941176451,null,null,60,0.61874999999999991,0.5665573770491803,0.56727272727272726,0.57882352941176451,0.57882352941176451]
[null,null,null,null,null,null,null,null,null,599.99,0.56000000000000005,0.56000000000000005,null,599.99,0.5,0.5,null,599.99,0.53200000000000003,0.36099999999999999,20,4,null,null,null,55,0.60000000000000009,{"$f":"$AB$123*(1-($Z$123-$Z128)*$AB$115)","v":0.55081967213114746},{"$f":"$AC$126*(1-($Z$126-$Z128)*$AB$115)","v":0.55272727272727262},{"$f":"N109","v":0.56470588235294106},0.56470588235294106,null,null,55,0.60000000000000009,0.55081967213114746,0.55272727272727262,{"$f":"V109","v":0.56470588235294106},0.56470588235294106]
[null,null,null,null,null,null,null,null,null,399.99,0.56000000000000005,0.56000000000000005,null,399.99,0.52,0.52,null,399.99,0.53200000000000003,0.371,25,5.5,null,null,null,-20,{"$f":"AA128","v":0.60000000000000009},{"$f":"AB128","v":0.55081967213114746},{"$f":"AC128","v":0.55272727272727262},{"$f":"AD128","v":0.56470588235294106},{"$f":"AE128","v":0.56470588235294106},null,null,-20,{"$f":"AI128","v":0.60000000000000009},{"$f":"AJ128","v":0.55081967213114746},{"$f":"AK128","v":0.55272727272727262},{"$f":"AL128","v":0.56470588235294106},{"$f":"AM128","v":0.56470588235294106}]
[null,null,null,null,null,null,null,null,null,299.99,0.61,0.61,null,299.99,0.55000000000000004,0.55000000000000004,null,299.99,0.57999999999999996,0.38,30,5.5]
[null,null,null,null,null,null,null,null,null,149.99,0.61,0.61,null,149.99,0.55000000000000004,0.55000000000000004,null,149.99,0.57999999999999996,0.41799999999999998,25,4.5,null,null,null,"Proposed Chiller Performance Table - System 1",null,null,null,null,null,null,null,"Proposed Chiller Performance Table - System 2"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"OAT",1,0.75,0.5,0.25,-0.01,null,null,"OAT",1,0.75,0.5,0.25,-0.01]
[null,null,null,null,null,null,null,null,null,"Water-Cooled Non-Centrifugal",null,null,null,"Water-Cooled Non-Centrifugal",null,null,null,"Water-Cooled Non-Centrifugal",null,null,null,null,null,null,null,105,{"$f":"AA134","v":0},{"$f":"AB134","v":0},{"$f":"AC134","v":0},{"$f":"AD134","v":0},{"$f":"AE134","v":0},null,null,105,{"$f":"AI134","v":0},{"$f":"AJ134","v":0},{"$f":"AK134","v":0},{"$f":"AL134","v":0},{"$f":"AM134","v":0}]
[null,null,null,null,null,null,null,null,null,null,"FL","FL",null,null,"IPLV","IPLV",null,null,"Max","Max","Base","Perf",null,null,null,95,{"$f":"K110","v":0},{"$f":"$AB$137*(1-($Z$137-$Z134)*$AB$116)","v":0},{"$f":"$AC$140*(1-($Z$140-$Z134)*$AB$116)","v":0},{"$f":"$AD$142*(1-($Z$142-$Z134)*$AB$116)","v":0},{"$f":"AD134","v":0},null,null,95,{"$f":"S110","v":0},{"$f":"$AJ$137*(1-($AH$137-$AH134)*$AB$115)","v":0},{"$f":"$AK$140*(1-($AH$140-$AH134)*$AB$115)","v":0},{"$f":"$AL$142*(1-($AH$142-$AH134)*$AB$115)","v":0},{"$f":"AL134","v":0}]
[null,null,null,null,null,null,null,null,null,"Max tons",2015,2018,null,"Max tons",2015,2018,null,"Max tons","FL","IPLV","$/ton","Rate",null,null,null,90,{"$f":"$AA$134*(1-($Z$134-$Z135)*$AB$116)","v":0},{"$f":"$AB$137*(1-($Z$137-$Z135)*$AB$116)","v":0},{"$f":"$AC$140*(1-($Z$140-$Z135)*$AB$116)","v":0},{"$f":"$AD$142*(1-($Z$142-$Z135)*$AB$116)","v":0},{"$f":"AD135","v":0},null,null,90,{"$f":"$AI$134*(1-($AH$134-$AH135)*$AB$115)","v":0},{"$f":"$AJ$137*(1-($AH$137-$AH135)*$AB$115)","v":0},{"$f":"$AK$140*(1-($AH$140-$AH135)*$AB$115)","v":0},{"$f":"$AL$142*(1-($AH$142-$AH135)*$AB$115)","v":0},{"$f":"AL135","v":0}]
[null,null,null,null,null,null,null,null,null,10000,0.56000000000000005,0.56000000000000005,null,10000,0.5,0.5,null,10000,0,0,0,0,null,null,null,85,{"$f":"$AA$134*(1-($Z$134-$Z136)*$AB$116)","v":0},0,0,0,0,null,null,85,{"$f":"$AI$134*(1-($AH$134-$AH136)*$AB$115)","v":0},0,0,0,0]
[null,null,null,null,null,null,null,null,null,599.99,0.61,0.61,null,599.99,0.52,0.52,null,599.99,0.57999999999999996,0.39,22,4.5,null,null,null,80,0,{"$f":"L110","v":0},0,0,0,null,null,80,0,{"$f":"T110","v":0},0,0,0]
[null,null,null,null,null,null,null,null,null,299.99,0.66,0.66,null,299.99,0.54,0.54,null,299.99,0.627,0.41799999999999998,22,4.5,null,null,null,75,0,0,0,0,0,null,null,75,0,0,0,0,0]
[null,null,null,null,null,null,null,null,null,149.99,0.72,0.72,null,149.99,0.56000000000000005,0.56000000000000005,null,149.99,0.68400000000000005,0.46600000000000003,25,5,null,null,null,70,0,0,0,0,0,null,null,70,0,0,0,0,0]
[null,null,null,null,null,null,null,null,null,74.989999999999995,0.75,0.75,null,74.989999999999995,0.6,0.6,null,74.989999999999995,0,0,0,0,null,null,null,65,0,0,{"$f":"M110","v":0},0,0,null,null,65,0,0,{"$f":"U110","v":0},0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,60,0,0,0,0,0,null,null,60,0,0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,55,0,0,0,{"$f":"N110","v":0},0,null,null,55,0,0,0,{"$f":"V110","v":0},0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,-20,{"$f":"AA142","v":0},{"$f":"AB142","v":0},{"$f":"AC142","v":0},{"$f":"AD142","v":0},{"$f":"AE142","v":0},null,null,-20,{"$f":"AI142","v":0},{"$f":"AJ142","v":0},{"$f":"AK142","v":0},{"$f":"AL142","v":0},{"$f":"AM142","v":0}]

{"sheet":"Variable Frequency Drives","index":13,"n_rows":224,"n_cols":119,"rows_kept":224,"cut":false,"hidden":true,"merged":[[1,10,4,17],[1,19,11,27],[16,11,16,13],[17,11,17,13],[18,11,18,13],[16,18,16,19],[17,18,17,19],[18,18,18,19],[25,11,25,13],[22,11,22,13],[23,11,23,13],[24,11,24,13],[19,11,19,13],[20,11,20,13],[21,11,21,13],[24,18,24,19],[25,18,25,19],[19,18,19,19],[20,18,20,19],[21,18,21,19],[22,18,22,19],[23,18,23,19]]}
["Savings Summary",null,null,null,null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,null,null,"Notes (Optional)"]
["Annual kWh Savings",null,null,{"$f":"X27","v":0},null,null,null,"Value","Unit",null,"This measure considers savings from installing variable speed drives to control fans and/or pumps.  The tool analyzes this measure prescriptively, following the Prescriptive VSD guidelines for incentive eligibility based on motor category, size, and control strategy.  Savings are only considered for drives/motors that are eligible for prescriptive incentives."]
["% On Peak",null,null,{"$f":"IF(D2<=0,0,MIN(1,A15+C15))","v":0},null,"Annual Electric Savings",null,{"$f":"D2","v":0},"kWh"]
["Max kW",null,null,{"$f":"MAX(Y27:Z27)","v":0},null,"Annual Fuel Savings",null,{"$f":"D7*C28","v":{"$error":"#N/A"}},{"$f":"D20","v":{"$error":"#N/A"}}]
["Summer kW",null,null,{"$f":"Y27","v":0},null,"Incremental","Default Calc",{"$f":"SUMPRODUCT(Q17:Q26,W17:W26)","v":0},"$"]
["Winter kW",null,null,{"$f":"Z27","v":0},null,"Cost","Project Specific",null,"$ (Optional)"]
["Annual Fuel Savings (MMBtu)",null,null,0,null,"Estimated Incentive",null,{"$f":"SUMPRODUCT(Q17:Q26,W17:W26)","v":0},"$"]
["Incremental Cost (Default Calc)",null,null,{"$f":"SUMPRODUCT(Q17:Q26,W17:W26)*2","v":0}]
["Incremental Cost (for Summary)",null,null,{"$f":"IF(H6>0,H6,D8)","v":0},null,"Project Information Summary"]
["kWh Savings by Peak Period",null,null,null,null,null,"STATE",{"$f":"'Project Info'!C15","v":"NH"}]
["Winter","Winter","Summer","Summer",null,null,"Program Year",{"$f":"'Project Info'!C19","v":0}]
["On-Peak","Off-Peak","On-Peak","Off-Peak",null,null,"Code IECC Version",{"$f":"MID('Project Info'!C20,1,4)","v":"2018"}]
["kWh","kWh","kWh","kWh",null,null,"Electric PA",{"$f":"'Project Info'!F3","v":0},null,null,"Table 1: Motor and Control Parameters"]
[{"$f":"SUMPRODUCT(M125:M148,$S$125:$S$148)+SUMPRODUCT(M155:M178,$S$155:$S$178)","v":0},{"$f":"SUMPRODUCT(N125:N148,$S$125:$S$148)+SUMPRODUCT(N155:N178,$S$155:$S$178)","v":0},{"$f":"SUMPRODUCT(O125:O148,$S$125:$S$148)+SUMPRODUCT(O155:O178,$S$155:$S$178)","v":0},{"$f":"SUMPRODUCT(P125:P148,$S$125:$S$148)+SUMPRODUCT(P155:P178,$S$155:$S$178)","v":0},null,null,"Gas PA",{"$f":"'Project Info'!I3","v":0},null,null,null,null,1,null,2,3,4,5,6,null,7,null,null,"TRM Savings Factors"]
[{"$f":"ROUND(IF(A14<=0,0,A14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(B14<=0,0,B14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(C14<=0,0,C14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"IF(SUM(A14:D14)=0,0,1-SUM(A15:C15))","v":0},null,"Building Type",null,{"$f":"'Project Info'!C18","v":0},null,null,"Line",null,null,null,"Mtr Eligible If","Nameplate","Motor","Max Operating",null,null,"Minimum","VFD Savings","Per Mtr","Annual","Summer","Winter"]
[null,null,null,null,null,"Building Area (ft²)",null,{"$f":"'Project Info'!C17","v":0},null,null,"No.","Installation Type",null,null,"Less Than (hp)","Motor HP","Qty","Qty","Control Type (Req.)",null,"Speed (%)","Eligible?","Incentive","kWh/HP","kW/HP","kW/HP"]
["Utility Rates",null,null,null,null,"*NOTE: Baseline values are automated and cannot be changed.",null,null,null,null,1,null,null,null,{"$f":"IF($L17=\"\",\"\",LOOKUP($L17,$G$34:$G$40,$K$34:$K$40))","v":""},null,null,null,null,null,null,{"$f":"IF($L17=\"\",\"\",IF(P17>=O17,$G$56,IF(OR(S17=\"\",S17=$Z$48,S17=$Z$52),$G$56,$G$55)))","v":""},{"$f":"(L17<>\"\")*(V17=$G$55)*LOOKUP(P17,$S$49:$S$62,$T$49:$T$62)","v":0},{"$f":"IF(AND(L17<>\"\",V17=$G$55),LOOKUP($L17,$G$34:$G$40,$L$34:$L$40),0)","v":0},{"$f":"IF(AND(L17<>\"\",V17=$G$55),LOOKUP($L17,$G$34:$G$40,$M$34:$M$40),0)","v":0},{"$f":"IF(AND(L17<>\"\",V17=$G$55),LOOKUP($L17,$G$34:$G$40,$N$34:$N$40),0)","v":0}]
[null,null,"Rate","Unit",null,null,null,null,null,null,2,null,null,null,"",null,null,null,null,null,null,{"$f":"IF($L18=\"\",\"\",IF(P18>=O18,$G$56,IF(OR(S18=\"\",S18=$Z$48,S18=$Z$52),$G$56,$G$55)))","v":""},0,{"$f":"IF(AND(L18<>\"\",V18=$G$55),LOOKUP($L18,$G$34:$G$40,$L$34:$L$40),0)","v":0},{"$f":"IF(AND(L18<>\"\",V18=$G$55),LOOKUP($L18,$G$34:$G$40,$M$34:$M$40),0)","v":0},{"$f":"IF(AND(L18<>\"\",V18=$G$55),LOOKUP($L18,$G$34:$G$40,$N$34:$N$40),0)","v":0}]
["Electric",null,{"$f":"'ECM Summary'!$E$31","v":0.1593},"kWh",null,null,null,null,null,null,3,null,null,null,"",null,null,null,null,null,null,"",0,0,0,0]
[{"$f":"'ECM Summary'!$C$32","v":0},null,{"$f":"'ECM Summary'!$E$32","v":{"$error":"#N/A"}},{"$f":"'ECM Summary'!$F$32","v":{"$error":"#N/A"}},null,null,null,null,null,null,4,null,null,null,"",null,null,null,null,null,null,"",0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,5,null,null,null,"",null,null,null,null,null,null,"",0,0,0,0]
["Custom Incentive Rates",null,null,null,null,null,null,null,null,null,6,null,null,null,"",null,null,null,null,null,null,"",0,0,0,0]
[null,null,"Rate","Unit",null,null,null,null,null,null,7,null,null,null,"",null,null,null,null,null,null,"",0,0,0,0]
["Electric",null,{"$f":"'ECM Summary'!$J$31","v":0.28000000000000003},"kWh",null,null,null,null,null,null,8,null,null,null,"",null,null,null,null,null,null,"",0,0,0,0]
[{"$f":"'ECM Summary'!$H$32","v":0},null,{"$f":"'ECM Summary'!$J$32","v":0},{"$f":"'ECM Summary'!$K$32","v":{"$error":"#N/A"}},null,null,null,null,null,null,9,null,null,null,"",null,null,null,null,null,null,"",0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,10,null,null,null,"",null,null,null,null,null,null,"",0,0,0,0]
["Fossil Fuel",null,{"$f":"'Project Info'!C21","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"TOTAL",{"$f":"SUMPRODUCT(W17:W26,Q17:Q26)","v":0},{"$f":"SUMPRODUCT(X17:X26,$R$17:$R$26,$P$17:$P$26)","v":0},{"$f":"SUMPRODUCT(Y17:Y26,$R$17:$R$26,$P$17:$P$26)","v":0},{"$f":"SUMPRODUCT(Z17:Z26,$R$17:$R$26,$P$17:$P$26)","v":0}]
["Fuel Conversion",null,{"$f":"LOOKUP(C27,'Project Info'!X102:X104,'Project Info'!Z102:Z104)","v":{"$error":"#N/A"}}]
[]
[null,null,null,null,null,null,null,null,null,null,null,"TRM Savings Estimates ",null,null,null,null,null,null,"CUSTOM SAVINGS ASSUMPTIONS (CURRENTLY NOT USED)"]
[null,null,null,null,null,null,null,null,null,null,null,"Based on Project Building Type",null,null,null,null,null,null,null,"Occupied Hours % Flow Profile",null,null,null,"Unoccupied Hours % Flow Profile"]
[null,null,null,null,null,null,null,null,null,null,"NH","Annual","Summer","Winter",null,null,null,null,"Cube Law","Cooling OAT Range",null,"Heating OAT Range",null,"Cooling OAT Range",null,"Heating OAT Range"]
[null,null,null,null,null,null,"Intallation Types",null,null,null,"Max HP","kWh/HP","kW/HP","kW/HP",null,null,null,null,"SP Ratio",95,{"$f":"M211","v":50},{"$f":"M212","v":60},0,95,{"$f":"M211","v":50},{"$f":"M212","v":60},0]
[null,null,null,null,null,null,"BDF - Boiler Draft Fan",null,null,null,25,{"$f":"OFFSET($I$69,MATCH($J$66,$H$70:$H$79,0),MATCH($G34,$J$69:$U$69,0))","v":{"$error":"#N/A"}},{"$f":"OFFSET($I$80,MATCH($J$66,$H$81:$H$90,0),MATCH($G34,$J$69:$U$69,0))","v":{"$error":"#N/A"}},{"$f":"OFFSET($I$91,MATCH($J$66,$H$92:$H$101,0),MATCH($G34,$J$69:$U$69,0))","v":{"$error":"#N/A"}},null,null,null,null,0,0,0,0,0.95,0,0,0,0.8]
[null,null,null,null,null,null,"CHWP - Chilled Water Pump",null,null,null,7.5,{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},null,null,null,null,0,0.95,0,0,0,0.75,0,0,0]
[null,null,null,null,null,null,"CTF - Cooling Tower Fan",null,null,null,5,{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},null,null,null,null,0.3,0.95,0,0,0,0.75,0,0,0]
[null,null,null,null,null,null,"CWP - Condenser Water Pump",null,null,null,7.5,{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},null,null,null,null,0.3,0.95,0.3,0,0,0.75,0.2,0,0]
[null,null,null,null,null,null,"FWP - Boiler Feed Water Pump",null,null,null,15,{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},null,null,null,null,0.3,0,0,0.3,0.95,0,0,0.2,0.75]
[null,null,null,null,null,null,"HWP - Hot Water Circulator Pump",null,null,null,7.5,{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},null,null,null,null,0.3,0,0,0,0.95,0,0,0,0.8]
[null,null,null,null,null,null,"WHP - WS Heat Pump Loop Circulator Pump",null,null,null,5,{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},null,null,null,null,0.3,0.75,0.75,0.75,0.75,0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.3,0.7,0.7,0.7,0.7,0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.3,0.7,0.7,0.7,0.7,0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.3,0.95,0.4,0.4,0.5,0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.3,0.95,0.4,0.4,0.5,0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.3,0.95,0.5,0.5,0.95,0.6,0.2,0.2,0.6]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Prescr. Incentive",null,null,null,null,null,"Control Types"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"HP","NH","Incr Cost $","FL Eff %",null,null,null,"BAL - VFD for Balancing Only"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,{"$f":"T49*2","v":0},1,null,null,null,"DP - Pressure Differential"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,800,{"$f":"T50*2","v":1600},0.85499999999999998,null,null,null,"DT - Temperature Differential"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.5,800,1600,0.86499999999999999,null,null,null,"OTH - Other Automatic VFD Modulation"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,800,1600,0.86499999999999999,null,null,null,"ST- Static/Constant Speed Setting"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,800,1600,0.89500000000000002]
[null,null,null,null,null,null,"Yes/No",null,null,null,null,null,null,null,null,null,null,null,5,900,1800,0.89500000000000002]
[null,null,null,null,null,null,"Yes",null,null,null,null,null,null,null,null,null,null,null,7.5,900,1800,0.91]
[null,null,null,null,null,null,"No",null,null,null,null,null,null,null,null,null,null,null,10,1000,2000,0.91700000000000004]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,15,1125,2250,0.93]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,20,1575,3150,0.93]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,25,0,0,0.93600000000000005]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,30,0,0,0.94099999999999995]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,40,0,0,0.94099999999999995]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,50,0,0,0.94499999999999995]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,60,null,null,0.95]
[]
[null,null,null,null,null,null,"Bldg Type from Project Info Tab",null,null,{"$f":"$H$15","v":0}]
[null,null,null,null,null,null,"Matched Bldg Type for TRM Calc",null,null,{"$f":"LOOKUP(J65,W70:W111,Z70:Z111)","v":{"$error":"#N/A"}}]
[]
[null,null,null,null,null,null,"Savings Factors from MA TRM 2019-2021"]
[null,null,null,null,null,null,"Savings Factor","Building Type",null,{"$f":"G34","v":"BDF - Boiler Draft Fan"},{"$f":"G35","v":"CHWP - Chilled Water Pump"},{"$f":"G36","v":"CTF - Cooling Tower Fan"},{"$f":"G37","v":"CWP - Condenser Water Pump"},{"$f":"G38","v":"FWP - Boiler Feed Water Pump"},{"$f":"G39","v":"HWP - Hot Water Circulator Pump"},"NA (not in 2025 App)","NA (not in 2025 App)","NA (not in 2025 App)","NA (not in 2025 App)","NA (not in 2025 App)",{"$f":"G40","v":"WHP - WS Heat Pump Loop Circulator Pump"},null,"Project Info Bldg Type Matched to TRM Bldg Types for VFD Calc"]
[null,null,null,null,null,null,"kWh/HP","University/College",null,{"$f":"L70","v":449},745,449,{"$f":"L70","v":449},2316,2344,3220,{"$f":"L70","v":449},3641,1067,1023,3061,null,{"$f":"'Project Info'!E102","v":"Automotive facility"},null,null,"Warehouse"]
[null,null,null,null,null,null,null,"Elm/H School",null,{"$f":"L71","v":365},628,365,{"$f":"L71","v":365},1933,1957,3402,{"$f":"L71","v":365},3563,879,840,2561,null,{"$f":"'Project Info'!E103","v":"Convention center"},null,null,"Offices"]
[null,null,null,null,null,null,null,"Multi-Family",null,889,1374,889,889,2340,2400,3082,889,3202,1374,1319,3713,null,{"$f":"'Project Info'!E104","v":"Courthouse"},null,null,"Offices"]
[null,null,null,null,null,null,null,"Hotel/Motel",null,809,1239,809,809,2195,2239,3368,809,3151,1334,1290,3433,null,{"$f":"'Project Info'!E105","v":"Daycare"},null,null,"Elm/H School"]
[null,null,null,null,null,null,null,"Health",null,1705,2427,1705,1705,2349,2406,3002,1705,3375,1577,1487,3670,null,{"$f":"'Project Info'!E106","v":"Dining: bar/lounge/leisure"},null,null,"Restaurant"]
[null,null,null,null,null,null,null,"Warehouse",null,455,816,455,455,2002,2087,3229,455,3310,1253,1205,2818,null,{"$f":"'Project Info'!E107","v":"Dining: Cafeteria/Fast Food"},null,null,"Restaurant"]
[null,null,null,null,null,null,null,"Restaurant",null,993,1566,993,993,1977,2047,2628,993,3440,1425,1363,3542,null,{"$f":"'Project Info'!E108","v":"Dining: Family"},null,null,"Restaurant"]
[null,null,null,null,null,null,null,"Retail",null,633,1049,633,633,1949,2000,2392,633,3092,1206,1146,2998,null,{"$f":"'Project Info'!E109","v":"Dormitory"},null,null,"University/College"]
[null,null,null,null,null,null,null,"Grocery",null,918,1632,918,918,1653,1681,2230,918,3126,1408,1297,3285,null,{"$f":"'Project Info'!E110","v":"Education - College/University"},null,null,"University/College"]
[null,null,null,null,null,null,null,"Offices",null,950,1370,950,950,1866,1896,3346,950,3332,1135,1076,3235,null,{"$f":"'Project Info'!E111","v":"Education - Community College"},null,null,"University/College"]
[null,null,null,null,null,null,"Summer kW/HP",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E112","v":"Education - K-12 School"},null,null,"Elm/H School"]
[null,null,null,null,null,null,null,"University/College",null,6.0000000000000001E-3,0.17399999999999999,-2.3E-2,2.3E-2,0.45700000000000002,9.0999999999999998E-2,0.109,2.3E-2,0.109,0.28699999999999998,0.27400000000000002,0.218,null,{"$f":"'Project Info'!E113","v":"Exercise center"},null,null,"Health"]
[null,null,null,null,null,null,null,"Elm/H School",null,6.0000000000000001E-3,0.17399999999999999,-2.3E-2,2.3E-2,0.45700000000000002,9.0999999999999998E-2,0.109,2.3E-2,0.377,0.28699999999999998,0.27400000000000002,0.218,null,{"$f":"'Project Info'!E114","v":"Fire station"},null,null,"Warehouse"]
[null,null,null,null,null,null,null,"Multi-Family",null,6.0000000000000001E-3,0.17399999999999999,-2.3E-2,2.3E-2,0.45700000000000002,9.0999999999999998E-2,0.109,2.3E-2,0.109,0.28699999999999998,0.27400000000000002,0.218,null,{"$f":"'Project Info'!E115","v":"Grocery"},null,null,"Grocery"]
[null,null,null,null,null,null,null,"Hotel/Motel",null,6.0000000000000001E-3,0.17399999999999999,-2.3E-2,2.3E-2,0.45700000000000002,9.0999999999999998E-2,0.109,2.3E-2,0.109,0.28699999999999998,0.27400000000000002,0.218,null,{"$f":"'Project Info'!E116","v":"Gymnasium"},null,null,"Health"]
[null,null,null,null,null,null,null,"Health",null,6.0000000000000001E-3,0.17399999999999999,-2.3E-2,2.3E-2,0.45700000000000002,9.0999999999999998E-2,0.109,2.3E-2,0.109,0.28699999999999998,0.27400000000000002,0.218,null,{"$f":"'Project Info'!E117","v":"Health/Medical - Clinic"},null,null,"Health"]
[null,null,null,null,null,null,null,"Warehouse",null,6.0000000000000001E-3,0.17399999999999999,-2.3E-2,2.3E-2,0.45700000000000002,9.0999999999999998E-2,0.109,2.3E-2,0.109,0.28699999999999998,0.27400000000000002,0.218,null,{"$f":"'Project Info'!E118","v":"Hospital"},null,null,"Health"]
[null,null,null,null,null,null,null,"Restaurant",null,6.0000000000000001E-3,0.17399999999999999,-2.3E-2,2.3E-2,0.45700000000000002,9.0999999999999998E-2,0.26100000000000001,2.3E-2,0.26100000000000001,0.28699999999999998,0.27400000000000002,0.218,null,{"$f":"'Project Info'!E119","v":"Hotel/Motel/Lodging"},null,null,"Hotel/Motel"]
[null,null,null,null,null,null,null,"Retail",null,6.0000000000000001E-3,0.17399999999999999,-2.3E-2,2.3E-2,0.45700000000000002,9.0999999999999998E-2,0.109,2.3E-2,0.109,0.28699999999999998,0.27400000000000002,0.218,null,{"$f":"'Project Info'!E120","v":"Industrial/Manufacturing - 1 Shift"},null,null,"Warehouse"]
[null,null,null,null,null,null,null,"Grocery",null,6.0000000000000001E-3,0.17399999999999999,-2.3E-2,2.3E-2,0.45700000000000002,9.0999999999999998E-2,0.26100000000000001,2.3E-2,0.26100000000000001,0.28699999999999998,0.27400000000000002,0.218,null,{"$f":"'Project Info'!E121","v":"Industrial/Manufacturing - 2 Shifts"},null,null,"Warehouse"]
[null,null,null,null,null,null,null,"Offices",null,6.0000000000000001E-3,0.17399999999999999,-2.3E-2,2.3E-2,0.45700000000000002,9.0999999999999998E-2,0.109,2.3E-2,0.109,0.28699999999999998,0.27400000000000002,0.218,null,{"$f":"'Project Info'!E122","v":"Industrial/Manufacturing - 3 Shifts"},null,null,"Warehouse"]
[null,null,null,null,null,null,"Winter kW/HP",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E123","v":"Library"},null,null,"Offices"]
[null,null,null,null,null,null,null,"University/College",null,2.3E-2,0.184,-6.0000000000000001E-3,6.0000000000000001E-3,0.45700000000000002,0.21,0.109,2.3E-2,0.377,0.26,0.252,0.28199999999999997,null,{"$f":"'Project Info'!E124","v":"Motion picture theater"},null,null,"Retail"]
[null,null,null,null,null,null,null,"Elm/H School",null,2.3E-2,0.184,-6.0000000000000001E-3,6.0000000000000001E-3,0.45700000000000002,0.21,0.109,2.3E-2,0.45700000000000002,0.26,0.252,0.28199999999999997,null,{"$f":"'Project Info'!E125","v":"Multifamily"},null,null,"Multi-Family"]
[null,null,null,null,null,null,null,"Multi-Family",null,2.3E-2,0.184,-6.0000000000000001E-3,6.0000000000000001E-3,0.35499999999999998,0.21,0.109,2.3E-2,0.109,0.26,0.252,0.28199999999999997,null,{"$f":"'Project Info'!E126","v":"Museum"},null,null,"Retail"]
[null,null,null,null,null,null,null,"Hotel/Motel",null,2.3E-2,0.184,-6.0000000000000001E-3,6.0000000000000001E-3,0.41799999999999998,0.21,0.109,2.3E-2,0.109,0.26,0.252,0.28199999999999997,null,{"$f":"'Project Info'!E127","v":"Nursing Home"},null,null,"Multi-Family"]
[null,null,null,null,null,null,null,"Health",null,2.3E-2,0.184,-6.0000000000000001E-3,6.0000000000000001E-3,0.27500000000000002,0.21,0.109,2.3E-2,0.377,0.26,0.252,0.28199999999999997,null,{"$f":"'Project Info'!E128","v":"Office - Medium/Large ( > 20,000 ft²)"},null,null,"Offices"]
[null,null,null,null,null,null,null,"Warehouse",null,2.3E-2,0.184,-6.0000000000000001E-3,6.0000000000000001E-3,0.17799999999999999,0.21,0.26100000000000001,2.3E-2,0.377,0.26,0.252,0.28199999999999997,null,{"$f":"'Project Info'!E129","v":"Office - Small ( < 20,000 ft²)"},null,null,"Offices"]
[null,null,null,null,null,null,null,"Restaurant",null,2.3E-2,0.184,-6.0000000000000001E-3,6.0000000000000001E-3,0.35499999999999998,0.21,0.109,2.3E-2,0.109,0.26,0.252,0.28199999999999997,null,{"$f":"'Project Info'!E130","v":"Parking garage"},null,null,"Warehouse"]
[null,null,null,null,null,null,null,"Retail",null,2.3E-2,0.184,-6.0000000000000001E-3,6.0000000000000001E-3,0.27500000000000002,0.21,0.109,2.3E-2,0.109,0.26,0.252,0.28199999999999997,null,{"$f":"'Project Info'!E131","v":"Penitentiary"},null,null,"Hotel/Motel"]
[null,null,null,null,null,null,null,"Grocery",null,2.3E-2,0.184,-6.0000000000000001E-3,6.0000000000000001E-3,0.41799999999999998,0.21,0.109,2.3E-2,0.45700000000000002,0.26,0.252,0.28199999999999997,null,{"$f":"'Project Info'!E132","v":"Performing arts theater"},null,null,"Retail"]
[null,null,null,null,null,null,null,"Offices",null,2.3E-2,0.184,-6.0000000000000001E-3,6.0000000000000001E-3,0.41799999999999998,0.21,0.109,2.3E-2,0.45700000000000002,0.26,0.252,0.28199999999999997,null,{"$f":"'Project Info'!E133","v":"Police station"},null,null,"Offices"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E134","v":"Post office"},null,null,"Retail"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E135","v":"Religious Worship/Church"},null,null,"Offices"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E136","v":"Retail"},null,null,"Retail"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E137","v":"Sports arena"},null,null,"Health"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E138","v":"Storage Facility"},null,null,"Warehouse"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E139","v":"Town hall"},null,null,"Offices"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E140","v":"Transportation"},null,null,"Warehouse"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E141","v":"Warehouse - Distribution Center"},null,null,"Warehouse"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E142","v":"Warehouse - Inactive Storage"},null,null,"Warehouse"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"'Project Info'!E143","v":"Workshop"},null,null,"Warehouse"]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,"CUSTOM SAVINGS CALCULATIONS BELOW - CURRENTLY NOT USED; EXCEPT FOR %ON PEAK SAVINGS; TOOL USES TRM SAVINGS"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Line No","Eligible?","Install Type","Qty","Mtr HP","Mtr Eff.","Min. Spd","SP Ratio","VFD kW",null,"Line No","Eligible?","Install Type","Qty","Mtr HP","Mtr Eff.","Min. Spd","SP Ratio","VFD kW",null,"Line No","Eligible?","Install Type","Qty","Mtr HP","Mtr Eff.","Min. Spd","SP Ratio","VFD kW",null,"Line No","Eligible?","Install Type","Qty","Mtr HP","Mtr Eff.","Min. Spd","SP Ratio","VFD kW",null,"Line No","Eligible?","Install Type","Qty","Mtr HP","Mtr Eff.","Min. Spd","SP Ratio","VFD kW",null,"Line No","Eligible?","Install Type","Qty","Mtr HP","Mtr Eff.","Min. Spd","SP Ratio","VFD kW",null,"Line No","Eligible?","Install Type","Qty","Mtr HP","Mtr Eff.","Min. Spd","SP Ratio","VFD kW",null,"Line No","Eligible?","Install Type","Qty","Mtr HP","Mtr Eff.","Min. Spd","SP Ratio","VFD kW",null,"Line No","Eligible?","Install Type","Qty","Mtr HP","Mtr Eff.","Min. Spd","SP Ratio","VFD kW",null,"Line No","Eligible?","Install Type","Qty","Mtr HP","Mtr Eff.","Min. Spd","SP Ratio","VFD kW"]
[null,null,null,null,null,null,"Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown",null,null,null,null,null,null,"Total",null,1,{"$f":"1*(LOOKUP(U121,$K$17:$K$26,$L$17:$L$26)<>\"\")*(LOOKUP(U121,$K$17:$K$26,$P$17:$P$26)>0)*(LOOKUP(U121,$K$17:$K$26,$V$17:$V$26)=$G$55)","v":0},{"$f":"LOOKUP(U121,$K$17:$K$26,$L$17:$L$26)","v":0},{"$f":"LOOKUP(U121,$K$17:$K$26,$R$17:$R$26)","v":0},{"$f":"LOOKUP(U121,$K$17:$K$26,$P$17:$P$26)","v":0},{"$f":"LOOKUP(Y121,$S$49:$S$62,$V$49:$V$62)","v":1},{"$f":"LOOKUP(U121,$K$17:$K$26,$U$17:$U$26)","v":0},{"$f":"IF(OR(W121=0,W121=\"\"),0,LOOKUP(W121,$G$34:$G$44,$S$34:$S$45))","v":0},{"$f":"0.03*Y121","v":0},null,{"$f":"U121+1","v":2},{"$f":"1*(LOOKUP(AE121,$K$17:$K$26,$L$17:$L$26)<>\"\")*(LOOKUP(AE121,$K$17:$K$26,$P$17:$P$26)>0)*(LOOKUP(AE121,$K$17:$K$26,$V$17:$V$26)=$G$55)","v":0},{"$f":"LOOKUP(AE121,$K$17:$K$26,$L$17:$L$26)","v":0},{"$f":"LOOKUP(AE121,$K$17:$K$26,$R$17:$R$26)","v":0},{"$f":"LOOKUP(AE121,$K$17:$K$26,$P$17:$P$26)","v":0},{"$f":"LOOKUP(AI121,$S$49:$S$62,$V$49:$V$62)","v":1},{"$f":"LOOKUP(AE121,$K$17:$K$26,$U$17:$U$26)","v":0},{"$f":"IF(OR(AG121=0,AG121=\"\"),0,LOOKUP(AG121,$G$34:$G$44,$S$34:$S$45))","v":0},{"$f":"0.03*AI121","v":0},null,{"$f":"AE121+1","v":3},{"$f":"1*(LOOKUP(AO121,$K$17:$K$26,$L$17:$L$26)<>\"\")*(LOOKUP(AO121,$K$17:$K$26,$P$17:$P$26)>0)*(LOOKUP(AO121,$K$17:$K$26,$V$17:$V$26)=$G$55)","v":0},{"$f":"LOOKUP(AO121,$K$17:$K$26,$L$17:$L$26)","v":0},{"$f":"LOOKUP(AO121,$K$17:$K$26,$R$17:$R$26)","v":0},{"$f":"LOOKUP(AO121,$K$17:$K$26,$P$17:$P$26)","v":0},{"$f":"LOOKUP(AS121,$S$49:$S$62,$V$49:$V$62)","v":1},{"$f":"LOOKUP(AO121,$K$17:$K$26,$U$17:$U$26)","v":0},{"$f":"IF(OR(AQ121=0,AQ121=\"\"),0,LOOKUP(AQ121,$G$34:$G$44,$S$34:$S$45))","v":0},{"$f":"0.03*AS121","v":0},null,{"$f":"AO121+1","v":4},{"$f":"1*(LOOKUP(AY121,$K$17:$K$26,$L$17:$L$26)<>\"\")*(LOOKUP(AY121,$K$17:$K$26,$P$17:$P$26)>0)*(LOOKUP(AY121,$K$17:$K$26,$V$17:$V$26)=$G$55)","v":0},{"$f":"LOOKUP(AY121,$K$17:$K$26,$L$17:$L$26)","v":0},{"$f":"LOOKUP(AY121,$K$17:$K$26,$R$17:$R$26)","v":0},{"$f":"LOOKUP(AY121,$K$17:$K$26,$P$17:$P$26)","v":0},{"$f":"LOOKUP(BC121,$S$49:$S$62,$V$49:$V$62)","v":1},{"$f":"LOOKUP(AY121,$K$17:$K$26,$U$17:$U$26)","v":0},{"$f":"IF(OR(BA121=0,BA121=\"\"),0,LOOKUP(BA121,$G$34:$G$44,$S$34:$S$45))","v":0},{"$f":"0.03*BC121","v":0},null,{"$f":"AY121+1","v":5},{"$f":"1*(LOOKUP(BI121,$K$17:$K$26,$L$17:$L$26)<>\"\")*(LOOKUP(BI121,$K$17:$K$26,$P$17:$P$26)>0)*(LOOKUP(BI121,$K$17:$K$26,$V$17:$V$26)=$G$55)","v":0},{"$f":"LOOKUP(BI121,$K$17:$K$26,$L$17:$L$26)","v":0},{"$f":"LOOKUP(BI121,$K$17:$K$26,$R$17:$R$26)","v":0},{"$f":"LOOKUP(BI121,$K$17:$K$26,$P$17:$P$26)","v":0},{"$f":"LOOKUP(BM121,$S$49:$S$62,$V$49:$V$62)","v":1},{"$f":"LOOKUP(BI121,$K$17:$K$26,$U$17:$U$26)","v":0},{"$f":"IF(OR(BK121=0,BK121=\"\"),0,LOOKUP(BK121,$G$34:$G$44,$S$34:$S$45))","v":0},{"$f":"0.03*BM121","v":0},null,{"$f":"BI121+1","v":6},{"$f":"1*(LOOKUP(BS121,$K$17:$K$26,$L$17:$L$26)<>\"\")*(LOOKUP(BS121,$K$17:$K$26,$P$17:$P$26)>0)*(LOOKUP(BS121,$K$17:$K$26,$V$17:$V$26)=$G$55)","v":0},{"$f":"LOOKUP(BS121,$K$17:$K$26,$L$17:$L$26)","v":0},{"$f":"LOOKUP(BS121,$K$17:$K$26,$R$17:$R$26)","v":0},{"$f":"LOOKUP(BS121,$K$17:$K$26,$P$17:$P$26)","v":0},{"$f":"LOOKUP(BW121,$S$49:$S$62,$V$49:$V$62)","v":1},{"$f":"LOOKUP(BS121,$K$17:$K$26,$U$17:$U$26)","v":0},{"$f":"IF(OR(BU121=0,BU121=\"\"),0,LOOKUP(BU121,$G$34:$G$44,$S$34:$S$45))","v":0},{"$f":"0.03*BW121","v":0},null,{"$f":"BS121+1","v":7},{"$f":"1*(LOOKUP(CC121,$K$17:$K$26,$L$17:$L$26)<>\"\")*(LOOKUP(CC121,$K$17:$K$26,$P$17:$P$26)>0)*(LOOKUP(CC121,$K$17:$K$26,$V$17:$V$26)=$G$55)","v":0},{"$f":"LOOKUP(CC121,$K$17:$K$26,$L$17:$L$26)","v":0},{"$f":"LOOKUP(CC121,$K$17:$K$26,$R$17:$R$26)","v":0},{"$f":"LOOKUP(CC121,$K$17:$K$26,$P$17:$P$26)","v":0},{"$f":"LOOKUP(CG121,$S$49:$S$62,$V$49:$V$62)","v":1},{"$f":"LOOKUP(CC121,$K$17:$K$26,$U$17:$U$26)","v":0},{"$f":"IF(OR(CE121=0,CE121=\"\"),0,LOOKUP(CE121,$G$34:$G$44,$S$34:$S$45))","v":0},{"$f":"0.03*CG121","v":0},null,{"$f":"CC121+1","v":8},{"$f":"1*(LOOKUP(CM121,$K$17:$K$26,$L$17:$L$26)<>\"\")*(LOOKUP(CM121,$K$17:$K$26,$P$17:$P$26)>0)*(LOOKUP(CM121,$K$17:$K$26,$V$17:$V$26)=$G$55)","v":0},{"$f":"LOOKUP(CM121,$K$17:$K$26,$L$17:$L$26)","v":0},{"$f":"LOOKUP(CM121,$K$17:$K$26,$R$17:$R$26)","v":0},{"$f":"LOOKUP(CM121,$K$17:$K$26,$P$17:$P$26)","v":0},{"$f":"LOOKUP(CQ121,$S$49:$S$62,$V$49:$V$62)","v":1},{"$f":"LOOKUP(CM121,$K$17:$K$26,$U$17:$U$26)","v":0},{"$f":"IF(OR(CO121=0,CO121=\"\"),0,LOOKUP(CO121,$G$34:$G$44,$S$34:$S$45))","v":0},{"$f":"0.03*CQ121","v":0},null,{"$f":"CM121+1","v":9},{"$f":"1*(LOOKUP(CW121,$K$17:$K$26,$L$17:$L$26)<>\"\")*(LOOKUP(CW121,$K$17:$K$26,$P$17:$P$26)>0)*(LOOKUP(CW121,$K$17:$K$26,$V$17:$V$26)=$G$55)","v":0},{"$f":"LOOKUP(CW121,$K$17:$K$26,$L$17:$L$26)","v":0},{"$f":"LOOKUP(CW121,$K$17:$K$26,$R$17:$R$26)","v":0},{"$f":"LOOKUP(CW121,$K$17:$K$26,$P$17:$P$26)","v":0},{"$f":"LOOKUP(DA121,$S$49:$S$62,$V$49:$V$62)","v":1},{"$f":"LOOKUP(CW121,$K$17:$K$26,$U$17:$U$26)","v":0},{"$f":"IF(OR(CY121=0,CY121=\"\"),0,LOOKUP(CY121,$G$34:$G$44,$S$34:$S$45))","v":0},{"$f":"0.03*DA121","v":0},null,{"$f":"CW121+1","v":10},{"$f":"1*(LOOKUP(DG121,$K$17:$K$26,$L$17:$L$26)<>\"\")*(LOOKUP(DG121,$K$17:$K$26,$P$17:$P$26)>0)*(LOOKUP(DG121,$K$17:$K$26,$V$17:$V$26)=$G$55)","v":0},{"$f":"LOOKUP(DG121,$K$17:$K$26,$L$17:$L$26)","v":0},{"$f":"LOOKUP(DG121,$K$17:$K$26,$R$17:$R$26)","v":0},{"$f":"LOOKUP(DG121,$K$17:$K$26,$P$17:$P$26)","v":0},{"$f":"LOOKUP(DK121,$S$49:$S$62,$V$49:$V$62)","v":1},{"$f":"LOOKUP(DG121,$K$17:$K$26,$U$17:$U$26)","v":0},{"$f":"IF(OR(DI121=0,DI121=\"\"),0,LOOKUP(DI121,$G$34:$G$44,$S$34:$S$45))","v":0},{"$f":"0.03*DK121","v":0}]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Demand",null,"System","VFD","Design Motor",null,null,"Base Motor",null,null,"Demand",null,"System","VFD","Design Motor",null,null,"Base Motor",null,null,"Demand",null,"System","VFD","Design Motor",null,null,"Base Motor",null,null,"Demand",null,"System","VFD","Design Motor",null,null,"Base Motor",null,null,"Demand",null,"System","VFD","Design Motor",null,null,"Base Motor",null,null,"Demand",null,"System","VFD","Design Motor",null,null,"Base Motor",null,null,"Demand",null,"System","VFD","Design Motor",null,null,"Base Motor",null,null,"Demand",null,"System","VFD","Design Motor",null,null,"Base Motor",null,null,"Demand",null,"System","VFD","Design Motor",null,null,"Base Motor",null,null,"Demand",null,"System","VFD","Design Motor",null,null,"Base Motor",null,null,"Demand"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Savings",null,"Flow","Speed","BHP","Eff","Pwr","BHP","Eff","Pwr","Savings",null,"Flow","Speed","BHP","Eff","Pwr","BHP","Eff","Pwr","Savings",null,"Flow","Speed","BHP","Eff","Pwr","BHP","Eff","Pwr","Savings",null,"Flow","Speed","BHP","Eff","Pwr","BHP","Eff","Pwr","Savings",null,"Flow","Speed","BHP","Eff","Pwr","BHP","Eff","Pwr","Savings",null,"Flow","Speed","BHP","Eff","Pwr","BHP","Eff","Pwr","Savings",null,"Flow","Speed","BHP","Eff","Pwr","BHP","Eff","Pwr","Savings",null,"Flow","Speed","BHP","Eff","Pwr","BHP","Eff","Pwr","Savings",null,"Flow","Speed","BHP","Eff","Pwr","BHP","Eff","Pwr","Savings",null,"Flow","Speed","BHP","Eff","Pwr","BHP","Eff","Pwr","Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","kW",null,"%","%","%","%","kW","%","%","kW","kW",null,"%","%","%","%","kW","%","%","kW","kW",null,"%","%","%","%","kW","%","%","kW","kW",null,"%","%","%","%","kW","%","%","kW","kW",null,"%","%","%","%","kW","%","%","kW","kW",null,"%","%","%","%","kW","%","%","kW","kW",null,"%","%","%","%","kW","%","%","kW","kW",null,"%","%","%","%","kW","%","%","kW","kW",null,"%","%","%","%","kW","%","%","kW","kW",null,"%","%","%","%","kW","%","%","kW","kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A44","v":100},{"$f":"'Project Info'!B44","v":105},{"$f":"'Project Info'!C44","v":102},{"$f":"'Project Info'!D44","v":76},{"$f":"'Project Info'!E44","v":40},{"$f":"'Project Info'!F44","v":0},{"$f":"'Project Info'!G44","v":0},{"$f":"'Project Info'!H44","v":0},{"$f":"'Project Info'!I44","v":0},{"$f":"'Project Info'!J44","v":0},{"$f":"'Project Info'!K44","v":0},{"$f":"'Project Info'!L44","v":0},{"$f":"AC125+AM125+AW125+BG125+BQ125+CA125+CK125+CU125+DE125+DO125","v":0},null,{"$f":"IF(OR(W$121=0,W$121=\"\"),0,OFFSET($J$182,MATCH(W$121,$J$183:$J$194,0),MATCH($I125,$K$182:$AH$182,-1)))","v":0},{"$f":"IF(U125<=0,0,MAX(U125,AA$121))","v":0},{"$f":"AB$121*V125+(1-AB$121)*V125^3","v":0},{"$f":"IF(W125=0,0,Z$121*TREND(OFFSET($K$216,MATCH(W125,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(W125,$K$217:$K$224,1),0,2,1),W125))","v":0},{"$f":"IF(W125=0,0,(W125*Y$121*0.746/X125+AC$121)*X$121)","v":0},{"$f":"V125","v":0},{"$f":"IF(Z125=0,0,Z$121*TREND(OFFSET($K$216,MATCH(Z125,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(Z125,$K$217:$K$224,1),0,2,1),Z125))","v":0},{"$f":"IF(Z125=0,0,Z125*Y$121*0.746/AA125*X$121)","v":0},{"$f":"AB125-Y125","v":0},null,{"$f":"IF(OR(AG$121=0,AG$121=\"\"),0,OFFSET($J$182,MATCH(AG$121,$J$183:$J$194,0),MATCH($I125,$K$182:$AH$182,-1)))","v":0},{"$f":"IF(AE125<=0,0,MAX(AE125,AK$121))","v":0},{"$f":"AL$121*AF125+(1-AL$121)*AF125^3","v":0},{"$f":"IF(AG125=0,0,AJ$121*TREND(OFFSET($K$216,MATCH(AG125,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(AG125,$K$217:$K$224,1),0,2,1),AG125))","v":0},{"$f":"IF(AG125=0,0,(AG125*AI$121*0.746/AH125+AM$121)*AH$121)","v":0},{"$f":"AF125","v":0},{"$f":"AJ$121","v":1},{"$f":"IF(AJ125=0,0,AJ125*AI$121*0.746/AK125*AH$121)","v":0},{"$f":"AL125-AI125","v":0},null,{"$f":"IF(OR(AQ$121=0,AQ$121=\"\"),0,OFFSET($J$182,MATCH(AQ$121,$J$183:$J$194,0),MATCH($I125,$K$182:$AH$182,-1)))","v":0},{"$f":"IF(AO125<=0,0,MAX(AO125,AU$121))","v":0},{"$f":"AV$121*AP125+(1-AV$121)*AP125^3","v":0},{"$f":"IF(AQ125=0,0,AT$121*TREND(OFFSET($K$216,MATCH(AQ125,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(AQ125,$K$217:$K$224,1),0,2,1),AQ125))","v":0},{"$f":"IF(AQ125=0,0,(AQ125*AS$121*0.746/AR125+AW$121)*AR$121)","v":0},{"$f":"AP125","v":0},{"$f":"IF(AT125=0,0,AT$121*TREND(OFFSET($K$216,MATCH(AT125,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(AT125,$K$217:$K$224,1),0,2,1),AT125))","v":0},{"$f":"IF(AT125=0,0,AT125*AS$121*0.746/AU125*AR$121)","v":0},{"$f":"AV125-AS125","v":0},null,{"$f":"IF(OR(BA$121=0,BA$121=\"\"),0,OFFSET($J$182,MATCH(BA$121,$J$183:$J$194,0),MATCH($I125,$K$182:$AH$182,-1)))","v":0},{"$f":"IF(AY125<=0,0,MAX(AY125,BE$121))","v":0},{"$f":"BF$121*AZ125+(1-BF$121)*AZ125^3","v":0},{"$f":"IF(BA125=0,0,BD$121*TREND(OFFSET($K$216,MATCH(BA125,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(BA125,$K$217:$K$224,1),0,2,1),BA125))","v":0},{"$f":"IF(BA125=0,0,(BA125*BC$121*0.746/BB125+BG$121)*BB$121)","v":0},{"$f":"AZ125","v":0},{"$f":"IF(BD125=0,0,BD$121*TREND(OFFSET($K$216,MATCH(BD125,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(BD125,$K$217:$K$224,1),0,2,1),BD125))","v":0},{"$f":"IF(BD125=0,0,BD125*BC$121*0.746/BE125*BB$121)","v":0},{"$f":"BF125-BC125","v":0},null,{"$f":"IF(OR(BK$121=0,BK$121=\"\"),0,OFFSET($J$182,MATCH(BK$121,$J$183:$J$194,0),MATCH($I125,$K$182:$AH$182,-1)))","v":0},{"$f":"IF(BI125<=0,0,MAX(BI125,BO$121))","v":0},{"$f":"BP$121*BJ125+(1-BP$121)*BJ125^3","v":0},{"$f":"IF(BK125=0,0,BN$121*TREND(OFFSET($K$216,MATCH(BK125,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(BK125,$K$217:$K$224,1),0,2,1),BK125))","v":0},{"$f":"IF(BK125=0,0,(BK125*BM$121*0.746/BL125+BQ$121)*BL$121)","v":0},{"$f":"BJ125","v":0},{"$f":"IF(BN125=0,0,BN$121*TREND(OFFSET($K$216,MATCH(BN125,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(BN125,$K$217:$K$224,1),0,2,1),BN125))","v":0},{"$f":"IF(BN125=0,0,BN125*BM$121*0.746/BO125*BL$121)","v":0},{"$f":"BP125-BM125","v":0},null,{"$f":"IF(OR(BU$121=0,BU$121=\"\"),0,OFFSET($J$182,MATCH(BU$121,$J$183:$J$194,0),MATCH($I125,$K$182:$AH$182,-1)))","v":0},{"$f":"IF(BS125<=0,0,MAX(BS125,BY$121))","v":0},{"$f":"BZ$121*BT125+(1-BZ$121)*BT125^3","v":0},{"$f":"IF(BU125=0,0,BX$121*TREND(OFFSET($K$216,MATCH(BU125,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(BU125,$K$217:$K$224,1),0,2,1),BU125))","v":0},{"$f":"IF(BU125=0,0,(BU125*BW$121*0.746/BV125+CA$121)*BV$121)","v":0},{"$f":"BT125","v":0},{"$f":"IF(BX125=0,0,BX$121*TREND(OFFSET($K$216,MATCH(BX125,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(BX125,$K$217:$K$224,1),0,2,1),BX125))","v":0},{"$f":"IF(BX125=0,0,BX125*BW$121*0.746/BY125*BV$121)","v":0},{"$f":"BZ125-BW125","v":0},null,{"$f":"IF(OR(CE$121=0,CE$121=\"\"),0,OFFSET($J$182,MATCH(CE$121,$J$183:$J$194,0),MATCH($I125,$K$182:$AH$182,-1)))","v":0},{"$f":"IF(CC125<=0,0,MAX(CC125,CI$121))","v":0},{"$f":"CJ$121*CD125+(1-CJ$121)*CD125^3","v":0},{"$f":"IF(CE125=0,0,CH$121*TREND(OFFSET($K$216,MATCH(CE125,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(CE125,$K$217:$K$224,1),0,2,1),CE125))","v":0},{"$f":"IF(CE125=0,0,(CE125*CG$121*0.746/CF125+CK$121)*CF$121)","v":0},{"$f":"CD125","v":0},{"$f":"IF(CH125=0,0,CH$121*TREND(OFFSET($K$216,MATCH(CH125,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(CH125,$K$217:$K$224,1),0,2,1),CH125))","v":0},{"$f":"IF(CH125=0,0,CH125*CG$121*0.746/CI125*CF$121)","v":0},{"$f":"CJ125-CG125","v":0},null,{"$f":"IF(OR(CO$121=0,CO$121=\"\"),0,OFFSET($J$182,MATCH(CO$121,$J$183:$J$194,0),MATCH($I125,$K$182:$AH$182,-1)))","v":0},{"$f":"IF(CM125<=0,0,MAX(CM125,CS$121))","v":0},{"$f":"CT$121*CN125+(1-CT$121)*CN125^3","v":0},{"$f":"IF(CO125=0,0,CR$121*TREND(OFFSET($K$216,MATCH(CO125,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(CO125,$K$217:$K$224,1),0,2,1),CO125))","v":0},{"$f":"IF(CO125=0,0,(CO125*CQ$121*0.746/CP125+CU$121)*CP$121)","v":0},{"$f":"CN125","v":0},{"$f":"IF(CR125=0,0,CR$121*TREND(OFFSET($K$216,MATCH(CR125,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(CR125,$K$217:$K$224,1),0,2,1),CR125))","v":0},{"$f":"IF(CR125=0,0,CR125*CQ$121*0.746/CS125*CP$121)","v":0},{"$f":"CT125-CQ125","v":0},null,{"$f":"IF(OR(CY$121=0,CY$121=\"\"),0,OFFSET($J$182,MATCH(CY$121,$J$183:$J$194,0),MATCH($I125,$K$182:$AH$182,-1)))","v":0},{"$f":"IF(CW125<=0,0,MAX(CW125,DC$121))","v":0},{"$f":"DD$121*CX125+(1-DD$121)*CX125^3","v":0},{"$f":"IF(CY125=0,0,DB$121*TREND(OFFSET($K$216,MATCH(CY125,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(CY125,$K$217:$K$224,1),0,2,1),CY125))","v":0},{"$f":"IF(CY125=0,0,(CY125*DA$121*0.746/CZ125+DE$121)*CZ$121)","v":0},{"$f":"CX125","v":0},{"$f":"IF(DB125=0,0,DB$121*TREND(OFFSET($K$216,MATCH(DB125,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(DB125,$K$217:$K$224,1),0,2,1),DB125))","v":0},{"$f":"IF(DB125=0,0,DB125*DA$121*0.746/DC125*CZ$121)","v":0},{"$f":"DD125-DA125","v":0},null,{"$f":"IF(OR(DI$121=0,DI$121=\"\"),0,OFFSET($J$182,MATCH(DI$121,$J$183:$J$194,0),MATCH($I125,$K$182:$AH$182,-1)))","v":0},{"$f":"IF(DG125<=0,0,MAX(DG125,DM$121))","v":0},{"$f":"DN$121*DH125+(1-DN$121)*DH125^3","v":0},{"$f":"IF(DI125=0,0,DL$121*TREND(OFFSET($K$216,MATCH(DI125,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(DI125,$K$217:$K$224,1),0,2,1),DI125))","v":0},{"$f":"IF(DI125=0,0,(DI125*DK$121*0.746/DJ125+DO$121)*DJ$121)","v":0},{"$f":"DH125","v":0},{"$f":"IF(DL125=0,0,DL$121*TREND(OFFSET($K$216,MATCH(DL125,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(DL125,$K$217:$K$224,1),0,2,1),DL125))","v":0},{"$f":"IF(DL125=0,0,DL125*DK$121*0.746/DM125*DJ$121)","v":0},{"$f":"DN125-DK125","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A45","v":95},{"$f":"'Project Info'!B45","v":100},{"$f":"'Project Info'!C45","v":95.219272727272724},{"$f":"'Project Info'!D45","v":74.534025272781079},{"$f":"'Project Info'!E45","v":37.923296058061368},{"$f":"'Project Info'!F45","v":0},{"$f":"'Project Info'!G45","v":0},{"$f":"'Project Info'!H45","v":0},{"$f":"'Project Info'!I45","v":0},{"$f":"'Project Info'!J45","v":0},{"$f":"'Project Info'!K45","v":0},{"$f":"'Project Info'!L45","v":0},{"$f":"AC126+AM126+AW126+BG126+BQ126+CA126+CK126+CU126+DE126+DO126","v":0},null,0,0,0,0,0,{"$f":"V126","v":0},0,0,{"$f":"AB126-Y126","v":0},null,0,0,0,0,0,{"$f":"AF126","v":0},1,0,{"$f":"AL126-AI126","v":0},null,0,0,0,0,0,{"$f":"AP126","v":0},0,0,{"$f":"AV126-AS126","v":0},null,0,0,0,0,0,{"$f":"AZ126","v":0},0,0,{"$f":"BF126-BC126","v":0},null,0,0,0,0,0,{"$f":"BJ126","v":0},0,0,{"$f":"BP126-BM126","v":0},null,0,0,0,0,0,{"$f":"BT126","v":0},0,0,{"$f":"BZ126-BW126","v":0},null,0,0,0,0,0,{"$f":"CD126","v":0},0,0,{"$f":"CJ126-CG126","v":0},null,0,0,0,0,0,{"$f":"CN126","v":0},0,0,{"$f":"CT126-CQ126","v":0},null,0,0,0,0,0,{"$f":"CX126","v":0},0,0,{"$f":"DD126-DA126","v":0},null,0,0,0,0,0,{"$f":"DH126","v":0},0,0,{"$f":"DN126-DK126","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A46","v":90},{"$f":"'Project Info'!B46","v":95},{"$f":"'Project Info'!C46","v":92.016049160256074},{"$f":"'Project Info'!D46","v":72.911561930607689},{"$f":"'Project Info'!E46","v":36.467095439351091},{"$f":"'Project Info'!F46","v":0},{"$f":"'Project Info'!G46","v":0},{"$f":"'Project Info'!H46","v":0},{"$f":"'Project Info'!I46","v":0},{"$f":"'Project Info'!J46","v":0},{"$f":"'Project Info'!K46","v":0},{"$f":"'Project Info'!L46","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,1,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A47","v":85},{"$f":"'Project Info'!B47","v":90},{"$f":"'Project Info'!C47","v":87.457811360655285},{"$f":"'Project Info'!D47","v":70.80538329449476},{"$f":"'Project Info'!E47","v":34.679413213566804},{"$f":"'Project Info'!F47","v":0},{"$f":"'Project Info'!G47","v":0},{"$f":"'Project Info'!H47","v":0},{"$f":"'Project Info'!I47","v":0},{"$f":"'Project Info'!J47","v":0},{"$f":"'Project Info'!K47","v":0},{"$f":"'Project Info'!L47","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,1,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A48","v":80},{"$f":"'Project Info'!B48","v":85},{"$f":"'Project Info'!C48","v":82.136788830239965},{"$f":"'Project Info'!D48","v":67.872393622439333},{"$f":"'Project Info'!E48","v":32.296248223809314},{"$f":"'Project Info'!F48","v":0},{"$f":"'Project Info'!G48","v":0},{"$f":"'Project Info'!H48","v":0},{"$f":"'Project Info'!I48","v":0},{"$f":"'Project Info'!J48","v":0},{"$f":"'Project Info'!K48","v":0},{"$f":"'Project Info'!L48","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,1,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A49","v":75},{"$f":"'Project Info'!B49","v":80},{"$f":"'Project Info'!C49","v":76.988400157585886},{"$f":"'Project Info'!D49","v":65.129261896908645},{"$f":"'Project Info'!E49","v":30.190476812806729},{"$f":"'Project Info'!F49","v":0},{"$f":"'Project Info'!G49","v":0},{"$f":"'Project Info'!H49","v":0},{"$f":"'Project Info'!I49","v":0},{"$f":"'Project Info'!J49","v":0},{"$f":"'Project Info'!K49","v":0},{"$f":"'Project Info'!L49","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,1,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A50","v":70},{"$f":"'Project Info'!B50","v":75},{"$f":"'Project Info'!C50","v":72.457982050814195},{"$f":"'Project Info'!D50","v":63.604425012889301},{"$f":"'Project Info'!E50","v":29.088683095945193},{"$f":"'Project Info'!F50","v":0},{"$f":"'Project Info'!G50","v":0},{"$f":"'Project Info'!H50","v":0},{"$f":"'Project Info'!I50","v":0},{"$f":"'Project Info'!J50","v":0},{"$f":"'Project Info'!K50","v":0},{"$f":"'Project Info'!L50","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,1,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A51","v":65},{"$f":"'Project Info'!B51","v":70},{"$f":"'Project Info'!C51","v":67.815831070966169},{"$f":"'Project Info'!D51","v":61.631331368130574},{"$f":"'Project Info'!E51","v":27.661514889731574},{"$f":"'Project Info'!F51","v":0},{"$f":"'Project Info'!G51","v":0},{"$f":"'Project Info'!H51","v":0},{"$f":"'Project Info'!I51","v":0},{"$f":"'Project Info'!J51","v":0},{"$f":"'Project Info'!K51","v":0},{"$f":"'Project Info'!L51","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,1,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A52","v":60},{"$f":"'Project Info'!B52","v":65},{"$f":"'Project Info'!C52","v":62.535961472271332},{"$f":"'Project Info'!D52","v":57.135476922863582},{"$f":"'Project Info'!E52","v":24.623037157728302},{"$f":"'Project Info'!F52","v":0},{"$f":"'Project Info'!G52","v":0},{"$f":"'Project Info'!H52","v":0},{"$f":"'Project Info'!I52","v":0},{"$f":"'Project Info'!J52","v":0},{"$f":"'Project Info'!K52","v":0},{"$f":"'Project Info'!L52","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,1,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A53","v":55},{"$f":"'Project Info'!B53","v":60},{"$f":"'Project Info'!C53","v":57.125792270740902},{"$f":"'Project Info'!D53","v":52.596971157053673},{"$f":"'Project Info'!E53","v":21.818001539159841},{"$f":"'Project Info'!F53","v":0},{"$f":"'Project Info'!G53","v":0},{"$f":"'Project Info'!H53","v":0},{"$f":"'Project Info'!I53","v":0},{"$f":"'Project Info'!J53","v":0},{"$f":"'Project Info'!K53","v":0},{"$f":"'Project Info'!L53","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,1,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A54","v":50},{"$f":"'Project Info'!B54","v":55},{"$f":"'Project Info'!C54","v":52.235698854337961},{"$f":"'Project Info'!D54","v":48.022768090099298},{"$f":"'Project Info'!E54","v":19.246640192796217},{"$f":"'Project Info'!F54","v":0},{"$f":"'Project Info'!G54","v":0},{"$f":"'Project Info'!H54","v":0},{"$f":"'Project Info'!I54","v":0},{"$f":"'Project Info'!J54","v":0},{"$f":"'Project Info'!K54","v":0},{"$f":"'Project Info'!L54","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,1,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A55","v":45},{"$f":"'Project Info'!B55","v":50},{"$f":"'Project Info'!C55","v":47.459170258371508},{"$f":"'Project Info'!D55","v":43.465397050422162},{"$f":"'Project Info'!E55","v":16.894183241713304},{"$f":"'Project Info'!F55","v":0},{"$f":"'Project Info'!G55","v":0},{"$f":"'Project Info'!H55","v":0},{"$f":"'Project Info'!I55","v":0},{"$f":"'Project Info'!J55","v":0},{"$f":"'Project Info'!K55","v":0},{"$f":"'Project Info'!L55","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,1,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A56","v":40},{"$f":"'Project Info'!B56","v":45},{"$f":"'Project Info'!C56","v":42.677030404888129},{"$f":"'Project Info'!D56","v":38.812544504634097},{"$f":"'Project Info'!E56","v":14.690265649465921},{"$f":"'Project Info'!F56","v":0},{"$f":"'Project Info'!G56","v":0},{"$f":"'Project Info'!H56","v":0},{"$f":"'Project Info'!I56","v":0},{"$f":"'Project Info'!J56","v":0},{"$f":"'Project Info'!K56","v":0},{"$f":"'Project Info'!L56","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,1,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A57","v":35},{"$f":"'Project Info'!B57","v":40},{"$f":"'Project Info'!C57","v":37.333046773755832},{"$f":"'Project Info'!D57","v":33.904706919479686},{"$f":"'Project Info'!E57","v":12.53841602318813},{"$f":"'Project Info'!F57","v":0},{"$f":"'Project Info'!G57","v":0},{"$f":"'Project Info'!H57","v":0},{"$f":"'Project Info'!I57","v":0},{"$f":"'Project Info'!J57","v":0},{"$f":"'Project Info'!K57","v":0},{"$f":"'Project Info'!L57","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,1,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A58","v":30},{"$f":"'Project Info'!B58","v":35},{"$f":"'Project Info'!C58","v":32.638179845662044},{"$f":"'Project Info'!D58","v":29.547170928664851},{"$f":"'Project Info'!E58","v":10.728972818165861},{"$f":"'Project Info'!F58","v":0},{"$f":"'Project Info'!G58","v":0},{"$f":"'Project Info'!H58","v":0},{"$f":"'Project Info'!I58","v":0},{"$f":"'Project Info'!J58","v":0},{"$f":"'Project Info'!K58","v":0},{"$f":"'Project Info'!L58","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,1,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A59","v":25},{"$f":"'Project Info'!B59","v":30},{"$f":"'Project Info'!C59","v":27.529264646850947},{"$f":"'Project Info'!D59","v":24.652717392657845},{"$f":"'Project Info'!E59","v":8.8041305482613303},{"$f":"'Project Info'!F59","v":0},{"$f":"'Project Info'!G59","v":0},{"$f":"'Project Info'!H59","v":0},{"$f":"'Project Info'!I59","v":0},{"$f":"'Project Info'!J59","v":0},{"$f":"'Project Info'!K59","v":0},{"$f":"'Project Info'!L59","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,1,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A60","v":20},{"$f":"'Project Info'!B60","v":25},{"$f":"'Project Info'!C60","v":22.998111483544687},{"$f":"'Project Info'!D60","v":20.383306659827422},{"$f":"'Project Info'!E60","v":7.246164547543378},{"$f":"'Project Info'!F60","v":0},{"$f":"'Project Info'!G60","v":0},{"$f":"'Project Info'!H60","v":0},{"$f":"'Project Info'!I60","v":0},{"$f":"'Project Info'!J60","v":0},{"$f":"'Project Info'!K60","v":0},{"$f":"'Project Info'!L60","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,1,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A61","v":15},{"$f":"'Project Info'!B61","v":20},{"$f":"'Project Info'!C61","v":17.808510327474309},{"$f":"'Project Info'!D61","v":15.420865796304254},{"$f":"'Project Info'!E61","v":5.5490484131518292},{"$f":"'Project Info'!F61","v":0},{"$f":"'Project Info'!G61","v":0},{"$f":"'Project Info'!H61","v":0},{"$f":"'Project Info'!I61","v":0},{"$f":"'Project Info'!J61","v":0},{"$f":"'Project Info'!K61","v":0},{"$f":"'Project Info'!L61","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,1,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A62","v":10},{"$f":"'Project Info'!B62","v":15},{"$f":"'Project Info'!C62","v":12.269931130346862},{"$f":"'Project Info'!D62","v":10.318264913023604},{"$f":"'Project Info'!E62","v":3.9082824916941998},{"$f":"'Project Info'!F62","v":0},{"$f":"'Project Info'!G62","v":0},{"$f":"'Project Info'!H62","v":0},{"$f":"'Project Info'!I62","v":0},{"$f":"'Project Info'!J62","v":0},{"$f":"'Project Info'!K62","v":0},{"$f":"'Project Info'!L62","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,1,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A63","v":5},{"$f":"'Project Info'!B63","v":10},{"$f":"'Project Info'!C63","v":7.3137581369917548},{"$f":"'Project Info'!D63","v":5.7052382449247707},{"$f":"'Project Info'!E63","v":2.5019418419888937},{"$f":"'Project Info'!F63","v":0},{"$f":"'Project Info'!G63","v":0},{"$f":"'Project Info'!H63","v":0},{"$f":"'Project Info'!I63","v":0},{"$f":"'Project Info'!J63","v":0},{"$f":"'Project Info'!K63","v":0},{"$f":"'Project Info'!L63","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,1,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A64","v":0},{"$f":"'Project Info'!B64","v":5},{"$f":"'Project Info'!C64","v":2.6119461836144886},{"$f":"'Project Info'!D64","v":1.2699770062067783},{"$f":"'Project Info'!E64","v":1.2046477897733283},{"$f":"'Project Info'!F64","v":0},{"$f":"'Project Info'!G64","v":0},{"$f":"'Project Info'!H64","v":0},{"$f":"'Project Info'!I64","v":0},{"$f":"'Project Info'!J64","v":0},{"$f":"'Project Info'!K64","v":0},{"$f":"'Project Info'!L64","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,1,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A65","v":-5},{"$f":"'Project Info'!B65","v":0},{"$f":"'Project Info'!C65","v":-1.6731398516793925},{"$f":"'Project Info'!D65","v":-2.7083318773557807},{"$f":"'Project Info'!E65","v":7.9391832815876459E-2},{"$f":"'Project Info'!F65","v":0},{"$f":"'Project Info'!G65","v":0},{"$f":"'Project Info'!H65","v":0},{"$f":"'Project Info'!I65","v":0},{"$f":"'Project Info'!J65","v":0},{"$f":"'Project Info'!K65","v":0},{"$f":"'Project Info'!L65","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,1,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A66","v":-10},{"$f":"'Project Info'!B66","v":-5},{"$f":"'Project Info'!C66","v":-6.5729865085377277},{"$f":"'Project Info'!D66","v":-7.2465935998252222},{"$f":"'Project Info'!E66","v":-1.168423365310433},{"$f":"'Project Info'!F66","v":0},{"$f":"'Project Info'!G66","v":0},{"$f":"'Project Info'!H66","v":0},{"$f":"'Project Info'!I66","v":0},{"$f":"'Project Info'!J66","v":0},{"$f":"'Project Info'!K66","v":0},{"$f":"'Project Info'!L66","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,1,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A67","v":-15},{"$f":"'Project Info'!B67","v":-10},{"$f":"'Project Info'!C67","v":-15.32570353422995},{"$f":"'Project Info'!D67","v":-15.707838211108999},{"$f":"'Project Info'!E67","v":-3.4051318156661381},{"$f":"'Project Info'!F67","v":0},{"$f":"'Project Info'!G67","v":0},{"$f":"'Project Info'!H67","v":0},{"$f":"'Project Info'!I67","v":0},{"$f":"'Project Info'!J67","v":0},{"$f":"'Project Info'!K67","v":0},{"$f":"'Project Info'!L67","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,1,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[]
[]
[null,null,null,null,null,null,"Unoccupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown",null,null,null,null,null,null,"Total"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Demand",null,"System","VFD","Design Motor",null,null,"Base Motor",null,null,"Demand",null,"System","VFD","Design Motor",null,null,"Base Motor",null,null,"Demand",null,"System","VFD","Design Motor",null,null,"Base Motor",null,null,"Demand",null,"System","VFD","Design Motor",null,null,"Base Motor",null,null,"Demand",null,"System","VFD","Design Motor",null,null,"Base Motor",null,null,"Demand",null,"System","VFD","Design Motor",null,null,"Base Motor",null,null,"Demand",null,"System","VFD","Design Motor",null,null,"Base Motor",null,null,"Demand",null,"System","VFD","Design Motor",null,null,"Base Motor",null,null,"Demand",null,"System","VFD","Design Motor",null,null,"Base Motor",null,null,"Demand",null,"System","VFD","Design Motor",null,null,"Base Motor",null,null,"Demand"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Savings",null,"Flow","Speed","BHP","Eff","Pwr","BHP","Eff","Pwr","Savings",null,"Flow","Speed","BHP","Eff","Pwr","BHP","Eff","Pwr","Savings",null,"Flow","Speed","BHP","Eff","Pwr","BHP","Eff","Pwr","Savings",null,"Flow","Speed","BHP","Eff","Pwr","BHP","Eff","Pwr","Savings",null,"Flow","Speed","BHP","Eff","Pwr","BHP","Eff","Pwr","Savings",null,"Flow","Speed","BHP","Eff","Pwr","BHP","Eff","Pwr","Savings",null,"Flow","Speed","BHP","Eff","Pwr","BHP","Eff","Pwr","Savings",null,"Flow","Speed","BHP","Eff","Pwr","BHP","Eff","Pwr","Savings",null,"Flow","Speed","BHP","Eff","Pwr","BHP","Eff","Pwr","Savings",null,"Flow","Speed","BHP","Eff","Pwr","BHP","Eff","Pwr","Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","kW",null,"%","%","%","%","kW","%","%","kW","kW",null,"%","%","%","%","kW","%","%","kW","kW",null,"%","%","%","%","kW","%","%","kW","kW",null,"%","%","%","%","kW","%","%","kW","kW",null,"%","%","%","%","kW","%","%","kW","kW",null,"%","%","%","%","kW","%","%","kW","kW",null,"%","%","%","%","kW","%","%","kW","kW",null,"%","%","%","%","kW","%","%","kW","kW",null,"%","%","%","%","kW","%","%","kW","kW",null,"%","%","%","%","kW","%","%","kW","kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A74","v":100},{"$f":"'Project Info'!B74","v":105},{"$f":"'Project Info'!C74","v":102},{"$f":"'Project Info'!D74","v":76},{"$f":"'Project Info'!E74","v":40},{"$f":"'Project Info'!F74","v":0},{"$f":"'Project Info'!G74","v":0},{"$f":"'Project Info'!H74","v":0},{"$f":"'Project Info'!I74","v":0},{"$f":"'Project Info'!J74","v":0},{"$f":"'Project Info'!K74","v":0},{"$f":"'Project Info'!L74","v":0},{"$f":"AC155+AM155+AW155+BG155+BQ155+CA155+CK155+CU155+DE155+DO155","v":0},null,{"$f":"IF(OR(W$121=0,W$121=\"\"),0,OFFSET($J$197,MATCH(W$121,$J$198:$J$209,0),MATCH($I155,$K$197:$AH$197,-1)))","v":0},{"$f":"IF(U155<=0,0,MAX(U155,AA$121))","v":0},{"$f":"AB$121*V155+(1-AB$121)*V155^3","v":0},{"$f":"IF(W155=0,0,Z$121*TREND(OFFSET($K$216,MATCH(W155,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(W155,$K$217:$K$224,1),0,2,1),W155))","v":0},{"$f":"IF(W155=0,0,(W155*Y$121*0.746/X155+AC$121)*X$121)","v":0},{"$f":"V155","v":0},{"$f":"IF(Z155=0,0,Z$121*TREND(OFFSET($K$216,MATCH(Z155,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(Z155,$K$217:$K$224,1),0,2,1),Z155))","v":0},{"$f":"IF(Z155=0,0,Z155*Y$121*0.746/AA155*X$121)","v":0},{"$f":"AB155-Y155","v":0},null,{"$f":"IF(OR(AG$121=0,AG$121=\"\"),0,OFFSET($J$197,MATCH(AG$121,$J$198:$J$209,0),MATCH($I155,$K$197:$AH$197,-1)))","v":0},{"$f":"IF(AE155<=0,0,MAX(AE155,AK$121))","v":0},{"$f":"AL$121*AF155+(1-AL$121)*AF155^3","v":0},{"$f":"IF(AG155=0,0,AJ$121*TREND(OFFSET($K$216,MATCH(AG155,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(AG155,$K$217:$K$224,1),0,2,1),AG155))","v":0},{"$f":"IF(AG155=0,0,(AG155*AI$121*0.746/AH155+AM$121)*AH$121)","v":0},{"$f":"AF155","v":0},{"$f":"IF(AJ155=0,0,AJ$121*TREND(OFFSET($K$216,MATCH(AJ155,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(AJ155,$K$217:$K$224,1),0,2,1),AJ155))","v":0},{"$f":"IF(AJ155=0,0,AJ155*AI$121*0.746/AK155*AH$121)","v":0},{"$f":"AL155-AI155","v":0},null,{"$f":"IF(OR(AQ$121=0,AQ$121=\"\"),0,OFFSET($J$197,MATCH(AQ$121,$J$198:$J$209,0),MATCH($I155,$K$197:$AH$197,-1)))","v":0},{"$f":"IF(AO155<=0,0,MAX(AO155,AU$121))","v":0},{"$f":"AV$121*AP155+(1-AV$121)*AP155^3","v":0},{"$f":"IF(AQ155=0,0,AT$121*TREND(OFFSET($K$216,MATCH(AQ155,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(AQ155,$K$217:$K$224,1),0,2,1),AQ155))","v":0},{"$f":"IF(AQ155=0,0,(AQ155*AS$121*0.746/AR155+AW$121)*AR$121)","v":0},{"$f":"AP155","v":0},{"$f":"IF(AT155=0,0,AT$121*TREND(OFFSET($K$216,MATCH(AT155,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(AT155,$K$217:$K$224,1),0,2,1),AT155))","v":0},{"$f":"IF(AT155=0,0,AT155*AS$121*0.746/AU155*AR$121)","v":0},{"$f":"AV155-AS155","v":0},null,{"$f":"IF(OR(BA$121=0,BA$121=\"\"),0,OFFSET($J$197,MATCH(BA$121,$J$198:$J$209,0),MATCH($I155,$K$197:$AH$197,-1)))","v":0},{"$f":"IF(AY155<=0,0,MAX(AY155,BE$121))","v":0},{"$f":"BF$121*AZ155+(1-BF$121)*AZ155^3","v":0},{"$f":"IF(BA155=0,0,BD$121*TREND(OFFSET($K$216,MATCH(BA155,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(BA155,$K$217:$K$224,1),0,2,1),BA155))","v":0},{"$f":"IF(BA155=0,0,(BA155*BC$121*0.746/BB155+BG$121)*BB$121)","v":0},{"$f":"AZ155","v":0},{"$f":"IF(BD155=0,0,BD$121*TREND(OFFSET($K$216,MATCH(BD155,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(BD155,$K$217:$K$224,1),0,2,1),BD155))","v":0},{"$f":"IF(BD155=0,0,BD155*BC$121*0.746/BE155*BB$121)","v":0},{"$f":"BF155-BC155","v":0},null,{"$f":"IF(OR(BK$121=0,BK$121=\"\"),0,OFFSET($J$197,MATCH(BK$121,$J$198:$J$209,0),MATCH($I155,$K$197:$AH$197,-1)))","v":0},{"$f":"IF(BI155<=0,0,MAX(BI155,BO$121))","v":0},{"$f":"BP$121*BJ155+(1-BP$121)*BJ155^3","v":0},{"$f":"IF(BK155=0,0,BN$121*TREND(OFFSET($K$216,MATCH(BK155,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(BK155,$K$217:$K$224,1),0,2,1),BK155))","v":0},{"$f":"IF(BK155=0,0,(BK155*BM$121*0.746/BL155+BQ$121)*BL$121)","v":0},{"$f":"BJ155","v":0},{"$f":"IF(BN155=0,0,BN$121*TREND(OFFSET($K$216,MATCH(BN155,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(BN155,$K$217:$K$224,1),0,2,1),BN155))","v":0},{"$f":"IF(BN155=0,0,BN155*BM$121*0.746/BO155*BL$121)","v":0},{"$f":"BP155-BM155","v":0},null,{"$f":"IF(OR(BU$121=0,BU$121=\"\"),0,OFFSET($J$197,MATCH(BU$121,$J$198:$J$209,0),MATCH($I155,$K$197:$AH$197,-1)))","v":0},{"$f":"IF(BS155<=0,0,MAX(BS155,BY$121))","v":0},{"$f":"BZ$121*BT155+(1-BZ$121)*BT155^3","v":0},{"$f":"IF(BU155=0,0,BX$121*TREND(OFFSET($K$216,MATCH(BU155,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(BU155,$K$217:$K$224,1),0,2,1),BU155))","v":0},{"$f":"IF(BU155=0,0,(BU155*BW$121*0.746/BV155+CA$121)*BV$121)","v":0},{"$f":"BT155","v":0},{"$f":"IF(BX155=0,0,BX$121*TREND(OFFSET($K$216,MATCH(BX155,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(BX155,$K$217:$K$224,1),0,2,1),BX155))","v":0},{"$f":"IF(BX155=0,0,BX155*BW$121*0.746/BY155*BV$121)","v":0},{"$f":"BZ155-BW155","v":0},null,{"$f":"IF(OR(CE$121=0,CE$121=\"\"),0,OFFSET($J$197,MATCH(CE$121,$J$198:$J$209,0),MATCH($I155,$K$197:$AH$197,-1)))","v":0},{"$f":"IF(CC155<=0,0,MAX(CC155,CI$121))","v":0},{"$f":"CJ$121*CD155+(1-CJ$121)*CD155^3","v":0},{"$f":"IF(CE155=0,0,CH$121*TREND(OFFSET($K$216,MATCH(CE155,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(CE155,$K$217:$K$224,1),0,2,1),CE155))","v":0},{"$f":"IF(CE155=0,0,(CE155*CG$121*0.746/CF155+CK$121)*CF$121)","v":0},{"$f":"CD155","v":0},{"$f":"IF(CH155=0,0,CH$121*TREND(OFFSET($K$216,MATCH(CH155,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(CH155,$K$217:$K$224,1),0,2,1),CH155))","v":0},{"$f":"IF(CH155=0,0,CH155*CG$121*0.746/CI155*CF$121)","v":0},{"$f":"CJ155-CG155","v":0},null,{"$f":"IF(OR(CO$121=0,CO$121=\"\"),0,OFFSET($J$197,MATCH(CO$121,$J$198:$J$209,0),MATCH($I155,$K$197:$AH$197,-1)))","v":0},{"$f":"IF(CM155<=0,0,MAX(CM155,CS$121))","v":0},{"$f":"CT$121*CN155+(1-CT$121)*CN155^3","v":0},{"$f":"IF(CO155=0,0,CR$121*TREND(OFFSET($K$216,MATCH(CO155,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(CO155,$K$217:$K$224,1),0,2,1),CO155))","v":0},{"$f":"IF(CO155=0,0,(CO155*CQ$121*0.746/CP155+CU$121)*CP$121)","v":0},{"$f":"CN155","v":0},{"$f":"IF(CR155=0,0,CR$121*TREND(OFFSET($K$216,MATCH(CR155,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(CR155,$K$217:$K$224,1),0,2,1),CR155))","v":0},{"$f":"IF(CR155=0,0,CR155*CQ$121*0.746/CS155*CP$121)","v":0},{"$f":"CT155-CQ155","v":0},null,{"$f":"IF(OR(CY$121=0,CY$121=\"\"),0,OFFSET($J$197,MATCH(CY$121,$J$198:$J$209,0),MATCH($I155,$K$197:$AH$197,-1)))","v":0},{"$f":"IF(CW155<=0,0,MAX(CW155,DC$121))","v":0},{"$f":"DD$121*CX155+(1-DD$121)*CX155^3","v":0},{"$f":"IF(CY155=0,0,DB$121*TREND(OFFSET($K$216,MATCH(CY155,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(CY155,$K$217:$K$224,1),0,2,1),CY155))","v":0},{"$f":"IF(CY155=0,0,(CY155*DA$121*0.746/CZ155+DE$121)*CZ$121)","v":0},{"$f":"CX155","v":0},{"$f":"IF(DB155=0,0,DB$121*TREND(OFFSET($K$216,MATCH(DB155,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(DB155,$K$217:$K$224,1),0,2,1),DB155))","v":0},{"$f":"IF(DB155=0,0,DB155*DA$121*0.746/DC155*CZ$121)","v":0},{"$f":"DD155-DA155","v":0},null,{"$f":"IF(OR(DI$121=0,DI$121=\"\"),0,OFFSET($J$197,MATCH(DI$121,$J$198:$J$209,0),MATCH($I155,$K$197:$AH$197,-1)))","v":0},{"$f":"IF(DG155<=0,0,MAX(DG155,DM$121))","v":0},{"$f":"DN$121*DH155+(1-DN$121)*DH155^3","v":0},{"$f":"IF(DI155=0,0,DL$121*TREND(OFFSET($K$216,MATCH(DI155,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(DI155,$K$217:$K$224,1),0,2,1),DI155))","v":0},{"$f":"IF(DI155=0,0,(DI155*DK$121*0.746/DJ155+DO$121)*DJ$121)","v":0},{"$f":"DH155","v":0},{"$f":"IF(DL155=0,0,DL$121*TREND(OFFSET($K$216,MATCH(DL155,$K$217:$K$224,1),1,2,1),OFFSET($K$216,MATCH(DL155,$K$217:$K$224,1),0,2,1),DL155))","v":0},{"$f":"IF(DL155=0,0,DL155*DK$121*0.746/DM155*DJ$121)","v":0},{"$f":"DN155-DK155","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A75","v":95},{"$f":"'Project Info'!B75","v":100},{"$f":"'Project Info'!C75","v":95.219272727272724},{"$f":"'Project Info'!D75","v":74.534025272781079},{"$f":"'Project Info'!E75","v":37.923296058061368},{"$f":"'Project Info'!F75","v":0},{"$f":"'Project Info'!G75","v":0},{"$f":"'Project Info'!H75","v":0},{"$f":"'Project Info'!I75","v":0},{"$f":"'Project Info'!J75","v":0},{"$f":"'Project Info'!K75","v":0},{"$f":"'Project Info'!L75","v":0},{"$f":"AC156+AM156+AW156+BG156+BQ156+CA156+CK156+CU156+DE156+DO156","v":0},null,0,0,0,0,0,{"$f":"V156","v":0},0,0,{"$f":"AB156-Y156","v":0},null,0,0,0,0,0,{"$f":"AF156","v":0},0,0,{"$f":"AL156-AI156","v":0},null,0,0,0,0,0,{"$f":"AP156","v":0},0,0,{"$f":"AV156-AS156","v":0},null,0,0,0,0,0,{"$f":"AZ156","v":0},0,0,{"$f":"BF156-BC156","v":0},null,0,0,0,0,0,{"$f":"BJ156","v":0},0,0,{"$f":"BP156-BM156","v":0},null,0,0,0,0,0,{"$f":"BT156","v":0},0,0,{"$f":"BZ156-BW156","v":0},null,0,0,0,0,0,{"$f":"CD156","v":0},0,0,{"$f":"CJ156-CG156","v":0},null,0,0,0,0,0,{"$f":"CN156","v":0},0,0,{"$f":"CT156-CQ156","v":0},null,0,0,0,0,0,{"$f":"CX156","v":0},0,0,{"$f":"DD156-DA156","v":0},null,0,0,0,0,0,{"$f":"DH156","v":0},0,0,{"$f":"DN156-DK156","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A76","v":90},{"$f":"'Project Info'!B76","v":95},{"$f":"'Project Info'!C76","v":92.016049160256074},{"$f":"'Project Info'!D76","v":72.911561930607689},{"$f":"'Project Info'!E76","v":36.467095439351091},{"$f":"'Project Info'!F76","v":0},{"$f":"'Project Info'!G76","v":0},{"$f":"'Project Info'!H76","v":0},{"$f":"'Project Info'!I76","v":0},{"$f":"'Project Info'!J76","v":0},{"$f":"'Project Info'!K76","v":0},{"$f":"'Project Info'!L76","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A77","v":85},{"$f":"'Project Info'!B77","v":90},{"$f":"'Project Info'!C77","v":87.457811360655285},{"$f":"'Project Info'!D77","v":70.80538329449476},{"$f":"'Project Info'!E77","v":34.679413213566804},{"$f":"'Project Info'!F77","v":0},{"$f":"'Project Info'!G77","v":0},{"$f":"'Project Info'!H77","v":0},{"$f":"'Project Info'!I77","v":0},{"$f":"'Project Info'!J77","v":0},{"$f":"'Project Info'!K77","v":0},{"$f":"'Project Info'!L77","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A78","v":80},{"$f":"'Project Info'!B78","v":85},{"$f":"'Project Info'!C78","v":82.136788830239965},{"$f":"'Project Info'!D78","v":67.872393622439333},{"$f":"'Project Info'!E78","v":32.296248223809314},{"$f":"'Project Info'!F78","v":0},{"$f":"'Project Info'!G78","v":0},{"$f":"'Project Info'!H78","v":0},{"$f":"'Project Info'!I78","v":0},{"$f":"'Project Info'!J78","v":0},{"$f":"'Project Info'!K78","v":0},{"$f":"'Project Info'!L78","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A79","v":75},{"$f":"'Project Info'!B79","v":80},{"$f":"'Project Info'!C79","v":76.988400157585886},{"$f":"'Project Info'!D79","v":65.129261896908645},{"$f":"'Project Info'!E79","v":30.190476812806729},{"$f":"'Project Info'!F79","v":0},{"$f":"'Project Info'!G79","v":0},{"$f":"'Project Info'!H79","v":0},{"$f":"'Project Info'!I79","v":0},{"$f":"'Project Info'!J79","v":0},{"$f":"'Project Info'!K79","v":0},{"$f":"'Project Info'!L79","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A80","v":70},{"$f":"'Project Info'!B80","v":75},{"$f":"'Project Info'!C80","v":72.457982050814195},{"$f":"'Project Info'!D80","v":63.604425012889301},{"$f":"'Project Info'!E80","v":29.088683095945193},{"$f":"'Project Info'!F80","v":0},{"$f":"'Project Info'!G80","v":0},{"$f":"'Project Info'!H80","v":0},{"$f":"'Project Info'!I80","v":0},{"$f":"'Project Info'!J80","v":0},{"$f":"'Project Info'!K80","v":0},{"$f":"'Project Info'!L80","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A81","v":65},{"$f":"'Project Info'!B81","v":70},{"$f":"'Project Info'!C81","v":67.815831070966169},{"$f":"'Project Info'!D81","v":61.631331368130574},{"$f":"'Project Info'!E81","v":27.661514889731574},{"$f":"'Project Info'!F81","v":0},{"$f":"'Project Info'!G81","v":0},{"$f":"'Project Info'!H81","v":0},{"$f":"'Project Info'!I81","v":0},{"$f":"'Project Info'!J81","v":0},{"$f":"'Project Info'!K81","v":0},{"$f":"'Project Info'!L81","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A82","v":60},{"$f":"'Project Info'!B82","v":65},{"$f":"'Project Info'!C82","v":62.535961472271332},{"$f":"'Project Info'!D82","v":57.135476922863582},{"$f":"'Project Info'!E82","v":24.623037157728302},{"$f":"'Project Info'!F82","v":0},{"$f":"'Project Info'!G82","v":0},{"$f":"'Project Info'!H82","v":0},{"$f":"'Project Info'!I82","v":0},{"$f":"'Project Info'!J82","v":0},{"$f":"'Project Info'!K82","v":0},{"$f":"'Project Info'!L82","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A83","v":55},{"$f":"'Project Info'!B83","v":60},{"$f":"'Project Info'!C83","v":57.125792270740902},{"$f":"'Project Info'!D83","v":52.596971157053673},{"$f":"'Project Info'!E83","v":21.818001539159841},{"$f":"'Project Info'!F83","v":0},{"$f":"'Project Info'!G83","v":0},{"$f":"'Project Info'!H83","v":0},{"$f":"'Project Info'!I83","v":0},{"$f":"'Project Info'!J83","v":0},{"$f":"'Project Info'!K83","v":0},{"$f":"'Project Info'!L83","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A84","v":50},{"$f":"'Project Info'!B84","v":55},{"$f":"'Project Info'!C84","v":52.235698854337961},{"$f":"'Project Info'!D84","v":48.022768090099298},{"$f":"'Project Info'!E84","v":19.246640192796217},{"$f":"'Project Info'!F84","v":0},{"$f":"'Project Info'!G84","v":0},{"$f":"'Project Info'!H84","v":0},{"$f":"'Project Info'!I84","v":0},{"$f":"'Project Info'!J84","v":0},{"$f":"'Project Info'!K84","v":0},{"$f":"'Project Info'!L84","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A85","v":45},{"$f":"'Project Info'!B85","v":50},{"$f":"'Project Info'!C85","v":47.459170258371508},{"$f":"'Project Info'!D85","v":43.465397050422162},{"$f":"'Project Info'!E85","v":16.894183241713304},{"$f":"'Project Info'!F85","v":0},{"$f":"'Project Info'!G85","v":0},{"$f":"'Project Info'!H85","v":0},{"$f":"'Project Info'!I85","v":0},{"$f":"'Project Info'!J85","v":0},{"$f":"'Project Info'!K85","v":0},{"$f":"'Project Info'!L85","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A86","v":40},{"$f":"'Project Info'!B86","v":45},{"$f":"'Project Info'!C86","v":42.677030404888129},{"$f":"'Project Info'!D86","v":38.812544504634097},{"$f":"'Project Info'!E86","v":14.690265649465921},{"$f":"'Project Info'!F86","v":0},{"$f":"'Project Info'!G86","v":0},{"$f":"'Project Info'!H86","v":0},{"$f":"'Project Info'!I86","v":0},{"$f":"'Project Info'!J86","v":0},{"$f":"'Project Info'!K86","v":0},{"$f":"'Project Info'!L86","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A87","v":35},{"$f":"'Project Info'!B87","v":40},{"$f":"'Project Info'!C87","v":37.333046773755832},{"$f":"'Project Info'!D87","v":33.904706919479686},{"$f":"'Project Info'!E87","v":12.53841602318813},{"$f":"'Project Info'!F87","v":0},{"$f":"'Project Info'!G87","v":0},{"$f":"'Project Info'!H87","v":0},{"$f":"'Project Info'!I87","v":0},{"$f":"'Project Info'!J87","v":0},{"$f":"'Project Info'!K87","v":0},{"$f":"'Project Info'!L87","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A88","v":30},{"$f":"'Project Info'!B88","v":35},{"$f":"'Project Info'!C88","v":32.638179845662044},{"$f":"'Project Info'!D88","v":29.547170928664851},{"$f":"'Project Info'!E88","v":10.728972818165861},{"$f":"'Project Info'!F88","v":0},{"$f":"'Project Info'!G88","v":0},{"$f":"'Project Info'!H88","v":0},{"$f":"'Project Info'!I88","v":0},{"$f":"'Project Info'!J88","v":0},{"$f":"'Project Info'!K88","v":0},{"$f":"'Project Info'!L88","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A89","v":25},{"$f":"'Project Info'!B89","v":30},{"$f":"'Project Info'!C89","v":27.529264646850947},{"$f":"'Project Info'!D89","v":24.652717392657845},{"$f":"'Project Info'!E89","v":8.8041305482613303},{"$f":"'Project Info'!F89","v":0},{"$f":"'Project Info'!G89","v":0},{"$f":"'Project Info'!H89","v":0},{"$f":"'Project Info'!I89","v":0},{"$f":"'Project Info'!J89","v":0},{"$f":"'Project Info'!K89","v":0},{"$f":"'Project Info'!L89","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A90","v":20},{"$f":"'Project Info'!B90","v":25},{"$f":"'Project Info'!C90","v":22.998111483544687},{"$f":"'Project Info'!D90","v":20.383306659827422},{"$f":"'Project Info'!E90","v":7.246164547543378},{"$f":"'Project Info'!F90","v":0},{"$f":"'Project Info'!G90","v":0},{"$f":"'Project Info'!H90","v":0},{"$f":"'Project Info'!I90","v":0},{"$f":"'Project Info'!J90","v":0},{"$f":"'Project Info'!K90","v":0},{"$f":"'Project Info'!L90","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A91","v":15},{"$f":"'Project Info'!B91","v":20},{"$f":"'Project Info'!C91","v":17.808510327474309},{"$f":"'Project Info'!D91","v":15.420865796304254},{"$f":"'Project Info'!E91","v":5.5490484131518292},{"$f":"'Project Info'!F91","v":0},{"$f":"'Project Info'!G91","v":0},{"$f":"'Project Info'!H91","v":0},{"$f":"'Project Info'!I91","v":0},{"$f":"'Project Info'!J91","v":0},{"$f":"'Project Info'!K91","v":0},{"$f":"'Project Info'!L91","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A92","v":10},{"$f":"'Project Info'!B92","v":15},{"$f":"'Project Info'!C92","v":12.269931130346862},{"$f":"'Project Info'!D92","v":10.318264913023604},{"$f":"'Project Info'!E92","v":3.9082824916941998},{"$f":"'Project Info'!F92","v":0},{"$f":"'Project Info'!G92","v":0},{"$f":"'Project Info'!H92","v":0},{"$f":"'Project Info'!I92","v":0},{"$f":"'Project Info'!J92","v":0},{"$f":"'Project Info'!K92","v":0},{"$f":"'Project Info'!L92","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A93","v":5},{"$f":"'Project Info'!B93","v":10},{"$f":"'Project Info'!C93","v":7.3137581369917548},{"$f":"'Project Info'!D93","v":5.7052382449247707},{"$f":"'Project Info'!E93","v":2.5019418419888937},{"$f":"'Project Info'!F93","v":0},{"$f":"'Project Info'!G93","v":0},{"$f":"'Project Info'!H93","v":0},{"$f":"'Project Info'!I93","v":0},{"$f":"'Project Info'!J93","v":0},{"$f":"'Project Info'!K93","v":0},{"$f":"'Project Info'!L93","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A94","v":0},{"$f":"'Project Info'!B94","v":5},{"$f":"'Project Info'!C94","v":2.6119461836144886},{"$f":"'Project Info'!D94","v":1.2699770062067783},{"$f":"'Project Info'!E94","v":1.2046477897733283},{"$f":"'Project Info'!F94","v":8760},{"$f":"'Project Info'!G94","v":2672},{"$f":"'Project Info'!H94","v":3160},{"$f":"'Project Info'!I94","v":1344},{"$f":"'Project Info'!J94","v":1584},{"$f":"'Project Info'!K94","v":88},{"$f":"'Project Info'!L94","v":264},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A95","v":-5},{"$f":"'Project Info'!B95","v":0},{"$f":"'Project Info'!C95","v":-1.6731398516793925},{"$f":"'Project Info'!D95","v":-2.7083318773557807},{"$f":"'Project Info'!E95","v":7.9391832815876459E-2},{"$f":"'Project Info'!F95","v":0},{"$f":"'Project Info'!G95","v":0},{"$f":"'Project Info'!H95","v":0},{"$f":"'Project Info'!I95","v":0},{"$f":"'Project Info'!J95","v":0},{"$f":"'Project Info'!K95","v":0},{"$f":"'Project Info'!L95","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A96","v":-10},{"$f":"'Project Info'!B96","v":-5},{"$f":"'Project Info'!C96","v":-6.5729865085377277},{"$f":"'Project Info'!D96","v":-7.2465935998252222},{"$f":"'Project Info'!E96","v":-1.168423365310433},{"$f":"'Project Info'!F96","v":0},{"$f":"'Project Info'!G96","v":0},{"$f":"'Project Info'!H96","v":0},{"$f":"'Project Info'!I96","v":0},{"$f":"'Project Info'!J96","v":0},{"$f":"'Project Info'!K96","v":0},{"$f":"'Project Info'!L96","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A97","v":-15},{"$f":"'Project Info'!B97","v":-10},{"$f":"'Project Info'!C97","v":-15.32570353422995},{"$f":"'Project Info'!D97","v":-15.707838211108999},{"$f":"'Project Info'!E97","v":-3.4051318156661381},{"$f":"'Project Info'!F97","v":0},{"$f":"'Project Info'!G97","v":0},{"$f":"'Project Info'!H97","v":0},{"$f":"'Project Info'!I97","v":0},{"$f":"'Project Info'!J97","v":0},{"$f":"'Project Info'!K97","v":0},{"$f":"'Project Info'!L97","v":0},0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,0,0,0,0]
[]
[]
[null,null,null,null,null,null,null,null,null,null,"Occupied VFD Speed Profiles"]
[null,null,null,null,null,null,"Installation Tyoe",null,null,null,102.5,97.5,92.5,87.5,82.5,77.5,72.5,67.5,62.5,57.5,52.5,47.5,42.5,37.5,32.5,27.5,22.5,17.5,12.5,7.5,2.5,-2.5,-7.5,-12.5]
[null,null,null,null,null,null,null,null,null,{"$f":"G34","v":"BDF - Boiler Draft Fan"},{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($T34:$U34,$T$33:$U$33,K$182),TREND($V34:$W34,$V$33:$W$33,K$182))))","v":0},0,0,0,0,0,0,0,0,0,0.11875000000000002,0.19791666666666663,0.27708333333333335,0.35624999999999996,0.43541666666666656,0.51458333333333317,0.59374999999999978,0.6729166666666665,0.7520833333333331,0.83124999999999982,0.91041666666666643,0.95,0.95,0.95]
[null,null,null,null,null,null,null,null,null,"CHWP - Chilled Water Pump",{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($T35:$U35,$T$33:$U$33,K$182),TREND($V35:$W35,$V$33:$W$33,K$182))))","v":0.95},0.95,0.89722222222222237,0.79166666666666674,0.68611111111111134,0.58055555555555571,0.47500000000000009,0.36944444444444469,0.26388888888888906,0.15833333333333366,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,null,null,null,"CTF - Cooling Tower Fan",{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($T36:$U36,$T$33:$U$33,K$182),TREND($V36:$W36,$V$33:$W$33,K$182))))","v":0.95},0.95,0.89722222222222237,0.79166666666666674,0.68611111111111134,0.58055555555555571,0.47500000000000009,0.36944444444444469,0.26388888888888906,0.15833333333333366,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,null,null,null,"CWP - Condenser Water Pump",{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($T37:$U37,$T$33:$U$33,K$182),TREND($V37:$W37,$V$33:$W$33,K$182))))","v":0.95},0.95,0.91388888888888897,0.84166666666666679,0.7694444444444446,0.69722222222222219,0.625,0.55277777777777792,0.48055555555555574,0.40833333333333344,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,null,null,null,"FWP - Boiler Feed Water Pump",{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($T38:$U38,$T$33:$U$33,K$182),TREND($V38:$W38,$V$33:$W$33,K$182))))","v":0},0,0,0,0,0,0,0,0,0,0.38124999999999998,0.43541666666666667,0.48958333333333337,0.54374999999999996,0.59791666666666665,0.65208333333333335,0.70625000000000004,0.76041666666666663,0.81458333333333333,0.86874999999999991,0.92291666666666661,0.95,0.95,0.95]
[null,null,null,null,null,null,null,null,null,"HWP - Hot Water Circulator Pump",{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($T39:$U39,$T$33:$U$33,K$182),TREND($V39:$W39,$V$33:$W$33,K$182))))","v":0},0,0,0,0,0,0,0,0,0,0.11875000000000002,0.19791666666666663,0.27708333333333335,0.35624999999999996,0.43541666666666656,0.51458333333333317,0.59374999999999978,0.6729166666666665,0.7520833333333331,0.83124999999999982,0.91041666666666643,0.95,0.95,0.95]
[null,null,null,null,null,null,null,null,null,{"$f":"#REF!","v":{"$error":"#REF!"}},{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($T40:$U40,$T$33:$U$33,K$182),TREND($V40:$W40,$V$33:$W$33,K$182))))","v":0.75},0.75,0.75,0.75,0.75,0.75,0.75,0.75,0.75,0.75,0.75,0.75,0.75,0.75,0.75,0.75,0.75,0.75,0.75,0.75,0.75,0.75,0.75,0.75]
[null,null,null,null,null,null,null,null,null,0,{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($T41:$U41,$T$33:$U$33,K$182),TREND($V41:$W41,$V$33:$W$33,K$182))))","v":0.7},0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7]
[null,null,null,null,null,null,null,null,null,0,{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($T42:$U42,$T$33:$U$33,K$182),TREND($V42:$W42,$V$33:$W$33,K$182))))","v":0.7},0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7]
[null,null,null,null,null,null,null,null,null,0,{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($T43:$U43,$T$33:$U$33,K$182),TREND($V43:$W43,$V$33:$W$33,K$182))))","v":0.95},0.95,0.91944444444444429,0.85833333333333339,0.79722222222222228,0.73611111111111116,0.67500000000000004,0.61388888888888904,0.55277777777777792,0.49166666666666681,0.41250000000000003,0.42083333333333334,0.4291666666666667,0.4375,0.44583333333333336,0.45416666666666666,0.46250000000000002,0.47083333333333333,0.47916666666666669,0.48749999999999999,0.49583333333333335,0.50416666666666665,0.51249999999999996,0.52083333333333337]
[null,null,null,null,null,null,null,null,null,0,{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($T44:$U44,$T$33:$U$33,K$182),TREND($V44:$W44,$V$33:$W$33,K$182))))","v":0.95},0.95,0.91944444444444429,0.85833333333333339,0.79722222222222228,0.73611111111111116,0.67500000000000004,0.61388888888888904,0.55277777777777792,0.49166666666666681,0.41250000000000003,0.42083333333333334,0.4291666666666667,0.4375,0.44583333333333336,0.45416666666666666,0.46250000000000002,0.47083333333333333,0.47916666666666669,0.48749999999999999,0.49583333333333335,0.50416666666666665,0.51249999999999996,0.52083333333333337]
[null,null,null,null,null,null,null,null,null,{"$f":"G40","v":"WHP - WS Heat Pump Loop Circulator Pump"},{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($T45:$U45,$T$33:$U$33,K$182),TREND($V45:$W45,$V$33:$W$33,K$182))))","v":0.95},0.95,0.92499999999999993,0.87499999999999989,0.82499999999999996,0.77500000000000002,0.72499999999999998,0.67500000000000004,0.625,0.57500000000000007,0.55625000000000013,0.59375,0.63125000000000009,0.66874999999999996,0.70625000000000004,0.74375000000000002,0.78125,0.81874999999999998,0.85624999999999996,0.89374999999999993,0.93124999999999991,0.95,0.95,0.95]
[]
[null,null,null,null,null,null,null,null,null,null,"UNoccupied VFD Speed Profiles"]
[null,null,null,null,null,null,null,null,null,null,102.5,97.5,92.5,87.5,82.5,77.5,72.5,67.5,62.5,57.5,52.5,47.5,42.5,37.5,32.5,27.5,22.5,17.5,12.5,7.5,2.5,-2.5,-7.5,-12.5]
[null,null,null,null,null,null,null,null,null,{"$f":"G34","v":"BDF - Boiler Draft Fan"},{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($X34:$Y34,$X$33:$Y$33,K$182),TREND($Z34:$AA34,$Z$33:$AA$33,K$182))))","v":0},0,0,0,0,0,0,0,0,0,0.10000000000000009,0.16666666666666674,0.23333333333333339,0.3000000000000001,0.36666666666666675,0.4333333333333334,0.5,0.56666666666666676,0.63333333333333341,0.70000000000000007,0.76666666666666672,0.83333333333333337,0.9,0.95]
[null,null,null,null,null,null,null,null,null,"CHWP - Chilled Water Pump",{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($X35:$Y35,$X$33:$Y$33,K$182),TREND($Z35:$AA35,$Z$33:$AA$33,K$182))))","v":0.87500000000000022},0.79166666666666674,0.70833333333333348,0.62500000000000022,0.54166666666666674,0.45833333333333348,0.375,0.29166666666666674,0.20833333333333348,0.125,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,null,null,null,"CTF - Cooling Tower Fan",{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($X36:$Y36,$X$33:$Y$33,K$182),TREND($Z36:$AA36,$Z$33:$AA$33,K$182))))","v":0.87500000000000022},0.79166666666666674,0.70833333333333348,0.62500000000000022,0.54166666666666674,0.45833333333333348,0.375,0.29166666666666674,0.20833333333333348,0.125,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,null,null,null,"CWP - Condenser Water Pump",{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($X37:$Y37,$X$33:$Y$33,K$182),TREND($Z37:$AA37,$Z$33:$AA$33,K$182))))","v":0.84166666666666656},0.78055555555555545,0.71944444444444433,0.65833333333333321,0.5972222222222221,0.53611111111111098,0.47499999999999998,0.41388888888888886,0.35277777777777775,0.29166666666666663,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,null,null,null,"FWP - Boiler Feed Water Pump",{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($X38:$Y38,$X$33:$Y$33,K$182),TREND($Z38:$AA38,$Z$33:$AA$33,K$182))))","v":0},0,0,0,0,0,0,0,0,0,0.26875000000000004,0.31458333333333338,0.36041666666666672,0.40625,0.45208333333333334,0.49791666666666667,0.54374999999999996,0.58958333333333335,0.63541666666666663,0.68124999999999991,0.72708333333333319,0.77291666666666659,0.81874999999999987,0.86458333333333315]
[null,null,null,null,null,null,null,null,null,"HWP - Hot Water Circulator Pump",{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($X39:$Y39,$X$33:$Y$33,K$182),TREND($Z39:$AA39,$Z$33:$AA$33,K$182))))","v":0},0,0,0,0,0,0,0,0,0,0.10000000000000009,0.16666666666666674,0.23333333333333339,0.3000000000000001,0.36666666666666675,0.4333333333333334,0.5,0.56666666666666676,0.63333333333333341,0.70000000000000007,0.76666666666666672,0.83333333333333337,0.9,0.95]
[null,null,null,null,null,null,null,null,null,{"$f":"#REF!","v":{"$error":"#REF!"}},{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($X40:$Y40,$X$33:$Y$33,K$182),TREND($Z40:$AA40,$Z$33:$AA$33,K$182))))","v":0},0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,null,null,null,0,{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($X41:$Y41,$X$33:$Y$33,K$182),TREND($Z41:$AA41,$Z$33:$AA$33,K$182))))","v":0},0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,null,null,null,0,{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($X42:$Y42,$X$33:$Y$33,K$182),TREND($Z42:$AA42,$Z$33:$AA$33,K$182))))","v":0},0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,null,null,null,0,{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($X43:$Y43,$X$33:$Y$33,K$182),TREND($Z43:$AA43,$Z$33:$AA$33,K$182))))","v":0},0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,null,null,null,0,{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($X44:$Y44,$X$33:$Y$33,K$182),TREND($Z44:$AA44,$Z$33:$AA$33,K$182))))","v":0},0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,null,null,null,{"$f":"G40","v":"WHP - WS Heat Pump Loop Circulator Pump"},{"$f":"MAX(0,MIN(0.95,IF(K$182>=$M$213,TREND($X45:$Y45,$X$33:$Y$33,K$182),TREND($Z45:$AA45,$Z$33:$AA$33,K$182))))","v":0.66666666666666663},0.62222222222222223,0.57777777777777772,0.53333333333333333,0.48888888888888893,0.44444444444444453,0.4,0.35555555555555562,0.31111111111111123,0.26666666666666683,0.25,0.28333333333333333,0.31666666666666665,0.35,0.3833333333333333,0.41666666666666663,0.44999999999999996,0.48333333333333334,0.51666666666666661,0.54999999999999993,0.58333333333333326,0.6166666666666667,0.65,0.68333333333333335]
[]
[null,null,null,null,null,null,null,null,null,null,"Cooling Min OAT",null,50,"F"]
[null,null,null,null,null,null,null,null,null,null,"Heating Max OAT",null,60,"F"]
[null,null,null,null,null,null,null,null,null,null,"Bin Model Cool/Heat OAT",null,55]
[]
[null,null,null,null,null,null,null,null,null,null,"Motor %of FL Eff vs %BHP"]
[null,null,null,null,null,null,null,null,null,null,"% BHP","% of FL Eff"]
[null,null,null,null,null,null,null,null,null,null,0,0.05]
[null,null,null,null,null,null,null,null,null,null,0.1,0.4]
[null,null,null,null,null,null,null,null,null,null,0.2,0.6]
[null,null,null,null,null,null,null,null,null,null,0.4,0.92]
[null,null,null,null,null,null,null,null,null,null,0.6,0.98]
[null,null,null,null,null,null,null,null,null,null,0.8,1]
[null,null,null,null,null,null,null,null,null,null,1,1]
[null,null,null,null,null,null,null,null,null,null,1.1000000000000001,0.97]

{"sheet":"Energy Recovery","index":14,"n_rows":167,"n_cols":248,"rows_kept":167,"cut":false,"hidden":true,"merged":[[47,7,60,11],[1,10,4,17],[1,19,11,27],[152,8,152,21],[154,13,154,20],[30,7,30,8],[27,13,27,14],[28,13,28,14],[29,13,29,14],[30,13,30,14],[26,13,26,14],[29,7,29,8],[21,7,21,8],[22,7,22,8],[23,7,23,8],[24,7,24,8],[25,7,25,8],[26,7,26,8],[27,7,27,8],[28,7,28,8],[21,13,21,14],[22,13,22,14],[23,13,23,14],[24,13,24,14],[25,13,25,14]]}
["Savings Summary",null,null,null,null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,null,null,"Notes (Optional)"]
["Annual kWh Savings",null,null,{"$f":"SUM(A14:D14)","v":0},null,null,null,"Value","Unit",null,"This measure considers savings from high performance airside energy recovery systems that exceed the minimum energy code requirements for recovery performance.\nNOTE: this tool is designed for systems with typical EER/IEER cooling ratings. It is not designed to calculate savings based on ISMRE/moisture removal ratings. "]
["% On Peak",null,null,{"$f":"IF(D2<=0,0,MIN(1,A15+C15))","v":0},null,"Annual Electric Savings",null,{"$f":"D2","v":0},"kWh"]
["Max kW",null,null,{"$f":"MAX(W103:W126,BQ102:BQ125)","v":0},null,"Annual Fuel Savings",null,{"$f":"D7*C28","v":{"$error":"#N/A"}},{"$f":"D20","v":{"$error":"#N/A"}}]
["Summer kW",null,null,{"$f":"SUMPRODUCT(W103:W126,R72:R95)/SUM(R72:R95)","v":{"$error":"#DIV/0!"}},null,"Incremental","Default Calc",{"$f":"$AQ$152","v":0},"$"]
["Winter kW",null,null,{"$f":"SUMPRODUCT(W103:W126,Q72:Q95)/SUM(Q72:Q95)","v":{"$error":"#DIV/0!"}},null,"Cost","Project Specific",null,"$ (Optional)"]
["Annual Fuel Savings (MMBtu)",null,null,{"$f":"(SUMPRODUCT($L$72:$L$95,$X$103:$X$126))/1000","v":0},null,"Estimated Incentive",null,{"$f":"IF(AND($C$24>=0,$C$25>=0),MAX(0,H3)*C24+MAX(0,H4)*C25,\"TBD\")","v":{"$error":"#N/A"}},"$"]
["Incremental Cost (Default Calc)",null,null,{"$f":"$AQ$152","v":0}]
["Incremental Cost (for Summary)",null,null,{"$f":"IF(H6>0,H6,D8)","v":0},null,"Project Information Summary"]
["kWh Savings by Peak Period",null,null,null,null,null,"STATE",{"$f":"'Project Info'!C15","v":"NH"}]
["Winter","Winter","Summer","Summer",null,null,"Program Year",{"$f":"'Project Info'!C19","v":0}]
["On-Peak","Off-Peak","On-Peak","Off-Peak",null,null,"Code IECC Version",{"$f":"MID('Project Info'!C20,1,4)","v":"2018"}]
["kWh","kWh","kWh","kWh",null,null,"Electric PA",{"$f":"'Project Info'!F3","v":0}]
[{"$f":"SUMPRODUCT($W$103:$W$126,M72:M95)","v":0},{"$f":"SUMPRODUCT($W$103:$W$126,N72:N95)","v":0},{"$f":"SUMPRODUCT($W$103:$W$126,O72:O95)","v":0},{"$f":"SUMPRODUCT($W$103:$W$126,P72:P95)","v":0},null,null,"Gas PA",{"$f":"'Project Info'!I3","v":0}]
[{"$f":"ROUND(IF(A14<=0,0,A14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(B14<=0,0,B14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(C14<=0,0,C14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"IF(SUM(A14:D14)=0,0,1-SUM(A15:C15))","v":0},null,"*NOTE: Baseline values are automated and cannot be changed."]
[]
["Utility Rates",null,null,null,null,null,"Table 1: Energy Recovery Air Handling Unit Parameters"]
[null,null,"Rate","Unit",null,null,1,2,null,3,4,5,6,7,null,8,9,10,11,12,13,14,15,16,17,18,19,null,"Baseline vs. Proposed Assumptions Summary"]
["Electric",null,{"$f":"'ECM Summary'!$E$31","v":0.1593},"kWh",null,null,null,null,null,"System","Manufacturer","Total","Total","Recovery",null,"Design ERV Performance",null,"Cooling",null,null,"Heating",null,null,"Base ERV","Note","(Optional) Recovery Section",null,null,"Baseline",null,"Proposed"]
[{"$f":"'ECM Summary'!$C$32","v":0},null,{"$f":"'ECM Summary'!$E$32","v":{"$error":"#N/A"}},{"$f":"'ECM Summary'!$F$32","v":{"$error":"#N/A"}},null,null,"Line","Unit",null,"Airflow Control Type /","& Model","Supply","OA","Section",null,"Winter","Summer","Cooling","BASELINE Peformance",null,"Heat","Fossil Fuel","Electric","Requirement","Exemption","Static Pressure Drop (in. wc)",null,null,"Sensible","Total","Sensible","Total"]
[null,null,null,null,null,null,"#","Tag/Name",null,"Terminal Unit Type","(Optional)","CFM","CFM","Type",null,"Sensible Eff","Total Eff","Included?","EER","SEER/IEER","Source","Baseline Eff%","Baseline COP","Code Exemption?","Used","Supply","Exhaust",null,"Eff","Eff","Eff","Eff"]
["Custom Incentive Rates",null,null,null,null,null,1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(L22=0,0,IF(M22/L22<10%,0,50%*(L22>=LOOKUP(M22/L22,$L$134:$S$134,IF($N$130<$K$137,$L$137:$S$137,$L$138:$S$138)))))*(X22<>\"Exempt\")","v":0},{"$f":"AC22","v":0},{"$f":"P22","v":0},{"$f":"Q22","v":0}]
[null,null,"Rate","Unit",null,null,2,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0]
["Electric",null,{"$f":"'ECM Summary'!$J$31","v":0.28000000000000003},"kWh",null,null,3,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0]
[{"$f":"'ECM Summary'!$H$32","v":0},null,{"$f":"'ECM Summary'!$J$32","v":0},{"$f":"'ECM Summary'!$K$32","v":{"$error":"#N/A"}},null,null,4,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0]
[null,null,null,null,null,null,5,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(L26=0,0,IF(M26/L26<10%,0,50%*(L26>=LOOKUP(M26/L26,$L$134:$S$134,IF($N$130<$K$137,$L$137:$S$137,$L$138:$S$138)))))*(X26<>\"Exempt\")","v":0},{"$f":"AC26","v":0},{"$f":"P26","v":0},{"$f":"Q26","v":0}]
["Fossil Fuel",null,{"$f":"'Project Info'!C21","v":0},null,null,null,6,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0]
["Fuel Conversion",null,{"$f":"LOOKUP(C27,'Project Info'!X102:X104,'Project Info'!Z102:Z104)","v":{"$error":"#N/A"}},null,null,null,7,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0]
[null,null,null,null,null,null,8,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0]
[null,null,null,null,null,null,9,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0]
[null,null,null,null,null,null,10,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0]
[null,null,null,null,null,null,null,null,null,"System Type",null,null,null,"Recovery Type",null,null,null,"Cooling?",null,null,"Heat Source",null,null,"Base ERV Exempt?"]
[null,null,null,null,null,null,null,null,null,"Variable Volume (VAV)",null,null,null,{"$f":"I107","v":"Fixed Heat Exchanger"},null,null,null,"Yes",null,null,"Elec",null,null,"N/A"]
[null,null,null,null,null,null,null,null,null,"Constant Volume",null,null,null,{"$f":"I108","v":"Heat Pipe"},null,null,null,"No",null,null,"Fossil Fuel",null,null,"Exempt"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Run-Around Loop"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"I110","v":"Wheel"}]
[]
[]
[null,null,null,null,null,null,null,"Legend for (Optional) Effectiveness Calculator",null,null,null,null,null,"(OPTIONAL) Energy Recovery Effectiveness Calculator"]
[null,null,null,null,null,null,null,"EA:","Exhaust Air leaving the Recovery HXer in exhaust stream"]
[null,null,null,null,null,null,null,"OA:","Outside Air entering the Recovery HXer in supply stream"]
[null,null,null,null,null,null,null,"RA:","Return Air from space entering Recovery HXer in exhaust stream",null,null,null,null,null,"Calculated Effectiveness"]
[null,null,null,null,null,null,null,"SA:","Supply Air leaving Recovery Hxer in supply stream",null,null,null,null,null,{"$f":"IF(AND(Q52<>\"\",U52<>\"\",U47<>\"\"),(U52-Q52)/(U47-Q52),\"---\")","v":"---"},"Winter Sensible"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(AND(Q54<>\"\",U54<>\"\",U49<>\"\"),(Q54-U54)/(Q54-U49),\"---\")","v":"---"},"Summer Total (Enthalpy)"]
[null,null,null,null,null,null,null,"*For SENSIBLE effectiveness, enter drybulb temperature (°F db) values."]
[null,null,null,null,null,null,null,"*For TOTAL effectiveness, enter enthalpy (Btu/lb) values."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"WINTER: RA °F db"]
[null,null,null,null,null,null,null,"Notes for using the (Optional) Effectiveness Calculator:\n1. Inputs should reflect the air immediately entering/leaving the recovery heat exchanger, before any mechanical heating or cooling components.\n2. Temperature/Enthalpy inputs must reflect the ratio of OA CFM to EA CFM at which the system will operate under regular operating conditions (e.g. if the EA CFM at the HXer will be less than the OA CFM due to some air being exhausted through separate building risers, the entered temperatures must reflect that unbalanced OA-to-EA ratio at the recovery air handler.)\n3. Inputs to the Effectiveness Calculator do not directly impact the savings calculations.  Effectiveness must still be input in Table 1.",null,null,null,null,null,null,null,null,null,"EA",null,"RA"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SUMMER: RA Enthalpy"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"WINTER: OA °F db",null,null,null,null,null,"WINTER: SA °F db "]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"OA",null,"SA"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SUMMER: OA Enthalpy",null,null,null,null,null,"SUMMER: SA Enthalpy"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Recovery"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Heat Exchanger"]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AHU Heating Performance",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AHU Heating Performance",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AHU Heating Performance",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AHU Heating Performance",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AHU Heating Performance",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AHU Heating Performance",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AHU Heating Performance",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AHU Heating Performance",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AHU Heating Performance",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AHU Heating Performance"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Airflow",null,"Total","Design Min","Recovery","Min Flow ","DAT Reset",null,"Base ERV Eff",null,"Proposed ERV Eff",null,null,"Heating","Avg. Eff","Avg.","Recovery SP",null,null,null,null,null,null,"Airflow",null,"Total","Design Min","Recovery","Min Flow ","DAT Reset",null,"Base ERV Eff",null,"Proposed ERV Eff",null,null,"Heating","Avg. Eff","Avg.","Recovery SP",null,null,null,null,null,null,"Airflow",null,"Total","Design Min","Recovery","Min Flow ","DAT Reset",null,"Base ERV Eff",null,"Proposed ERV Eff",null,null,"Heating","Avg. Eff","Avg.","Recovery SP",null,null,null,null,null,null,"Airflow",null,"Total","Design Min","Recovery","Min Flow ","DAT Reset",null,"Base ERV Eff",null,"Proposed ERV Eff",null,null,"Heating","Avg. Eff","Avg.","Recovery SP",null,null,null,null,null,null,"Airflow",null,"Total","Design Min","Recovery","Min Flow ","DAT Reset",null,"Base ERV Eff",null,"Proposed ERV Eff",null,null,"Heating","Avg. Eff","Avg.","Recovery SP",null,null,null,null,null,null,"Airflow",null,"Total","Design Min","Recovery","Min Flow ","DAT Reset",null,"Base ERV Eff",null,"Proposed ERV Eff",null,null,"Heating","Avg. Eff","Avg.","Recovery SP",null,null,null,null,null,null,"Airflow",null,"Total","Design Min","Recovery","Min Flow ","DAT Reset",null,"Base ERV Eff",null,"Proposed ERV Eff",null,null,"Heating","Avg. Eff","Avg.","Recovery SP",null,null,null,null,null,null,"Airflow",null,"Total","Design Min","Recovery","Min Flow ","DAT Reset",null,"Base ERV Eff",null,"Proposed ERV Eff",null,null,"Heating","Avg. Eff","Avg.","Recovery SP",null,null,null,null,null,null,"Airflow",null,"Total","Design Min","Recovery","Min Flow ","DAT Reset",null,"Base ERV Eff",null,"Proposed ERV Eff",null,null,"Heating","Avg. Eff","Avg.","Recovery SP",null,null,null,null,null,null,"Airflow",null,"Total","Design Min","Recovery","Min Flow ","DAT Reset",null,"Base ERV Eff",null,"Proposed ERV Eff",null,null,"Heating","Avg. Eff","Avg.","Recovery SP"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Line#","Tag","System Type",null,"Control",null,"Supply","OA CFM","Type","%","Min °F","Max °F","Sensible","Total","Sensible","Total","Cooling?","Fuel","%","COP","in.wc",null,null,"Line#","Tag","System Type",null,"Control",null,"Supply","OA CFM","Type","%","Min °F","Max °F","Sensible","Total","Sensible","Total","Cooling?","Fuel","%","COP","in.wc",null,null,"Line#","Tag","System Type",null,"Control",null,"Supply","OA CFM","Type","%","Min °F","Max °F","Sensible","Total","Sensible","Total","Cooling?","Fuel","%","COP","in.wc",null,null,"Line#","Tag","System Type",null,"Control",null,"Supply","OA CFM","Type","%","Min °F","Max °F","Sensible","Total","Sensible","Total","Cooling?","Fuel","%","COP","in.wc",null,null,"Line#","Tag","System Type",null,"Control",null,"Supply","OA CFM","Type","%","Min °F","Max °F","Sensible","Total","Sensible","Total","Cooling?","Fuel","%","COP","in.wc",null,null,"Line#","Tag","System Type",null,"Control",null,"Supply","OA CFM","Type","%","Min °F","Max °F","Sensible","Total","Sensible","Total","Cooling?","Fuel","%","COP","in.wc",null,null,"Line#","Tag","System Type",null,"Control",null,"Supply","OA CFM","Type","%","Min °F","Max °F","Sensible","Total","Sensible","Total","Cooling?","Fuel","%","COP","in.wc",null,null,"Line#","Tag","System Type",null,"Control",null,"Supply","OA CFM","Type","%","Min °F","Max °F","Sensible","Total","Sensible","Total","Cooling?","Fuel","%","COP","in.wc",null,null,"Line#","Tag","System Type",null,"Control",null,"Supply","OA CFM","Type","%","Min °F","Max °F","Sensible","Total","Sensible","Total","Cooling?","Fuel","%","COP","in.wc",null,null,"Line#","Tag","System Type",null,"Control",null,"Supply","OA CFM","Type","%","Min °F","Max °F","Sensible","Total","Sensible","Total","Cooling?","Fuel","%","COP","in.wc"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,{"$f":"LOOKUP(S67,$G$22:$G$31,$H$22:$H$31)","v":0},{"$f":"IF(W67=0,0,IF(W67=$J$33,IF(Z67<Y67,$G$100,$G$102),IF(Z67<Y67,$G$101,$G$103)))","v":0},null,{"$f":"LOOKUP(S67,$G$22:$G$31,$J$22:$J$31)","v":0},null,{"$f":"LOOKUP(S$67,$G$22:$G$31,$L$22:$L$31)","v":0},{"$f":"LOOKUP(S$67,$G$22:$G$31,$M$22:$M$31)","v":0},{"$f":"LOOKUP(S$67,$G$22:$G$31,$N$22:$N$31)","v":0},{"$f":"IF(Y67=0,0,MAX(Z67/Y67,LOOKUP(S$67,$Z$128:$Z$137,$AF$128:$AF$137)))","v":0},{"$f":"LOOKUP(S$67,$Z$113:$Z$122,$AE$113:$AE$122)","v":0},{"$f":"LOOKUP(S$67,$Z$113:$Z$122,$AF$113:$AF$122)","v":0},{"$f":"LOOKUP(S$67,$G$22:$G$31,$AC$22:$AC$31)","v":0},{"$f":"LOOKUP(S$67,$G$22:$G$31,$AD$22:$AD$31)","v":0},{"$f":"LOOKUP(S$67,$G$22:$G$31,$P$22:$P$31)","v":0},{"$f":"LOOKUP(S$67,$G$22:$G$31,$Q$22:$Q$31)","v":0},{"$f":"LOOKUP(S$67,$G$22:$G$31,$R$22:$R$31)","v":0},{"$f":"LOOKUP(S$67,$G$22:$G$31,$U$22:$U$31)","v":0},{"$f":"IF(AJ67=$U$34,LOOKUP(S$67,$G$22:$G$31,$V$22:$V$31),\"NA\")","v":"NA"},{"$f":"IF(AJ67=$U$33,LOOKUP(S$67,$G$22:$G$31,$W$22:$W$31),\"NA\")","v":"NA"},{"$f":"IF(LOOKUP(S67,$G$22:$G$31,$Z$22:$Z$31)+LOOKUP(S67,$G$22:$G$31,$AA$22:$AA$31)>0,LOOKUP(S67,$G$22:$G$31,$Z$22:$Z$31)+LOOKUP(S67,$G$22:$G$31,$AA$22:$AA$31),$AK$115)","v":1.6},null,null,{"$f":"S67+1","v":2},{"$f":"LOOKUP(AP67,$G$22:$G$31,$H$22:$H$31)","v":0},{"$f":"IF(AT67=0,0,IF(AT67=$J$33,IF(AW67<AV67,$G$100,$G$102),IF(AW67<AV67,$G$101,$G$103)))","v":0},null,{"$f":"LOOKUP(AP67,$G$22:$G$31,$J$22:$J$31)","v":0},null,{"$f":"LOOKUP(AP$67,$G$22:$G$31,$L$22:$L$31)","v":0},{"$f":"LOOKUP(AP$67,$G$22:$G$31,$M$22:$M$31)","v":0},{"$f":"LOOKUP(AP$67,$G$22:$G$31,$N$22:$N$31)","v":0},{"$f":"IF(AV67=0,0,MAX(AW67/AV67,LOOKUP(AP$67,$Z$128:$Z$137,$AF$128:$AF$137)))","v":0},{"$f":"LOOKUP(AP$67,$Z$113:$Z$122,$AE$113:$AE$122)","v":0},{"$f":"LOOKUP(AP$67,$Z$113:$Z$122,$AF$113:$AF$122)","v":0},{"$f":"LOOKUP(AP$67,$G$22:$G$31,$AC$22:$AC$31)","v":0},{"$f":"LOOKUP(AP$67,$G$22:$G$31,$AD$22:$AD$31)","v":0},{"$f":"LOOKUP(AP$67,$G$22:$G$31,$P$22:$P$31)","v":0},{"$f":"LOOKUP(AP$67,$G$22:$G$31,$Q$22:$Q$31)","v":0},{"$f":"LOOKUP(AP$67,$G$22:$G$31,$R$22:$R$31)","v":0},{"$f":"LOOKUP(AP$67,$G$22:$G$31,$U$22:$U$31)","v":0},{"$f":"IF(BG67=$U$34,LOOKUP(AP$67,$G$22:$G$31,$V$22:$V$31),\"NA\")","v":"NA"},{"$f":"IF(BG67=$U$33,LOOKUP(AP$67,$G$22:$G$31,$W$22:$W$31),\"NA\")","v":"NA"},{"$f":"IF(LOOKUP(AP67,$G$22:$G$31,$Z$22:$Z$31)+LOOKUP(AP67,$G$22:$G$31,$AA$22:$AA$31)>0,LOOKUP(AP67,$G$22:$G$31,$Z$22:$Z$31)+LOOKUP(AP67,$G$22:$G$31,$AA$22:$AA$31),$AK$115)","v":1.6},null,null,{"$f":"AP67+1","v":3},{"$f":"LOOKUP(BM67,$G$22:$G$31,$H$22:$H$31)","v":0},{"$f":"IF(BQ67=0,0,IF(BQ67=$J$33,IF(BT67<BS67,$G$100,$G$102),IF(BT67<BS67,$G$101,$G$103)))","v":0},null,{"$f":"LOOKUP(BM67,$G$22:$G$31,$J$22:$J$31)","v":0},null,{"$f":"LOOKUP(BM$67,$G$22:$G$31,$L$22:$L$31)","v":0},{"$f":"LOOKUP(BM$67,$G$22:$G$31,$M$22:$M$31)","v":0},{"$f":"LOOKUP(BM$67,$G$22:$G$31,$N$22:$N$31)","v":0},{"$f":"IF(BS67=0,0,MAX(BT67/BS67,LOOKUP(BM$67,$Z$128:$Z$137,$AF$128:$AF$137)))","v":0},{"$f":"LOOKUP(BM$67,$Z$113:$Z$122,$AE$113:$AE$122)","v":0},{"$f":"LOOKUP(BM$67,$Z$113:$Z$122,$AF$113:$AF$122)","v":0},{"$f":"LOOKUP(BM$67,$G$22:$G$31,$AC$22:$AC$31)","v":0},{"$f":"LOOKUP(BM$67,$G$22:$G$31,$AD$22:$AD$31)","v":0},{"$f":"LOOKUP(BM$67,$G$22:$G$31,$P$22:$P$31)","v":0},{"$f":"LOOKUP(BM$67,$G$22:$G$31,$Q$22:$Q$31)","v":0},{"$f":"LOOKUP(BM$67,$G$22:$G$31,$R$22:$R$31)","v":0},{"$f":"LOOKUP(BM$67,$G$22:$G$31,$U$22:$U$31)","v":0},{"$f":"IF(CD67=$U$34,LOOKUP(BM$67,$G$22:$G$31,$V$22:$V$31),\"NA\")","v":"NA"},{"$f":"IF(CD67=$U$33,LOOKUP(BM$67,$G$22:$G$31,$W$22:$W$31),\"NA\")","v":"NA"},{"$f":"IF(LOOKUP(BM67,$G$22:$G$31,$Z$22:$Z$31)+LOOKUP(BM67,$G$22:$G$31,$AA$22:$AA$31)>0,LOOKUP(BM67,$G$22:$G$31,$Z$22:$Z$31)+LOOKUP(BM67,$G$22:$G$31,$AA$22:$AA$31),$AK$115)","v":1.6},null,null,{"$f":"BM67+1","v":4},{"$f":"LOOKUP(CJ67,$G$22:$G$31,$H$22:$H$31)","v":0},{"$f":"IF(CN67=0,0,IF(CN67=$J$33,IF(CQ67<CP67,$G$100,$G$102),IF(CQ67<CP67,$G$101,$G$103)))","v":0},null,{"$f":"LOOKUP(CJ67,$G$22:$G$31,$J$22:$J$31)","v":0},null,{"$f":"LOOKUP(CJ$67,$G$22:$G$31,$L$22:$L$31)","v":0},{"$f":"LOOKUP(CJ$67,$G$22:$G$31,$M$22:$M$31)","v":0},{"$f":"LOOKUP(CJ$67,$G$22:$G$31,$N$22:$N$31)","v":0},{"$f":"IF(CP67=0,0,MAX(CQ67/CP67,LOOKUP(CJ$67,$Z$128:$Z$137,$AF$128:$AF$137)))","v":0},{"$f":"LOOKUP(CJ$67,$Z$113:$Z$122,$AE$113:$AE$122)","v":0},{"$f":"LOOKUP(CJ$67,$Z$113:$Z$122,$AF$113:$AF$122)","v":0},{"$f":"LOOKUP(CJ$67,$G$22:$G$31,$AC$22:$AC$31)","v":0},{"$f":"LOOKUP(CJ$67,$G$22:$G$31,$AD$22:$AD$31)","v":0},{"$f":"LOOKUP(CJ$67,$G$22:$G$31,$P$22:$P$31)","v":0},{"$f":"LOOKUP(CJ$67,$G$22:$G$31,$Q$22:$Q$31)","v":0},{"$f":"LOOKUP(CJ$67,$G$22:$G$31,$R$22:$R$31)","v":0},{"$f":"LOOKUP(CJ$67,$G$22:$G$31,$U$22:$U$31)","v":0},{"$f":"IF(DA67=$U$34,LOOKUP(CJ$67,$G$22:$G$31,$V$22:$V$31),\"NA\")","v":"NA"},{"$f":"IF(DA67=$U$33,LOOKUP(CJ$67,$G$22:$G$31,$W$22:$W$31),\"NA\")","v":"NA"},{"$f":"IF(LOOKUP(CJ67,$G$22:$G$31,$Z$22:$Z$31)+LOOKUP(CJ67,$G$22:$G$31,$AA$22:$AA$31)>0,LOOKUP(CJ67,$G$22:$G$31,$Z$22:$Z$31)+LOOKUP(CJ67,$G$22:$G$31,$AA$22:$AA$31),$AK$115)","v":1.6},null,null,{"$f":"CJ67+1","v":5},{"$f":"LOOKUP(DG67,$G$22:$G$31,$H$22:$H$31)","v":0},{"$f":"IF(DK67=0,0,IF(DK67=$J$33,IF(DN67<DM67,$G$100,$G$102),IF(DN67<DM67,$G$101,$G$103)))","v":0},null,{"$f":"LOOKUP(DG67,$G$22:$G$31,$J$22:$J$31)","v":0},null,{"$f":"LOOKUP(DG$67,$G$22:$G$31,$L$22:$L$31)","v":0},{"$f":"LOOKUP(DG$67,$G$22:$G$31,$M$22:$M$31)","v":0},{"$f":"LOOKUP(DG$67,$G$22:$G$31,$N$22:$N$31)","v":0},{"$f":"IF(DM67=0,0,MAX(DN67/DM67,LOOKUP(DG$67,$Z$128:$Z$137,$AF$128:$AF$137)))","v":0},{"$f":"LOOKUP(DG$67,$Z$113:$Z$122,$AE$113:$AE$122)","v":0},{"$f":"LOOKUP(DG$67,$Z$113:$Z$122,$AF$113:$AF$122)","v":0},{"$f":"LOOKUP(DG$67,$G$22:$G$31,$AC$22:$AC$31)","v":0},{"$f":"LOOKUP(DG$67,$G$22:$G$31,$AD$22:$AD$31)","v":0},{"$f":"LOOKUP(DG$67,$G$22:$G$31,$P$22:$P$31)","v":0},{"$f":"LOOKUP(DG$67,$G$22:$G$31,$Q$22:$Q$31)","v":0},{"$f":"LOOKUP(DG$67,$G$22:$G$31,$R$22:$R$31)","v":0},{"$f":"LOOKUP(DG$67,$G$22:$G$31,$U$22:$U$31)","v":0},{"$f":"IF(DX67=$U$34,LOOKUP(DG$67,$G$22:$G$31,$V$22:$V$31),\"NA\")","v":"NA"},{"$f":"IF(DX67=$U$33,LOOKUP(DG$67,$G$22:$G$31,$W$22:$W$31),\"NA\")","v":"NA"},{"$f":"IF(LOOKUP(DG67,$G$22:$G$31,$Z$22:$Z$31)+LOOKUP(DG67,$G$22:$G$31,$AA$22:$AA$31)>0,LOOKUP(DG67,$G$22:$G$31,$Z$22:$Z$31)+LOOKUP(DG67,$G$22:$G$31,$AA$22:$AA$31),$AK$115)","v":1.6},null,null,{"$f":"DG67+1","v":6},{"$f":"LOOKUP(ED67,$G$22:$G$31,$H$22:$H$31)","v":0},{"$f":"IF(EH67=0,0,IF(EH67=$J$33,IF(EK67<EJ67,$G$100,$G$102),IF(EK67<EJ67,$G$101,$G$103)))","v":0},null,{"$f":"LOOKUP(ED67,$G$22:$G$31,$J$22:$J$31)","v":0},null,{"$f":"LOOKUP(ED$67,$G$22:$G$31,$L$22:$L$31)","v":0},{"$f":"LOOKUP(ED$67,$G$22:$G$31,$M$22:$M$31)","v":0},{"$f":"LOOKUP(ED$67,$G$22:$G$31,$N$22:$N$31)","v":0},{"$f":"IF(EJ67=0,0,MAX(EK67/EJ67,LOOKUP(ED$67,$Z$128:$Z$137,$AF$128:$AF$137)))","v":0},{"$f":"LOOKUP(ED$67,$Z$113:$Z$122,$AE$113:$AE$122)","v":0},{"$f":"LOOKUP(ED$67,$Z$113:$Z$122,$AF$113:$AF$122)","v":0},{"$f":"LOOKUP(ED$67,$G$22:$G$31,$AC$22:$AC$31)","v":0},{"$f":"LOOKUP(ED$67,$G$22:$G$31,$AD$22:$AD$31)","v":0},{"$f":"LOOKUP(ED$67,$G$22:$G$31,$P$22:$P$31)","v":0},{"$f":"LOOKUP(ED$67,$G$22:$G$31,$Q$22:$Q$31)","v":0},{"$f":"LOOKUP(ED$67,$G$22:$G$31,$R$22:$R$31)","v":0},{"$f":"LOOKUP(ED$67,$G$22:$G$31,$U$22:$U$31)","v":0},{"$f":"IF(EU67=$U$34,LOOKUP(ED$67,$G$22:$G$31,$V$22:$V$31),\"NA\")","v":"NA"},{"$f":"IF(EU67=$U$33,LOOKUP(ED$67,$G$22:$G$31,$W$22:$W$31),\"NA\")","v":"NA"},{"$f":"IF(LOOKUP(ED67,$G$22:$G$31,$Z$22:$Z$31)+LOOKUP(ED67,$G$22:$G$31,$AA$22:$AA$31)>0,LOOKUP(ED67,$G$22:$G$31,$Z$22:$Z$31)+LOOKUP(ED67,$G$22:$G$31,$AA$22:$AA$31),$AK$115)","v":1.6},null,null,{"$f":"ED67+1","v":7},{"$f":"LOOKUP(FA67,$G$22:$G$31,$H$22:$H$31)","v":0},{"$f":"IF(FE67=0,0,IF(FE67=$J$33,IF(FH67<FG67,$G$100,$G$102),IF(FH67<FG67,$G$101,$G$103)))","v":0},null,{"$f":"LOOKUP(FA67,$G$22:$G$31,$J$22:$J$31)","v":0},null,{"$f":"LOOKUP(FA$67,$G$22:$G$31,$L$22:$L$31)","v":0},{"$f":"LOOKUP(FA$67,$G$22:$G$31,$M$22:$M$31)","v":0},{"$f":"LOOKUP(FA$67,$G$22:$G$31,$N$22:$N$31)","v":0},{"$f":"IF(FG67=0,0,MAX(FH67/FG67,LOOKUP(FA$67,$Z$128:$Z$137,$AF$128:$AF$137)))","v":0},{"$f":"LOOKUP(FA$67,$Z$113:$Z$122,$AE$113:$AE$122)","v":0},{"$f":"LOOKUP(FA$67,$Z$113:$Z$122,$AF$113:$AF$122)","v":0},{"$f":"LOOKUP(FA$67,$G$22:$G$31,$AC$22:$AC$31)","v":0},{"$f":"LOOKUP(FA$67,$G$22:$G$31,$AD$22:$AD$31)","v":0},{"$f":"LOOKUP(FA$67,$G$22:$G$31,$P$22:$P$31)","v":0},{"$f":"LOOKUP(FA$67,$G$22:$G$31,$Q$22:$Q$31)","v":0},{"$f":"LOOKUP(FA$67,$G$22:$G$31,$R$22:$R$31)","v":0},{"$f":"LOOKUP(FA$67,$G$22:$G$31,$U$22:$U$31)","v":0},{"$f":"IF(FR67=$U$34,LOOKUP(FA$67,$G$22:$G$31,$V$22:$V$31),\"NA\")","v":"NA"},{"$f":"IF(FR67=$U$33,LOOKUP(FA$67,$G$22:$G$31,$W$22:$W$31),\"NA\")","v":"NA"},{"$f":"IF(LOOKUP(FA67,$G$22:$G$31,$Z$22:$Z$31)+LOOKUP(FA67,$G$22:$G$31,$AA$22:$AA$31)>0,LOOKUP(FA67,$G$22:$G$31,$Z$22:$Z$31)+LOOKUP(FA67,$G$22:$G$31,$AA$22:$AA$31),$AK$115)","v":1.6},null,null,{"$f":"FA67+1","v":8},{"$f":"LOOKUP(FX67,$G$22:$G$31,$H$22:$H$31)","v":0},{"$f":"IF(GB67=0,0,IF(GB67=$J$33,IF(GE67<GD67,$G$100,$G$102),IF(GE67<GD67,$G$101,$G$103)))","v":0},null,{"$f":"LOOKUP(FX67,$G$22:$G$31,$J$22:$J$31)","v":0},null,{"$f":"LOOKUP(FX$67,$G$22:$G$31,$L$22:$L$31)","v":0},{"$f":"LOOKUP(FX$67,$G$22:$G$31,$M$22:$M$31)","v":0},{"$f":"LOOKUP(FX$67,$G$22:$G$31,$N$22:$N$31)","v":0},{"$f":"IF(GD67=0,0,MAX(GE67/GD67,LOOKUP(FX$67,$Z$128:$Z$137,$AF$128:$AF$137)))","v":0},{"$f":"LOOKUP(FX$67,$Z$113:$Z$122,$AE$113:$AE$122)","v":0},{"$f":"LOOKUP(FX$67,$Z$113:$Z$122,$AF$113:$AF$122)","v":0},{"$f":"LOOKUP(FX$67,$G$22:$G$31,$AC$22:$AC$31)","v":0},{"$f":"LOOKUP(FX$67,$G$22:$G$31,$AD$22:$AD$31)","v":0},{"$f":"LOOKUP(FX$67,$G$22:$G$31,$P$22:$P$31)","v":0},{"$f":"LOOKUP(FX$67,$G$22:$G$31,$Q$22:$Q$31)","v":0},{"$f":"LOOKUP(FX$67,$G$22:$G$31,$R$22:$R$31)","v":0},{"$f":"LOOKUP(FX$67,$G$22:$G$31,$U$22:$U$31)","v":0},{"$f":"IF(GO67=$U$34,LOOKUP(FX$67,$G$22:$G$31,$V$22:$V$31),\"NA\")","v":"NA"},{"$f":"IF(GO67=$U$33,LOOKUP(FX$67,$G$22:$G$31,$W$22:$W$31),\"NA\")","v":"NA"},{"$f":"IF(LOOKUP(FX67,$G$22:$G$31,$Z$22:$Z$31)+LOOKUP(FX67,$G$22:$G$31,$AA$22:$AA$31)>0,LOOKUP(FX67,$G$22:$G$31,$Z$22:$Z$31)+LOOKUP(FX67,$G$22:$G$31,$AA$22:$AA$31),$AK$115)","v":1.6},null,null,{"$f":"FX67+1","v":9},{"$f":"LOOKUP(GU67,$G$22:$G$31,$H$22:$H$31)","v":0},{"$f":"IF(GY67=0,0,IF(GY67=$J$33,IF(HB67<HA67,$G$100,$G$102),IF(HB67<HA67,$G$101,$G$103)))","v":0},null,{"$f":"LOOKUP(GU67,$G$22:$G$31,$J$22:$J$31)","v":0},null,{"$f":"LOOKUP(GU$67,$G$22:$G$31,$L$22:$L$31)","v":0},{"$f":"LOOKUP(GU$67,$G$22:$G$31,$M$22:$M$31)","v":0},{"$f":"LOOKUP(GU$67,$G$22:$G$31,$N$22:$N$31)","v":0},{"$f":"IF(HA67=0,0,MAX(HB67/HA67,LOOKUP(GU$67,$Z$128:$Z$137,$AF$128:$AF$137)))","v":0},{"$f":"LOOKUP(GU$67,$Z$113:$Z$122,$AE$113:$AE$122)","v":0},{"$f":"LOOKUP(GU$67,$Z$113:$Z$122,$AF$113:$AF$122)","v":0},{"$f":"LOOKUP(GU$67,$G$22:$G$31,$AC$22:$AC$31)","v":0},{"$f":"LOOKUP(GU$67,$G$22:$G$31,$AD$22:$AD$31)","v":0},{"$f":"LOOKUP(GU$67,$G$22:$G$31,$P$22:$P$31)","v":0},{"$f":"LOOKUP(GU$67,$G$22:$G$31,$Q$22:$Q$31)","v":0},{"$f":"LOOKUP(GU$67,$G$22:$G$31,$R$22:$R$31)","v":0},{"$f":"LOOKUP(GU$67,$G$22:$G$31,$U$22:$U$31)","v":0},{"$f":"IF(HL67=$U$34,LOOKUP(GU$67,$G$22:$G$31,$V$22:$V$31),\"NA\")","v":"NA"},{"$f":"IF(HL67=$U$33,LOOKUP(GU$67,$G$22:$G$31,$W$22:$W$31),\"NA\")","v":"NA"},{"$f":"IF(LOOKUP(GU67,$G$22:$G$31,$Z$22:$Z$31)+LOOKUP(GU67,$G$22:$G$31,$AA$22:$AA$31)>0,LOOKUP(GU67,$G$22:$G$31,$Z$22:$Z$31)+LOOKUP(GU67,$G$22:$G$31,$AA$22:$AA$31),$AK$115)","v":1.6},null,null,{"$f":"GU67+1","v":10},{"$f":"LOOKUP(HR67,$G$22:$G$31,$H$22:$H$31)","v":0},{"$f":"IF(HV67=0,0,IF(HV67=$J$33,IF(HY67<HX67,$G$100,$G$102),IF(HY67<HX67,$G$101,$G$103)))","v":0},null,{"$f":"LOOKUP(HR67,$G$22:$G$31,$J$22:$J$31)","v":0},null,{"$f":"LOOKUP(HR$67,$G$22:$G$31,$L$22:$L$31)","v":0},{"$f":"LOOKUP(HR$67,$G$22:$G$31,$M$22:$M$31)","v":0},{"$f":"LOOKUP(HR$67,$G$22:$G$31,$N$22:$N$31)","v":0},{"$f":"IF(HX67=0,0,MAX(HY67/HX67,LOOKUP(HR$67,$Z$128:$Z$137,$AF$128:$AF$137)))","v":0},{"$f":"LOOKUP(HR$67,$Z$113:$Z$122,$AE$113:$AE$122)","v":0},{"$f":"LOOKUP(HR$67,$Z$113:$Z$122,$AF$113:$AF$122)","v":0},{"$f":"LOOKUP(HR$67,$G$22:$G$31,$AC$22:$AC$31)","v":0},{"$f":"LOOKUP(HR$67,$G$22:$G$31,$AD$22:$AD$31)","v":0},{"$f":"LOOKUP(HR$67,$G$22:$G$31,$P$22:$P$31)","v":0},{"$f":"LOOKUP(HR$67,$G$22:$G$31,$Q$22:$Q$31)","v":0},{"$f":"LOOKUP(HR$67,$G$22:$G$31,$R$22:$R$31)","v":0},{"$f":"LOOKUP(HR$67,$G$22:$G$31,$U$22:$U$31)","v":0},{"$f":"IF(II67=$U$34,LOOKUP(HR$67,$G$22:$G$31,$V$22:$V$31),\"NA\")","v":"NA"},{"$f":"IF(II67=$U$33,LOOKUP(HR$67,$G$22:$G$31,$W$22:$W$31),\"NA\")","v":"NA"},{"$f":"IF(LOOKUP(HR67,$G$22:$G$31,$Z$22:$Z$31)+LOOKUP(HR67,$G$22:$G$31,$AA$22:$AA$31)>0,LOOKUP(HR67,$G$22:$G$31,$Z$22:$Z$31)+LOOKUP(HR67,$G$22:$G$31,$AA$22:$AA$31),$AK$115)","v":1.6}]
[null,null,null,null,null,null,"Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Cooling","Heating","Total","% OA","Return","Return","Mixed Air","Mixed Air","Discharge","Discharge","ERV Eff",null,"ERV DAT",null,"ERV DAH",null,"Cool Load","Heat Load","Cooling",null,"Heating",null,"Fan","Cooling","Heating","Total","% OA","Return","Return","Mixed Air","Mixed Air","Discharge","Discharge","ERV Eff",null,"ERV DAT",null,"ERV DAH",null,"Cool Load","Heat Load","Cooling",null,"Heating",null,"Fan","Cooling","Heating","Total","% OA","Return","Return","Mixed Air","Mixed Air","Discharge","Discharge","ERV Eff",null,"ERV DAT",null,"ERV DAH",null,"Cool Load","Heat Load","Cooling",null,"Heating",null,"Fan","Cooling","Heating","Total","% OA","Return","Return","Mixed Air","Mixed Air","Discharge","Discharge","ERV Eff",null,"ERV DAT",null,"ERV DAH",null,"Cool Load","Heat Load","Cooling",null,"Heating",null,"Fan","Cooling","Heating","Total","% OA","Return","Return","Mixed Air","Mixed Air","Discharge","Discharge","ERV Eff",null,"ERV DAT",null,"ERV DAH",null,"Cool Load","Heat Load","Cooling",null,"Heating",null,"Fan","Cooling","Heating","Total","% OA","Return","Return","Mixed Air","Mixed Air","Discharge","Discharge","ERV Eff",null,"ERV DAT",null,"ERV DAH",null,"Cool Load","Heat Load","Cooling",null,"Heating",null,"Fan","Cooling","Heating","Total","% OA","Return","Return","Mixed Air","Mixed Air","Discharge","Discharge","ERV Eff",null,"ERV DAT",null,"ERV DAH",null,"Cool Load","Heat Load","Cooling",null,"Heating",null,"Fan","Cooling","Heating","Total","% OA","Return","Return","Mixed Air","Mixed Air","Discharge","Discharge","ERV Eff",null,"ERV DAT",null,"ERV DAH",null,"Cool Load","Heat Load","Cooling",null,"Heating",null,"Fan","Cooling","Heating","Total","% OA","Return","Return","Mixed Air","Mixed Air","Discharge","Discharge","ERV Eff",null,"ERV DAT",null,"ERV DAH",null,"Cool Load","Heat Load","Cooling",null,"Heating",null,"Fan","Cooling","Heating","Total","% OA","Return","Return","Mixed Air","Mixed Air","Discharge","Discharge","ERV Eff",null,"ERV DAT",null,"ERV DAH",null,"Cool Load","Heat Load","Cooling",null,"Heating",null,"Fan"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","%","%","Flow","Flow","Temp","Enth","DB","Enth","Temp","Enth","Base","Design","Base","Design","Base","Design","Reduction","Reduction","Perf","Reduc","Perf","Reduc","Penalty","%","%","Flow","Flow","Temp","Enth","DB","Enth","Temp","Enth","Base","Design","Base","Design","Base","Design","Reduction","Reduction","Perf","Reduc","Perf","Reduc","Penalty","%","%","Flow","Flow","Temp","Enth","DB","Enth","Temp","Enth","Base","Design","Base","Design","Base","Design","Reduction","Reduction","Perf","Reduc","Perf","Reduc","Penalty","%","%","Flow","Flow","Temp","Enth","DB","Enth","Temp","Enth","Base","Design","Base","Design","Base","Design","Reduction","Reduction","Perf","Reduc","Perf","Reduc","Penalty","%","%","Flow","Flow","Temp","Enth","DB","Enth","Temp","Enth","Base","Design","Base","Design","Base","Design","Reduction","Reduction","Perf","Reduc","Perf","Reduc","Penalty","%","%","Flow","Flow","Temp","Enth","DB","Enth","Temp","Enth","Base","Design","Base","Design","Base","Design","Reduction","Reduction","Perf","Reduc","Perf","Reduc","Penalty","%","%","Flow","Flow","Temp","Enth","DB","Enth","Temp","Enth","Base","Design","Base","Design","Base","Design","Reduction","Reduction","Perf","Reduc","Perf","Reduc","Penalty","%","%","Flow","Flow","Temp","Enth","DB","Enth","Temp","Enth","Base","Design","Base","Design","Base","Design","Reduction","Reduction","Perf","Reduc","Perf","Reduc","Penalty","%","%","Flow","Flow","Temp","Enth","DB","Enth","Temp","Enth","Base","Design","Base","Design","Base","Design","Reduction","Reduction","Perf","Reduc","Perf","Reduc","Penalty","%","%","Flow","Flow","Temp","Enth","DB","Enth","Temp","Enth","Base","Design","Base","Design","Base","Design","Reduction","Reduction","Perf","Reduc","Perf","Reduc","Penalty"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","Load","Load","CFM","%","°F","Btu/lb","°F","Btu/lb","°F","Btu/lb","%","%","°F","°F","Btu/lb","Btu/lb","MBH","MBH","EER","kW","COP","MBH","kW","Load","Load","CFM","%","°F","Btu/lb","°F","Btu/lb","°F","Btu/lb","%","%","°F","°F","Btu/lb","Btu/lb","MBH","MBH","EER","kW","COP","MBH","kW","Load","Load","CFM","%","°F","Btu/lb","°F","Btu/lb","°F","Btu/lb","%","%","°F","°F","Btu/lb","Btu/lb","MBH","MBH","EER","kW","COP","MBH","kW","Load","Load","CFM","%","°F","Btu/lb","°F","Btu/lb","°F","Btu/lb","%","%","°F","°F","Btu/lb","Btu/lb","MBH","MBH","EER","kW","COP","MBH","kW","Load","Load","CFM","%","°F","Btu/lb","°F","Btu/lb","°F","Btu/lb","%","%","°F","°F","Btu/lb","Btu/lb","MBH","MBH","EER","kW","COP","MBH","kW","Load","Load","CFM","%","°F","Btu/lb","°F","Btu/lb","°F","Btu/lb","%","%","°F","°F","Btu/lb","Btu/lb","MBH","MBH","EER","kW","COP","MBH","kW","Load","Load","CFM","%","°F","Btu/lb","°F","Btu/lb","°F","Btu/lb","%","%","°F","°F","Btu/lb","Btu/lb","MBH","MBH","EER","kW","COP","MBH","kW","Load","Load","CFM","%","°F","Btu/lb","°F","Btu/lb","°F","Btu/lb","%","%","°F","°F","Btu/lb","Btu/lb","MBH","MBH","EER","kW","COP","MBH","kW","Load","Load","CFM","%","°F","Btu/lb","°F","Btu/lb","°F","Btu/lb","%","%","°F","°F","Btu/lb","Btu/lb","MBH","MBH","EER","kW","COP","MBH","kW","Load","Load","CFM","%","°F","Btu/lb","°F","Btu/lb","°F","Btu/lb","%","%","°F","°F","Btu/lb","Btu/lb","MBH","MBH","EER","kW","COP","MBH","kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A44","v":100},{"$f":"'Project Info'!B44","v":105},{"$f":"'Project Info'!C44","v":102},{"$f":"'Project Info'!D44","v":76},{"$f":"'Project Info'!E44","v":40},{"$f":"'Project Info'!F44","v":0},{"$f":"'Project Info'!G44","v":0},{"$f":"'Project Info'!H44","v":0},{"$f":"'Project Info'!I44","v":0},{"$f":"'Project Info'!J44","v":0},{"$f":"'Project Info'!K44","v":0},{"$f":"'Project Info'!L44","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$102:$AF$102,$AC$102:$AD$102,$I72)))*(AI$67=\"Yes\")","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$107:$AF$107,$AC$107:$AD$107,$I72)))","v":0},{"$f":"MAX(AB$67,TREND(OFFSET($Z$127,MATCH(S$67,$Z$128:$Z$137,0),5,1,2),OFFSET($Z$127,MATCH(S$67,$Z$128:$Z$137,0),3,1,2),S72))*Y$67","v":0},{"$f":"IF(U72=0,0,MIN(1,Z$67/U72))","v":0},{"$f":"IF(S72>0,$W$131,$X$131)","v":70},{"$f":"IF(S72>0,$W$134,$X$134)","v":25.099807999999999},{"$f":"V72*$I72+(1-V72)*W72","v":70},{"$f":"V72*$K72+(1-V72)*X72","v":25.099807999999999},{"$f":"MAX(MIN(AD$67,TREND(OFFSET($Z$112,MATCH(S$67,$Z$113:$Z$122,0),5,1,2),OFFSET($Z$112,MATCH(S$67,$Z$113:$Z$122,0),3,1,2),$I72)),AC$67)","v":0},{"$f":"$AI$107+$AI$108*AA72","v":-12.336},{"$f":"IF(S72>0,AF$67,AE$67)","v":0},{"$f":"IF(S72>0,AH$67,AG$67)","v":0},{"$f":"IF(S72>0,MAX(AA72,$I72-AC72*($I72-W72)),MIN(AA72,$I72-AC72*($I72-W72)))","v":0},{"$f":"IF(S72>0,MAX(AA72,$I72-AD72*($I72-W72)),MIN(AA72,$I72-AD72*($I72-W72)))","v":0},{"$f":"IF(S72>0,MAX(AB72,$K72-AC72*($K72-X72)),MIN(AB72,$K72-AC72*($K72-X72)))","v":-12.336},{"$f":"IF(S72>0,MAX(AB72,$K72-AD72*($K72-X72)),MIN(AB72,$K72-AD72*($K72-X72)))","v":-12.336},{"$f":"(S72>0)*OR($I72<$AI$111,$I72>$AI$112)*4.45*V72*U72*(AG72-AH72)/1000","v":0},{"$f":"(T72>0)*1.08*V72*U72*(AF72-AE72)/1000","v":0},{"$f":"TREND(OFFSET($Z$141,MATCH(S$67,$Z$142:$Z$151,0),MATCH(S72,$AA$141:$AE$141,-1),1,2),OFFSET($Z$141,0,MATCH(S72,$AA$141:$AE$141,-1),1,2),S72)","v":0},{"$f":"IF(AK72=0,0,AI72/AK72)","v":0},{"$f":"IF(AJ$67=0,0,IF(AJ$67=$U$34,AK$67,AL$67))","v":0},{"$f":"IF(AM72=0,0,AJ72/AM72)","v":0},{"$f":"IF(AC72>0,0,-1*((V72*U72)*(AM$67*0.746/4131/$AK$116+LOOKUP(S$67,$AH$142:$AH$151,$AL$142:$AL$151)))*(OR($I72<$AI$111,$I72>$AI$112)))","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$102:$AF$102,$AC$102:$AD$102,$I72)))*(BF$67=\"Yes\")","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$107:$AF$107,$AC$107:$AD$107,$I72)))","v":0},{"$f":"MAX(AY$67,TREND(OFFSET($Z$127,MATCH(AP$67,$Z$128:$Z$137,0),5,1,2),OFFSET($Z$127,MATCH(AP$67,$Z$128:$Z$137,0),3,1,2),AP72))*AV$67","v":0},{"$f":"IF(AR72=0,0,MIN(1,AW$67/AR72))","v":0},{"$f":"IF(AP72>0,$W$131,$X$131)","v":70},{"$f":"IF(AP72>0,$W$134,$X$134)","v":25.099807999999999},{"$f":"AS72*$I72+(1-AS72)*AT72","v":70},{"$f":"AS72*$K72+(1-AS72)*AU72","v":25.099807999999999},{"$f":"MAX(MIN(BA$67,TREND(OFFSET($Z$112,MATCH(AP$67,$Z$113:$Z$122,0),5,1,2),OFFSET($Z$112,MATCH(AP$67,$Z$113:$Z$122,0),3,1,2),$I72)),AZ$67)","v":0},{"$f":"$AI$107+$AI$108*AX72","v":-12.336},{"$f":"IF(AP72>0,BC$67,BB$67)","v":0},{"$f":"IF(AP72>0,BE$67,BD$67)","v":0},{"$f":"IF(AP72>0,MAX(AX72,$I72-AZ72*($I72-AT72)),MIN(AX72,$I72-AZ72*($I72-AT72)))","v":0},{"$f":"IF(AP72>0,MAX(AX72,$I72-BA72*($I72-AT72)),MIN(AX72,$I72-BA72*($I72-AT72)))","v":0},{"$f":"IF(AP72>0,MAX(AY72,$K72-AZ72*($K72-AU72)),MIN(AY72,$K72-AZ72*($K72-AU72)))","v":-12.336},{"$f":"IF(AP72>0,MAX(AY72,$K72-BA72*($K72-AU72)),MIN(AY72,$K72-BA72*($K72-AU72)))","v":-12.336},{"$f":"(AP72>0)*OR($I72<$AI$111,$I72>$AI$112)*4.45*AS72*AR72*(BD72-BE72)/1000","v":0},{"$f":"(AQ72>0)*1.08*AS72*AR72*(BC72-BB72)/1000","v":0},{"$f":"TREND(OFFSET($Z$141,MATCH(AP$67,$Z$142:$Z$151,0),MATCH(AP72,$AA$141:$AE$141,-1),1,2),OFFSET($Z$141,0,MATCH(AP72,$AA$141:$AE$141,-1),1,2),AP72)","v":0},{"$f":"IF(BH72=0,0,BF72/BH72)","v":0},{"$f":"IF(BG$67=0,0,IF(BG$67=$U$34,BH$67,BI$67))","v":0},{"$f":"IF(BJ72=0,0,BG72/BJ72)","v":0},{"$f":"IF(AZ72>0,0,-1*((AS72*AR72)*(BJ$67*0.746/4131/$AK$116+LOOKUP(AP$67,$AH$142:$AH$151,$AL$142:$AL$151)))*(OR($I72<$AI$111,$I72>$AI$112)))","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$102:$AF$102,$AC$102:$AD$102,$I72)))*(CC$67=\"Yes\")","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$107:$AF$107,$AC$107:$AD$107,$I72)))","v":0},{"$f":"MAX(BV$67,TREND(OFFSET($Z$127,MATCH(BM$67,$Z$128:$Z$137,0),5,1,2),OFFSET($Z$127,MATCH(BM$67,$Z$128:$Z$137,0),3,1,2),BM72))*BS$67","v":0},{"$f":"IF(BO72=0,0,MIN(1,BT$67/BO72))","v":0},{"$f":"IF(BM72>0,$W$131,$X$131)","v":70},{"$f":"IF(BM72>0,$W$134,$X$134)","v":25.099807999999999},{"$f":"BP72*$I72+(1-BP72)*BQ72","v":70},{"$f":"BP72*$K72+(1-BP72)*BR72","v":25.099807999999999},{"$f":"MAX(MIN(BX$67,TREND(OFFSET($Z$112,MATCH(BM$67,$Z$113:$Z$122,0),5,1,2),OFFSET($Z$112,MATCH(BM$67,$Z$113:$Z$122,0),3,1,2),$I72)),BW$67)","v":0},{"$f":"$AI$107+$AI$108*BU72","v":-12.336},{"$f":"IF(BM72>0,BZ$67,BY$67)","v":0},{"$f":"IF(BM72>0,CB$67,CA$67)","v":0},{"$f":"IF(BM72>0,MAX(BU72,$I72-BW72*($I72-BQ72)),MIN(BU72,$I72-BW72*($I72-BQ72)))","v":0},{"$f":"IF(BM72>0,MAX(BU72,$I72-BX72*($I72-BQ72)),MIN(BU72,$I72-BX72*($I72-BQ72)))","v":0},{"$f":"IF(BM72>0,MAX(BV72,$K72-BW72*($K72-BR72)),MIN(BV72,$K72-BW72*($K72-BR72)))","v":-12.336},{"$f":"IF(BM72>0,MAX(BV72,$K72-BX72*($K72-BR72)),MIN(BV72,$K72-BX72*($K72-BR72)))","v":-12.336},{"$f":"(BM72>0)*OR($I72<$AI$111,$I72>$AI$112)*4.45*BP72*BO72*(CA72-CB72)/1000","v":0},{"$f":"(BN72>0)*1.08*BP72*BO72*(BZ72-BY72)/1000","v":0},{"$f":"TREND(OFFSET($Z$141,MATCH(BM$67,$Z$142:$Z$151,0),MATCH(BM72,$AA$141:$AE$141,-1),1,2),OFFSET($Z$141,0,MATCH(BM72,$AA$141:$AE$141,-1),1,2),BM72)","v":0},{"$f":"IF(CE72=0,0,CC72/CE72)","v":0},{"$f":"IF(CD$67=0,0,IF(CD$67=$U$34,CE$67,CF$67))","v":0},{"$f":"IF(CG72=0,0,CD72/CG72)","v":0},{"$f":"IF(BW72>0,0,-1*((BP72*BO72)*(CG$67*0.746/4131/$AK$116+LOOKUP(BM$67,$AH$142:$AH$151,$AL$142:$AL$151)))*(OR($I72<$AI$111,$I72>$AI$112)))","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$102:$AF$102,$AC$102:$AD$102,$I72)))*(CZ$67=\"Yes\")","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$107:$AF$107,$AC$107:$AD$107,$I72)))","v":0},{"$f":"MAX(CS$67,TREND(OFFSET($Z$127,MATCH(CJ$67,$Z$128:$Z$137,0),5,1,2),OFFSET($Z$127,MATCH(CJ$67,$Z$128:$Z$137,0),3,1,2),CJ72))*CP$67","v":0},{"$f":"IF(CL72=0,0,MIN(1,CQ$67/CL72))","v":0},{"$f":"IF(CJ72>0,$W$131,$X$131)","v":70},{"$f":"IF(CJ72>0,$W$134,$X$134)","v":25.099807999999999},{"$f":"CM72*$I72+(1-CM72)*CN72","v":70},{"$f":"CM72*$K72+(1-CM72)*CO72","v":25.099807999999999},{"$f":"MAX(MIN(CU$67,TREND(OFFSET($Z$112,MATCH(CJ$67,$Z$113:$Z$122,0),5,1,2),OFFSET($Z$112,MATCH(CJ$67,$Z$113:$Z$122,0),3,1,2),$I72)),CT$67)","v":0},{"$f":"$AI$107+$AI$108*CR72","v":-12.336},{"$f":"IF(CJ72>0,CW$67,CV$67)","v":0},{"$f":"IF(CJ72>0,CY$67,CX$67)","v":0},{"$f":"IF(CJ72>0,MAX(CR72,$I72-CT72*($I72-CN72)),MIN(CR72,$I72-CT72*($I72-CN72)))","v":0},{"$f":"IF(CJ72>0,MAX(CR72,$I72-CU72*($I72-CN72)),MIN(CR72,$I72-CU72*($I72-CN72)))","v":0},{"$f":"IF(CJ72>0,MAX(CS72,$K72-CT72*($K72-CO72)),MIN(CS72,$K72-CT72*($K72-CO72)))","v":-12.336},{"$f":"IF(CJ72>0,MAX(CS72,$K72-CU72*($K72-CO72)),MIN(CS72,$K72-CU72*($K72-CO72)))","v":-12.336},{"$f":"(CJ72>0)*OR($I72<$AI$111,$I72>$AI$112)*4.45*CM72*CL72*(CX72-CY72)/1000","v":0},{"$f":"(CK72>0)*1.08*CM72*CL72*(CW72-CV72)/1000","v":0},{"$f":"TREND(OFFSET($Z$141,MATCH(CJ$67,$Z$142:$Z$151,0),MATCH(CJ72,$AA$141:$AE$141,-1),1,2),OFFSET($Z$141,0,MATCH(CJ72,$AA$141:$AE$141,-1),1,2),CJ72)","v":0},{"$f":"IF(DB72=0,0,CZ72/DB72)","v":0},{"$f":"IF(DA$67=0,0,IF(DA$67=$U$34,DB$67,DC$67))","v":0},{"$f":"IF(DD72=0,0,DA72/DD72)","v":0},{"$f":"IF(CT72>0,0,-1*((CM72*CL72)*(DD$67*0.746/4131/$AK$116+LOOKUP(CJ$67,$AH$142:$AH$151,$AL$142:$AL$151)))*(OR($I72<$AI$111,$I72>$AI$112)))","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$102:$AF$102,$AC$102:$AD$102,$I72)))*(DW$67=\"Yes\")","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$107:$AF$107,$AC$107:$AD$107,$I72)))","v":0},{"$f":"MAX(DP$67,TREND(OFFSET($Z$127,MATCH(DG$67,$Z$128:$Z$137,0),5,1,2),OFFSET($Z$127,MATCH(DG$67,$Z$128:$Z$137,0),3,1,2),DG72))*DM$67","v":0},{"$f":"IF(DI72=0,0,MIN(1,DN$67/DI72))","v":0},{"$f":"IF(DG72>0,$W$131,$X$131)","v":70},{"$f":"IF(DG72>0,$W$134,$X$134)","v":25.099807999999999},{"$f":"DJ72*$I72+(1-DJ72)*DK72","v":70},{"$f":"DJ72*$K72+(1-DJ72)*DL72","v":25.099807999999999},{"$f":"MAX(MIN(DR$67,TREND(OFFSET($Z$112,MATCH(DG$67,$Z$113:$Z$122,0),5,1,2),OFFSET($Z$112,MATCH(DG$67,$Z$113:$Z$122,0),3,1,2),$I72)),DQ$67)","v":0},{"$f":"$AI$107+$AI$108*DO72","v":-12.336},{"$f":"IF(DG72>0,DT$67,DS$67)","v":0},{"$f":"IF(DG72>0,DV$67,DU$67)","v":0},{"$f":"IF(DG72>0,MAX(DO72,$I72-DQ72*($I72-DK72)),MIN(DO72,$I72-DQ72*($I72-DK72)))","v":0},{"$f":"IF(DG72>0,MAX(DO72,$I72-DR72*($I72-DK72)),MIN(DO72,$I72-DR72*($I72-DK72)))","v":0},{"$f":"IF(DG72>0,MAX(DP72,$K72-DQ72*($K72-DL72)),MIN(DP72,$K72-DQ72*($K72-DL72)))","v":-12.336},{"$f":"IF(DG72>0,MAX(DP72,$K72-DR72*($K72-DL72)),MIN(DP72,$K72-DR72*($K72-DL72)))","v":-12.336},{"$f":"(DG72>0)*OR($I72<$AI$111,$I72>$AI$112)*4.45*DJ72*DI72*(DU72-DV72)/1000","v":0},{"$f":"(DH72>0)*1.08*DJ72*DI72*(DT72-DS72)/1000","v":0},{"$f":"TREND(OFFSET($Z$141,MATCH(DG$67,$Z$142:$Z$151,0),MATCH(DG72,$AA$141:$AE$141,-1),1,2),OFFSET($Z$141,0,MATCH(DG72,$AA$141:$AE$141,-1),1,2),DG72)","v":0},{"$f":"IF(DY72=0,0,DW72/DY72)","v":0},{"$f":"IF(DX$67=0,0,IF(DX$67=$U$34,DY$67,DZ$67))","v":0},{"$f":"IF(EA72=0,0,DX72/EA72)","v":0},{"$f":"IF(DQ72>0,0,-1*((DJ72*DI72)*(EA$67*0.746/4131/$AK$116+LOOKUP(DG$67,$AH$142:$AH$151,$AL$142:$AL$151)))*(OR($I72<$AI$111,$I72>$AI$112)))","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$102:$AF$102,$AC$102:$AD$102,$I72)))*(ET$67=\"Yes\")","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$107:$AF$107,$AC$107:$AD$107,$I72)))","v":0},{"$f":"MAX(EM$67,TREND(OFFSET($Z$127,MATCH(ED$67,$Z$128:$Z$137,0),5,1,2),OFFSET($Z$127,MATCH(ED$67,$Z$128:$Z$137,0),3,1,2),ED72))*EJ$67","v":0},{"$f":"IF(EF72=0,0,MIN(1,EK$67/EF72))","v":0},{"$f":"IF(ED72>0,$W$131,$X$131)","v":70},{"$f":"IF(ED72>0,$W$134,$X$134)","v":25.099807999999999},{"$f":"EG72*$I72+(1-EG72)*EH72","v":70},{"$f":"EG72*$K72+(1-EG72)*EI72","v":25.099807999999999},{"$f":"MAX(MIN(EO$67,TREND(OFFSET($Z$112,MATCH(ED$67,$Z$113:$Z$122,0),5,1,2),OFFSET($Z$112,MATCH(ED$67,$Z$113:$Z$122,0),3,1,2),$I72)),EN$67)","v":0},{"$f":"$AI$107+$AI$108*EL72","v":-12.336},{"$f":"IF(ED72>0,EQ$67,EP$67)","v":0},{"$f":"IF(ED72>0,ES$67,ER$67)","v":0},{"$f":"IF(ED72>0,MAX(EL72,$I72-EN72*($I72-EH72)),MIN(EL72,$I72-EN72*($I72-EH72)))","v":0},{"$f":"IF(ED72>0,MAX(EL72,$I72-EO72*($I72-EH72)),MIN(EL72,$I72-EO72*($I72-EH72)))","v":0},{"$f":"IF(ED72>0,MAX(EM72,$K72-EN72*($K72-EI72)),MIN(EM72,$K72-EN72*($K72-EI72)))","v":-12.336},{"$f":"IF(ED72>0,MAX(EM72,$K72-EO72*($K72-EI72)),MIN(EM72,$K72-EO72*($K72-EI72)))","v":-12.336},{"$f":"(ED72>0)*OR($I72<$AI$111,$I72>$AI$112)*4.45*EG72*EF72*(ER72-ES72)/1000","v":0},{"$f":"(EE72>0)*1.08*EG72*EF72*(EQ72-EP72)/1000","v":0},{"$f":"TREND(OFFSET($Z$141,MATCH(ED$67,$Z$142:$Z$151,0),MATCH(ED72,$AA$141:$AE$141,-1),1,2),OFFSET($Z$141,0,MATCH(ED72,$AA$141:$AE$141,-1),1,2),ED72)","v":0},{"$f":"IF(EV72=0,0,ET72/EV72)","v":0},{"$f":"IF(EU$67=0,0,IF(EU$67=$U$34,EV$67,EW$67))","v":0},{"$f":"IF(EX72=0,0,EU72/EX72)","v":0},{"$f":"IF(EN72>0,0,-1*((EG72*EF72)*(EX$67*0.746/4131/$AK$116+LOOKUP(ED$67,$AH$142:$AH$151,$AL$142:$AL$151)))*(OR($I72<$AI$111,$I72>$AI$112)))","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$102:$AF$102,$AC$102:$AD$102,$I72)))*(FQ$67=\"Yes\")","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$107:$AF$107,$AC$107:$AD$107,$I72)))","v":0},{"$f":"MAX(FJ$67,TREND(OFFSET($Z$127,MATCH(FA$67,$Z$128:$Z$137,0),5,1,2),OFFSET($Z$127,MATCH(FA$67,$Z$128:$Z$137,0),3,1,2),FA72))*FG$67","v":0},{"$f":"IF(FC72=0,0,MIN(1,FH$67/FC72))","v":0},{"$f":"IF(FA72>0,$W$131,$X$131)","v":70},{"$f":"IF(FA72>0,$W$134,$X$134)","v":25.099807999999999},{"$f":"FD72*$I72+(1-FD72)*FE72","v":70},{"$f":"FD72*$K72+(1-FD72)*FF72","v":25.099807999999999},{"$f":"MAX(MIN(FL$67,TREND(OFFSET($Z$112,MATCH(FA$67,$Z$113:$Z$122,0),5,1,2),OFFSET($Z$112,MATCH(FA$67,$Z$113:$Z$122,0),3,1,2),$I72)),FK$67)","v":0},{"$f":"$AI$107+$AI$108*FI72","v":-12.336},{"$f":"IF(FA72>0,FN$67,FM$67)","v":0},{"$f":"IF(FA72>0,FP$67,FO$67)","v":0},{"$f":"IF(FA72>0,MAX(FI72,$I72-FK72*($I72-FE72)),MIN(FI72,$I72-FK72*($I72-FE72)))","v":0},{"$f":"IF(FA72>0,MAX(FI72,$I72-FL72*($I72-FE72)),MIN(FI72,$I72-FL72*($I72-FE72)))","v":0},{"$f":"IF(FA72>0,MAX(FJ72,$K72-FK72*($K72-FF72)),MIN(FJ72,$K72-FK72*($K72-FF72)))","v":-12.336},{"$f":"IF(FA72>0,MAX(FJ72,$K72-FL72*($K72-FF72)),MIN(FJ72,$K72-FL72*($K72-FF72)))","v":-12.336},{"$f":"(FA72>0)*OR($I72<$AI$111,$I72>$AI$112)*4.45*FD72*FC72*(FO72-FP72)/1000","v":0},{"$f":"(FB72>0)*1.08*FD72*FC72*(FN72-FM72)/1000","v":0},{"$f":"TREND(OFFSET($Z$141,MATCH(FA$67,$Z$142:$Z$151,0),MATCH(FA72,$AA$141:$AE$141,-1),1,2),OFFSET($Z$141,0,MATCH(FA72,$AA$141:$AE$141,-1),1,2),FA72)","v":0},{"$f":"IF(FS72=0,0,FQ72/FS72)","v":0},{"$f":"IF(FR$67=0,0,IF(FR$67=$U$34,FS$67,FT$67))","v":0},{"$f":"IF(FU72=0,0,FR72/FU72)","v":0},{"$f":"IF(FK72>0,0,-1*((FD72*FC72)*(FU$67*0.746/4131/$AK$116+LOOKUP(FA$67,$AH$142:$AH$151,$AL$142:$AL$151)))*(OR($I72<$AI$111,$I72>$AI$112)))","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$102:$AF$102,$AC$102:$AD$102,$I72)))*(GN$67=\"Yes\")","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$107:$AF$107,$AC$107:$AD$107,$I72)))","v":0},{"$f":"MAX(GG$67,TREND(OFFSET($Z$127,MATCH(FX$67,$Z$128:$Z$137,0),5,1,2),OFFSET($Z$127,MATCH(FX$67,$Z$128:$Z$137,0),3,1,2),FX72))*GD$67","v":0},{"$f":"IF(FZ72=0,0,MIN(1,GE$67/FZ72))","v":0},{"$f":"IF(FX72>0,$W$131,$X$131)","v":70},{"$f":"IF(FX72>0,$W$134,$X$134)","v":25.099807999999999},{"$f":"GA72*$I72+(1-GA72)*GB72","v":70},{"$f":"GA72*$K72+(1-GA72)*GC72","v":25.099807999999999},{"$f":"MAX(MIN(GI$67,TREND(OFFSET($Z$112,MATCH(FX$67,$Z$113:$Z$122,0),5,1,2),OFFSET($Z$112,MATCH(FX$67,$Z$113:$Z$122,0),3,1,2),$I72)),GH$67)","v":0},{"$f":"$AI$107+$AI$108*GF72","v":-12.336},{"$f":"IF(FX72>0,GK$67,GJ$67)","v":0},{"$f":"IF(FX72>0,GM$67,GL$67)","v":0},{"$f":"IF(FX72>0,MAX(GF72,$I72-GH72*($I72-GB72)),MIN(GF72,$I72-GH72*($I72-GB72)))","v":0},{"$f":"IF(FX72>0,MAX(GF72,$I72-GI72*($I72-GB72)),MIN(GF72,$I72-GI72*($I72-GB72)))","v":0},{"$f":"IF(FX72>0,MAX(GG72,$K72-GH72*($K72-GC72)),MIN(GG72,$K72-GH72*($K72-GC72)))","v":-12.336},{"$f":"IF(FX72>0,MAX(GG72,$K72-GI72*($K72-GC72)),MIN(GG72,$K72-GI72*($K72-GC72)))","v":-12.336},{"$f":"(FX72>0)*OR($I72<$AI$111,$I72>$AI$112)*4.45*GA72*FZ72*(GL72-GM72)/1000","v":0},{"$f":"(FY72>0)*1.08*GA72*FZ72*(GK72-GJ72)/1000","v":0},{"$f":"TREND(OFFSET($Z$141,MATCH(FX$67,$Z$142:$Z$151,0),MATCH(FX72,$AA$141:$AE$141,-1),1,2),OFFSET($Z$141,0,MATCH(FX72,$AA$141:$AE$141,-1),1,2),FX72)","v":0},{"$f":"IF(GP72=0,0,GN72/GP72)","v":0},{"$f":"IF(GO$67=0,0,IF(GO$67=$U$34,GP$67,GQ$67))","v":0},{"$f":"IF(GR72=0,0,GO72/GR72)","v":0},{"$f":"IF(GH72>0,0,-1*((GA72*FZ72)*(GR$67*0.746/4131/$AK$116+LOOKUP(FX$67,$AH$142:$AH$151,$AL$142:$AL$151)))*(OR($I72<$AI$111,$I72>$AI$112)))","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$102:$AF$102,$AC$102:$AD$102,$I72)))*(HK$67=\"Yes\")","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$107:$AF$107,$AC$107:$AD$107,$I72)))","v":0},{"$f":"MAX(HD$67,TREND(OFFSET($Z$127,MATCH(GU$67,$Z$128:$Z$137,0),5,1,2),OFFSET($Z$127,MATCH(GU$67,$Z$128:$Z$137,0),3,1,2),GU72))*HA$67","v":0},{"$f":"IF(GW72=0,0,MIN(1,HB$67/GW72))","v":0},{"$f":"IF(GU72>0,$W$131,$X$131)","v":70},{"$f":"IF(GU72>0,$W$134,$X$134)","v":25.099807999999999},{"$f":"GX72*$I72+(1-GX72)*GY72","v":70},{"$f":"GX72*$K72+(1-GX72)*GZ72","v":25.099807999999999},{"$f":"MAX(MIN(HF$67,TREND(OFFSET($Z$112,MATCH(GU$67,$Z$113:$Z$122,0),5,1,2),OFFSET($Z$112,MATCH(GU$67,$Z$113:$Z$122,0),3,1,2),$I72)),HE$67)","v":0},{"$f":"$AI$107+$AI$108*HC72","v":-12.336},{"$f":"IF(GU72>0,HH$67,HG$67)","v":0},{"$f":"IF(GU72>0,HJ$67,HI$67)","v":0},{"$f":"IF(GU72>0,MAX(HC72,$I72-HE72*($I72-GY72)),MIN(HC72,$I72-HE72*($I72-GY72)))","v":0},{"$f":"IF(GU72>0,MAX(HC72,$I72-HF72*($I72-GY72)),MIN(HC72,$I72-HF72*($I72-GY72)))","v":0},{"$f":"IF(GU72>0,MAX(HD72,$K72-HE72*($K72-GZ72)),MIN(HD72,$K72-HE72*($K72-GZ72)))","v":-12.336},{"$f":"IF(GU72>0,MAX(HD72,$K72-HF72*($K72-GZ72)),MIN(HD72,$K72-HF72*($K72-GZ72)))","v":-12.336},{"$f":"(GU72>0)*OR($I72<$AI$111,$I72>$AI$112)*4.45*GX72*GW72*(HI72-HJ72)/1000","v":0},{"$f":"(GV72>0)*1.08*GX72*GW72*(HH72-HG72)/1000","v":0},{"$f":"TREND(OFFSET($Z$141,MATCH(GU$67,$Z$142:$Z$151,0),MATCH(GU72,$AA$141:$AE$141,-1),1,2),OFFSET($Z$141,0,MATCH(GU72,$AA$141:$AE$141,-1),1,2),GU72)","v":0},{"$f":"IF(HM72=0,0,HK72/HM72)","v":0},{"$f":"IF(HL$67=0,0,IF(HL$67=$U$34,HM$67,HN$67))","v":0},{"$f":"IF(HO72=0,0,HL72/HO72)","v":0},{"$f":"IF(HE72>0,0,-1*((GX72*GW72)*(HO$67*0.746/4131/$AK$116+LOOKUP(GU$67,$AH$142:$AH$151,$AL$142:$AL$151)))*(OR($I72<$AI$111,$I72>$AI$112)))","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$102:$AF$102,$AC$102:$AD$102,$I72)))*(IH$67=\"Yes\")","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$107:$AF$107,$AC$107:$AD$107,$I72)))","v":0},{"$f":"MAX(IA$67,TREND(OFFSET($Z$127,MATCH(HR$67,$Z$128:$Z$137,0),5,1,2),OFFSET($Z$127,MATCH(HR$67,$Z$128:$Z$137,0),3,1,2),HR72))*HX$67","v":0},{"$f":"IF(HT72=0,0,MIN(1,HY$67/HT72))","v":0},{"$f":"IF(HR72>0,$W$131,$X$131)","v":70},{"$f":"IF(HR72>0,$W$134,$X$134)","v":25.099807999999999},{"$f":"HU72*$I72+(1-HU72)*HV72","v":70},{"$f":"HU72*$K72+(1-HU72)*HW72","v":25.099807999999999},{"$f":"MAX(MIN(IC$67,TREND(OFFSET($Z$112,MATCH(HR$67,$Z$113:$Z$122,0),5,1,2),OFFSET($Z$112,MATCH(HR$67,$Z$113:$Z$122,0),3,1,2),$I72)),IB$67)","v":0},{"$f":"$AI$107+$AI$108*HZ72","v":-12.336},{"$f":"IF(HR72>0,IE$67,ID$67)","v":0},{"$f":"IF(HR72>0,IG$67,IF$67)","v":0},{"$f":"IF(HR72>0,MAX(HZ72,$I72-IB72*($I72-HV72)),MIN(HZ72,$I72-IB72*($I72-HV72)))","v":0},{"$f":"IF(HR72>0,MAX(HZ72,$I72-IC72*($I72-HV72)),MIN(HZ72,$I72-IC72*($I72-HV72)))","v":0},{"$f":"IF(HR72>0,MAX(IA72,$K72-IB72*($K72-HW72)),MIN(IA72,$K72-IB72*($K72-HW72)))","v":-12.336},{"$f":"IF(HR72>0,MAX(IA72,$K72-IC72*($K72-HW72)),MIN(IA72,$K72-IC72*($K72-HW72)))","v":-12.336},{"$f":"(HR72>0)*OR($I72<$AI$111,$I72>$AI$112)*4.45*HU72*HT72*(IF72-IG72)/1000","v":0},{"$f":"(HS72>0)*1.08*HU72*HT72*(IE72-ID72)/1000","v":0},{"$f":"TREND(OFFSET($Z$141,MATCH(HR$67,$Z$142:$Z$151,0),MATCH(HR72,$AA$141:$AE$141,-1),1,2),OFFSET($Z$141,0,MATCH(HR72,$AA$141:$AE$141,-1),1,2),HR72)","v":0},{"$f":"IF(IJ72=0,0,IH72/IJ72)","v":0},{"$f":"IF(II$67=0,0,IF(II$67=$U$34,IJ$67,IK$67))","v":0},{"$f":"IF(IL72=0,0,II72/IL72)","v":0},{"$f":"IF(IB72>0,0,-1*((HU72*HT72)*(IL$67*0.746/4131/$AK$116+LOOKUP(HR$67,$AH$142:$AH$151,$AL$142:$AL$151)))*(OR($I72<$AI$111,$I72>$AI$112)))","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A45","v":95},{"$f":"'Project Info'!B45","v":100},{"$f":"'Project Info'!C45","v":95.219272727272724},{"$f":"'Project Info'!D45","v":74.534025272781079},{"$f":"'Project Info'!E45","v":37.923296058061368},{"$f":"'Project Info'!F45","v":0},{"$f":"'Project Info'!G45","v":0},{"$f":"'Project Info'!H45","v":0},{"$f":"'Project Info'!I45","v":0},{"$f":"'Project Info'!J45","v":0},{"$f":"'Project Info'!K45","v":0},{"$f":"'Project Info'!L45","v":0},0,0,0,0,70,25.099807999999999,{"$f":"V73*$I73+(1-V73)*W73","v":70},{"$f":"V73*$K73+(1-V73)*X73","v":25.099807999999999},0,-12.336,0,0,{"$f":"IF(S73>0,MAX(AA73,$I73-AC73*($I73-W73)),MIN(AA73,$I73-AC73*($I73-W73)))","v":0},{"$f":"IF(S73>0,MAX(AA73,$I73-AD73*($I73-W73)),MIN(AA73,$I73-AD73*($I73-W73)))","v":0},{"$f":"IF(S73>0,MAX(AB73,$K73-AC73*($K73-X73)),MIN(AB73,$K73-AC73*($K73-X73)))","v":-12.336},{"$f":"IF(S73>0,MAX(AB73,$K73-AD73*($K73-X73)),MIN(AB73,$K73-AD73*($K73-X73)))","v":-12.336},0,0,{"$f":"TREND(OFFSET($Z$141,MATCH(S$67,$Z$142:$Z$151,0),MATCH(S73,$AA$141:$AE$141,-1),1,2),OFFSET($Z$141,0,MATCH(S73,$AA$141:$AE$141,-1),1,2),S73)","v":0},{"$f":"IF(AK73=0,0,AI73/AK73)","v":0},0,0,{"$f":"IF(AC73>0,0,-1*((V73*U73)*(AM$67*0.746/4131/$AK$116+LOOKUP(S$67,$AH$142:$AH$151,$AL$142:$AL$151)))*(OR($I73<$AI$111,$I73>$AI$112)))","v":0},0,0,0,0,70,25.099807999999999,{"$f":"AS73*$I73+(1-AS73)*AT73","v":70},{"$f":"AS73*$K73+(1-AS73)*AU73","v":25.099807999999999},0,-12.336,0,0,{"$f":"IF(AP73>0,MAX(AX73,$I73-AZ73*($I73-AT73)),MIN(AX73,$I73-AZ73*($I73-AT73)))","v":0},{"$f":"IF(AP73>0,MAX(AX73,$I73-BA73*($I73-AT73)),MIN(AX73,$I73-BA73*($I73-AT73)))","v":0},{"$f":"IF(AP73>0,MAX(AY73,$K73-AZ73*($K73-AU73)),MIN(AY73,$K73-AZ73*($K73-AU73)))","v":-12.336},{"$f":"IF(AP73>0,MAX(AY73,$K73-BA73*($K73-AU73)),MIN(AY73,$K73-BA73*($K73-AU73)))","v":-12.336},0,0,{"$f":"TREND(OFFSET($Z$141,MATCH(AP$67,$Z$142:$Z$151,0),MATCH(AP73,$AA$141:$AE$141,-1),1,2),OFFSET($Z$141,0,MATCH(AP73,$AA$141:$AE$141,-1),1,2),AP73)","v":0},{"$f":"IF(BH73=0,0,BF73/BH73)","v":0},0,0,{"$f":"IF(AZ73>0,0,-1*((AS73*AR73)*(BJ$67*0.746/4131/$AK$116+LOOKUP(AP$67,$AH$142:$AH$151,$AL$142:$AL$151)))*(OR($I73<$AI$111,$I73>$AI$112)))","v":0},0,0,0,0,70,25.099807999999999,{"$f":"BP73*$I73+(1-BP73)*BQ73","v":70},{"$f":"BP73*$K73+(1-BP73)*BR73","v":25.099807999999999},0,-12.336,0,0,{"$f":"IF(BM73>0,MAX(BU73,$I73-BW73*($I73-BQ73)),MIN(BU73,$I73-BW73*($I73-BQ73)))","v":0},{"$f":"IF(BM73>0,MAX(BU73,$I73-BX73*($I73-BQ73)),MIN(BU73,$I73-BX73*($I73-BQ73)))","v":0},{"$f":"IF(BM73>0,MAX(BV73,$K73-BW73*($K73-BR73)),MIN(BV73,$K73-BW73*($K73-BR73)))","v":-12.336},{"$f":"IF(BM73>0,MAX(BV73,$K73-BX73*($K73-BR73)),MIN(BV73,$K73-BX73*($K73-BR73)))","v":-12.336},0,0,{"$f":"TREND(OFFSET($Z$141,MATCH(BM$67,$Z$142:$Z$151,0),MATCH(BM73,$AA$141:$AE$141,-1),1,2),OFFSET($Z$141,0,MATCH(BM73,$AA$141:$AE$141,-1),1,2),BM73)","v":0},{"$f":"IF(CE73=0,0,CC73/CE73)","v":0},0,0,{"$f":"IF(BW73>0,0,-1*((BP73*BO73)*(CG$67*0.746/4131/$AK$116+LOOKUP(BM$67,$AH$142:$AH$151,$AL$142:$AL$151)))*(OR($I73<$AI$111,$I73>$AI$112)))","v":0},0,0,0,0,70,25.099807999999999,{"$f":"CM73*$I73+(1-CM73)*CN73","v":70},{"$f":"CM73*$K73+(1-CM73)*CO73","v":25.099807999999999},0,-12.336,0,0,{"$f":"IF(CJ73>0,MAX(CR73,$I73-CT73*($I73-CN73)),MIN(CR73,$I73-CT73*($I73-CN73)))","v":0},{"$f":"IF(CJ73>0,MAX(CR73,$I73-CU73*($I73-CN73)),MIN(CR73,$I73-CU73*($I73-CN73)))","v":0},{"$f":"IF(CJ73>0,MAX(CS73,$K73-CT73*($K73-CO73)),MIN(CS73,$K73-CT73*($K73-CO73)))","v":-12.336},{"$f":"IF(CJ73>0,MAX(CS73,$K73-CU73*($K73-CO73)),MIN(CS73,$K73-CU73*($K73-CO73)))","v":-12.336},0,0,{"$f":"TREND(OFFSET($Z$141,MATCH(CJ$67,$Z$142:$Z$151,0),MATCH(CJ73,$AA$141:$AE$141,-1),1,2),OFFSET($Z$141,0,MATCH(CJ73,$AA$141:$AE$141,-1),1,2),CJ73)","v":0},{"$f":"IF(DB73=0,0,CZ73/DB73)","v":0},0,0,{"$f":"IF(CT73>0,0,-1*((CM73*CL73)*(DD$67*0.746/4131/$AK$116+LOOKUP(CJ$67,$AH$142:$AH$151,$AL$142:$AL$151)))*(OR($I73<$AI$111,$I73>$AI$112)))","v":0},0,0,0,0,70,25.099807999999999,{"$f":"DJ73*$I73+(1-DJ73)*DK73","v":70},{"$f":"DJ73*$K73+(1-DJ73)*DL73","v":25.099807999999999},0,-12.336,0,0,{"$f":"IF(DG73>0,MAX(DO73,$I73-DQ73*($I73-DK73)),MIN(DO73,$I73-DQ73*($I73-DK73)))","v":0},{"$f":"IF(DG73>0,MAX(DO73,$I73-DR73*($I73-DK73)),MIN(DO73,$I73-DR73*($I73-DK73)))","v":0},{"$f":"IF(DG73>0,MAX(DP73,$K73-DQ73*($K73-DL73)),MIN(DP73,$K73-DQ73*($K73-DL73)))","v":-12.336},{"$f":"IF(DG73>0,MAX(DP73,$K73-DR73*($K73-DL73)),MIN(DP73,$K73-DR73*($K73-DL73)))","v":-12.336},0,0,{"$f":"TREND(OFFSET($Z$141,MATCH(DG$67,$Z$142:$Z$151,0),MATCH(DG73,$AA$141:$AE$141,-1),1,2),OFFSET($Z$141,0,MATCH(DG73,$AA$141:$AE$141,-1),1,2),DG73)","v":0},{"$f":"IF(DY73=0,0,DW73/DY73)","v":0},0,0,{"$f":"IF(DQ73>0,0,-1*((DJ73*DI73)*(EA$67*0.746/4131/$AK$116+LOOKUP(DG$67,$AH$142:$AH$151,$AL$142:$AL$151)))*(OR($I73<$AI$111,$I73>$AI$112)))","v":0},0,0,0,0,70,25.099807999999999,{"$f":"EG73*$I73+(1-EG73)*EH73","v":70},{"$f":"EG73*$K73+(1-EG73)*EI73","v":25.099807999999999},0,-12.336,0,0,{"$f":"IF(ED73>0,MAX(EL73,$I73-EN73*($I73-EH73)),MIN(EL73,$I73-EN73*($I73-EH73)))","v":0},{"$f":"IF(ED73>0,MAX(EL73,$I73-EO73*($I73-EH73)),MIN(EL73,$I73-EO73*($I73-EH73)))","v":0},{"$f":"IF(ED73>0,MAX(EM73,$K73-EN73*($K73-EI73)),MIN(EM73,$K73-EN73*($K73-EI73)))","v":-12.336},{"$f":"IF(ED73>0,MAX(EM73,$K73-EO73*($K73-EI73)),MIN(EM73,$K73-EO73*($K73-EI73)))","v":-12.336},0,0,{"$f":"TREND(OFFSET($Z$141,MATCH(ED$67,$Z$142:$Z$151,0),MATCH(ED73,$AA$141:$AE$141,-1),1,2),OFFSET($Z$141,0,MATCH(ED73,$AA$141:$AE$141,-1),1,2),ED73)","v":0},{"$f":"IF(EV73=0,0,ET73/EV73)","v":0},0,0,{"$f":"IF(EN73>0,0,-1*((EG73*EF73)*(EX$67*0.746/4131/$AK$116+LOOKUP(ED$67,$AH$142:$AH$151,$AL$142:$AL$151)))*(OR($I73<$AI$111,$I73>$AI$112)))","v":0},0,0,0,0,70,25.099807999999999,{"$f":"FD73*$I73+(1-FD73)*FE73","v":70},{"$f":"FD73*$K73+(1-FD73)*FF73","v":25.099807999999999},0,-12.336,0,0,{"$f":"IF(FA73>0,MAX(FI73,$I73-FK73*($I73-FE73)),MIN(FI73,$I73-FK73*($I73-FE73)))","v":0},{"$f":"IF(FA73>0,MAX(FI73,$I73-FL73*($I73-FE73)),MIN(FI73,$I73-FL73*($I73-FE73)))","v":0},{"$f":"IF(FA73>0,MAX(FJ73,$K73-FK73*($K73-FF73)),MIN(FJ73,$K73-FK73*($K73-FF73)))","v":-12.336},{"$f":"IF(FA73>0,MAX(FJ73,$K73-FL73*($K73-FF73)),MIN(FJ73,$K73-FL73*($K73-FF73)))","v":-12.336},0,0,{"$f":"TREND(OFFSET($Z$141,MATCH(FA$67,$Z$142:$Z$151,0),MATCH(FA73,$AA$141:$AE$141,-1),1,2),OFFSET($Z$141,0,MATCH(FA73,$AA$141:$AE$141,-1),1,2),FA73)","v":0},{"$f":"IF(FS73=0,0,FQ73/FS73)","v":0},0,0,{"$f":"IF(FK73>0,0,-1*((FD73*FC73)*(FU$67*0.746/4131/$AK$116+LOOKUP(FA$67,$AH$142:$AH$151,$AL$142:$AL$151)))*(OR($I73<$AI$111,$I73>$AI$112)))","v":0},0,0,0,0,70,25.099807999999999,{"$f":"GA73*$I73+(1-GA73)*GB73","v":70},{"$f":"GA73*$K73+(1-GA73)*GC73","v":25.099807999999999},0,-12.336,0,0,{"$f":"IF(FX73>0,MAX(GF73,$I73-GH73*($I73-GB73)),MIN(GF73,$I73-GH73*($I73-GB73)))","v":0},{"$f":"IF(FX73>0,MAX(GF73,$I73-GI73*($I73-GB73)),MIN(GF73,$I73-GI73*($I73-GB73)))","v":0},{"$f":"IF(FX73>0,MAX(GG73,$K73-GH73*($K73-GC73)),MIN(GG73,$K73-GH73*($K73-GC73)))","v":-12.336},{"$f":"IF(FX73>0,MAX(GG73,$K73-GI73*($K73-GC73)),MIN(GG73,$K73-GI73*($K73-GC73)))","v":-12.336},0,0,{"$f":"TREND(OFFSET($Z$141,MATCH(FX$67,$Z$142:$Z$151,0),MATCH(FX73,$AA$141:$AE$141,-1),1,2),OFFSET($Z$141,0,MATCH(FX73,$AA$141:$AE$141,-1),1,2),FX73)","v":0},{"$f":"IF(GP73=0,0,GN73/GP73)","v":0},0,0,{"$f":"IF(GH73>0,0,-1*((GA73*FZ73)*(GR$67*0.746/4131/$AK$116+LOOKUP(FX$67,$AH$142:$AH$151,$AL$142:$AL$151)))*(OR($I73<$AI$111,$I73>$AI$112)))","v":0},0,0,0,0,70,25.099807999999999,{"$f":"GX73*$I73+(1-GX73)*GY73","v":70},{"$f":"GX73*$K73+(1-GX73)*GZ73","v":25.099807999999999},0,-12.336,0,0,{"$f":"IF(GU73>0,MAX(HC73,$I73-HE73*($I73-GY73)),MIN(HC73,$I73-HE73*($I73-GY73)))","v":0},{"$f":"IF(GU73>0,MAX(HC73,$I73-HF73*($I73-GY73)),MIN(HC73,$I73-HF73*($I73-GY73)))","v":0},{"$f":"IF(GU73>0,MAX(HD73,$K73-HE73*($K73-GZ73)),MIN(HD73,$K73-HE73*($K73-GZ73)))","v":-12.336},{"$f":"IF(GU73>0,MAX(HD73,$K73-HF73*($K73-GZ73)),MIN(HD73,$K73-HF73*($K73-GZ73)))","v":-12.336},0,0,{"$f":"TREND(OFFSET($Z$141,MATCH(GU$67,$Z$142:$Z$151,0),MATCH(GU73,$AA$141:$AE$141,-1),1,2),OFFSET($Z$141,0,MATCH(GU73,$AA$141:$AE$141,-1),1,2),GU73)","v":0},{"$f":"IF(HM73=0,0,HK73/HM73)","v":0},0,0,{"$f":"IF(HE73>0,0,-1*((GX73*GW73)*(HO$67*0.746/4131/$AK$116+LOOKUP(GU$67,$AH$142:$AH$151,$AL$142:$AL$151)))*(OR($I73<$AI$111,$I73>$AI$112)))","v":0},0,0,0,0,70,25.099807999999999,{"$f":"HU73*$I73+(1-HU73)*HV73","v":70},{"$f":"HU73*$K73+(1-HU73)*HW73","v":25.099807999999999},0,-12.336,0,0,{"$f":"IF(HR73>0,MAX(HZ73,$I73-IB73*($I73-HV73)),MIN(HZ73,$I73-IB73*($I73-HV73)))","v":0},{"$f":"IF(HR73>0,MAX(HZ73,$I73-IC73*($I73-HV73)),MIN(HZ73,$I73-IC73*($I73-HV73)))","v":0},{"$f":"IF(HR73>0,MAX(IA73,$K73-IB73*($K73-HW73)),MIN(IA73,$K73-IB73*($K73-HW73)))","v":-12.336},{"$f":"IF(HR73>0,MAX(IA73,$K73-IC73*($K73-HW73)),MIN(IA73,$K73-IC73*($K73-HW73)))","v":-12.336},0,0,{"$f":"TREND(OFFSET($Z$141,MATCH(HR$67,$Z$142:$Z$151,0),MATCH(HR73,$AA$141:$AE$141,-1),1,2),OFFSET($Z$141,0,MATCH(HR73,$AA$141:$AE$141,-1),1,2),HR73)","v":0},{"$f":"IF(IJ73=0,0,IH73/IJ73)","v":0},0,0,{"$f":"IF(IB73>0,0,-1*((HU73*HT73)*(IL$67*0.746/4131/$AK$116+LOOKUP(HR$67,$AH$142:$AH$151,$AL$142:$AL$151)))*(OR($I73<$AI$111,$I73>$AI$112)))","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A46","v":90},{"$f":"'Project Info'!B46","v":95},{"$f":"'Project Info'!C46","v":92.016049160256074},{"$f":"'Project Info'!D46","v":72.911561930607689},{"$f":"'Project Info'!E46","v":36.467095439351091},{"$f":"'Project Info'!F46","v":0},{"$f":"'Project Info'!G46","v":0},{"$f":"'Project Info'!H46","v":0},{"$f":"'Project Info'!I46","v":0},{"$f":"'Project Info'!J46","v":0},{"$f":"'Project Info'!K46","v":0},{"$f":"'Project Info'!L46","v":0},0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A47","v":85},{"$f":"'Project Info'!B47","v":90},{"$f":"'Project Info'!C47","v":87.457811360655285},{"$f":"'Project Info'!D47","v":70.80538329449476},{"$f":"'Project Info'!E47","v":34.679413213566804},{"$f":"'Project Info'!F47","v":0},{"$f":"'Project Info'!G47","v":0},{"$f":"'Project Info'!H47","v":0},{"$f":"'Project Info'!I47","v":0},{"$f":"'Project Info'!J47","v":0},{"$f":"'Project Info'!K47","v":0},{"$f":"'Project Info'!L47","v":0},0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A48","v":80},{"$f":"'Project Info'!B48","v":85},{"$f":"'Project Info'!C48","v":82.136788830239965},{"$f":"'Project Info'!D48","v":67.872393622439333},{"$f":"'Project Info'!E48","v":32.296248223809314},{"$f":"'Project Info'!F48","v":0},{"$f":"'Project Info'!G48","v":0},{"$f":"'Project Info'!H48","v":0},{"$f":"'Project Info'!I48","v":0},{"$f":"'Project Info'!J48","v":0},{"$f":"'Project Info'!K48","v":0},{"$f":"'Project Info'!L48","v":0},0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A49","v":75},{"$f":"'Project Info'!B49","v":80},{"$f":"'Project Info'!C49","v":76.988400157585886},{"$f":"'Project Info'!D49","v":65.129261896908645},{"$f":"'Project Info'!E49","v":30.190476812806729},{"$f":"'Project Info'!F49","v":0},{"$f":"'Project Info'!G49","v":0},{"$f":"'Project Info'!H49","v":0},{"$f":"'Project Info'!I49","v":0},{"$f":"'Project Info'!J49","v":0},{"$f":"'Project Info'!K49","v":0},{"$f":"'Project Info'!L49","v":0},0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A50","v":70},{"$f":"'Project Info'!B50","v":75},{"$f":"'Project Info'!C50","v":72.457982050814195},{"$f":"'Project Info'!D50","v":63.604425012889301},{"$f":"'Project Info'!E50","v":29.088683095945193},{"$f":"'Project Info'!F50","v":0},{"$f":"'Project Info'!G50","v":0},{"$f":"'Project Info'!H50","v":0},{"$f":"'Project Info'!I50","v":0},{"$f":"'Project Info'!J50","v":0},{"$f":"'Project Info'!K50","v":0},{"$f":"'Project Info'!L50","v":0},0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A51","v":65},{"$f":"'Project Info'!B51","v":70},{"$f":"'Project Info'!C51","v":67.815831070966169},{"$f":"'Project Info'!D51","v":61.631331368130574},{"$f":"'Project Info'!E51","v":27.661514889731574},{"$f":"'Project Info'!F51","v":0},{"$f":"'Project Info'!G51","v":0},{"$f":"'Project Info'!H51","v":0},{"$f":"'Project Info'!I51","v":0},{"$f":"'Project Info'!J51","v":0},{"$f":"'Project Info'!K51","v":0},{"$f":"'Project Info'!L51","v":0},0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A52","v":60},{"$f":"'Project Info'!B52","v":65},{"$f":"'Project Info'!C52","v":62.535961472271332},{"$f":"'Project Info'!D52","v":57.135476922863582},{"$f":"'Project Info'!E52","v":24.623037157728302},{"$f":"'Project Info'!F52","v":0},{"$f":"'Project Info'!G52","v":0},{"$f":"'Project Info'!H52","v":0},{"$f":"'Project Info'!I52","v":0},{"$f":"'Project Info'!J52","v":0},{"$f":"'Project Info'!K52","v":0},{"$f":"'Project Info'!L52","v":0},0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A53","v":55},{"$f":"'Project Info'!B53","v":60},{"$f":"'Project Info'!C53","v":57.125792270740902},{"$f":"'Project Info'!D53","v":52.596971157053673},{"$f":"'Project Info'!E53","v":21.818001539159841},{"$f":"'Project Info'!F53","v":0},{"$f":"'Project Info'!G53","v":0},{"$f":"'Project Info'!H53","v":0},{"$f":"'Project Info'!I53","v":0},{"$f":"'Project Info'!J53","v":0},{"$f":"'Project Info'!K53","v":0},{"$f":"'Project Info'!L53","v":0},0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A54","v":50},{"$f":"'Project Info'!B54","v":55},{"$f":"'Project Info'!C54","v":52.235698854337961},{"$f":"'Project Info'!D54","v":48.022768090099298},{"$f":"'Project Info'!E54","v":19.246640192796217},{"$f":"'Project Info'!F54","v":0},{"$f":"'Project Info'!G54","v":0},{"$f":"'Project Info'!H54","v":0},{"$f":"'Project Info'!I54","v":0},{"$f":"'Project Info'!J54","v":0},{"$f":"'Project Info'!K54","v":0},{"$f":"'Project Info'!L54","v":0},0,4.2721017705686037E-2,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,4.2721017705686037E-2,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,4.2721017705686037E-2,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,4.2721017705686037E-2,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,4.2721017705686037E-2,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,4.2721017705686037E-2,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,4.2721017705686037E-2,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,4.2721017705686037E-2,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,4.2721017705686037E-2,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,4.2721017705686037E-2,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A55","v":45},{"$f":"'Project Info'!B55","v":50},{"$f":"'Project Info'!C55","v":47.459170258371508},{"$f":"'Project Info'!D55","v":43.465397050422162},{"$f":"'Project Info'!E55","v":16.894183241713304},{"$f":"'Project Info'!F55","v":0},{"$f":"'Project Info'!G55","v":0},{"$f":"'Project Info'!H55","v":0},{"$f":"'Project Info'!I55","v":0},{"$f":"'Project Info'!J55","v":0},{"$f":"'Project Info'!K55","v":0},{"$f":"'Project Info'!L55","v":0},0,0.11654009600698578,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.11654009600698578,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.11654009600698578,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.11654009600698578,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.11654009600698578,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.11654009600698578,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.11654009600698578,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.11654009600698578,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.11654009600698578,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.11654009600698578,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A56","v":40},{"$f":"'Project Info'!B56","v":45},{"$f":"'Project Info'!C56","v":42.677030404888129},{"$f":"'Project Info'!D56","v":38.812544504634097},{"$f":"'Project Info'!E56","v":14.690265649465921},{"$f":"'Project Info'!F56","v":0},{"$f":"'Project Info'!G56","v":0},{"$f":"'Project Info'!H56","v":0},{"$f":"'Project Info'!I56","v":0},{"$f":"'Project Info'!J56","v":0},{"$f":"'Project Info'!K56","v":0},{"$f":"'Project Info'!L56","v":0},0,0.19044589374263798,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.19044589374263798,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.19044589374263798,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.19044589374263798,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.19044589374263798,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.19044589374263798,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.19044589374263798,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.19044589374263798,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.19044589374263798,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.19044589374263798,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A57","v":35},{"$f":"'Project Info'!B57","v":40},{"$f":"'Project Info'!C57","v":37.333046773755832},{"$f":"'Project Info'!D57","v":33.904706919479686},{"$f":"'Project Info'!E57","v":12.53841602318813},{"$f":"'Project Info'!F57","v":0},{"$f":"'Project Info'!G57","v":0},{"$f":"'Project Info'!H57","v":0},{"$f":"'Project Info'!I57","v":0},{"$f":"'Project Info'!J57","v":0},{"$f":"'Project Info'!K57","v":0},{"$f":"'Project Info'!L57","v":0},0,0.27303473167831893,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.27303473167831893,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.27303473167831893,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.27303473167831893,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.27303473167831893,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.27303473167831893,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.27303473167831893,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.27303473167831893,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.27303473167831893,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.27303473167831893,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A58","v":30},{"$f":"'Project Info'!B58","v":35},{"$f":"'Project Info'!C58","v":32.638179845662044},{"$f":"'Project Info'!D58","v":29.547170928664851},{"$f":"'Project Info'!E58","v":10.728972818165861},{"$f":"'Project Info'!F58","v":0},{"$f":"'Project Info'!G58","v":0},{"$f":"'Project Info'!H58","v":0},{"$f":"'Project Info'!I58","v":0},{"$f":"'Project Info'!J58","v":0},{"$f":"'Project Info'!K58","v":0},{"$f":"'Project Info'!L58","v":0},0,0.34559176602158659,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.34559176602158659,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.34559176602158659,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.34559176602158659,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.34559176602158659,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.34559176602158659,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.34559176602158659,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.34559176602158659,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.34559176602158659,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.34559176602158659,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A59","v":25},{"$f":"'Project Info'!B59","v":30},{"$f":"'Project Info'!C59","v":27.529264646850947},{"$f":"'Project Info'!D59","v":24.652717392657845},{"$f":"'Project Info'!E59","v":8.8041305482613303},{"$f":"'Project Info'!F59","v":0},{"$f":"'Project Info'!G59","v":0},{"$f":"'Project Info'!H59","v":0},{"$f":"'Project Info'!I59","v":0},{"$f":"'Project Info'!J59","v":0},{"$f":"'Project Info'!K59","v":0},{"$f":"'Project Info'!L59","v":0},0,0.42454772818503078,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.42454772818503078,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.42454772818503078,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.42454772818503078,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.42454772818503078,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.42454772818503078,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.42454772818503078,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.42454772818503078,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.42454772818503078,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.42454772818503078,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A60","v":20},{"$f":"'Project Info'!B60","v":25},{"$f":"'Project Info'!C60","v":22.998111483544687},{"$f":"'Project Info'!D60","v":20.383306659827422},{"$f":"'Project Info'!E60","v":7.246164547543378},{"$f":"'Project Info'!F60","v":0},{"$f":"'Project Info'!G60","v":0},{"$f":"'Project Info'!H60","v":0},{"$f":"'Project Info'!I60","v":0},{"$f":"'Project Info'!J60","v":0},{"$f":"'Project Info'!K60","v":0},{"$f":"'Project Info'!L60","v":0},0,0.49457464070885476,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.49457464070885476,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.49457464070885476,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.49457464070885476,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.49457464070885476,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.49457464070885476,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.49457464070885476,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.49457464070885476,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.49457464070885476,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.49457464070885476,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A61","v":15},{"$f":"'Project Info'!B61","v":20},{"$f":"'Project Info'!C61","v":17.808510327474309},{"$f":"'Project Info'!D61","v":15.420865796304254},{"$f":"'Project Info'!E61","v":5.5490484131518292},{"$f":"'Project Info'!F61","v":0},{"$f":"'Project Info'!G61","v":0},{"$f":"'Project Info'!H61","v":0},{"$f":"'Project Info'!I61","v":0},{"$f":"'Project Info'!J61","v":0},{"$f":"'Project Info'!K61","v":0},{"$f":"'Project Info'!L61","v":0},0,0.57477756766630606,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.57477756766630606,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.57477756766630606,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.57477756766630606,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.57477756766630606,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.57477756766630606,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.57477756766630606,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.57477756766630606,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.57477756766630606,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.57477756766630606,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A62","v":10},{"$f":"'Project Info'!B62","v":15},{"$f":"'Project Info'!C62","v":12.269931130346862},{"$f":"'Project Info'!D62","v":10.318264913023604},{"$f":"'Project Info'!E62","v":3.9082824916941998},{"$f":"'Project Info'!F62","v":0},{"$f":"'Project Info'!G62","v":0},{"$f":"'Project Info'!H62","v":0},{"$f":"'Project Info'!I62","v":0},{"$f":"'Project Info'!J62","v":0},{"$f":"'Project Info'!K62","v":0},{"$f":"'Project Info'!L62","v":0},0,0.66037379162191201,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.66037379162191201,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.66037379162191201,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.66037379162191201,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.66037379162191201,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.66037379162191201,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.66037379162191201,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.66037379162191201,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.66037379162191201,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.66037379162191201,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A63","v":5},{"$f":"'Project Info'!B63","v":10},{"$f":"'Project Info'!C63","v":7.3137581369917548},{"$f":"'Project Info'!D63","v":5.7052382449247707},{"$f":"'Project Info'!E63","v":2.5019418419888937},{"$f":"'Project Info'!F63","v":0},{"$f":"'Project Info'!G63","v":0},{"$f":"'Project Info'!H63","v":0},{"$f":"'Project Info'!I63","v":0},{"$f":"'Project Info'!J63","v":0},{"$f":"'Project Info'!K63","v":0},{"$f":"'Project Info'!L63","v":0},0,0.73696919242830916,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.73696919242830916,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.73696919242830916,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.73696919242830916,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.73696919242830916,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.73696919242830916,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.73696919242830916,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.73696919242830916,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.73696919242830916,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.73696919242830916,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A64","v":0},{"$f":"'Project Info'!B64","v":5},{"$f":"'Project Info'!C64","v":2.6119461836144886},{"$f":"'Project Info'!D64","v":1.2699770062067783},{"$f":"'Project Info'!E64","v":1.2046477897733283},{"$f":"'Project Info'!F64","v":0},{"$f":"'Project Info'!G64","v":0},{"$f":"'Project Info'!H64","v":0},{"$f":"'Project Info'!I64","v":0},{"$f":"'Project Info'!J64","v":0},{"$f":"'Project Info'!K64","v":0},{"$f":"'Project Info'!L64","v":0},0,0.80963355898050327,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.80963355898050327,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.80963355898050327,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.80963355898050327,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.80963355898050327,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.80963355898050327,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.80963355898050327,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.80963355898050327,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.80963355898050327,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0,0,0.80963355898050327,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,0,0,-12.336,-12.336,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A65","v":-5},{"$f":"'Project Info'!B65","v":0},{"$f":"'Project Info'!C65","v":-1.6731398516793925},{"$f":"'Project Info'!D65","v":-2.7083318773557807},{"$f":"'Project Info'!E65","v":7.9391832815876459E-2},{"$f":"'Project Info'!F65","v":0},{"$f":"'Project Info'!G65","v":0},{"$f":"'Project Info'!H65","v":0},{"$f":"'Project Info'!I65","v":0},{"$f":"'Project Info'!J65","v":0},{"$f":"'Project Info'!K65","v":0},{"$f":"'Project Info'!L65","v":0},0,0.87585761588959044,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-1.6731398516793925,-1.6731398516793925,-12.336,-12.336,0,0,0,0,0,0,0,0,0.87585761588959044,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-1.6731398516793925,-1.6731398516793925,-12.336,-12.336,0,0,0,0,0,0,0,0,0.87585761588959044,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-1.6731398516793925,-1.6731398516793925,-12.336,-12.336,0,0,0,0,0,0,0,0,0.87585761588959044,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-1.6731398516793925,-1.6731398516793925,-12.336,-12.336,0,0,0,0,0,0,0,0,0.87585761588959044,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-1.6731398516793925,-1.6731398516793925,-12.336,-12.336,0,0,0,0,0,0,0,0,0.87585761588959044,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-1.6731398516793925,-1.6731398516793925,-12.336,-12.336,0,0,0,0,0,0,0,0,0.87585761588959044,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-1.6731398516793925,-1.6731398516793925,-12.336,-12.336,0,0,0,0,0,0,0,0,0.87585761588959044,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-1.6731398516793925,-1.6731398516793925,-12.336,-12.336,0,0,0,0,0,0,0,0,0.87585761588959044,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-1.6731398516793925,-1.6731398516793925,-12.336,-12.336,0,0,0,0,0,0,0,0,0.87585761588959044,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-1.6731398516793925,-1.6731398516793925,-12.336,-12.336,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A66","v":-10},{"$f":"'Project Info'!B66","v":-5},{"$f":"'Project Info'!C66","v":-6.5729865085377277},{"$f":"'Project Info'!D66","v":-7.2465935998252222},{"$f":"'Project Info'!E66","v":-1.168423365310433},{"$f":"'Project Info'!F66","v":0},{"$f":"'Project Info'!G66","v":0},{"$f":"'Project Info'!H66","v":0},{"$f":"'Project Info'!I66","v":0},{"$f":"'Project Info'!J66","v":0},{"$f":"'Project Info'!K66","v":0},{"$f":"'Project Info'!L66","v":0},0,0.95158251876831024,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-6.5729865085377277,-6.5729865085377277,-12.336,-12.336,0,0,0,0,0,0,0,0,0.95158251876831024,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-6.5729865085377277,-6.5729865085377277,-12.336,-12.336,0,0,0,0,0,0,0,0,0.95158251876831024,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-6.5729865085377277,-6.5729865085377277,-12.336,-12.336,0,0,0,0,0,0,0,0,0.95158251876831024,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-6.5729865085377277,-6.5729865085377277,-12.336,-12.336,0,0,0,0,0,0,0,0,0.95158251876831024,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-6.5729865085377277,-6.5729865085377277,-12.336,-12.336,0,0,0,0,0,0,0,0,0.95158251876831024,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-6.5729865085377277,-6.5729865085377277,-12.336,-12.336,0,0,0,0,0,0,0,0,0.95158251876831024,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-6.5729865085377277,-6.5729865085377277,-12.336,-12.336,0,0,0,0,0,0,0,0,0.95158251876831024,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-6.5729865085377277,-6.5729865085377277,-12.336,-12.336,0,0,0,0,0,0,0,0,0.95158251876831024,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-6.5729865085377277,-6.5729865085377277,-12.336,-12.336,0,0,0,0,0,0,0,0,0.95158251876831024,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-6.5729865085377277,-6.5729865085377277,-12.336,-12.336,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A67","v":-15},{"$f":"'Project Info'!B67","v":-10},{"$f":"'Project Info'!C67","v":-15.32570353422995},{"$f":"'Project Info'!D67","v":-15.707838211108999},{"$f":"'Project Info'!E67","v":-3.4051318156661381},{"$f":"'Project Info'!F67","v":0},{"$f":"'Project Info'!G67","v":0},{"$f":"'Project Info'!H67","v":0},{"$f":"'Project Info'!I67","v":0},{"$f":"'Project Info'!J67","v":0},{"$f":"'Project Info'!K67","v":0},{"$f":"'Project Info'!L67","v":0},0,1,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-15.32570353422995,-15.32570353422995,-12.336,-12.336,0,0,0,0,0,0,0,0,1,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-15.32570353422995,-15.32570353422995,-12.336,-12.336,0,0,0,0,0,0,0,0,1,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-15.32570353422995,-15.32570353422995,-12.336,-12.336,0,0,0,0,0,0,0,0,1,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-15.32570353422995,-15.32570353422995,-12.336,-12.336,0,0,0,0,0,0,0,0,1,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-15.32570353422995,-15.32570353422995,-12.336,-12.336,0,0,0,0,0,0,0,0,1,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-15.32570353422995,-15.32570353422995,-12.336,-12.336,0,0,0,0,0,0,0,0,1,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-15.32570353422995,-15.32570353422995,-12.336,-12.336,0,0,0,0,0,0,0,0,1,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-15.32570353422995,-15.32570353422995,-12.336,-12.336,0,0,0,0,0,0,0,0,1,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-15.32570353422995,-15.32570353422995,-12.336,-12.336,0,0,0,0,0,0,0,0,1,0,0,70,25.099807999999999,70,25.099807999999999,0,-12.336,0,0,-15.32570353422995,-15.32570353422995,-12.336,-12.336,0,0,0,0,0,0,0]
[]
[null,null,null,null,null,null,null,null,null,"DAT Reset: OAT Range",null,"Min","Min","Max"]
[null,null,null,null,null,null,null,null,null,"Max OAT","Min OAT","Flow","DAT","DAT",null,null,null,null,"TOTAL FROM ALL SYSTEMS",null,null,null,null,null,null,"Cooling Load Profiles"]
[null,null,null,null,null,null,"System Type Options",null,null,"°F","°F","Ratio %","°F","°F",null,null,null,null,"End Use",null,null,null,"Total","Total",null,null,null,null,"Occupied Profile"]
[null,null,null,null,null,null,"1-Mixed Air w/ VAV Terminal Units",null,null,85,55,0.5,55,60,null,null,null,null,"Demand Reduction",null,null,null,"Demand","Demand",null,null,null,null,"Max OAT","Min OAT","% Load @","%Load @"]
[null,null,null,null,null,null,"2-Mix Air Constant Volume",null,null,85,15,1,55,95,null,null,null,null,"Cooling","Heating","Heating","Fans","Reduction","Reduction",null,null,null,null,"°F","°F","Max OAT","Min OAT"]
[null,null,null,null,null,null,"3-100% OA w/ VAV Terminal Units",null,null,85,55,0.75,55,68,null,null,null,null,"kW","MBH","kW","kW","kW","MBH",null,null,null,null,95,55,0.85,0]
[null,null,null,null,null,null,"4-100% OA - Constant Volume",null,null,85,55,1,55,68,null,null,null,null,{"$f":"AL72+BI72+CF72+DC72+DZ72+EW72+FT72+GQ72+HN72+IK72","v":0},{"$f":"AN72*($U$22=$U$34)+BK72*($U$23=$U$34)+CH72*($U$24=$U$34)+DE72*($U$25=$U$34)+EB72*($U$26=$U$34)+EY72*($U$27=$U$34)+FV72*($U$28=$U$34)+GS72*($U$29=$U$34)+HP72*($U$30=$U$34)+IM72*($U$31=$U$34)","v":0},{"$f":"(AN72*($U$22=\"Elec\")+BK72*($U$23=\"Elec\")+CH72*($U$24=\"Elec\")+DE72*($U$25=\"Elec\")+EB72*($U$26=\"Elec\")+EY72*($U$27=\"Elec\")+FV72*($U$28=\"Elec\")+GS72*($U$29=\"Elec\")+HP72*($U$30=\"Elec\")+IM72*($U$31=\"Elec\"))/3.412","v":0},{"$f":"AO72+BL72+CI72+DF72+EC72+EZ72+FW72+GT72+HQ72+IN72","v":0},{"$f":"S103+U103+V103","v":0},{"$f":"T103","v":0},null,"Heating Load Profiles"]
[null,null,null,null,null,null,"5-Other",null,null,85,55,0.5,55,60,null,null,null,null,0,{"$f":"AN73*($U$22=$U$34)+BK73*($U$23=$U$34)+CH73*($U$24=$U$34)+DE73*($U$25=$U$34)+EB73*($U$26=$U$34)+EY73*($U$27=$U$34)+FV73*($U$28=$U$34)+GS73*($U$29=$U$34)+HP73*($U$30=$U$34)+IM73*($U$31=$U$34)","v":0},{"$f":"(AN73*($U$22=\"Elec\")+BK73*($U$23=\"Elec\")+CH73*($U$24=\"Elec\")+DE73*($U$25=\"Elec\")+EB73*($U$26=\"Elec\")+EY73*($U$27=\"Elec\")+FV73*($U$28=\"Elec\")+GS73*($U$29=\"Elec\")+HP73*($U$30=\"Elec\")+IM73*($U$31=\"Elec\"))/3.412","v":0},{"$f":"AO73+BL73+CI73+DF73+EC73+EZ73+FW73+GT73+HQ73+IN73","v":0},{"$f":"S104+U104+V104","v":0},{"$f":"T104","v":0},null,null,null,null,"Occupied Profile"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,null,null,null,"Max OAT","Min OAT","% Load @","%Load @",null,"°F Db to Sat. Btu/lb"]
[null,null,null,null,null,null,null,null,"Recovery Types",null,"kW/CFM","Source",null,null,null,null,null,null,0,0,0,0,0,0,null,null,null,null,"°F","°F","Max OAT","Min OAT",null,"Conversion"]
[null,null,null,null,null,null,null,null,"Fixed Heat Exchanger",null,0,null,null,null,null,null,null,null,0,0,0,0,0,0,null,null,null,null,55,0,0,0.85,null,"constant",-12.336]
[null,null,null,null,null,null,null,null,"Heat Pipe",null,0,null,null,null,null,null,null,null,0,0,0,0,0,0,null,null,null,null,null,null,null,null,null,"x-term",0.64859999999999995]
[null,null,null,null,null,null,null,null,"Run-Around Loop",null,3.8499999999999998E-4,"sample Konvekta submittal",null,null,null,null,null,null,0,0,0,0,0,0,null,"AHU Discharge Air Temperature Reset Profiles"]
[null,null,null,null,null,null,null,null,"Wheel",null,8.5000000000000006E-5,"eQUEST default",null,null,null,null,null,null,0,0,0,0,0,0,null,"System",null,null,"Occupied Profile",null,null,null,null,"Economizer Range"]
[null,null,null,null,null,null,null,null,0,null,0,null,null,null,null,null,null,null,0,0,0,0,0,0,null,"Type","Description",null,"Max OAT","Min OAT","DAT @","DAT @",null,"Min °Fdb",55]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,"#",null,null,"°F","°F","Max OAT","Min OAT",null,"Max °F db",70]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,1,{"$f":"$U$67","v":0},null,{"$f":"IF(AA113=0,0,LOOKUP(AA113,$G$100:$G$104,$J$100:$J$104))","v":0},{"$f":"IF(AA113=0,0,LOOKUP(AA113,$G$100:$G$104,$K$100:$K$104))","v":0},{"$f":"IF(AA113=0,0,LOOKUP(AA113,$G$100:$G$104,$M$100:$M$104))","v":0},{"$f":"IF(AA113=0,0,LOOKUP(AA113,$G$100:$G$104,$N$100:$N$104))","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,2,{"$f":"$AR$67","v":0},null,0,0,{"$f":"IF(AA114=0,0,LOOKUP(AA114,$G$100:$G$104,$M$100:$M$104))","v":0},{"$f":"IF(AA114=0,0,LOOKUP(AA114,$G$100:$G$104,$N$100:$N$104))","v":0},null,"ERV Fan Penalty"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,3,{"$f":"$BO$67","v":0},null,0,0,0,0,null,"Added SP with ERV (Supp+Exh)",null,null,1.6,"in. w.c.","(0.8 in supply + 0.8 in exhaust)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,4,{"$f":"$CL$67","v":0},null,0,0,0,0,null,"Avg. Motor Eff",null,null,0.92]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,5,{"$f":"$DI$67","v":0},null,0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,6,{"$f":"$EF$67","v":0},null,0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,7,{"$f":"$FC$67","v":0},null,0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,8,{"$f":"$FZ$67","v":0},null,0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,9,{"$f":"$GW$67","v":0},null,0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,10,{"$f":"$HT$67","v":0},null,0,0,0,0,null,null,null,null,null,"Base ERV Exemption Used"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,null,null,null,null,null,null,null,null,null,null,null,null,"C403.2.7-1"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,"AHU Airflow Profiles",null,null,null,null,null,null,null,null,null,null,null,"C403.2.7-2"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,"System",null,null,"Occupied Profile",null,null,null,null,null,null,null,null,"C403.2.7-3"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,"Type","Description",null,"Max Cool","Min Cool","%Flow @","%Flow @",null,null,null,null,null,"C403.2.7-4"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"#",null,null,"%","%","Max","Min",null,null,null,null,null,"C403.2.7-5"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,{"$f":"$U$67","v":0},null,1,0.05,1,{"$f":"IF(AA128=0,0,LOOKUP(AA128,$G$100:$G$104,$L$100:$L$104))","v":0},null,null,null,null,null,"C403.2.7-6"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Return Air Conditions",null,null,null,null,2,{"$f":"$AR$67","v":0},null,1,0.05,1,{"$f":"IF(AA129=0,0,LOOKUP(AA129,$G$100:$G$104,$L$100:$L$104))","v":0},null,null,null,null,null,"C403.2.7-7"]
[null,null,null,null,null,null,null,null,null,null,"Site HAV Operating Hours",null,null,{"$f":"SUM($L$72:$L$95)","v":0},null,null,null,null,null,null,null,null,"Cooling","Heating",null,3,{"$f":"$BO$67","v":0},null,1,0.05,1,0,null,null,null,null,null,"C403.2.7-8"]
[null,null,null,null,null,null,null,null,null,"Baseline Energy Recovery Requirements ",null,null,null,null,null,null,null,null,null,null,"Temp db (°F)",null,75,70,null,4,{"$f":"$CL$67","v":0},null,1,0.05,1,0,null,null,null,null,null,"C403.2.7-9"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"%RH",null,0.5,0.4,null,5,{"$f":"$DI$67","v":0},null,1,0.05,1,0,null,null,null,null,null,"C403.2.7-10"]
[null,null,null,null,null,null,null,null,null,null,null,"PERCENT (%) OUTDOOR AIR AT FULL DESIGN AIRFLOW RATE",null,null,null,null,null,null,null,null,"RH (lb/lb)",null,{"$f":"FORECAST($W$132,OFFSET($V$157:$V$165,MATCH($W$132,$M$157:$M$165,1)-1,0,2),OFFSET($M$157:$M$165,MATCH($W$132,$M$157:$M$165,1)-1,0,2))","v":9.5499999999999977E-3},{"$f":"FORECAST($X$132,OFFSET($V$157:$V$165,MATCH($X$132,$M$157:$M$165,1)-1,0,2),OFFSET($M$157:$M$165,MATCH($X$132,$M$157:$M$165,1)-1,0,2))","v":7.5999999999999991E-3},null,6,{"$f":"$EF$67","v":0},null,1,0.05,1,0,null,null,null,null,null,"C403.2.7-11"]
[null,null,null,null,null,null,null,null,null,null,null,0.1,0.2,0.3,0.4,0.5,0.6,0.7,0.8,null,"Enthalpy (Btu/lb)",null,{"$f":"(0.24*W131)+(W133*(1061+0.444*W131))","v":28.450564999999997},{"$f":"(0.24*X131)+(X133*(1061+0.444*X131))","v":25.099807999999999},null,7,{"$f":"$FC$67","v":0},null,1,0.05,1,0]
[null,null,null,null,null,null,null,null,null,null,null,0.2,0.3,0.4,0.5,0.6,0.7,0.8,1,null,null,null,null,null,null,8,{"$f":"$FZ$67","v":0},null,1,0.05,1,0]
[null,null,null,null,null,null,null,null,"IECC","Operating Hours",null,"DESIGN SUPPLY AIRFLOW RATE (CFM)",null,null,null,null,null,null,null,null,null,null,null,null,null,9,{"$f":"$GW$67","v":0},null,1,0.05,1,0]
[null,null,null,null,null,null,null,null,{"$f":"MID('Project Info'!C20,1,4)","v":"2018"},"<",8000,{"$f":"IF($I$137=\"2015\",L147,L149)","v":26000},{"$f":"IF($I$137=\"2015\",M147,M149)","v":16000},5500,4500,3500,2000,1000,120,null,null,null,null,null,null,10,{"$f":"$HT$67","v":0},null,1,0.05,1,0]
[null,null,null,null,null,null,null,null,null,">=",8000,{"$f":"IF($I$137=\"2015\",L148,L150)","v":200},130,100,80,70,60,50,40,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Recovery Section Power (Wheel Motor or Pump)",null,null,null,null,null,"Incremental Cost Estimates"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Part Load Cooling Performance Assumptions",null,null,null,null,null,null,null,"Design",null,null,"Recovery",null,null,"Design","% Eff","Increm-"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Line",0.01,0.42,0.45,0.12,null,"SEER/",null,"Line","Min OA","Recovery",null,"Demand",null,"Line","Min OA","Improve-","ental"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"#",1,0.75,0.5,0.25,-0.01,"IEER",null,"#","%","Type",null,"kW/CFM",null,"#","CFM","ment","Cost"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,{"$f":"S22","v":0},{"$f":"IF(AA142=0,0,($AF142/$AA142)*AB$153*$AA142)","v":0},0,0,{"$f":"AD142/2","v":0},{"$f":"T22","v":0},null,1,{"$f":"IF(L22=\"\",0,M22/L22)","v":0},{"$f":"IF(L22=\"\",\"\",N22)","v":""},null,{"$f":"IF(AJ142=\"\",0,LOOKUP(AJ142,$I$107:$I$111,$K$107:$K$111))","v":0},null,1,{"$f":"M22","v":0},{"$f":"P22-AD22","v":0},{"$f":"$AN$154*AO142*AP142","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,"PERCENT (%) OUTDOOR AIR AT FULL DESIGN AIRFLOW RATE",null,null,null,null,null,null,null,null,null,null,null,null,null,2,0,0,0,0,{"$f":"AD143/2","v":0},0,null,2,0,"",null,{"$f":"IF(AJ143=\"\",0,LOOKUP(AJ143,$I$107:$I$111,$K$107:$K$111))","v":0},null,2,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,0.1,0.2,0.3,0.4,0.5,0.6,0.7,0.8,null,null,null,null,null,null,3,0,0,0,0,0,0,null,3,0,"",null,0,null,3,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,0.2,0.3,0.4,0.5,0.6,0.7,0.8,1,null,null,null,null,null,null,4,0,0,0,0,0,0,null,4,0,"",null,0,null,4,0,0,0]
[null,null,null,null,null,null,null,null,"IECC","Operating Hours",null,"DESIGN SUPPLY AIRFLOW RATE (CFM)",null,null,null,null,null,null,null,null,null,null,null,null,null,5,0,0,0,0,0,0,null,5,0,"",null,0,null,5,0,0,0]
[null,null,null,null,null,null,null,null,2015,"<",8000,26000,16000,5500,4500,3500,2000,1000,0,null,null,null,null,null,null,6,0,0,0,0,0,0,null,6,0,"",null,0,null,6,0,0,0]
[null,null,null,null,null,null,null,null,null,">=",8000,0,0,0,0,0,0,0,0,null,null,null,null,null,null,7,0,0,0,0,0,0,null,7,0,"",null,0,null,7,0,0,0]
[null,null,null,null,null,null,null,null,2018,"<",8000,26000,16000,5500,4500,3500,2000,1000,120,null,null,null,null,null,null,8,0,0,0,0,0,0,null,8,0,"",null,0,null,8,0,0,0]
[null,null,null,null,null,null,null,null,null,">=",8000,200,130,100,80,70,60,50,40,null,null,null,null,null,null,9,0,0,0,0,0,0,null,9,0,"",null,0,null,9,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,0,0,0,0,0,0,null,10,0,"",null,0,null,10,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"TOTAL INCREMENTAL COST",null,null,{"$f":"SUM(AQ142:AQ151)","v":0}]
[null,null,null,null,null,null,null,null,"Return Air Relative Humidity and Enthalpy Calcs",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"PL EER Factors",null,0.95312499999999978,1.0312499999999998,1.0625]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.75,0.5,0.25,null,null,null,null,null,null,null,null,null,3,"Incremental Cost/CFM/%Improvement in Effectiveness"]
[null,null,null,null,null,null,null,null,null,null,null,null,"RH","Deg F"]
[null,null,null,null,null,null,null,null,"RA Temperature",75," Deg F",null,null,30,40,50,60,70,80,90,100,"Check"]
[null,null,null,null,null,null,null,null,"RA Humidity Ratio",0.6,"%",null,0.1,4.0000000000000002E-4,5.9999999999999995E-4,8.9999999999999998E-4,1.1000000000000001E-3,1.6000000000000001E-3,2.3E-3,3.0000000000000001E-3,4.1000000000000003E-3,{"$f":"FORECAST($J$156,OFFSET(N157:U157,0,MATCH($J$156,$N$156:$U$156,1)-1,1,2),OFFSET($N$156:$U$156,0,MATCH($J$156,$N$156:$U$156,1)-1,1,2))","v":1.9499999999999999E-3}]
[null,null,null,null,null,null,null,null,"Relat. Humidity",{"$f":"FORECAST($W$132,OFFSET($V$157:$V$165,MATCH($W$132,$M$157:$M$165,1)-1,0,2),OFFSET($M$157:$M$165,MATCH($W$132,$M$157:$M$165,1)-1,0,2))","v":9.5499999999999977E-3},"lb/lb",null,0.2,6.9999999999999999E-4,1E-3,1.4E-3,2.3E-3,3.0000000000000001E-3,4.3E-3,6.0000000000000001E-3,8.3000000000000001E-3,3.6500000000000005E-3]
[null,null,null,null,null,null,null,null,"Retun Air Enthalpy",{"$f":"(0.24*W131)+(W133*(1061+0.444*W131))","v":28.450564999999997},"Btu/lb",null,0.3,1E-3,1.6000000000000001E-3,2E-3,3.0999999999999999E-3,4.8999999999999998E-3,6.6E-3,9.2999999999999992E-3,1.24E-2,5.7499999999999999E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,0.4,1.2999999999999999E-3,2E-3,2.8999999999999998E-3,4.3E-3,6.3E-3,8.8999999999999999E-3,1.2200000000000001E-2,1.66E-2,7.5999999999999991E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,0.5,1.6999999999999999E-3,2.5999999999999999E-3,3.7000000000000002E-3,5.5999999999999999E-3,7.9000000000000008E-3,1.12E-2,1.54E-2,2.1000000000000001E-2,9.5499999999999995E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,0.6,2E-3,3.0999999999999999E-3,4.5999999999999999E-3,6.8999999999999999E-3,9.4000000000000004E-3,1.32E-2,1.83E-2,2.52E-2,1.1300000000000001E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,0.7,2.3999999999999998E-3,3.7000000000000002E-3,5.4000000000000003E-3,7.7000000000000002E-3,1.12E-2,1.54E-2,2.1700000000000001E-2,2.9700000000000001E-2,1.3299999999999999E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,0.8,2.7000000000000001E-3,4.1000000000000003E-3,6.0000000000000001E-3,8.8999999999999999E-3,1.26E-2,1.7899999999999999E-2,2.47E-2,"-",1.525E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,0.9,3.0000000000000001E-3,4.7000000000000002E-3,6.8999999999999999E-3,0.01,1.43E-2,0.02,2.7199999999999998E-2,"-",1.7149999999999999E-2]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,"Source:","http://www.engineeringtoolbox.com/water-vapor-air-d_854.html"]

{"sheet":"Demand Control Ventilation","index":15,"n_rows":162,"n_cols":267,"rows_kept":162,"cut":false,"hidden":true,"merged":[[1,10,4,17],[1,19,11,27],[147,8,147,21],[149,13,149,20],[29,7,29,8],[29,9,29,10],[30,7,30,8],[30,9,30,10],[26,7,26,8],[26,9,26,10],[27,7,27,8],[27,9,27,10],[28,7,28,8],[28,9,28,10],[23,7,23,8],[23,9,23,10],[24,7,24,8],[24,9,24,10],[25,7,25,8],[25,9,25,10],[21,7,21,8],[21,9,21,10],[22,7,22,8],[22,9,22,10]]}
["Savings Summary",null,null,null,null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,null,null,"Notes (Optional)"]
["Annual kWh Savings",null,null,{"$f":"SUM(A14:D14)","v":0},null,null,null,"Value","Unit",null,"This measure considers savings from implementing demand controlled ventilation (DCV) in HVAC systems or zones where it is not required by the energy code."]
["% On Peak",null,null,{"$f":"IF(D2<=0,0,MIN(1,A15+C15))","v":0},null,"Annual Electric Savings",null,{"$f":"D2","v":0},"kWh"]
["Max kW",null,null,{"$f":"MAX(W98:W121,BR97:BR120)","v":0},null,"Annual Fuel Savings",null,{"$f":"D7*C28","v":{"$error":"#N/A"}},{"$f":"D20","v":{"$error":"#N/A"}}]
["Summer kW",null,null,{"$f":"SUMPRODUCT(W98:W121,R67:R90)/SUM(R67:R90)","v":{"$error":"#DIV/0!"}},null,"Incremental","Default Calc",{"$f":"$AK$147","v":0},"$"]
["Winter kW",null,null,{"$f":"SUMPRODUCT(W98:W121,Q67:Q90)/SUM(Q67:Q90)","v":{"$error":"#DIV/0!"}},null,"Cost","Project Specific",null,"$ (Optional)"]
["Annual Fuel Savings (MMBtu)",null,null,{"$f":"(SUMPRODUCT($L$67:$L$90,$X$98:$X$121))/1000","v":0},null,"Estimated Incentive",null,{"$f":"IF(AND($C$24>=0,$C$25>=0),MAX(0,H3)*C24+MAX(0,H4)*C25,\"TBD\")","v":{"$error":"#N/A"}},"$"]
["Incremental Cost (Default Calc)",null,null,{"$f":"$AK$147","v":0}]
["Incremental Cost (for Summary)",null,null,{"$f":"IF(H6>0,H6,D8)","v":0},null,"Project Information Summary"]
["kWh Savings by Peak Period",null,null,null,null,null,"STATE",{"$f":"'Project Info'!C15","v":"NH"}]
["Winter","Winter","Summer","Summer",null,null,"Program Year",{"$f":"'Project Info'!C19","v":0}]
["On-Peak","Off-Peak","On-Peak","Off-Peak",null,null,"Code IECC Version",{"$f":"MID('Project Info'!C20,1,4)","v":"2018"}]
["kWh","kWh","kWh","kWh",null,null,"Electric PA",{"$f":"'Project Info'!F3","v":0}]
[{"$f":"SUMPRODUCT($W$98:$W$121,M67:M90)","v":0},{"$f":"SUMPRODUCT($W$98:$W$121,N67:N90)","v":0},{"$f":"SUMPRODUCT($W$98:$W$121,O67:O90)","v":0},{"$f":"SUMPRODUCT($W$98:$W$121,P67:P90)","v":0},null,null,"Gas PA",{"$f":"'Project Info'!I3","v":0}]
[{"$f":"ROUND(IF(A14<=0,0,A14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(B14<=0,0,B14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(C14<=0,0,C14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"IF(SUM(A14:D14)=0,0,1-SUM(A15:C15))","v":0},null,"*NOTE: Baseline values are automated and cannot be changed."]
[]
["Utility Rates",null,null,null,null,null,"Table 1: Air Handling Unit Parameters"]
[null,null,"Rate","Unit",null,null,1,2,null,3,null,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18]
["Electric",null,{"$f":"'ECM Summary'!$E$31","v":0.1593},"kWh",null,null,null,null,null,"System",null,"Total","Total","% of OA","Includes","Design ERV Performance",null,"Cooling",null,null,"Air Handler Heating",null,null," Zone Heating"]
[{"$f":"'ECM Summary'!$C$32","v":0},null,{"$f":"'ECM Summary'!$E$32","v":{"$error":"#N/A"}},{"$f":"'ECM Summary'!$F$32","v":{"$error":"#N/A"}},null,null,"Line","Unit",null,"Airflow Control Type /",null,"Supply","OA","Eligible for","Energy","Winter","Summer","Cooling","Peformance",null,"Heat","Fossil Fuel","Electric","Heat","Fossil Fuel","Electric"]
[null,null,null,null,null,null,"#","Tag/Name",null,"Terminal Unit Type",null,"CFM","CFM","Savings","Recovery?","Sensible Eff","Total Eff","Included?","EER","SEER/IEER","Source","Baseline Eff%","Baseline COP","Source","Baseline Eff%","Baseline COP"]
["Custom Incentive Rates",null,null,null,null,null,1]
[null,null,"Rate","Unit",null,null,2]
["Electric",null,{"$f":"'ECM Summary'!$J$31","v":0.28000000000000003},"kWh",null,null,3]
[{"$f":"'ECM Summary'!$H$32","v":0},null,{"$f":"'ECM Summary'!$J$32","v":0},{"$f":"'ECM Summary'!$K$32","v":{"$error":"#N/A"}},null,null,4]
[null,null,null,null,null,null,5]
["Fossil Fuel",null,{"$f":"'Project Info'!C21","v":0},null,null,null,6]
["Fuel Conversion",null,{"$f":"LOOKUP(C27,'Project Info'!X102:X104,'Project Info'!Z102:Z104)","v":{"$error":"#N/A"}},null,null,null,7]
[null,null,null,null,null,null,8]
[null,null,null,null,null,null,9]
[null,null,null,null,null,null,10]
[null,null,null,null,null,null,null,null,null,"System Type",null,null,null,null,"ERV?",null,null,"Cooling?",null,null,"Heat Source",null,null,"Heat Source"]
[null,null,null,null,null,null,null,null,null,"Variable Volume (VAV)",null,null,null,null,"Yes",null,null,"Yes",null,null,"Elec",null,null,{"$f":"U33","v":"Elec"}]
[null,null,null,null,null,null,null,null,null,"Constant Volume",null,null,null,null,"No",null,null,"No",null,null,"Fossil Fuel",null,null,{"$f":"U34","v":"Fossil Fuel"}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AHU Heating Performance",null,null,"ZONE Heating Performance",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AHU Heating Performance",null,null,"ZONE Heating Performance",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AHU Heating Performance",null,null,"ZONE Heating Performance",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AHU Heating Performance",null,null,"ZONE Heating Performance",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AHU Heating Performance",null,null,"ZONE Heating Performance",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AHU Heating Performance",null,null,"ZONE Heating Performance",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AHU Heating Performance",null,null,"ZONE Heating Performance",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AHU Heating Performance",null,null,"ZONE Heating Performance",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AHU Heating Performance",null,null,"ZONE Heating Performance",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AHU Heating Performance",null,null,"ZONE Heating Performance"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Airflow",null,"Total","Design Min","%OA","Estimated Fan Performance",null,null,"DAT Reset",null,"ERV Effectiveness",null,null,null,"Heating","Avg. Eff","Avg.","Heating","Avg. Eff","Avg.",null,null,null,null,null,"Airflow",null,"Total","Design Min","%OA","Estimated Fan Performance",null,null,"DAT Reset",null,"ERV Effectiveness",null,null,null,"Heating","Avg. Eff","Avg.","Heating","Avg. Eff","Avg.",null,null,null,null,null,"Airflow",null,"Total","Design Min","%OA","Estimated Fan Performance",null,null,"DAT Reset",null,"ERV Effectiveness",null,null,null,"Heating","Avg. Eff","Avg.","Heating","Avg. Eff","Avg.",null,null,null,null,null,"Airflow",null,"Total","Design Min","%OA","Estimated Fan Performance",null,null,"DAT Reset",null,"ERV Effectiveness",null,null,null,"Heating","Avg. Eff","Avg.","Heating","Avg. Eff","Avg.",null,null,null,null,null,"Airflow",null,"Total","Design Min","%OA","Estimated Fan Performance",null,null,"DAT Reset",null,"ERV Effectiveness",null,null,null,"Heating","Avg. Eff","Avg.","Heating","Avg. Eff","Avg.",null,null,null,null,null,"Airflow",null,"Total","Design Min","%OA","Estimated Fan Performance",null,null,"DAT Reset",null,"ERV Effectiveness",null,null,null,"Heating","Avg. Eff","Avg.","Heating","Avg. Eff","Avg.",null,null,null,null,null,"Airflow",null,"Total","Design Min","%OA","Estimated Fan Performance",null,null,"DAT Reset",null,"ERV Effectiveness",null,null,null,"Heating","Avg. Eff","Avg.","Heating","Avg. Eff","Avg.",null,null,null,null,null,"Airflow",null,"Total","Design Min","%OA","Estimated Fan Performance",null,null,"DAT Reset",null,"ERV Effectiveness",null,null,null,"Heating","Avg. Eff","Avg.","Heating","Avg. Eff","Avg.",null,null,null,null,null,"Airflow",null,"Total","Design Min","%OA","Estimated Fan Performance",null,null,"DAT Reset",null,"ERV Effectiveness",null,null,null,"Heating","Avg. Eff","Avg.","Heating","Avg. Eff","Avg.",null,null,null,null,null,"Airflow",null,"Total","Design Min","%OA","Estimated Fan Performance",null,null,"DAT Reset",null,"ERV Effectiveness",null,null,null,"Heating","Avg. Eff","Avg.","Heating","Avg. Eff","Avg."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Line#","Tag","System Type",null,"Control",null,"Supply","OA CFM","Eligible","BHP","Eff","Min Flow %","Min °F","Max °F","Has ERV?","Sensible","Latent","Cooling?","Fuel","%","COP","Fuel","%","COP",null,"Line#","Tag","System Type",null,"Control",null,"Supply","OA CFM","Eligible","BHP","Eff","Min Flow %","Min °F","Max °F","Has ERV?","Sensible","Latent","Cooling?","Fuel","%","COP","Fuel","%","COP",null,"Line#","Tag","System Type",null,"Control",null,"Supply","OA CFM","Eligible","BHP","Eff","Min Flow %","Min °F","Max °F","Has ERV?","Sensible","Latent","Cooling?","Fuel","%","COP","Fuel","%","COP",null,"Line#","Tag","System Type",null,"Control",null,"Supply","OA CFM","Eligible","BHP","Eff","Min Flow %","Min °F","Max °F","Has ERV?","Sensible","Latent","Cooling?","Fuel","%","COP","Fuel","%","COP",null,"Line#","Tag","System Type",null,"Control",null,"Supply","OA CFM","Eligible","BHP","Eff","Min Flow %","Min °F","Max °F","Has ERV?","Sensible","Latent","Cooling?","Fuel","%","COP","Fuel","%","COP",null,"Line#","Tag","System Type",null,"Control",null,"Supply","OA CFM","Eligible","BHP","Eff","Min Flow %","Min °F","Max °F","Has ERV?","Sensible","Latent","Cooling?","Fuel","%","COP","Fuel","%","COP",null,"Line#","Tag","System Type",null,"Control",null,"Supply","OA CFM","Eligible","BHP","Eff","Min Flow %","Min °F","Max °F","Has ERV?","Sensible","Latent","Cooling?","Fuel","%","COP","Fuel","%","COP",null,"Line#","Tag","System Type",null,"Control",null,"Supply","OA CFM","Eligible","BHP","Eff","Min Flow %","Min °F","Max °F","Has ERV?","Sensible","Latent","Cooling?","Fuel","%","COP","Fuel","%","COP",null,"Line#","Tag","System Type",null,"Control",null,"Supply","OA CFM","Eligible","BHP","Eff","Min Flow %","Min °F","Max °F","Has ERV?","Sensible","Latent","Cooling?","Fuel","%","COP","Fuel","%","COP",null,"Line#","Tag","System Type",null,"Control",null,"Supply","OA CFM","Eligible","BHP","Eff","Min Flow %","Min °F","Max °F","Has ERV?","Sensible","Latent","Cooling?","Fuel","%","COP","Fuel","%","COP"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,{"$f":"LOOKUP(S62,$G$22:$G$31,$H$22:$H$31)","v":0},{"$f":"IF(W62=0,0,IF(W62=$J$33,IF(Z62<Y62,$G$95,$G$97),IF(Z62<Y62,$G$96,$G$98)))","v":0},null,{"$f":"LOOKUP(S62,$G$22:$G$31,$J$22:$J$31)","v":0},null,{"$f":"LOOKUP(S$62,$G$22:$G$31,$L$22:$L$31)","v":0},{"$f":"LOOKUP(S$62,$G$22:$G$31,$M$22:$M$31)","v":0},{"$f":"LOOKUP(S$62,$G$22:$G$31,$N$22:$N$31)","v":0},{"$f":"0.0013*Y62","v":0},{"$f":"LOOKUP(AB62/2,$M$125:$M$145,$N$125:$N$145)","v":0.6},{"$f":"IF(Y62=0,0,MAX(Z62/Y62,LOOKUP(S$62,$Z$123:$Z$132,$AF$123:$AF$132)))","v":0},{"$f":"LOOKUP(S$62,$Z$108:$Z$117,$AE$108:$AE$117)","v":0},{"$f":"LOOKUP(S$62,$Z$108:$Z$117,$AF$108:$AF$117)","v":0},{"$f":"LOOKUP(S$62,$G$22:$G$31,$O$22:$O$31)","v":0},{"$f":"LOOKUP(S$62,$G$22:$G$31,$P$22:$P$31)*(AG62=$O$33)","v":0},{"$f":"LOOKUP(S$62,$G$22:$G$31,$Q$22:$Q$31)*(AG62=$O$33)","v":0},{"$f":"LOOKUP(S$62,$G$22:$G$31,$R$22:$R$31)","v":0},{"$f":"LOOKUP(S$62,$G$22:$G$31,$U$22:$U$31)","v":0},{"$f":"IF(AK62=$U$34,LOOKUP(S$62,$G$22:$G$31,$V$22:$V$31),\"NA\")","v":"NA"},{"$f":"IF(AK62=$U$33,LOOKUP(S$62,$G$22:$G$31,$W$22:$W$31),\"NA\")","v":"NA"},{"$f":"LOOKUP(S$62,$G$22:$G$31,$X$22:$X$31)","v":0},{"$f":"IF(AN62=$U$34,LOOKUP(S$62,$G$22:$G$31,$Y$22:$Y$31),\"NA\")","v":"NA"},{"$f":"IF(AN62=$U$33,LOOKUP(S$62,$G$22:$G$31,$Z$22:$Z$31),\"NA\")","v":"NA"},null,{"$f":"S62+1","v":2},{"$f":"LOOKUP(AR62,$G$22:$G$31,$H$22:$H$31)","v":0},{"$f":"IF(AV62=0,0,IF(AV62=$J$33,IF(AY62<AX62,$G$95,$G$97),IF(AY62<AX62,$G$96,$G$98)))","v":0},null,{"$f":"LOOKUP(AR62,$G$22:$G$31,$J$22:$J$31)","v":0},null,{"$f":"LOOKUP(AR$62,$G$22:$G$31,$L$22:$L$31)","v":0},{"$f":"LOOKUP(AR$62,$G$22:$G$31,$M$22:$M$31)","v":0},{"$f":"LOOKUP(AR$62,$G$22:$G$31,$N$22:$N$31)","v":0},{"$f":"0.0013*AX62","v":0},{"$f":"LOOKUP(BA62/2,$M$125:$M$145,$N$125:$N$145)","v":0.6},{"$f":"IF(AX62=0,0,MAX(AY62/AX62,LOOKUP(AR$62,$Z$123:$Z$132,$AF$123:$AF$132)))","v":0},{"$f":"LOOKUP(AR$62,$Z$108:$Z$117,$AE$108:$AE$117)","v":0},{"$f":"LOOKUP(AR$62,$Z$108:$Z$117,$AF$108:$AF$117)","v":0},{"$f":"LOOKUP(AR$62,$G$22:$G$31,$O$22:$O$31)","v":0},{"$f":"LOOKUP(AR$62,$G$22:$G$31,$P$22:$P$31)*(BF62=$O$33)","v":0},{"$f":"LOOKUP(AR$62,$G$22:$G$31,$Q$22:$Q$31)*(BF62=$O$33)","v":0},{"$f":"LOOKUP(AR$62,$G$22:$G$31,$R$22:$R$31)","v":0},{"$f":"LOOKUP(AR$62,$G$22:$G$31,$U$22:$U$31)","v":0},{"$f":"IF(BJ62=$U$34,LOOKUP(AR$62,$G$22:$G$31,$V$22:$V$31),\"NA\")","v":"NA"},{"$f":"IF(BJ62=$U$33,LOOKUP(AR$62,$G$22:$G$31,$W$22:$W$31),\"NA\")","v":"NA"},{"$f":"LOOKUP(AR$62,$G$22:$G$31,$X$22:$X$31)","v":0},{"$f":"IF(BM62=$U$34,LOOKUP(AR$62,$G$22:$G$31,$Y$22:$Y$31),\"NA\")","v":"NA"},{"$f":"IF(BM62=$U$33,LOOKUP(AR$62,$G$22:$G$31,$Z$22:$Z$31),\"NA\")","v":"NA"},null,{"$f":"AR62+1","v":3},{"$f":"LOOKUP(BQ62,$G$22:$G$31,$H$22:$H$31)","v":0},{"$f":"IF(BU62=0,0,IF(BU62=$J$33,IF(BX62<BW62,$G$95,$G$97),IF(BX62<BW62,$G$96,$G$98)))","v":0},null,{"$f":"LOOKUP(BQ62,$G$22:$G$31,$J$22:$J$31)","v":0},null,{"$f":"LOOKUP(BQ$62,$G$22:$G$31,$L$22:$L$31)","v":0},{"$f":"LOOKUP(BQ$62,$G$22:$G$31,$M$22:$M$31)","v":0},{"$f":"LOOKUP(BQ$62,$G$22:$G$31,$N$22:$N$31)","v":0},{"$f":"0.0013*BW62","v":0},{"$f":"LOOKUP(BZ62/2,$M$125:$M$145,$N$125:$N$145)","v":0.6},{"$f":"IF(BW62=0,0,MAX(BX62/BW62,LOOKUP(BQ$62,$Z$123:$Z$132,$AF$123:$AF$132)))","v":0},{"$f":"LOOKUP(BQ$62,$Z$108:$Z$117,$AE$108:$AE$117)","v":0},{"$f":"LOOKUP(BQ$62,$Z$108:$Z$117,$AF$108:$AF$117)","v":0},{"$f":"LOOKUP(BQ$62,$G$22:$G$31,$O$22:$O$31)","v":0},{"$f":"LOOKUP(BQ$62,$G$22:$G$31,$P$22:$P$31)*(CE62=$O$33)","v":0},{"$f":"LOOKUP(BQ$62,$G$22:$G$31,$Q$22:$Q$31)*(CE62=$O$33)","v":0},{"$f":"LOOKUP(BQ$62,$G$22:$G$31,$R$22:$R$31)","v":0},{"$f":"LOOKUP(BQ$62,$G$22:$G$31,$U$22:$U$31)","v":0},{"$f":"IF(CI62=$U$34,LOOKUP(BQ$62,$G$22:$G$31,$V$22:$V$31),\"NA\")","v":"NA"},{"$f":"IF(CI62=$U$33,LOOKUP(BQ$62,$G$22:$G$31,$W$22:$W$31),\"NA\")","v":"NA"},{"$f":"LOOKUP(BQ$62,$G$22:$G$31,$X$22:$X$31)","v":0},{"$f":"IF(CL62=$U$34,LOOKUP(BQ$62,$G$22:$G$31,$Y$22:$Y$31),\"NA\")","v":"NA"},{"$f":"IF(CL62=$U$33,LOOKUP(BQ$62,$G$22:$G$31,$Z$22:$Z$31),\"NA\")","v":"NA"},null,{"$f":"BQ62+1","v":4},{"$f":"LOOKUP(CP62,$G$22:$G$31,$H$22:$H$31)","v":0},{"$f":"IF(CT62=0,0,IF(CT62=$J$33,IF(CW62<CV62,$G$95,$G$97),IF(CW62<CV62,$G$96,$G$98)))","v":0},null,{"$f":"LOOKUP(CP62,$G$22:$G$31,$J$22:$J$31)","v":0},null,{"$f":"LOOKUP(CP$62,$G$22:$G$31,$L$22:$L$31)","v":0},{"$f":"LOOKUP(CP$62,$G$22:$G$31,$M$22:$M$31)","v":0},{"$f":"LOOKUP(CP$62,$G$22:$G$31,$N$22:$N$31)","v":0},{"$f":"0.0013*CV62","v":0},{"$f":"LOOKUP(CY62/2,$M$125:$M$145,$N$125:$N$145)","v":0.6},{"$f":"IF(CV62=0,0,MAX(CW62/CV62,LOOKUP(CP$62,$Z$123:$Z$132,$AF$123:$AF$132)))","v":0},{"$f":"LOOKUP(CP$62,$Z$108:$Z$117,$AE$108:$AE$117)","v":0},{"$f":"LOOKUP(CP$62,$Z$108:$Z$117,$AF$108:$AF$117)","v":0},{"$f":"LOOKUP(CP$62,$G$22:$G$31,$O$22:$O$31)","v":0},{"$f":"LOOKUP(CP$62,$G$22:$G$31,$P$22:$P$31)*(DD62=$O$33)","v":0},{"$f":"LOOKUP(CP$62,$G$22:$G$31,$Q$22:$Q$31)*(DD62=$O$33)","v":0},{"$f":"LOOKUP(CP$62,$G$22:$G$31,$R$22:$R$31)","v":0},{"$f":"LOOKUP(CP$62,$G$22:$G$31,$U$22:$U$31)","v":0},{"$f":"IF(DH62=$U$34,LOOKUP(CP$62,$G$22:$G$31,$V$22:$V$31),\"NA\")","v":"NA"},{"$f":"IF(DH62=$U$33,LOOKUP(CP$62,$G$22:$G$31,$W$22:$W$31),\"NA\")","v":"NA"},{"$f":"LOOKUP(CP$62,$G$22:$G$31,$X$22:$X$31)","v":0},{"$f":"IF(DK62=$U$34,LOOKUP(CP$62,$G$22:$G$31,$Y$22:$Y$31),\"NA\")","v":"NA"},{"$f":"IF(DK62=$U$33,LOOKUP(CP$62,$G$22:$G$31,$Z$22:$Z$31),\"NA\")","v":"NA"},null,{"$f":"CP62+1","v":5},{"$f":"LOOKUP(DO62,$G$22:$G$31,$H$22:$H$31)","v":0},{"$f":"IF(DS62=0,0,IF(DS62=$J$33,IF(DV62<DU62,$G$95,$G$97),IF(DV62<DU62,$G$96,$G$98)))","v":0},null,{"$f":"LOOKUP(DO62,$G$22:$G$31,$J$22:$J$31)","v":0},null,{"$f":"LOOKUP(DO$62,$G$22:$G$31,$L$22:$L$31)","v":0},{"$f":"LOOKUP(DO$62,$G$22:$G$31,$M$22:$M$31)","v":0},{"$f":"LOOKUP(DO$62,$G$22:$G$31,$N$22:$N$31)","v":0},{"$f":"0.0013*DU62","v":0},{"$f":"LOOKUP(DX62/2,$M$125:$M$145,$N$125:$N$145)","v":0.6},{"$f":"IF(DU62=0,0,MAX(DV62/DU62,LOOKUP(DO$62,$Z$123:$Z$132,$AF$123:$AF$132)))","v":0},{"$f":"LOOKUP(DO$62,$Z$108:$Z$117,$AE$108:$AE$117)","v":0},{"$f":"LOOKUP(DO$62,$Z$108:$Z$117,$AF$108:$AF$117)","v":0},{"$f":"LOOKUP(DO$62,$G$22:$G$31,$O$22:$O$31)","v":0},{"$f":"LOOKUP(DO$62,$G$22:$G$31,$P$22:$P$31)*(EC62=$O$33)","v":0},{"$f":"LOOKUP(DO$62,$G$22:$G$31,$Q$22:$Q$31)*(EC62=$O$33)","v":0},{"$f":"LOOKUP(DO$62,$G$22:$G$31,$R$22:$R$31)","v":0},{"$f":"LOOKUP(DO$62,$G$22:$G$31,$U$22:$U$31)","v":0},{"$f":"IF(EG62=$U$34,LOOKUP(DO$62,$G$22:$G$31,$V$22:$V$31),\"NA\")","v":"NA"},{"$f":"IF(EG62=$U$33,LOOKUP(DO$62,$G$22:$G$31,$W$22:$W$31),\"NA\")","v":"NA"},{"$f":"LOOKUP(DO$62,$G$22:$G$31,$X$22:$X$31)","v":0},{"$f":"IF(EJ62=$U$34,LOOKUP(DO$62,$G$22:$G$31,$Y$22:$Y$31),\"NA\")","v":"NA"},{"$f":"IF(EJ62=$U$33,LOOKUP(DO$62,$G$22:$G$31,$Z$22:$Z$31),\"NA\")","v":"NA"},null,{"$f":"DO62+1","v":6},{"$f":"LOOKUP(EN62,$G$22:$G$31,$H$22:$H$31)","v":0},{"$f":"IF(ER62=0,0,IF(ER62=$J$33,IF(EU62<ET62,$G$95,$G$97),IF(EU62<ET62,$G$96,$G$98)))","v":0},null,{"$f":"LOOKUP(EN62,$G$22:$G$31,$J$22:$J$31)","v":0},null,{"$f":"LOOKUP(EN$62,$G$22:$G$31,$L$22:$L$31)","v":0},{"$f":"LOOKUP(EN$62,$G$22:$G$31,$M$22:$M$31)","v":0},{"$f":"LOOKUP(EN$62,$G$22:$G$31,$N$22:$N$31)","v":0},{"$f":"0.0013*ET62","v":0},{"$f":"LOOKUP(EW62/2,$M$125:$M$145,$N$125:$N$145)","v":0.6},{"$f":"IF(ET62=0,0,MAX(EU62/ET62,LOOKUP(EN$62,$Z$123:$Z$132,$AF$123:$AF$132)))","v":0},{"$f":"LOOKUP(EN$62,$Z$108:$Z$117,$AE$108:$AE$117)","v":0},{"$f":"LOOKUP(EN$62,$Z$108:$Z$117,$AF$108:$AF$117)","v":0},{"$f":"LOOKUP(EN$62,$G$22:$G$31,$O$22:$O$31)","v":0},{"$f":"LOOKUP(EN$62,$G$22:$G$31,$P$22:$P$31)*(FB62=$O$33)","v":0},{"$f":"LOOKUP(EN$62,$G$22:$G$31,$Q$22:$Q$31)*(FB62=$O$33)","v":0},{"$f":"LOOKUP(EN$62,$G$22:$G$31,$R$22:$R$31)","v":0},{"$f":"LOOKUP(EN$62,$G$22:$G$31,$U$22:$U$31)","v":0},{"$f":"IF(FF62=$U$34,LOOKUP(EN$62,$G$22:$G$31,$V$22:$V$31),\"NA\")","v":"NA"},{"$f":"IF(FF62=$U$33,LOOKUP(EN$62,$G$22:$G$31,$W$22:$W$31),\"NA\")","v":"NA"},{"$f":"LOOKUP(EN$62,$G$22:$G$31,$X$22:$X$31)","v":0},{"$f":"IF(FI62=$U$34,LOOKUP(EN$62,$G$22:$G$31,$Y$22:$Y$31),\"NA\")","v":"NA"},{"$f":"IF(FI62=$U$33,LOOKUP(EN$62,$G$22:$G$31,$Z$22:$Z$31),\"NA\")","v":"NA"},null,{"$f":"EN62+1","v":7},{"$f":"LOOKUP(FM62,$G$22:$G$31,$H$22:$H$31)","v":0},{"$f":"IF(FQ62=0,0,IF(FQ62=$J$33,IF(FT62<FS62,$G$95,$G$97),IF(FT62<FS62,$G$96,$G$98)))","v":0},null,{"$f":"LOOKUP(FM62,$G$22:$G$31,$J$22:$J$31)","v":0},null,{"$f":"LOOKUP(FM$62,$G$22:$G$31,$L$22:$L$31)","v":0},{"$f":"LOOKUP(FM$62,$G$22:$G$31,$M$22:$M$31)","v":0},{"$f":"LOOKUP(FM$62,$G$22:$G$31,$N$22:$N$31)","v":0},{"$f":"0.0013*FS62","v":0},{"$f":"LOOKUP(FV62/2,$M$125:$M$145,$N$125:$N$145)","v":0.6},{"$f":"IF(FS62=0,0,MAX(FT62/FS62,LOOKUP(FM$62,$Z$123:$Z$132,$AF$123:$AF$132)))","v":0},{"$f":"LOOKUP(FM$62,$Z$108:$Z$117,$AE$108:$AE$117)","v":0},{"$f":"LOOKUP(FM$62,$Z$108:$Z$117,$AF$108:$AF$117)","v":0},{"$f":"LOOKUP(FM$62,$G$22:$G$31,$O$22:$O$31)","v":0},{"$f":"LOOKUP(FM$62,$G$22:$G$31,$P$22:$P$31)*(GA62=$O$33)","v":0},{"$f":"LOOKUP(FM$62,$G$22:$G$31,$Q$22:$Q$31)*(GA62=$O$33)","v":0},{"$f":"LOOKUP(FM$62,$G$22:$G$31,$R$22:$R$31)","v":0},{"$f":"LOOKUP(FM$62,$G$22:$G$31,$U$22:$U$31)","v":0},{"$f":"IF(GE62=$U$34,LOOKUP(FM$62,$G$22:$G$31,$V$22:$V$31),\"NA\")","v":"NA"},{"$f":"IF(GE62=$U$33,LOOKUP(FM$62,$G$22:$G$31,$W$22:$W$31),\"NA\")","v":"NA"},{"$f":"LOOKUP(FM$62,$G$22:$G$31,$X$22:$X$31)","v":0},{"$f":"IF(GH62=$U$34,LOOKUP(FM$62,$G$22:$G$31,$Y$22:$Y$31),\"NA\")","v":"NA"},{"$f":"IF(GH62=$U$33,LOOKUP(FM$62,$G$22:$G$31,$Z$22:$Z$31),\"NA\")","v":"NA"},null,{"$f":"FM62+1","v":8},{"$f":"LOOKUP(GL62,$G$22:$G$31,$H$22:$H$31)","v":0},{"$f":"IF(GP62=0,0,IF(GP62=$J$33,IF(GS62<GR62,$G$95,$G$97),IF(GS62<GR62,$G$96,$G$98)))","v":0},null,{"$f":"LOOKUP(GL62,$G$22:$G$31,$J$22:$J$31)","v":0},null,{"$f":"LOOKUP(GL$62,$G$22:$G$31,$L$22:$L$31)","v":0},{"$f":"LOOKUP(GL$62,$G$22:$G$31,$M$22:$M$31)","v":0},{"$f":"LOOKUP(GL$62,$G$22:$G$31,$N$22:$N$31)","v":0},{"$f":"0.0013*GR62","v":0},{"$f":"LOOKUP(GU62/2,$M$125:$M$145,$N$125:$N$145)","v":0.6},{"$f":"IF(GR62=0,0,MAX(GS62/GR62,LOOKUP(GL$62,$Z$123:$Z$132,$AF$123:$AF$132)))","v":0},{"$f":"LOOKUP(GL$62,$Z$108:$Z$117,$AE$108:$AE$117)","v":0},{"$f":"LOOKUP(GL$62,$Z$108:$Z$117,$AF$108:$AF$117)","v":0},{"$f":"LOOKUP(GL$62,$G$22:$G$31,$O$22:$O$31)","v":0},{"$f":"LOOKUP(GL$62,$G$22:$G$31,$P$22:$P$31)*(GZ62=$O$33)","v":0},{"$f":"LOOKUP(GL$62,$G$22:$G$31,$Q$22:$Q$31)*(GZ62=$O$33)","v":0},{"$f":"LOOKUP(GL$62,$G$22:$G$31,$R$22:$R$31)","v":0},{"$f":"LOOKUP(GL$62,$G$22:$G$31,$U$22:$U$31)","v":0},{"$f":"IF(HD62=$U$34,LOOKUP(GL$62,$G$22:$G$31,$V$22:$V$31),\"NA\")","v":"NA"},{"$f":"IF(HD62=$U$33,LOOKUP(GL$62,$G$22:$G$31,$W$22:$W$31),\"NA\")","v":"NA"},{"$f":"LOOKUP(GL$62,$G$22:$G$31,$X$22:$X$31)","v":0},{"$f":"IF(HG62=$U$34,LOOKUP(GL$62,$G$22:$G$31,$Y$22:$Y$31),\"NA\")","v":"NA"},{"$f":"IF(HG62=$U$33,LOOKUP(GL$62,$G$22:$G$31,$Z$22:$Z$31),\"NA\")","v":"NA"},null,{"$f":"GL62+1","v":9},{"$f":"LOOKUP(HK62,$G$22:$G$31,$H$22:$H$31)","v":0},{"$f":"IF(HO62=0,0,IF(HO62=$J$33,IF(HR62<HQ62,$G$95,$G$97),IF(HR62<HQ62,$G$96,$G$98)))","v":0},null,{"$f":"LOOKUP(HK62,$G$22:$G$31,$J$22:$J$31)","v":0},null,{"$f":"LOOKUP(HK$62,$G$22:$G$31,$L$22:$L$31)","v":0},{"$f":"LOOKUP(HK$62,$G$22:$G$31,$M$22:$M$31)","v":0},{"$f":"LOOKUP(HK$62,$G$22:$G$31,$N$22:$N$31)","v":0},{"$f":"0.0013*HQ62","v":0},{"$f":"LOOKUP(HT62/2,$M$125:$M$145,$N$125:$N$145)","v":0.6},{"$f":"IF(HQ62=0,0,MAX(HR62/HQ62,LOOKUP(HK$62,$Z$123:$Z$132,$AF$123:$AF$132)))","v":0},{"$f":"LOOKUP(HK$62,$Z$108:$Z$117,$AE$108:$AE$117)","v":0},{"$f":"LOOKUP(HK$62,$Z$108:$Z$117,$AF$108:$AF$117)","v":0},{"$f":"LOOKUP(HK$62,$G$22:$G$31,$O$22:$O$31)","v":0},{"$f":"LOOKUP(HK$62,$G$22:$G$31,$P$22:$P$31)*(HY62=$O$33)","v":0},{"$f":"LOOKUP(HK$62,$G$22:$G$31,$Q$22:$Q$31)*(HY62=$O$33)","v":0},{"$f":"LOOKUP(HK$62,$G$22:$G$31,$R$22:$R$31)","v":0},{"$f":"LOOKUP(HK$62,$G$22:$G$31,$U$22:$U$31)","v":0},{"$f":"IF(IC62=$U$34,LOOKUP(HK$62,$G$22:$G$31,$V$22:$V$31),\"NA\")","v":"NA"},{"$f":"IF(IC62=$U$33,LOOKUP(HK$62,$G$22:$G$31,$W$22:$W$31),\"NA\")","v":"NA"},{"$f":"LOOKUP(HK$62,$G$22:$G$31,$X$22:$X$31)","v":0},{"$f":"IF(IF62=$U$34,LOOKUP(HK$62,$G$22:$G$31,$Y$22:$Y$31),\"NA\")","v":"NA"},{"$f":"IF(IF62=$U$33,LOOKUP(HK$62,$G$22:$G$31,$Z$22:$Z$31),\"NA\")","v":"NA"},null,{"$f":"HK62+1","v":10},{"$f":"LOOKUP(IJ62,$G$22:$G$31,$H$22:$H$31)","v":0},{"$f":"IF(IN62=0,0,IF(IN62=$J$33,IF(IQ62<IP62,$G$95,$G$97),IF(IQ62<IP62,$G$96,$G$98)))","v":0},null,{"$f":"LOOKUP(IJ62,$G$22:$G$31,$J$22:$J$31)","v":0},null,{"$f":"LOOKUP(IJ$62,$G$22:$G$31,$L$22:$L$31)","v":0},{"$f":"LOOKUP(IJ$62,$G$22:$G$31,$M$22:$M$31)","v":0},{"$f":"LOOKUP(IJ$62,$G$22:$G$31,$N$22:$N$31)","v":0},{"$f":"0.0013*IP62","v":0},{"$f":"LOOKUP(IS62/2,$M$125:$M$145,$N$125:$N$145)","v":0.6},{"$f":"IF(IP62=0,0,MAX(IQ62/IP62,LOOKUP(IJ$62,$Z$123:$Z$132,$AF$123:$AF$132)))","v":0},{"$f":"LOOKUP(IJ$62,$Z$108:$Z$117,$AE$108:$AE$117)","v":0},{"$f":"LOOKUP(IJ$62,$Z$108:$Z$117,$AF$108:$AF$117)","v":0},{"$f":"LOOKUP(IJ$62,$G$22:$G$31,$O$22:$O$31)","v":0},{"$f":"LOOKUP(IJ$62,$G$22:$G$31,$P$22:$P$31)*(IX62=$O$33)","v":0},{"$f":"LOOKUP(IJ$62,$G$22:$G$31,$Q$22:$Q$31)*(IX62=$O$33)","v":0},{"$f":"LOOKUP(IJ$62,$G$22:$G$31,$R$22:$R$31)","v":0},{"$f":"LOOKUP(IJ$62,$G$22:$G$31,$U$22:$U$31)","v":0},{"$f":"IF(JB62=$U$34,LOOKUP(IJ$62,$G$22:$G$31,$V$22:$V$31),\"NA\")","v":"NA"},{"$f":"IF(JB62=$U$33,LOOKUP(IJ$62,$G$22:$G$31,$W$22:$W$31),\"NA\")","v":"NA"},{"$f":"LOOKUP(IJ$62,$G$22:$G$31,$X$22:$X$31)","v":0},{"$f":"IF(JE62=$U$34,LOOKUP(IJ$62,$G$22:$G$31,$Y$22:$Y$31),\"NA\")","v":"NA"},{"$f":"IF(JE62=$U$33,LOOKUP(IJ$62,$G$22:$G$31,$Z$22:$Z$31),\"NA\")","v":"NA"}]
[null,null,null,null,null,null,"Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Cooling","Heating","Total","Base","DCV","Return","Return","Base","Design","Fan Pwr","AHU Discharge",null,"ERV Impact",null,null,"Cool Load","Heat Load Reduction",null,"AHU Cooling",null,"AHU Heating",null,"Zone Heating",null,null,"Cooling","Heating","Total","Base","DCV","Return","Return","Base","Design","Fan Pwr","AHU Discharge",null,"ERV Impact",null,null,"Cool Load","Heat Load Reduction",null,"AHU Cooling",null,"AHU Heating",null,"Zone Heating",null,null,"Cooling","Heating","Total","Base","DCV","Return","Return","Base","Design","Fan Pwr","AHU Discharge",null,"ERV Impact",null,null,"Cool Load","Heat Load Reduction",null,"AHU Cooling",null,"AHU Heating",null,"Zone Heating",null,null,"Cooling","Heating","Total","Base","DCV","Return","Return","Base","Design","Fan Pwr","AHU Discharge",null,"ERV Impact",null,null,"Cool Load","Heat Load Reduction",null,"AHU Cooling",null,"AHU Heating",null,"Zone Heating",null,null,"Cooling","Heating","Total","Base","DCV","Return","Return","Base","Design","Fan Pwr","AHU Discharge",null,"ERV Impact",null,null,"Cool Load","Heat Load Reduction",null,"AHU Cooling",null,"AHU Heating",null,"Zone Heating",null,null,"Cooling","Heating","Total","Base","DCV","Return","Return","Base","Design","Fan Pwr","AHU Discharge",null,"ERV Impact",null,null,"Cool Load","Heat Load Reduction",null,"AHU Cooling",null,"AHU Heating",null,"Zone Heating",null,null,"Cooling","Heating","Total","Base","DCV","Return","Return","Base","Design","Fan Pwr","AHU Discharge",null,"ERV Impact",null,null,"Cool Load","Heat Load Reduction",null,"AHU Cooling",null,"AHU Heating",null,"Zone Heating",null,null,"Cooling","Heating","Total","Base","DCV","Return","Return","Base","Design","Fan Pwr","AHU Discharge",null,"ERV Impact",null,null,"Cool Load","Heat Load Reduction",null,"AHU Cooling",null,"AHU Heating",null,"Zone Heating",null,null,"Cooling","Heating","Total","Base","DCV","Return","Return","Base","Design","Fan Pwr","AHU Discharge",null,"ERV Impact",null,null,"Cool Load","Heat Load Reduction",null,"AHU Cooling",null,"AHU Heating",null,"Zone Heating",null,null,"Cooling","Heating","Total","Base","DCV","Return","Return","Base","Design","Fan Pwr","AHU Discharge",null,"ERV Impact",null,null,"Cool Load","Heat Load Reduction",null,"AHU Cooling",null,"AHU Heating",null,"Zone Heating"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","%","%","Supply","OA Flow","%OA Reduced","Temp","Enth","Fan Speed","Fan Speed","Reduction","Temp","Enth","Eff","DAT","DAH","Reduction","AHU","Zone","Perf","Reduc","Perf","Reduc","Perf","Reduc",null,"%","%","Supply","OA Flow","%OA Reduced","Temp","Enth","Fan Speed","Fan Speed","Reduction","Temp","Enth","Eff","DAT","DAH","Reduction","AHU","Zone","Perf","Reduc","Perf","Reduc","Perf","Reduc",null,"%","%","Supply","OA Flow","%OA Reduced","Temp","Enth","Fan Speed","Fan Speed","Reduction","Temp","Enth","Eff","DAT","DAH","Reduction","AHU","Zone","Perf","Reduc","Perf","Reduc","Perf","Reduc",null,"%","%","Supply","OA Flow","%OA Reduced","Temp","Enth","Fan Speed","Fan Speed","Reduction","Temp","Enth","Eff","DAT","DAH","Reduction","AHU","Zone","Perf","Reduc","Perf","Reduc","Perf","Reduc",null,"%","%","Supply","OA Flow","%OA Reduced","Temp","Enth","Fan Speed","Fan Speed","Reduction","Temp","Enth","Eff","DAT","DAH","Reduction","AHU","Zone","Perf","Reduc","Perf","Reduc","Perf","Reduc",null,"%","%","Supply","OA Flow","%OA Reduced","Temp","Enth","Fan Speed","Fan Speed","Reduction","Temp","Enth","Eff","DAT","DAH","Reduction","AHU","Zone","Perf","Reduc","Perf","Reduc","Perf","Reduc",null,"%","%","Supply","OA Flow","%OA Reduced","Temp","Enth","Fan Speed","Fan Speed","Reduction","Temp","Enth","Eff","DAT","DAH","Reduction","AHU","Zone","Perf","Reduc","Perf","Reduc","Perf","Reduc",null,"%","%","Supply","OA Flow","%OA Reduced","Temp","Enth","Fan Speed","Fan Speed","Reduction","Temp","Enth","Eff","DAT","DAH","Reduction","AHU","Zone","Perf","Reduc","Perf","Reduc","Perf","Reduc",null,"%","%","Supply","OA Flow","%OA Reduced","Temp","Enth","Fan Speed","Fan Speed","Reduction","Temp","Enth","Eff","DAT","DAH","Reduction","AHU","Zone","Perf","Reduc","Perf","Reduc","Perf","Reduc",null,"%","%","Supply","OA Flow","%OA Reduced","Temp","Enth","Fan Speed","Fan Speed","Reduction","Temp","Enth","Eff","DAT","DAH","Reduction","AHU","Zone","Perf","Reduc","Perf","Reduc","Perf","Reduc"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","Load","Load","CFM","CFM","%","°F","Btu/lb","%","%","kW","°F","Btu/lb","%","°F","Btu/lb","MBH","MBH","MBH","EER","kW","COP","MBH","COP","MBH",null,"Load","Load","CFM","CFM","%","°F","Btu/lb","%","%","kW","°F","Btu/lb","%","°F","Btu/lb","MBH","MBH","MBH","EER","kW","COP","MBH","COP","MBH",null,"Load","Load","CFM","CFM","%","°F","Btu/lb","%","%","kW","°F","Btu/lb","%","°F","Btu/lb","MBH","MBH","MBH","EER","kW","COP","MBH","COP","MBH",null,"Load","Load","CFM","CFM","%","°F","Btu/lb","%","%","kW","°F","Btu/lb","%","°F","Btu/lb","MBH","MBH","MBH","EER","kW","COP","MBH","COP","MBH",null,"Load","Load","CFM","CFM","%","°F","Btu/lb","%","%","kW","°F","Btu/lb","%","°F","Btu/lb","MBH","MBH","MBH","EER","kW","COP","MBH","COP","MBH",null,"Load","Load","CFM","CFM","%","°F","Btu/lb","%","%","kW","°F","Btu/lb","%","°F","Btu/lb","MBH","MBH","MBH","EER","kW","COP","MBH","COP","MBH",null,"Load","Load","CFM","CFM","%","°F","Btu/lb","%","%","kW","°F","Btu/lb","%","°F","Btu/lb","MBH","MBH","MBH","EER","kW","COP","MBH","COP","MBH",null,"Load","Load","CFM","CFM","%","°F","Btu/lb","%","%","kW","°F","Btu/lb","%","°F","Btu/lb","MBH","MBH","MBH","EER","kW","COP","MBH","COP","MBH",null,"Load","Load","CFM","CFM","%","°F","Btu/lb","%","%","kW","°F","Btu/lb","%","°F","Btu/lb","MBH","MBH","MBH","EER","kW","COP","MBH","COP","MBH",null,"Load","Load","CFM","CFM","%","°F","Btu/lb","%","%","kW","°F","Btu/lb","%","°F","Btu/lb","MBH","MBH","MBH","EER","kW","COP","MBH","COP","MBH"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A44","v":100},{"$f":"'Project Info'!B44","v":105},{"$f":"'Project Info'!C44","v":102},{"$f":"'Project Info'!D44","v":76},{"$f":"'Project Info'!E44","v":40},{"$f":"'Project Info'!F44","v":0},{"$f":"'Project Info'!G44","v":0},{"$f":"'Project Info'!H44","v":0},{"$f":"'Project Info'!I44","v":0},{"$f":"'Project Info'!J44","v":0},{"$f":"'Project Info'!K44","v":0},{"$f":"'Project Info'!L44","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$97:$AF$97,$AC$97:$AD$97,$I67)))*(AJ$62=\"Yes\")","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$102:$AF$102,$AC$102:$AD$102,$I67)))","v":0},{"$f":"MAX(AD$62,TREND(OFFSET($Z$122,MATCH(S$62,$Z$123:$Z$132,0),5,1,2),OFFSET($Z$122,MATCH(S$62,$Z$123:$Z$132,0),3,1,2),S67))*Y$62","v":0},{"$f":"Z$62","v":0},{"$f":"$I$101*AA$62","v":0},{"$f":"IF(S67>0,$J$123,$K$123)","v":70},{"$f":"IF(S67>0,$J$126,$K$126)","v":25.099807999999999},{"$f":"IF(Y$62=0,0,U67/Y$62)","v":0},{"$f":"IF(OR($I67<$AI$106,$I67>$AI$107),IF(Y$62=0,0,(U67-W67*V67)/Y$62),Z67)","v":0},{"$f":"IF(Y$62=0,0,AB$62*((Z67*$K$139+(1-$K$139)*Z67^3)-(AA67*$K$139+(1-$K$139)*AA67^3))*0.746/AC$62)","v":0},{"$f":"MAX(MIN(AF$62,X67,TREND(OFFSET($Z$107,MATCH(S$62,$Z$108:$Z$117,0),5,1,2),OFFSET($Z$107,MATCH(S$62,$Z$108:$Z$117,0),3,1,2),$I67)),AE$62)","v":0},{"$f":"$AI$102+$AI$103*AC67","v":-12.336},{"$f":"IF(S67>0,AI$62,AH$62)","v":0},{"$f":"IF(S67>0,MAX(AC67,$I67-AE67*($I67-X67)),MIN(AC67,$I67-AE67*($I67-X67)))","v":0},{"$f":"IF(S67>0,MAX(AD67,$K67-AE67*($K67-Y67)),MIN(AD67,$K67-AE67*($K67-Y67)))","v":-12.336},{"$f":"(S67>0)*OR($I67<$AI$106,$I67>$AI$107)*(4.45*V67*W67*(AG67-AD67)/1000+AB67/2*3.412)","v":0},{"$f":"(T67>0)*(AF67<AC67)*(1.08*W67*V67*(AC67-AF67)/1000-AB67/2*3.412)","v":0},{"$f":"(T67>0)*MAX(0,1.08*W67*V67*(X67-AC67)/1000)","v":0},{"$f":"TREND(OFFSET($Z$136,MATCH(S$62,$Z$137:$Z$146,0),MATCH(S67,$AA$136:$AE$136,-1),1,2),OFFSET($Z$136,0,MATCH(S67,$AA$136:$AE$136,-1),1,2),S67)","v":0},{"$f":"IF(AK67=0,0,AH67/AK67)","v":0},{"$f":"IF(AK$62=0,0,IF(AK$62=$U$34,AL$62,AM$62))","v":0},{"$f":"IF(AM67=0,0,AI67/AM67)","v":0},{"$f":"IF(AN$62=0,0,IF(AN$62=$U$34,AO$62,AP$62))","v":0},{"$f":"IF(AO67=0,0,AJ67/AO67)","v":0},null,{"$f":"MAX(0,MIN(1,TREND($AE$97:$AF$97,$AC$97:$AD$97,$I67)))*(BI$62=\"Yes\")","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$102:$AF$102,$AC$102:$AD$102,$I67)))","v":0},{"$f":"MAX(BC$62,TREND(OFFSET($Z$122,MATCH(AR$62,$Z$123:$Z$132,0),5,1,2),OFFSET($Z$122,MATCH(AR$62,$Z$123:$Z$132,0),3,1,2),AR67))*AX$62","v":0},{"$f":"AY$62","v":0},{"$f":"$I$101*AZ$62","v":0},{"$f":"IF(AR67>0,$J$123,$K$123)","v":70},{"$f":"IF(AR67>0,$J$126,$K$126)","v":25.099807999999999},{"$f":"IF(AX$62=0,0,AT67/AX$62)","v":0},{"$f":"IF(OR($I67<$AI$106,$I67>$AI$107),IF(AX$62=0,0,(AT67-AV67*AU67)/AX$62),AY67)","v":0},{"$f":"IF(AX$62=0,0,BA$62*((AY67*$K$139+(1-$K$139)*AY67^3)-(AZ67*$K$139+(1-$K$139)*AZ67^3))*0.746/BB$62)","v":0},{"$f":"MAX(MIN(BE$62,AW67,TREND(OFFSET($Z$107,MATCH(AR$62,$Z$108:$Z$117,0),5,1,2),OFFSET($Z$107,MATCH(AR$62,$Z$108:$Z$117,0),3,1,2),$I67)),BD$62)","v":0},{"$f":"$AI$102+$AI$103*BB67","v":-12.336},{"$f":"IF(AR67>0,BH$62,BG$62)","v":0},{"$f":"IF(AR67>0,MAX(BB67,$I67-BD67*($I67-AW67)),MIN(BB67,$I67-BD67*($I67-AW67)))","v":0},{"$f":"IF(AR67>0,MAX(BC67,$K67-BD67*($K67-AX67)),MIN(BC67,$K67-BD67*($K67-AX67)))","v":-12.336},{"$f":"(AR67>0)*OR($I67<$AI$106,$I67>$AI$107)*(4.45*AU67*AV67*(BF67-BC67)/1000+BA67/2*3.412)","v":0},{"$f":"(AS67>0)*(BE67<BB67)*(1.08*AV67*AU67*(BB67-BE67)/1000-BA67/2*3.412)","v":0},{"$f":"(AS67>0)*MAX(0,1.08*AV67*AU67*(AW67-BB67)/1000)","v":0},{"$f":"TREND(OFFSET($Z$136,MATCH(AR$62,$Z$137:$Z$146,0),MATCH(AR67,$AA$136:$AE$136,-1),1,2),OFFSET($Z$136,0,MATCH(AR67,$AA$136:$AE$136,-1),1,2),AR67)","v":0},{"$f":"IF(BJ67=0,0,BG67/BJ67)","v":0},{"$f":"IF(BJ$62=0,0,IF(BJ$62=$U$34,BK$62,BL$62))","v":0},{"$f":"IF(BL67=0,0,BH67/BL67)","v":0},{"$f":"IF(BM$62=0,0,IF(BM$62=$U$34,BN$62,BO$62))","v":0},{"$f":"IF(BN67=0,0,BI67/BN67)","v":0},null,{"$f":"MAX(0,MIN(1,TREND($AE$97:$AF$97,$AC$97:$AD$97,$I67)))*(CH$62=\"Yes\")","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$102:$AF$102,$AC$102:$AD$102,$I67)))","v":0},{"$f":"MAX(CB$62,TREND(OFFSET($Z$122,MATCH(BQ$62,$Z$123:$Z$132,0),5,1,2),OFFSET($Z$122,MATCH(BQ$62,$Z$123:$Z$132,0),3,1,2),BQ67))*BW$62","v":0},{"$f":"BX$62","v":0},{"$f":"$I$101*BY$62","v":0},{"$f":"IF(BQ67>0,$J$123,$K$123)","v":70},{"$f":"IF(BQ67>0,$J$126,$K$126)","v":25.099807999999999},{"$f":"IF(BW$62=0,0,BS67/BW$62)","v":0},{"$f":"IF(OR($I67<$AI$106,$I67>$AI$107),IF(BW$62=0,0,(BS67-BU67*BT67)/BW$62),BX67)","v":0},{"$f":"IF(BW$62=0,0,BZ$62*((BX67*$K$139+(1-$K$139)*BX67^3)-(BY67*$K$139+(1-$K$139)*BY67^3))*0.746/CA$62)","v":0},{"$f":"MAX(MIN(CD$62,BV67,TREND(OFFSET($Z$107,MATCH(BQ$62,$Z$108:$Z$117,0),5,1,2),OFFSET($Z$107,MATCH(BQ$62,$Z$108:$Z$117,0),3,1,2),$I67)),CC$62)","v":0},{"$f":"$AI$102+$AI$103*CA67","v":-12.336},{"$f":"IF(BQ67>0,CG$62,CF$62)","v":0},{"$f":"IF(BQ67>0,MAX(CA67,$I67-CC67*($I67-BV67)),MIN(CA67,$I67-CC67*($I67-BV67)))","v":0},{"$f":"IF(BQ67>0,MAX(CB67,$K67-CC67*($K67-BW67)),MIN(CB67,$K67-CC67*($K67-BW67)))","v":-12.336},{"$f":"(BQ67>0)*OR($I67<$AI$106,$I67>$AI$107)*(4.45*BT67*BU67*(CE67-CB67)/1000+BZ67/2*3.412)","v":0},{"$f":"(BR67>0)*(CD67<CA67)*(1.08*BU67*BT67*(CA67-CD67)/1000-BZ67/2*3.412)","v":0},{"$f":"(BR67>0)*MAX(0,1.08*BU67*BT67*(BV67-CA67)/1000)","v":0},{"$f":"TREND(OFFSET($Z$136,MATCH(BQ$62,$Z$137:$Z$146,0),MATCH(BQ67,$AA$136:$AE$136,-1),1,2),OFFSET($Z$136,0,MATCH(BQ67,$AA$136:$AE$136,-1),1,2),BQ67)","v":0},{"$f":"IF(CI67=0,0,CF67/CI67)","v":0},{"$f":"IF(CI$62=0,0,IF(CI$62=$U$34,CJ$62,CK$62))","v":0},{"$f":"IF(CK67=0,0,CG67/CK67)","v":0},{"$f":"IF(CL$62=0,0,IF(CL$62=$U$34,CM$62,CN$62))","v":0},{"$f":"IF(CM67=0,0,CH67/CM67)","v":0},null,{"$f":"MAX(0,MIN(1,TREND($AE$97:$AF$97,$AC$97:$AD$97,$I67)))*(DG$62=\"Yes\")","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$102:$AF$102,$AC$102:$AD$102,$I67)))","v":0},{"$f":"MAX(DA$62,TREND(OFFSET($Z$122,MATCH(CP$62,$Z$123:$Z$132,0),5,1,2),OFFSET($Z$122,MATCH(CP$62,$Z$123:$Z$132,0),3,1,2),CP67))*CV$62","v":0},{"$f":"CW$62","v":0},{"$f":"$I$101*CX$62","v":0},{"$f":"IF(CP67>0,$J$123,$K$123)","v":70},{"$f":"IF(CP67>0,$J$126,$K$126)","v":25.099807999999999},{"$f":"IF(CV$62=0,0,CR67/CV$62)","v":0},{"$f":"IF(OR($I67<$AI$106,$I67>$AI$107),IF(CV$62=0,0,(CR67-CT67*CS67)/CV$62),CW67)","v":0},{"$f":"IF(CV$62=0,0,CY$62*((CW67*$K$139+(1-$K$139)*CW67^3)-(CX67*$K$139+(1-$K$139)*CX67^3))*0.746/CZ$62)","v":0},{"$f":"MAX(MIN(DC$62,CU67,TREND(OFFSET($Z$107,MATCH(CP$62,$Z$108:$Z$117,0),5,1,2),OFFSET($Z$107,MATCH(CP$62,$Z$108:$Z$117,0),3,1,2),$I67)),DB$62)","v":0},{"$f":"$AI$102+$AI$103*CZ67","v":-12.336},{"$f":"IF(CP67>0,DF$62,DE$62)","v":0},{"$f":"IF(CP67>0,MAX(CZ67,$I67-DB67*($I67-CU67)),MIN(CZ67,$I67-DB67*($I67-CU67)))","v":0},{"$f":"IF(CP67>0,MAX(DA67,$K67-DB67*($K67-CV67)),MIN(DA67,$K67-DB67*($K67-CV67)))","v":-12.336},{"$f":"(CP67>0)*OR($I67<$AI$106,$I67>$AI$107)*(4.45*CS67*CT67*(DD67-DA67)/1000+CY67/2*3.412)","v":0},{"$f":"(CQ67>0)*(DC67<CZ67)*(1.08*CT67*CS67*(CZ67-DC67)/1000-CY67/2*3.412)","v":0},{"$f":"(CQ67>0)*MAX(0,1.08*CT67*CS67*(CU67-CZ67)/1000)","v":0},{"$f":"TREND(OFFSET($Z$136,MATCH(CP$62,$Z$137:$Z$146,0),MATCH(CP67,$AA$136:$AE$136,-1),1,2),OFFSET($Z$136,0,MATCH(CP67,$AA$136:$AE$136,-1),1,2),CP67)","v":0},{"$f":"IF(DH67=0,0,DE67/DH67)","v":0},{"$f":"IF(DH$62=0,0,IF(DH$62=$U$34,DI$62,DJ$62))","v":0},{"$f":"IF(DJ67=0,0,DF67/DJ67)","v":0},{"$f":"IF(DK$62=0,0,IF(DK$62=$U$34,DL$62,DM$62))","v":0},{"$f":"IF(DL67=0,0,DG67/DL67)","v":0},null,{"$f":"MAX(0,MIN(1,TREND($AE$97:$AF$97,$AC$97:$AD$97,$I67)))*(EF$62=\"Yes\")","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$102:$AF$102,$AC$102:$AD$102,$I67)))","v":0},{"$f":"MAX(DZ$62,TREND(OFFSET($Z$122,MATCH(DO$62,$Z$123:$Z$132,0),5,1,2),OFFSET($Z$122,MATCH(DO$62,$Z$123:$Z$132,0),3,1,2),DO67))*DU$62","v":0},{"$f":"DV$62","v":0},{"$f":"$I$101*DW$62","v":0},{"$f":"IF(DO67>0,$J$123,$K$123)","v":70},{"$f":"IF(DO67>0,$J$126,$K$126)","v":25.099807999999999},{"$f":"IF(DU$62=0,0,DQ67/DU$62)","v":0},{"$f":"IF(OR($I67<$AI$106,$I67>$AI$107),IF(DU$62=0,0,(DQ67-DS67*DR67)/DU$62),DV67)","v":0},{"$f":"IF(DU$62=0,0,DX$62*((DV67*$K$139+(1-$K$139)*DV67^3)-(DW67*$K$139+(1-$K$139)*DW67^3))*0.746/DY$62)","v":0},{"$f":"MAX(MIN(EB$62,DT67,TREND(OFFSET($Z$107,MATCH(DO$62,$Z$108:$Z$117,0),5,1,2),OFFSET($Z$107,MATCH(DO$62,$Z$108:$Z$117,0),3,1,2),$I67)),EA$62)","v":0},{"$f":"$AI$102+$AI$103*DY67","v":-12.336},{"$f":"IF(DO67>0,EE$62,ED$62)","v":0},{"$f":"IF(DO67>0,MAX(DY67,$I67-EA67*($I67-DT67)),MIN(DY67,$I67-EA67*($I67-DT67)))","v":0},{"$f":"IF(DO67>0,MAX(DZ67,$K67-EA67*($K67-DU67)),MIN(DZ67,$K67-EA67*($K67-DU67)))","v":-12.336},{"$f":"(DO67>0)*OR($I67<$AI$106,$I67>$AI$107)*(4.45*DR67*DS67*(EC67-DZ67)/1000+DX67/2*3.412)","v":0},{"$f":"(DP67>0)*(EB67<DY67)*(1.08*DS67*DR67*(DY67-EB67)/1000-DX67/2*3.412)","v":0},{"$f":"(DP67>0)*MAX(0,1.08*DS67*DR67*(DT67-DY67)/1000)","v":0},{"$f":"TREND(OFFSET($Z$136,MATCH(DO$62,$Z$137:$Z$146,0),MATCH(DO67,$AA$136:$AE$136,-1),1,2),OFFSET($Z$136,0,MATCH(DO67,$AA$136:$AE$136,-1),1,2),DO67)","v":0},{"$f":"IF(EG67=0,0,ED67/EG67)","v":0},{"$f":"IF(EG$62=0,0,IF(EG$62=$U$34,EH$62,EI$62))","v":0},{"$f":"IF(EI67=0,0,EE67/EI67)","v":0},{"$f":"IF(EJ$62=0,0,IF(EJ$62=$U$34,EK$62,EL$62))","v":0},{"$f":"IF(EK67=0,0,EF67/EK67)","v":0},null,{"$f":"MAX(0,MIN(1,TREND($AE$97:$AF$97,$AC$97:$AD$97,$I67)))*(FE$62=\"Yes\")","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$102:$AF$102,$AC$102:$AD$102,$I67)))","v":0},{"$f":"MAX(EY$62,TREND(OFFSET($Z$122,MATCH(EN$62,$Z$123:$Z$132,0),5,1,2),OFFSET($Z$122,MATCH(EN$62,$Z$123:$Z$132,0),3,1,2),EN67))*ET$62","v":0},{"$f":"EU$62","v":0},{"$f":"$I$101*EV$62","v":0},{"$f":"IF(EN67>0,$J$123,$K$123)","v":70},{"$f":"IF(EN67>0,$J$126,$K$126)","v":25.099807999999999},{"$f":"IF(ET$62=0,0,EP67/ET$62)","v":0},{"$f":"IF(OR($I67<$AI$106,$I67>$AI$107),IF(ET$62=0,0,(EP67-ER67*EQ67)/ET$62),EU67)","v":0},{"$f":"IF(ET$62=0,0,EW$62*((EU67*$K$139+(1-$K$139)*EU67^3)-(EV67*$K$139+(1-$K$139)*EV67^3))*0.746/EX$62)","v":0},{"$f":"MAX(MIN(FA$62,ES67,TREND(OFFSET($Z$107,MATCH(EN$62,$Z$108:$Z$117,0),5,1,2),OFFSET($Z$107,MATCH(EN$62,$Z$108:$Z$117,0),3,1,2),$I67)),EZ$62)","v":0},{"$f":"$AI$102+$AI$103*EX67","v":-12.336},{"$f":"IF(EN67>0,FD$62,FC$62)","v":0},{"$f":"IF(EN67>0,MAX(EX67,$I67-EZ67*($I67-ES67)),MIN(EX67,$I67-EZ67*($I67-ES67)))","v":0},{"$f":"IF(EN67>0,MAX(EY67,$K67-EZ67*($K67-ET67)),MIN(EY67,$K67-EZ67*($K67-ET67)))","v":-12.336},{"$f":"(EN67>0)*OR($I67<$AI$106,$I67>$AI$107)*(4.45*EQ67*ER67*(FB67-EY67)/1000+EW67/2*3.412)","v":0},{"$f":"(EO67>0)*(FA67<EX67)*(1.08*ER67*EQ67*(EX67-FA67)/1000-EW67/2*3.412)","v":0},{"$f":"(EO67>0)*MAX(0,1.08*ER67*EQ67*(ES67-EX67)/1000)","v":0},{"$f":"TREND(OFFSET($Z$136,MATCH(EN$62,$Z$137:$Z$146,0),MATCH(EN67,$AA$136:$AE$136,-1),1,2),OFFSET($Z$136,0,MATCH(EN67,$AA$136:$AE$136,-1),1,2),EN67)","v":0},{"$f":"IF(FF67=0,0,FC67/FF67)","v":0},{"$f":"IF(FF$62=0,0,IF(FF$62=$U$34,FG$62,FH$62))","v":0},{"$f":"IF(FH67=0,0,FD67/FH67)","v":0},{"$f":"IF(FI$62=0,0,IF(FI$62=$U$34,FJ$62,FK$62))","v":0},{"$f":"IF(FJ67=0,0,FE67/FJ67)","v":0},null,{"$f":"MAX(0,MIN(1,TREND($AE$97:$AF$97,$AC$97:$AD$97,$I67)))*(GD$62=\"Yes\")","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$102:$AF$102,$AC$102:$AD$102,$I67)))","v":0},{"$f":"MAX(FX$62,TREND(OFFSET($Z$122,MATCH(FM$62,$Z$123:$Z$132,0),5,1,2),OFFSET($Z$122,MATCH(FM$62,$Z$123:$Z$132,0),3,1,2),FM67))*FS$62","v":0},{"$f":"FT$62","v":0},{"$f":"$I$101*FU$62","v":0},{"$f":"IF(FM67>0,$J$123,$K$123)","v":70},{"$f":"IF(FM67>0,$J$126,$K$126)","v":25.099807999999999},{"$f":"IF(FS$62=0,0,FO67/FS$62)","v":0},{"$f":"IF(OR($I67<$AI$106,$I67>$AI$107),IF(FS$62=0,0,(FO67-FQ67*FP67)/FS$62),FT67)","v":0},{"$f":"IF(FS$62=0,0,FV$62*((FT67*$K$139+(1-$K$139)*FT67^3)-(FU67*$K$139+(1-$K$139)*FU67^3))*0.746/FW$62)","v":0},{"$f":"MAX(MIN(FZ$62,FR67,TREND(OFFSET($Z$107,MATCH(FM$62,$Z$108:$Z$117,0),5,1,2),OFFSET($Z$107,MATCH(FM$62,$Z$108:$Z$117,0),3,1,2),$I67)),FY$62)","v":0},{"$f":"$AI$102+$AI$103*FW67","v":-12.336},{"$f":"IF(FM67>0,GC$62,GB$62)","v":0},{"$f":"IF(FM67>0,MAX(FW67,$I67-FY67*($I67-FR67)),MIN(FW67,$I67-FY67*($I67-FR67)))","v":0},{"$f":"IF(FM67>0,MAX(FX67,$K67-FY67*($K67-FS67)),MIN(FX67,$K67-FY67*($K67-FS67)))","v":-12.336},{"$f":"(FM67>0)*OR($I67<$AI$106,$I67>$AI$107)*(4.45*FP67*FQ67*(GA67-FX67)/1000+FV67/2*3.412)","v":0},{"$f":"(FN67>0)*(FZ67<FW67)*(1.08*FQ67*FP67*(FW67-FZ67)/1000-FV67/2*3.412)","v":0},{"$f":"(FN67>0)*MAX(0,1.08*FQ67*FP67*(FR67-FW67)/1000)","v":0},{"$f":"TREND(OFFSET($Z$136,MATCH(FM$62,$Z$137:$Z$146,0),MATCH(FM67,$AA$136:$AE$136,-1),1,2),OFFSET($Z$136,0,MATCH(FM67,$AA$136:$AE$136,-1),1,2),FM67)","v":0},{"$f":"IF(GE67=0,0,GB67/GE67)","v":0},{"$f":"IF(GE$62=0,0,IF(GE$62=$U$34,GF$62,GG$62))","v":0},{"$f":"IF(GG67=0,0,GC67/GG67)","v":0},{"$f":"IF(GH$62=0,0,IF(GH$62=$U$34,GI$62,GJ$62))","v":0},{"$f":"IF(GI67=0,0,GD67/GI67)","v":0},null,{"$f":"MAX(0,MIN(1,TREND($AE$97:$AF$97,$AC$97:$AD$97,$I67)))*(HC$62=\"Yes\")","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$102:$AF$102,$AC$102:$AD$102,$I67)))","v":0},{"$f":"MAX(GW$62,TREND(OFFSET($Z$122,MATCH(GL$62,$Z$123:$Z$132,0),5,1,2),OFFSET($Z$122,MATCH(GL$62,$Z$123:$Z$132,0),3,1,2),GL67))*GR$62","v":0},{"$f":"GS$62","v":0},{"$f":"$I$101*GT$62","v":0},{"$f":"IF(GL67>0,$J$123,$K$123)","v":70},{"$f":"IF(GL67>0,$J$126,$K$126)","v":25.099807999999999},{"$f":"IF(GR$62=0,0,GN67/GR$62)","v":0},{"$f":"IF(OR($I67<$AI$106,$I67>$AI$107),IF(GR$62=0,0,(GN67-GP67*GO67)/GR$62),GS67)","v":0},{"$f":"IF(GR$62=0,0,GU$62*((GS67*$K$139+(1-$K$139)*GS67^3)-(GT67*$K$139+(1-$K$139)*GT67^3))*0.746/GV$62)","v":0},{"$f":"MAX(MIN(GY$62,GQ67,TREND(OFFSET($Z$107,MATCH(GL$62,$Z$108:$Z$117,0),5,1,2),OFFSET($Z$107,MATCH(GL$62,$Z$108:$Z$117,0),3,1,2),$I67)),GX$62)","v":0},{"$f":"$AI$102+$AI$103*GV67","v":-12.336},{"$f":"IF(GL67>0,HB$62,HA$62)","v":0},{"$f":"IF(GL67>0,MAX(GV67,$I67-GX67*($I67-GQ67)),MIN(GV67,$I67-GX67*($I67-GQ67)))","v":0},{"$f":"IF(GL67>0,MAX(GW67,$K67-GX67*($K67-GR67)),MIN(GW67,$K67-GX67*($K67-GR67)))","v":-12.336},{"$f":"(GL67>0)*OR($I67<$AI$106,$I67>$AI$107)*(4.45*GO67*GP67*(GZ67-GW67)/1000+GU67/2*3.412)","v":0},{"$f":"(GM67>0)*(GY67<GV67)*(1.08*GP67*GO67*(GV67-GY67)/1000-GU67/2*3.412)","v":0},{"$f":"(GM67>0)*MAX(0,1.08*GP67*GO67*(GQ67-GV67)/1000)","v":0},{"$f":"TREND(OFFSET($Z$136,MATCH(GL$62,$Z$137:$Z$146,0),MATCH(GL67,$AA$136:$AE$136,-1),1,2),OFFSET($Z$136,0,MATCH(GL67,$AA$136:$AE$136,-1),1,2),GL67)","v":0},{"$f":"IF(HD67=0,0,HA67/HD67)","v":0},{"$f":"IF(HD$62=0,0,IF(HD$62=$U$34,HE$62,HF$62))","v":0},{"$f":"IF(HF67=0,0,HB67/HF67)","v":0},{"$f":"IF(HG$62=0,0,IF(HG$62=$U$34,HH$62,HI$62))","v":0},{"$f":"IF(HH67=0,0,HC67/HH67)","v":0},null,{"$f":"MAX(0,MIN(1,TREND($AE$97:$AF$97,$AC$97:$AD$97,$I67)))*(IB$62=\"Yes\")","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$102:$AF$102,$AC$102:$AD$102,$I67)))","v":0},{"$f":"MAX(HV$62,TREND(OFFSET($Z$122,MATCH(HK$62,$Z$123:$Z$132,0),5,1,2),OFFSET($Z$122,MATCH(HK$62,$Z$123:$Z$132,0),3,1,2),HK67))*HQ$62","v":0},{"$f":"HR$62","v":0},{"$f":"$I$101*HS$62","v":0},{"$f":"IF(HK67>0,$J$123,$K$123)","v":70},{"$f":"IF(HK67>0,$J$126,$K$126)","v":25.099807999999999},{"$f":"IF(HQ$62=0,0,HM67/HQ$62)","v":0},{"$f":"IF(OR($I67<$AI$106,$I67>$AI$107),IF(HQ$62=0,0,(HM67-HO67*HN67)/HQ$62),HR67)","v":0},{"$f":"IF(HQ$62=0,0,HT$62*((HR67*$K$139+(1-$K$139)*HR67^3)-(HS67*$K$139+(1-$K$139)*HS67^3))*0.746/HU$62)","v":0},{"$f":"MAX(MIN(HX$62,HP67,TREND(OFFSET($Z$107,MATCH(HK$62,$Z$108:$Z$117,0),5,1,2),OFFSET($Z$107,MATCH(HK$62,$Z$108:$Z$117,0),3,1,2),$I67)),HW$62)","v":0},{"$f":"$AI$102+$AI$103*HU67","v":-12.336},{"$f":"IF(HK67>0,IA$62,HZ$62)","v":0},{"$f":"IF(HK67>0,MAX(HU67,$I67-HW67*($I67-HP67)),MIN(HU67,$I67-HW67*($I67-HP67)))","v":0},{"$f":"IF(HK67>0,MAX(HV67,$K67-HW67*($K67-HQ67)),MIN(HV67,$K67-HW67*($K67-HQ67)))","v":-12.336},{"$f":"(HK67>0)*OR($I67<$AI$106,$I67>$AI$107)*(4.45*HN67*HO67*(HY67-HV67)/1000+HT67/2*3.412)","v":0},{"$f":"(HL67>0)*(HX67<HU67)*(1.08*HO67*HN67*(HU67-HX67)/1000-HT67/2*3.412)","v":0},{"$f":"(HL67>0)*MAX(0,1.08*HO67*HN67*(HP67-HU67)/1000)","v":0},{"$f":"TREND(OFFSET($Z$136,MATCH(HK$62,$Z$137:$Z$146,0),MATCH(HK67,$AA$136:$AE$136,-1),1,2),OFFSET($Z$136,0,MATCH(HK67,$AA$136:$AE$136,-1),1,2),HK67)","v":0},{"$f":"IF(IC67=0,0,HZ67/IC67)","v":0},{"$f":"IF(IC$62=0,0,IF(IC$62=$U$34,ID$62,IE$62))","v":0},{"$f":"IF(IE67=0,0,IA67/IE67)","v":0},{"$f":"IF(IF$62=0,0,IF(IF$62=$U$34,IG$62,IH$62))","v":0},{"$f":"IF(IG67=0,0,IB67/IG67)","v":0},null,{"$f":"MAX(0,MIN(1,TREND($AE$97:$AF$97,$AC$97:$AD$97,$I67)))*(JA$62=\"Yes\")","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$102:$AF$102,$AC$102:$AD$102,$I67)))","v":0},{"$f":"MAX(IU$62,TREND(OFFSET($Z$122,MATCH(IJ$62,$Z$123:$Z$132,0),5,1,2),OFFSET($Z$122,MATCH(IJ$62,$Z$123:$Z$132,0),3,1,2),IJ67))*IP$62","v":0},{"$f":"IQ$62","v":0},{"$f":"$I$101*IR$62","v":0},{"$f":"IF(IJ67>0,$J$123,$K$123)","v":70},{"$f":"IF(IJ67>0,$J$126,$K$126)","v":25.099807999999999},{"$f":"IF(IP$62=0,0,IL67/IP$62)","v":0},{"$f":"IF(OR($I67<$AI$106,$I67>$AI$107),IF(IP$62=0,0,(IL67-IN67*IM67)/IP$62),IQ67)","v":0},{"$f":"IF(IP$62=0,0,IS$62*((IQ67*$K$139+(1-$K$139)*IQ67^3)-(IR67*$K$139+(1-$K$139)*IR67^3))*0.746/IT$62)","v":0},{"$f":"MAX(MIN(IW$62,IO67,TREND(OFFSET($Z$107,MATCH(IJ$62,$Z$108:$Z$117,0),5,1,2),OFFSET($Z$107,MATCH(IJ$62,$Z$108:$Z$117,0),3,1,2),$I67)),IV$62)","v":0},{"$f":"$AI$102+$AI$103*IT67","v":-12.336},{"$f":"IF(IJ67>0,IZ$62,IY$62)","v":0},{"$f":"IF(IJ67>0,MAX(IT67,$I67-IV67*($I67-IO67)),MIN(IT67,$I67-IV67*($I67-IO67)))","v":0},{"$f":"IF(IJ67>0,MAX(IU67,$K67-IV67*($K67-IP67)),MIN(IU67,$K67-IV67*($K67-IP67)))","v":-12.336},{"$f":"(IJ67>0)*OR($I67<$AI$106,$I67>$AI$107)*(4.45*IM67*IN67*(IX67-IU67)/1000+IS67/2*3.412)","v":0},{"$f":"(IK67>0)*(IW67<IT67)*(1.08*IN67*IM67*(IT67-IW67)/1000-IS67/2*3.412)","v":0},{"$f":"(IK67>0)*MAX(0,1.08*IN67*IM67*(IO67-IT67)/1000)","v":0},{"$f":"TREND(OFFSET($Z$136,MATCH(IJ$62,$Z$137:$Z$146,0),MATCH(IJ67,$AA$136:$AE$136,-1),1,2),OFFSET($Z$136,0,MATCH(IJ67,$AA$136:$AE$136,-1),1,2),IJ67)","v":0},{"$f":"IF(JB67=0,0,IY67/JB67)","v":0},{"$f":"IF(JB$62=0,0,IF(JB$62=$U$34,JC$62,JD$62))","v":0},{"$f":"IF(JD67=0,0,IZ67/JD67)","v":0},{"$f":"IF(JE$62=0,0,IF(JE$62=$U$34,JF$62,JG$62))","v":0},{"$f":"IF(JF67=0,0,JA67/JF67)","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A45","v":95},{"$f":"'Project Info'!B45","v":100},{"$f":"'Project Info'!C45","v":95.219272727272724},{"$f":"'Project Info'!D45","v":74.534025272781079},{"$f":"'Project Info'!E45","v":37.923296058061368},{"$f":"'Project Info'!F45","v":0},{"$f":"'Project Info'!G45","v":0},{"$f":"'Project Info'!H45","v":0},{"$f":"'Project Info'!I45","v":0},{"$f":"'Project Info'!J45","v":0},{"$f":"'Project Info'!K45","v":0},{"$f":"'Project Info'!L45","v":0},{"$f":"MAX(0,MIN(1,TREND($AE$97:$AF$97,$AC$97:$AD$97,$I68)))*(AJ$62=\"Yes\")","v":0},0,0,{"$f":"Z$62","v":0},{"$f":"$I$101*AA$62","v":0},70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,{"$f":"(S68>0)*OR($I68<$AI$106,$I68>$AI$107)*(4.45*V68*W68*(AG68-AD68)/1000+AB68/2*3.412)","v":0},{"$f":"(T68>0)*(AF68<AC68)*(1.08*W68*V68*(AC68-AF68)/1000-AB68/2*3.412)","v":0},{"$f":"(T68>0)*MAX(0,1.08*W68*V68*(X68-AC68)/1000)","v":0},0,0,0,0,0,{"$f":"IF(AO68=0,0,AJ68/AO68)","v":0},null,0,0,0,{"$f":"AY$62","v":0},{"$f":"$I$101*AZ$62","v":0},70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,{"$f":"(AR68>0)*OR($I68<$AI$106,$I68>$AI$107)*(4.45*AU68*AV68*(BF68-BC68)/1000+BA68/2*3.412)","v":0},{"$f":"(AS68>0)*(BE68<BB68)*(1.08*AV68*AU68*(BB68-BE68)/1000-BA68/2*3.412)","v":0},{"$f":"(AS68>0)*MAX(0,1.08*AV68*AU68*(AW68-BB68)/1000)","v":0},0,0,0,0,0,{"$f":"IF(BN68=0,0,BI68/BN68)","v":0},null,0,0,0,{"$f":"BX$62","v":0},{"$f":"$I$101*BY$62","v":0},70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,{"$f":"(BQ68>0)*OR($I68<$AI$106,$I68>$AI$107)*(4.45*BT68*BU68*(CE68-CB68)/1000+BZ68/2*3.412)","v":0},{"$f":"(BR68>0)*(CD68<CA68)*(1.08*BU68*BT68*(CA68-CD68)/1000-BZ68/2*3.412)","v":0},{"$f":"(BR68>0)*MAX(0,1.08*BU68*BT68*(BV68-CA68)/1000)","v":0},0,0,0,0,0,{"$f":"IF(CM68=0,0,CH68/CM68)","v":0},null,0,0,0,{"$f":"CW$62","v":0},{"$f":"$I$101*CX$62","v":0},70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,{"$f":"(CP68>0)*OR($I68<$AI$106,$I68>$AI$107)*(4.45*CS68*CT68*(DD68-DA68)/1000+CY68/2*3.412)","v":0},{"$f":"(CQ68>0)*(DC68<CZ68)*(1.08*CT68*CS68*(CZ68-DC68)/1000-CY68/2*3.412)","v":0},{"$f":"(CQ68>0)*MAX(0,1.08*CT68*CS68*(CU68-CZ68)/1000)","v":0},0,0,0,0,0,{"$f":"IF(DL68=0,0,DG68/DL68)","v":0},null,0,0,0,{"$f":"DV$62","v":0},{"$f":"$I$101*DW$62","v":0},70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,{"$f":"(DO68>0)*OR($I68<$AI$106,$I68>$AI$107)*(4.45*DR68*DS68*(EC68-DZ68)/1000+DX68/2*3.412)","v":0},{"$f":"(DP68>0)*(EB68<DY68)*(1.08*DS68*DR68*(DY68-EB68)/1000-DX68/2*3.412)","v":0},{"$f":"(DP68>0)*MAX(0,1.08*DS68*DR68*(DT68-DY68)/1000)","v":0},0,0,0,0,0,{"$f":"IF(EK68=0,0,EF68/EK68)","v":0},null,0,0,0,{"$f":"EU$62","v":0},{"$f":"$I$101*EV$62","v":0},70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,{"$f":"(EN68>0)*OR($I68<$AI$106,$I68>$AI$107)*(4.45*EQ68*ER68*(FB68-EY68)/1000+EW68/2*3.412)","v":0},{"$f":"(EO68>0)*(FA68<EX68)*(1.08*ER68*EQ68*(EX68-FA68)/1000-EW68/2*3.412)","v":0},{"$f":"(EO68>0)*MAX(0,1.08*ER68*EQ68*(ES68-EX68)/1000)","v":0},0,0,0,0,0,{"$f":"IF(FJ68=0,0,FE68/FJ68)","v":0},null,0,0,0,{"$f":"FT$62","v":0},{"$f":"$I$101*FU$62","v":0},70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,{"$f":"(FM68>0)*OR($I68<$AI$106,$I68>$AI$107)*(4.45*FP68*FQ68*(GA68-FX68)/1000+FV68/2*3.412)","v":0},{"$f":"(FN68>0)*(FZ68<FW68)*(1.08*FQ68*FP68*(FW68-FZ68)/1000-FV68/2*3.412)","v":0},{"$f":"(FN68>0)*MAX(0,1.08*FQ68*FP68*(FR68-FW68)/1000)","v":0},0,0,0,0,0,{"$f":"IF(GI68=0,0,GD68/GI68)","v":0},null,0,0,0,{"$f":"GS$62","v":0},{"$f":"$I$101*GT$62","v":0},70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,{"$f":"(GL68>0)*OR($I68<$AI$106,$I68>$AI$107)*(4.45*GO68*GP68*(GZ68-GW68)/1000+GU68/2*3.412)","v":0},{"$f":"(GM68>0)*(GY68<GV68)*(1.08*GP68*GO68*(GV68-GY68)/1000-GU68/2*3.412)","v":0},{"$f":"(GM68>0)*MAX(0,1.08*GP68*GO68*(GQ68-GV68)/1000)","v":0},0,0,0,0,0,{"$f":"IF(HH68=0,0,HC68/HH68)","v":0},null,0,0,0,{"$f":"HR$62","v":0},{"$f":"$I$101*HS$62","v":0},70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,{"$f":"(HK68>0)*OR($I68<$AI$106,$I68>$AI$107)*(4.45*HN68*HO68*(HY68-HV68)/1000+HT68/2*3.412)","v":0},{"$f":"(HL68>0)*(HX68<HU68)*(1.08*HO68*HN68*(HU68-HX68)/1000-HT68/2*3.412)","v":0},{"$f":"(HL68>0)*MAX(0,1.08*HO68*HN68*(HP68-HU68)/1000)","v":0},0,0,0,0,0,{"$f":"IF(IG68=0,0,IB68/IG68)","v":0},null,0,0,0,{"$f":"IQ$62","v":0},{"$f":"$I$101*IR$62","v":0},70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,{"$f":"(IJ68>0)*OR($I68<$AI$106,$I68>$AI$107)*(4.45*IM68*IN68*(IX68-IU68)/1000+IS68/2*3.412)","v":0},{"$f":"(IK68>0)*(IW68<IT68)*(1.08*IN68*IM68*(IT68-IW68)/1000-IS68/2*3.412)","v":0},{"$f":"(IK68>0)*MAX(0,1.08*IN68*IM68*(IO68-IT68)/1000)","v":0},0,0,0,0,0,{"$f":"IF(JF68=0,0,JA68/JF68)","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A46","v":90},{"$f":"'Project Info'!B46","v":95},{"$f":"'Project Info'!C46","v":92.016049160256074},{"$f":"'Project Info'!D46","v":72.911561930607689},{"$f":"'Project Info'!E46","v":36.467095439351091},{"$f":"'Project Info'!F46","v":0},{"$f":"'Project Info'!G46","v":0},{"$f":"'Project Info'!H46","v":0},{"$f":"'Project Info'!I46","v":0},{"$f":"'Project Info'!J46","v":0},{"$f":"'Project Info'!K46","v":0},{"$f":"'Project Info'!L46","v":0},0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A47","v":85},{"$f":"'Project Info'!B47","v":90},{"$f":"'Project Info'!C47","v":87.457811360655285},{"$f":"'Project Info'!D47","v":70.80538329449476},{"$f":"'Project Info'!E47","v":34.679413213566804},{"$f":"'Project Info'!F47","v":0},{"$f":"'Project Info'!G47","v":0},{"$f":"'Project Info'!H47","v":0},{"$f":"'Project Info'!I47","v":0},{"$f":"'Project Info'!J47","v":0},{"$f":"'Project Info'!K47","v":0},{"$f":"'Project Info'!L47","v":0},0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A48","v":80},{"$f":"'Project Info'!B48","v":85},{"$f":"'Project Info'!C48","v":82.136788830239965},{"$f":"'Project Info'!D48","v":67.872393622439333},{"$f":"'Project Info'!E48","v":32.296248223809314},{"$f":"'Project Info'!F48","v":0},{"$f":"'Project Info'!G48","v":0},{"$f":"'Project Info'!H48","v":0},{"$f":"'Project Info'!I48","v":0},{"$f":"'Project Info'!J48","v":0},{"$f":"'Project Info'!K48","v":0},{"$f":"'Project Info'!L48","v":0},0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A49","v":75},{"$f":"'Project Info'!B49","v":80},{"$f":"'Project Info'!C49","v":76.988400157585886},{"$f":"'Project Info'!D49","v":65.129261896908645},{"$f":"'Project Info'!E49","v":30.190476812806729},{"$f":"'Project Info'!F49","v":0},{"$f":"'Project Info'!G49","v":0},{"$f":"'Project Info'!H49","v":0},{"$f":"'Project Info'!I49","v":0},{"$f":"'Project Info'!J49","v":0},{"$f":"'Project Info'!K49","v":0},{"$f":"'Project Info'!L49","v":0},0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A50","v":70},{"$f":"'Project Info'!B50","v":75},{"$f":"'Project Info'!C50","v":72.457982050814195},{"$f":"'Project Info'!D50","v":63.604425012889301},{"$f":"'Project Info'!E50","v":29.088683095945193},{"$f":"'Project Info'!F50","v":0},{"$f":"'Project Info'!G50","v":0},{"$f":"'Project Info'!H50","v":0},{"$f":"'Project Info'!I50","v":0},{"$f":"'Project Info'!J50","v":0},{"$f":"'Project Info'!K50","v":0},{"$f":"'Project Info'!L50","v":0},0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A51","v":65},{"$f":"'Project Info'!B51","v":70},{"$f":"'Project Info'!C51","v":67.815831070966169},{"$f":"'Project Info'!D51","v":61.631331368130574},{"$f":"'Project Info'!E51","v":27.661514889731574},{"$f":"'Project Info'!F51","v":0},{"$f":"'Project Info'!G51","v":0},{"$f":"'Project Info'!H51","v":0},{"$f":"'Project Info'!I51","v":0},{"$f":"'Project Info'!J51","v":0},{"$f":"'Project Info'!K51","v":0},{"$f":"'Project Info'!L51","v":0},0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A52","v":60},{"$f":"'Project Info'!B52","v":65},{"$f":"'Project Info'!C52","v":62.535961472271332},{"$f":"'Project Info'!D52","v":57.135476922863582},{"$f":"'Project Info'!E52","v":24.623037157728302},{"$f":"'Project Info'!F52","v":0},{"$f":"'Project Info'!G52","v":0},{"$f":"'Project Info'!H52","v":0},{"$f":"'Project Info'!I52","v":0},{"$f":"'Project Info'!J52","v":0},{"$f":"'Project Info'!K52","v":0},{"$f":"'Project Info'!L52","v":0},0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A53","v":55},{"$f":"'Project Info'!B53","v":60},{"$f":"'Project Info'!C53","v":57.125792270740902},{"$f":"'Project Info'!D53","v":52.596971157053673},{"$f":"'Project Info'!E53","v":21.818001539159841},{"$f":"'Project Info'!F53","v":0},{"$f":"'Project Info'!G53","v":0},{"$f":"'Project Info'!H53","v":0},{"$f":"'Project Info'!I53","v":0},{"$f":"'Project Info'!J53","v":0},{"$f":"'Project Info'!K53","v":0},{"$f":"'Project Info'!L53","v":0},0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A54","v":50},{"$f":"'Project Info'!B54","v":55},{"$f":"'Project Info'!C54","v":52.235698854337961},{"$f":"'Project Info'!D54","v":48.022768090099298},{"$f":"'Project Info'!E54","v":19.246640192796217},{"$f":"'Project Info'!F54","v":0},{"$f":"'Project Info'!G54","v":0},{"$f":"'Project Info'!H54","v":0},{"$f":"'Project Info'!I54","v":0},{"$f":"'Project Info'!J54","v":0},{"$f":"'Project Info'!K54","v":0},{"$f":"'Project Info'!L54","v":0},0,4.2721017705686037E-2,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,4.2721017705686037E-2,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,4.2721017705686037E-2,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,4.2721017705686037E-2,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,4.2721017705686037E-2,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,4.2721017705686037E-2,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,4.2721017705686037E-2,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,4.2721017705686037E-2,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,4.2721017705686037E-2,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,4.2721017705686037E-2,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A55","v":45},{"$f":"'Project Info'!B55","v":50},{"$f":"'Project Info'!C55","v":47.459170258371508},{"$f":"'Project Info'!D55","v":43.465397050422162},{"$f":"'Project Info'!E55","v":16.894183241713304},{"$f":"'Project Info'!F55","v":0},{"$f":"'Project Info'!G55","v":0},{"$f":"'Project Info'!H55","v":0},{"$f":"'Project Info'!I55","v":0},{"$f":"'Project Info'!J55","v":0},{"$f":"'Project Info'!K55","v":0},{"$f":"'Project Info'!L55","v":0},0,0.11654009600698578,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.11654009600698578,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.11654009600698578,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.11654009600698578,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.11654009600698578,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.11654009600698578,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.11654009600698578,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.11654009600698578,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.11654009600698578,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.11654009600698578,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A56","v":40},{"$f":"'Project Info'!B56","v":45},{"$f":"'Project Info'!C56","v":42.677030404888129},{"$f":"'Project Info'!D56","v":38.812544504634097},{"$f":"'Project Info'!E56","v":14.690265649465921},{"$f":"'Project Info'!F56","v":0},{"$f":"'Project Info'!G56","v":0},{"$f":"'Project Info'!H56","v":0},{"$f":"'Project Info'!I56","v":0},{"$f":"'Project Info'!J56","v":0},{"$f":"'Project Info'!K56","v":0},{"$f":"'Project Info'!L56","v":0},0,0.19044589374263798,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.19044589374263798,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.19044589374263798,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.19044589374263798,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.19044589374263798,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.19044589374263798,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.19044589374263798,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.19044589374263798,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.19044589374263798,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.19044589374263798,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A57","v":35},{"$f":"'Project Info'!B57","v":40},{"$f":"'Project Info'!C57","v":37.333046773755832},{"$f":"'Project Info'!D57","v":33.904706919479686},{"$f":"'Project Info'!E57","v":12.53841602318813},{"$f":"'Project Info'!F57","v":0},{"$f":"'Project Info'!G57","v":0},{"$f":"'Project Info'!H57","v":0},{"$f":"'Project Info'!I57","v":0},{"$f":"'Project Info'!J57","v":0},{"$f":"'Project Info'!K57","v":0},{"$f":"'Project Info'!L57","v":0},0,0.27303473167831893,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.27303473167831893,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.27303473167831893,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.27303473167831893,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.27303473167831893,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.27303473167831893,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.27303473167831893,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.27303473167831893,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.27303473167831893,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.27303473167831893,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A58","v":30},{"$f":"'Project Info'!B58","v":35},{"$f":"'Project Info'!C58","v":32.638179845662044},{"$f":"'Project Info'!D58","v":29.547170928664851},{"$f":"'Project Info'!E58","v":10.728972818165861},{"$f":"'Project Info'!F58","v":0},{"$f":"'Project Info'!G58","v":0},{"$f":"'Project Info'!H58","v":0},{"$f":"'Project Info'!I58","v":0},{"$f":"'Project Info'!J58","v":0},{"$f":"'Project Info'!K58","v":0},{"$f":"'Project Info'!L58","v":0},0,0.34559176602158659,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.34559176602158659,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.34559176602158659,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.34559176602158659,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.34559176602158659,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.34559176602158659,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.34559176602158659,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.34559176602158659,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.34559176602158659,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.34559176602158659,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A59","v":25},{"$f":"'Project Info'!B59","v":30},{"$f":"'Project Info'!C59","v":27.529264646850947},{"$f":"'Project Info'!D59","v":24.652717392657845},{"$f":"'Project Info'!E59","v":8.8041305482613303},{"$f":"'Project Info'!F59","v":0},{"$f":"'Project Info'!G59","v":0},{"$f":"'Project Info'!H59","v":0},{"$f":"'Project Info'!I59","v":0},{"$f":"'Project Info'!J59","v":0},{"$f":"'Project Info'!K59","v":0},{"$f":"'Project Info'!L59","v":0},0,0.42454772818503078,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.42454772818503078,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.42454772818503078,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.42454772818503078,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.42454772818503078,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.42454772818503078,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.42454772818503078,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.42454772818503078,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.42454772818503078,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.42454772818503078,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A60","v":20},{"$f":"'Project Info'!B60","v":25},{"$f":"'Project Info'!C60","v":22.998111483544687},{"$f":"'Project Info'!D60","v":20.383306659827422},{"$f":"'Project Info'!E60","v":7.246164547543378},{"$f":"'Project Info'!F60","v":0},{"$f":"'Project Info'!G60","v":0},{"$f":"'Project Info'!H60","v":0},{"$f":"'Project Info'!I60","v":0},{"$f":"'Project Info'!J60","v":0},{"$f":"'Project Info'!K60","v":0},{"$f":"'Project Info'!L60","v":0},0,0.49457464070885476,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.49457464070885476,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.49457464070885476,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.49457464070885476,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.49457464070885476,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.49457464070885476,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.49457464070885476,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.49457464070885476,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.49457464070885476,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.49457464070885476,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A61","v":15},{"$f":"'Project Info'!B61","v":20},{"$f":"'Project Info'!C61","v":17.808510327474309},{"$f":"'Project Info'!D61","v":15.420865796304254},{"$f":"'Project Info'!E61","v":5.5490484131518292},{"$f":"'Project Info'!F61","v":0},{"$f":"'Project Info'!G61","v":0},{"$f":"'Project Info'!H61","v":0},{"$f":"'Project Info'!I61","v":0},{"$f":"'Project Info'!J61","v":0},{"$f":"'Project Info'!K61","v":0},{"$f":"'Project Info'!L61","v":0},0,0.57477756766630606,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.57477756766630606,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.57477756766630606,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.57477756766630606,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.57477756766630606,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.57477756766630606,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.57477756766630606,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.57477756766630606,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.57477756766630606,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.57477756766630606,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A62","v":10},{"$f":"'Project Info'!B62","v":15},{"$f":"'Project Info'!C62","v":12.269931130346862},{"$f":"'Project Info'!D62","v":10.318264913023604},{"$f":"'Project Info'!E62","v":3.9082824916941998},{"$f":"'Project Info'!F62","v":0},{"$f":"'Project Info'!G62","v":0},{"$f":"'Project Info'!H62","v":0},{"$f":"'Project Info'!I62","v":0},{"$f":"'Project Info'!J62","v":0},{"$f":"'Project Info'!K62","v":0},{"$f":"'Project Info'!L62","v":0},0,0.66037379162191201,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.66037379162191201,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.66037379162191201,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.66037379162191201,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.66037379162191201,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.66037379162191201,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.66037379162191201,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.66037379162191201,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.66037379162191201,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.66037379162191201,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A63","v":5},{"$f":"'Project Info'!B63","v":10},{"$f":"'Project Info'!C63","v":7.3137581369917548},{"$f":"'Project Info'!D63","v":5.7052382449247707},{"$f":"'Project Info'!E63","v":2.5019418419888937},{"$f":"'Project Info'!F63","v":0},{"$f":"'Project Info'!G63","v":0},{"$f":"'Project Info'!H63","v":0},{"$f":"'Project Info'!I63","v":0},{"$f":"'Project Info'!J63","v":0},{"$f":"'Project Info'!K63","v":0},{"$f":"'Project Info'!L63","v":0},0,0.73696919242830916,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.73696919242830916,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.73696919242830916,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.73696919242830916,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.73696919242830916,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.73696919242830916,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.73696919242830916,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.73696919242830916,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.73696919242830916,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.73696919242830916,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A64","v":0},{"$f":"'Project Info'!B64","v":5},{"$f":"'Project Info'!C64","v":2.6119461836144886},{"$f":"'Project Info'!D64","v":1.2699770062067783},{"$f":"'Project Info'!E64","v":1.2046477897733283},{"$f":"'Project Info'!F64","v":0},{"$f":"'Project Info'!G64","v":0},{"$f":"'Project Info'!H64","v":0},{"$f":"'Project Info'!I64","v":0},{"$f":"'Project Info'!J64","v":0},{"$f":"'Project Info'!K64","v":0},{"$f":"'Project Info'!L64","v":0},0,0.80963355898050327,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.80963355898050327,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.80963355898050327,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.80963355898050327,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.80963355898050327,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.80963355898050327,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.80963355898050327,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.80963355898050327,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.80963355898050327,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.80963355898050327,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,0,-12.336,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A65","v":-5},{"$f":"'Project Info'!B65","v":0},{"$f":"'Project Info'!C65","v":-1.6731398516793925},{"$f":"'Project Info'!D65","v":-2.7083318773557807},{"$f":"'Project Info'!E65","v":7.9391832815876459E-2},{"$f":"'Project Info'!F65","v":0},{"$f":"'Project Info'!G65","v":0},{"$f":"'Project Info'!H65","v":0},{"$f":"'Project Info'!I65","v":0},{"$f":"'Project Info'!J65","v":0},{"$f":"'Project Info'!K65","v":0},{"$f":"'Project Info'!L65","v":0},0,0.87585761588959044,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-1.6731398516793925,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.87585761588959044,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-1.6731398516793925,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.87585761588959044,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-1.6731398516793925,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.87585761588959044,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-1.6731398516793925,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.87585761588959044,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-1.6731398516793925,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.87585761588959044,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-1.6731398516793925,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.87585761588959044,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-1.6731398516793925,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.87585761588959044,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-1.6731398516793925,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.87585761588959044,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-1.6731398516793925,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.87585761588959044,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-1.6731398516793925,-12.336,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A66","v":-10},{"$f":"'Project Info'!B66","v":-5},{"$f":"'Project Info'!C66","v":-6.5729865085377277},{"$f":"'Project Info'!D66","v":-7.2465935998252222},{"$f":"'Project Info'!E66","v":-1.168423365310433},{"$f":"'Project Info'!F66","v":0},{"$f":"'Project Info'!G66","v":0},{"$f":"'Project Info'!H66","v":0},{"$f":"'Project Info'!I66","v":0},{"$f":"'Project Info'!J66","v":0},{"$f":"'Project Info'!K66","v":0},{"$f":"'Project Info'!L66","v":0},0,0.95158251876831024,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-6.5729865085377277,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.95158251876831024,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-6.5729865085377277,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.95158251876831024,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-6.5729865085377277,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.95158251876831024,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-6.5729865085377277,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.95158251876831024,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-6.5729865085377277,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.95158251876831024,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-6.5729865085377277,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.95158251876831024,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-6.5729865085377277,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.95158251876831024,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-6.5729865085377277,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.95158251876831024,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-6.5729865085377277,-12.336,0,0,0,0,0,0,0,0,0,null,0,0.95158251876831024,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-6.5729865085377277,-12.336,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A67","v":-15},{"$f":"'Project Info'!B67","v":-10},{"$f":"'Project Info'!C67","v":-15.32570353422995},{"$f":"'Project Info'!D67","v":-15.707838211108999},{"$f":"'Project Info'!E67","v":-3.4051318156661381},{"$f":"'Project Info'!F67","v":0},{"$f":"'Project Info'!G67","v":0},{"$f":"'Project Info'!H67","v":0},{"$f":"'Project Info'!I67","v":0},{"$f":"'Project Info'!J67","v":0},{"$f":"'Project Info'!K67","v":0},{"$f":"'Project Info'!L67","v":0},0,1,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-15.32570353422995,-12.336,0,0,0,0,0,0,0,0,0,null,0,1,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-15.32570353422995,-12.336,0,0,0,0,0,0,0,0,0,null,0,1,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-15.32570353422995,-12.336,0,0,0,0,0,0,0,0,0,null,0,1,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-15.32570353422995,-12.336,0,0,0,0,0,0,0,0,0,null,0,1,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-15.32570353422995,-12.336,0,0,0,0,0,0,0,0,0,null,0,1,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-15.32570353422995,-12.336,0,0,0,0,0,0,0,0,0,null,0,1,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-15.32570353422995,-12.336,0,0,0,0,0,0,0,0,0,null,0,1,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-15.32570353422995,-12.336,0,0,0,0,0,0,0,0,0,null,0,1,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-15.32570353422995,-12.336,0,0,0,0,0,0,0,0,0,null,0,1,0,0,0,70,25.099807999999999,0,0,0,0,-12.336,0,-15.32570353422995,-12.336,0,0,0,0,0,0,0,0,0]
[]
[null,null,null,null,null,null,null,null,null,"DAT Reset: OAT Range",null,"Min","Min","Max"]
[null,null,null,null,null,null,null,null,null,"Max OAT","Min OAT","Flow","DAT","DAT",null,null,null,null,"TOTAL FROM ALL SYSTEMS",null,null,null,null,null,null,"Cooling Load Profiles"]
[null,null,null,null,null,null,"System Type Options",null,null,"°F","°F","Ratio %","°F","°F",null,null,null,null,"End Use",null,null,null,"Total","Total",null,null,null,null,"Occupied Profile"]
[null,null,null,null,null,null,"1-Mixed Air w/ VAV Terminal Units",null,null,{"$f":"'Energy Recovery'!J100","v":85},{"$f":"'Energy Recovery'!K100","v":55},{"$f":"'Energy Recovery'!L100","v":0.5},{"$f":"'Energy Recovery'!M100","v":55},{"$f":"'Energy Recovery'!N100","v":60},null,null,null,null,"Demand Reduction",null,null,null,"Demand","Demand",null,null,null,null,"Max OAT","Min OAT","% Load @","%Load @"]
[null,null,null,null,null,null,"2-Mix Air Constant Volume",null,null,{"$f":"'Energy Recovery'!J101","v":85},{"$f":"'Energy Recovery'!K101","v":15},{"$f":"'Energy Recovery'!L101","v":1},{"$f":"'Energy Recovery'!M101","v":55},{"$f":"'Energy Recovery'!N101","v":95},null,null,null,null,"Cooling","Heating","Heating","Fans","Reduction","Reduction",null,null,null,null,"°F","°F","Max OAT","Min OAT"]
[null,null,null,null,null,null,"3-100% OA w/ VAV Terminal Units",null,null,{"$f":"'Energy Recovery'!J102","v":85},{"$f":"'Energy Recovery'!K102","v":55},1,{"$f":"'Energy Recovery'!M102","v":55},{"$f":"'Energy Recovery'!N102","v":68},null,null,null,null,"kW","MBH","kW","kW","kW","MBH",null,null,null,null,{"$f":"'Energy Recovery'!AC102","v":95},{"$f":"'Energy Recovery'!AD102","v":55},{"$f":"'Energy Recovery'!AE102","v":0.85},{"$f":"'Energy Recovery'!AF102","v":0}]
[null,null,null,null,null,null,"4-100% OA - Constant Volume",null,null,{"$f":"'Energy Recovery'!J103","v":85},{"$f":"'Energy Recovery'!K103","v":55},{"$f":"'Energy Recovery'!L103","v":1},{"$f":"'Energy Recovery'!M103","v":55},{"$f":"'Energy Recovery'!N103","v":68},null,null,null,null,{"$f":"AL67+BK67+CJ67+DI67+EH67+FG67+GF67+HE67+ID67+JC67","v":0},{"$f":"AN67*($AK$62=$U$34)+AP67*($AN$62=$U$34)+BM67*($BJ$62=$U$34)+BO67*($BM$62=$U$34)+CL67*($CI$62=$U$34)+CN67*($CL$62=$U$34)+DK67*($DH$62=$U$34)+DM67*($DK$62=$U$34)+EJ67*($EG$62=$U$34)+EL67*($EJ$62=$U$34)+FI67*($FF$62=$U$34)+FK67*($FI$62=$U$34)+GH67*($GE$62=$U$34)+GJ67*($GH$62=$U$34)+HG67*($HD$62=$U$34)+HI67*($HG$62=$U$34)+IF67*($IC$62=$U$34)+IH67*($IF$62=$U$34)+JE67*($JB$62=$U$34)+JG67*($JE$62=$U$34)","v":0},{"$f":"(AN67*($AK$62=$U$33)+AP67*($AN$62=$U$33)+BM67*($BJ$62=$U$33)+BO67*($BM$62=$U$33)+CL67*($CI$62=$U$33)+CN67*($CL$62=$U$33)+DK67*($DH$62=$U$33)+DM67*($DK$62=$U$33)+EJ67*($EG$62=$U$33)+EL67*($EJ$62=$U$33)+FI67*($FF$62=$U$33)+FK67*($FI$62=$U$33)+GH67*($GE$62=$U$33)+GJ67*($GH$62=$U$33)+HG67*($HD$62=$U$33)+HI67*($HG$62=$U$33)+IF67*($IC$62=$U$33)+IH67*($IF$62=$U$33)+JE67*($JB$62=$U$33)+JG67*($JE$62=$U$33))/3.412","v":0},{"$f":"AB67+BA67+BZ67+CY67+DX67+EW67+FV67+GU67+HT67+IS67","v":0},{"$f":"S98+U98+V98","v":0},{"$f":"T98","v":0},null,"Heating Load Profiles"]
[null,null,null,null,null,null,"5-Other",null,null,{"$f":"'Energy Recovery'!J104","v":85},{"$f":"'Energy Recovery'!K104","v":55},{"$f":"'Energy Recovery'!L104","v":0.5},{"$f":"'Energy Recovery'!M104","v":55},{"$f":"'Energy Recovery'!N104","v":60},null,null,null,null,{"$f":"AL68+BK68+CJ68+DI68+EH68+FG68+GF68+HE68+ID68+JC68","v":0},0,{"$f":"(AN68*($AK$62=$U$33)+AP68*($AN$62=$U$33)+BM68*($BJ$62=$U$33)+BO68*($BM$62=$U$33)+CL68*($CI$62=$U$33)+CN68*($CL$62=$U$33)+DK68*($DH$62=$U$33)+DM68*($DK$62=$U$33)+EJ68*($EG$62=$U$33)+EL68*($EJ$62=$U$33)+FI68*($FF$62=$U$33)+FK68*($FI$62=$U$33)+GH68*($GE$62=$U$33)+GJ68*($GH$62=$U$33)+HG68*($HD$62=$U$33)+HI68*($HG$62=$U$33)+IF68*($IC$62=$U$33)+IH68*($IF$62=$U$33)+JE68*($JB$62=$U$33)+JG68*($JE$62=$U$33))/3.412","v":0},{"$f":"AB68+BA68+BZ68+CY68+DX68+EW68+FV68+GU68+HT68+IS68","v":0},{"$f":"S99+U99+V99","v":0},{"$f":"T99","v":0},null,null,null,null,"Occupied Profile"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,null,null,null,"Max OAT","Min OAT","% Load @","%Load @",null,"°F Db to Sat. Btu/lb"]
[null,null,null,null,null,null,"AVG OA Reduction with DCV",null,0.25,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,null,null,null,"°F","°F","Max OAT","Min OAT",null,"Conversion"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,null,null,null,{"$f":"'Energy Recovery'!AC107","v":55},{"$f":"'Energy Recovery'!AD107","v":0},{"$f":"'Energy Recovery'!AE107","v":0},{"$f":"'Energy Recovery'!AF107","v":0.85},null,"constant",-12.336]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,null,null,null,null,null,null,null,null,"x-term",0.64859999999999995]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,"AHU Discharge Air Temperature Reset Profiles"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,"System",null,null,"Occupied Profile",null,null,null,null,"Economizer Range"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,"Type","Description",null,"Max OAT","Min OAT","DAT @","DAT @",null,"Min °Fdb",55]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,"#",null,null,"°F","°F","Max OAT","Min OAT",null,"Max °F db",70]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,1,{"$f":"$U$62","v":0},null,{"$f":"IF(AA108=0,0,LOOKUP(AA108,$G$95:$G$99,$J$95:$J$99))","v":0},{"$f":"IF(AA108=0,0,LOOKUP(AA108,$G$95:$G$99,$K$95:$K$99))","v":0},{"$f":"IF(AA108=0,0,LOOKUP(AA108,$G$95:$G$99,$M$95:$M$99))","v":0},{"$f":"IF(AA108=0,0,LOOKUP(AA108,$G$95:$G$99,$N$95:$N$99))","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,2,{"$f":"$AT$62","v":0},null,0,0,{"$f":"IF(AA109=0,0,LOOKUP(AA109,$G$95:$G$99,$M$95:$M$99))","v":0},{"$f":"IF(AA109=0,0,LOOKUP(AA109,$G$95:$G$99,$N$95:$N$99))","v":0},null,"ERV Fan Penalty"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,3,{"$f":"$BS$62","v":0},null,0,0,0,0,null,"Added SP with ERV",null,1.2,"in. w.c."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,4,{"$f":"$CR$62","v":0},null,0,0,0,0,null,"Avg. Motor Eff",null,0.92]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,5,{"$f":"$DQ$62","v":0},null,0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,6,{"$f":"$EP$62","v":0},null,0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,7,{"$f":"$FO$62","v":0},null,0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,8,{"$f":"$GN$62","v":0},null,0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,9,{"$f":"$HM$62","v":0},null,0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,10,{"$f":"$IL$62","v":0},null,0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,"AHU Airflow Profiles"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0,null,"System",null,null,"Occupied Profile"]
[null,null,null,null,null,null,null,"Return Air Conditions",null,null,null,null,"NEMA Premium",null,null,null,null,null,0,0,{"$f":"(AN90*($AK$62=$U$33)+AP90*($AN$62=$U$33)+BM90*($BJ$62=$U$33)+BO90*($BM$62=$U$33)+CL90*($CI$62=$U$33)+CN90*($CL$62=$U$33)+DK90*($DH$62=$U$33)+DM90*($DK$62=$U$33)+EJ90*($EG$62=$U$33)+EL90*($EJ$62=$U$33)+FI90*($FF$62=$U$33)+FK90*($FI$62=$U$33)+GH90*($GE$62=$U$33)+GJ90*($GH$62=$U$33)+HG90*($HD$62=$U$33)+HI90*($HG$62=$U$33)+IF90*($IC$62=$U$33)+IH90*($IF$62=$U$33)+JE90*($JB$62=$U$33)+JG90*($JE$62=$U$33))/3.412","v":0},0,0,0,null,"Type","Description",null,"Max Cool","Min Cool","%Flow @","%Flow @"]
[null,null,null,null,null,null,null,null,null,"Cooling","Heating",null,"Motor Efficiency",null,null,null,null,null,null,null,null,null,null,null,null,"#",null,null,"%","%","Max","Min"]
[null,null,null,null,null,null,null,"Temp db (°F)",null,75,70,null,null,"1800 rpm",null,null,null,null,null,null,null,null,null,null,null,1,{"$f":"$U$62","v":0},null,{"$f":"'Energy Recovery'!AC128","v":1},{"$f":"'Energy Recovery'!AD128","v":0.05},{"$f":"'Energy Recovery'!AE128","v":1},{"$f":"IF(AA123=0,0,LOOKUP(AA123,$G$95:$G$99,$L$95:$L$99))","v":0}]
[null,null,null,null,null,null,null,"%RH",null,0.5,0.4,null,"HP","Eff",null,null,null,null,null,null,null,null,null,null,null,2,{"$f":"$AT$62","v":0},null,{"$f":"'Energy Recovery'!AC129","v":1},{"$f":"'Energy Recovery'!AD129","v":0.05},{"$f":"'Energy Recovery'!AE129","v":1},{"$f":"IF(AA124=0,0,LOOKUP(AA124,$G$95:$G$99,$L$95:$L$99))","v":0}]
[null,null,null,null,null,null,null,"RH (lb/lb)",null,{"$f":"FORECAST($J$124,OFFSET($V$152:$V$160,MATCH($J$124,$M$152:$M$160,1)-1,0,2),OFFSET($M$152:$M$160,MATCH($J$124,$M$152:$M$160,1)-1,0,2))","v":9.5499999999999977E-3},{"$f":"FORECAST($K$124,OFFSET($V$152:$V$160,MATCH($K$124,$M$152:$M$160,1)-1,0,2),OFFSET($M$152:$M$160,MATCH($K$124,$M$152:$M$160,1)-1,0,2))","v":7.5999999999999991E-3},null,0,0.6,null,null,null,null,null,null,null,null,null,null,null,3,{"$f":"$BS$62","v":0},null,{"$f":"'Energy Recovery'!AC130","v":1},{"$f":"'Energy Recovery'!AD130","v":0.05},{"$f":"'Energy Recovery'!AE130","v":1},0]
[null,null,null,null,null,null,null,"Enthalpy (Btu/lb)",null,{"$f":"(0.24*J123)+(J125*(1061+0.444*J123))","v":28.450564999999997},{"$f":"(0.24*K123)+(K125*(1061+0.444*K123))","v":25.099807999999999},null,0.5,0.85,null,null,null,null,null,null,null,null,null,null,null,4,{"$f":"$CR$62","v":0},null,{"$f":"'Energy Recovery'!AC131","v":1},{"$f":"'Energy Recovery'!AD131","v":0.05},{"$f":"'Energy Recovery'!AE131","v":1},0]
[null,null,null,null,null,null,null,null,null,null,null,null,1,0.85499999999999998,null,null,null,null,null,null,null,null,null,null,null,5,{"$f":"$DQ$62","v":0},null,{"$f":"'Energy Recovery'!AC132","v":1},{"$f":"'Energy Recovery'!AD132","v":0.05},{"$f":"'Energy Recovery'!AE132","v":1},0]
[null,null,null,null,null,null,null,null,null,"Motor %of FL Eff vs %BHP",null,null,1.5,0.86499999999999999,null,null,null,null,null,null,null,null,null,null,null,6,{"$f":"$EP$62","v":0},null,{"$f":"'Energy Recovery'!AC133","v":1},{"$f":"'Energy Recovery'!AD133","v":0.05},{"$f":"'Energy Recovery'!AE133","v":1},0]
[null,null,null,null,null,null,null,null,null,"% BHP","% of FL Eff",null,2,0.86499999999999999,null,null,null,null,null,null,null,null,null,null,null,7,{"$f":"$FO$62","v":0},null,{"$f":"'Energy Recovery'!AC134","v":1},{"$f":"'Energy Recovery'!AD134","v":0.05},{"$f":"'Energy Recovery'!AE134","v":1},0]
[null,null,null,null,null,null,null,null,null,0,0.05,null,3,0.89500000000000002,null,null,null,null,null,null,null,null,null,null,null,8,{"$f":"$GN$62","v":0},null,{"$f":"'Energy Recovery'!AC135","v":1},{"$f":"'Energy Recovery'!AD135","v":0.05},{"$f":"'Energy Recovery'!AE135","v":1},0]
[null,null,null,null,null,null,null,null,null,0.1,0.4,null,5,0.89500000000000002,null,null,null,null,null,null,null,null,null,null,null,9,{"$f":"$HM$62","v":0},null,{"$f":"'Energy Recovery'!AC136","v":1},{"$f":"'Energy Recovery'!AD136","v":0.05},{"$f":"'Energy Recovery'!AE136","v":1},0]
[null,null,null,null,null,null,null,null,null,0.2,0.6,null,7.5,0.91,null,null,null,null,null,null,null,null,null,null,null,10,{"$f":"$IL$62","v":0},null,{"$f":"'Energy Recovery'!AC137","v":1},{"$f":"'Energy Recovery'!AD137","v":0.05},{"$f":"'Energy Recovery'!AE137","v":1},0]
[null,null,null,null,null,null,null,null,null,0.4,0.92,null,10,0.91700000000000004,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Incremental Cost Estimates"]
[null,null,null,null,null,null,null,null,null,0.6,0.98,null,15,0.93,null,null,null,null,null,null,null,null,null,null,null,null,"Part Load Cooling Performance Assumptions",null,null,null,null,null,null,null,"Design",null,"Increm-"]
[null,null,null,null,null,null,null,null,null,0.8,1,null,20,0.93,null,null,null,null,null,null,null,null,null,null,null,"Line",0.01,0.42,0.45,0.12,null,"SEER/",null,"Line","Min OA",null,"ental"]
[null,null,null,null,null,null,null,null,null,1,1,null,25,0.93599999999999994,null,null,null,null,null,null,null,null,null,null,null,"#",1,0.75,0.5,0.25,-0.01,"IEER",null,"#","CFM",null,"Cost"]
[null,null,null,null,null,null,null,null,null,1.1000000000000001,0.97,null,30,0.94099999999999995,null,null,null,null,null,null,null,null,null,null,null,1,{"$f":"S22","v":0},{"$f":"IF(AA137=0,0,($AF137/$AA137)*AB$148*$AA137)","v":0},0,0,{"$f":"AD137/2","v":0},{"$f":"T22","v":0},null,1,{"$f":"M22","v":0},null,{"$f":"AI137*$AH$149","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,40,0.94099999999999995,null,null,null,null,null,null,null,null,null,null,null,2,0,0,0,0,{"$f":"AD138/2","v":0},0,null,2,0,null,0]
[null,null,null,null,null,null,null,null,null,"SP Control Ratio",0.3,null,50,0.94499999999999995,null,null,null,null,null,null,null,null,null,null,null,3,0,0,0,0,0,0,null,3,0,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,60,0.95,null,null,null,null,null,null,null,null,null,null,null,4,0,0,0,0,0,0,null,4,0,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,75,0.95,null,null,null,null,null,null,null,null,null,null,null,5,0,0,0,0,0,0,null,5,0,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,100,0.95400000000000007,null,null,null,null,null,null,null,null,null,null,null,6,0,0,0,0,0,0,null,6,0,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,125,0.95400000000000007,null,null,null,null,null,null,null,null,null,null,null,7,0,0,0,0,0,0,null,7,0,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,150,0.95799999999999996,null,null,null,null,null,null,null,null,null,null,null,8,0,0,0,0,0,0,null,8,0,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,200,0.95799999999999996,null,null,null,null,null,null,null,null,null,null,null,9,0,0,0,0,0,0,null,9,0,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,0,0,0,0,0,0,null,10,0,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"TOTAL INCREMENTAL COST",null,null,{"$f":"SUM(AK137:AK146)","v":0}]
[null,null,null,null,null,null,null,null,"Return Air Relative Humidity and Enthalpy Calcs",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"PL EER Factors",null,0.95312499999999978,1.0312499999999998,1.0625]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.75,0.5,0.25,null,null,null,2,"Incremental Cost/CFM OA"]
[null,null,null,null,null,null,null,null,null,null,null,null,"RH","Deg F"]
[null,null,null,null,null,null,null,null,"RA Temperature",75," Deg F",null,null,30,40,50,60,70,80,90,100,"Check"]
[null,null,null,null,null,null,null,null,"RA Humidity Ratio",0.6,"%",null,0.1,4.0000000000000002E-4,5.9999999999999995E-4,8.9999999999999998E-4,1.1000000000000001E-3,1.6000000000000001E-3,2.3E-3,3.0000000000000001E-3,4.1000000000000003E-3,{"$f":"FORECAST($J$151,OFFSET(N152:U152,0,MATCH($J$151,$N$151:$U$151,1)-1,1,2),OFFSET($N$151:$U$151,0,MATCH($J$151,$N$151:$U$151,1)-1,1,2))","v":1.9499999999999999E-3}]
[null,null,null,null,null,null,null,null,"Relat. Humidity",{"$f":"FORECAST($J$124,OFFSET($V$152:$V$160,MATCH($J$124,$M$152:$M$160,1)-1,0,2),OFFSET($M$152:$M$160,MATCH($J$124,$M$152:$M$160,1)-1,0,2))","v":9.5499999999999977E-3},"lb/lb",null,0.2,6.9999999999999999E-4,1E-3,1.4E-3,2.3E-3,3.0000000000000001E-3,4.3E-3,6.0000000000000001E-3,8.3000000000000001E-3,3.6500000000000005E-3]
[null,null,null,null,null,null,null,null,"Retun Air Enthalpy",{"$f":"(0.24*J123)+(J125*(1061+0.444*J123))","v":28.450564999999997},"Btu/lb",null,0.3,1E-3,1.6000000000000001E-3,2E-3,3.0999999999999999E-3,4.8999999999999998E-3,6.6E-3,9.2999999999999992E-3,1.24E-2,5.7499999999999999E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,0.4,1.2999999999999999E-3,2E-3,2.8999999999999998E-3,4.3E-3,6.3E-3,8.8999999999999999E-3,1.2200000000000001E-2,1.66E-2,7.5999999999999991E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,0.5,1.6999999999999999E-3,2.5999999999999999E-3,3.7000000000000002E-3,5.5999999999999999E-3,7.9000000000000008E-3,1.12E-2,1.54E-2,2.1000000000000001E-2,9.5499999999999995E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,0.6,2E-3,3.0999999999999999E-3,4.5999999999999999E-3,6.8999999999999999E-3,9.4000000000000004E-3,1.32E-2,1.83E-2,2.52E-2,1.1300000000000001E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,0.7,2.3999999999999998E-3,3.7000000000000002E-3,5.4000000000000003E-3,7.7000000000000002E-3,1.12E-2,1.54E-2,2.1700000000000001E-2,2.9700000000000001E-2,1.3299999999999999E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,0.8,2.7000000000000001E-3,4.1000000000000003E-3,6.0000000000000001E-3,8.8999999999999999E-3,1.26E-2,1.7899999999999999E-2,2.47E-2,"-",1.525E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,0.9,3.0000000000000001E-3,4.7000000000000002E-3,6.8999999999999999E-3,0.01,1.43E-2,0.02,2.7199999999999998E-2,"-",1.7149999999999999E-2]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,"Source:","http://www.engineeringtoolbox.com/water-vapor-air-d_854.html"]

{"sheet":"Variable Flow Kitchen Hood","index":16,"n_rows":132,"n_cols":48,"rows_kept":132,"cut":false,"hidden":true,"merged":[[1,19,11,27],[1,10,4,17]]}
["Savings Summary",null,null,null,null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,null,null,"Notes (Optional)"]
["Annual kWh Savings",null,null,{"$f":"SUM(A14:D14)","v":{"$error":"#DIV/0!"}},null,null,null,"Value","Unit",null,"This measure considers savings from installing a variable flow kitchen hood control system to modulate hood exhaust and make-up air in response to cooking activity.  This control is generally required by energy code for hood systems with 5,000 CFM or more, but it is not required when total hood exhaust flow is less than 5,000 CFM."]
["% On Peak",null,null,{"$f":"IF(D2<=0,0,MIN(1,A15+C15))","v":{"$error":"#DIV/0!"}},null,"Annual Electric Savings",null,{"$f":"D2","v":{"$error":"#DIV/0!"}},"kWh"]
["Max kW",null,null,{"$f":"MAX(AU45:AU68)","v":0},null,"Annual Fuel Savings",null,{"$f":"D7*C28","v":{"$error":"#DIV/0!"}},{"$f":"D20","v":{"$error":"#N/A"}}]
["Summer kW",null,null,{"$f":"SUMPRODUCT(R45:R68,AU45:AU68)/SUM(R45:R68)","v":{"$error":"#DIV/0!"}},null,"Incremental","Default Calc",{"$f":"$V$130","v":0},"$"]
["Winter kW",null,null,{"$f":"SUMPRODUCT(Q45:Q68,AU45:AU68)/SUM(Q45:Q68)","v":{"$error":"#DIV/0!"}},null,"Cost","Project Specific",null,"$ (Optional)"]
["Annual Fuel Savings (MMBtu)",null,null,{"$f":"(SUMPRODUCT($L$45:$L$68,$S$45:$S$68,$AV$45:$AV$68))/1000","v":{"$error":"#DIV/0!"}},null,"Estimated Incentive",null,{"$f":"IF(AND($C$24>=0,$C$25>=0),MAX(0,H3)*C24+MAX(0,H4)*C25,\"TBD\")","v":{"$error":"#DIV/0!"}},"$"]
["Incremental Cost (Default Calc)",null,null,{"$f":"$V$130","v":0}]
["Incremental Cost (for Summary)",null,null,{"$f":"IF(H6>0,H6,D8)","v":0},null,"Project Information Summary"]
["kWh Savings by Peak Period",null,null,null,null,null,"STATE",{"$f":"'Project Info'!C15","v":"NH"}]
["Winter","Winter","Summer","Summer",null,null,"Program Year",{"$f":"'Project Info'!C19","v":0}]
["On-Peak","Off-Peak","On-Peak","Off-Peak",null,null,"Code IECC Version",{"$f":"MID('Project Info'!C20,1,4)","v":"2018"}]
["kWh","kWh","kWh","kWh",null,null,"Electric PA",{"$f":"'Project Info'!F3","v":0}]
[{"$f":"SUMPRODUCT($AU$45:$AU$68,M45:M68,$S$45:$S$68)","v":{"$error":"#DIV/0!"}},{"$f":"SUMPRODUCT($AU$45:$AU$68,N45:N68,$S$45:$S$68)","v":{"$error":"#DIV/0!"}},{"$f":"SUMPRODUCT($AU$45:$AU$68,O45:O68,$S$45:$S$68)","v":{"$error":"#DIV/0!"}},{"$f":"SUMPRODUCT($AU$45:$AU$68,P45:P68,$S$45:$S$68)","v":{"$error":"#DIV/0!"}},null,null,"Gas PA",{"$f":"'Project Info'!I3","v":0}]
[{"$f":"ROUND(IF(A14<=0,0,A14/SUMIF($A$14:$D$14,\">0\")),2)","v":{"$error":"#DIV/0!"}},{"$f":"ROUND(IF(B14<=0,0,B14/SUMIF($A$14:$D$14,\">0\")),2)","v":{"$error":"#DIV/0!"}},{"$f":"ROUND(IF(C14<=0,0,C14/SUMIF($A$14:$D$14,\">0\")),2)","v":{"$error":"#DIV/0!"}},{"$f":"IF(SUM(A14:D14)=0,0,1-SUM(A15:C15))","v":{"$error":"#DIV/0!"}},null,"*NOTE: Baseline values are automated and cannot be changed."]
[null,null,null,null,null,null,"Table 1: Exhaust and Make-Up Air Fan Parameters"]
["Utility Rates",null,null,null,null,null,null,null,null,"Fan Motor Nameplate HP",null,"Fan Motor BHP",null,null,"Proposed",null,"Total Kitchen Exhaust and Make-Up Air"]
[null,null,"Rate","Unit",null,null,null,null,"Airflow","Default","Or, User","Default","Or, User","Motor","VFD Burden",null,null,"Total","Total Fan","Total Fan","Avg. Fan","VFD Burden"]
["Electric",null,{"$f":"'ECM Summary'!$E$31","v":0.1593},"kWh",null,null,null,null,"CFM","Calc","Input","Calc","Input","Efficiency","kW",null,null,"CFM","Nameplate HP","BHP","Motor Eff","kW"]
[{"$f":"'ECM Summary'!$C$32","v":0},null,{"$f":"'ECM Summary'!$E$32","v":{"$error":"#N/A"}},{"$f":"'ECM Summary'!$F$32","v":{"$error":"#N/A"}},null,null,"EXHAUST HOOD FANS",null,null,null,null,null,null,null,null,null,"Hood Exhaust",{"$f":"SUM(I21:I23)","v":0},{"$f":"IF(K21=\"\",J21,K21)+IF(K22=\"\",J22,K22)+IF(K23=\"\",J23,K23)","v":0},{"$f":"IF(M21=\"\",L21,M21)+IF(M22=\"\",L22,M22)+IF(M23=\"\",L23,M23)","v":0},{"$f":"IF(R20=0,0,(IF(M21=\"\",L21,M21)*N21+IF(M22=\"\",L22,M22)*N22+IF(M23=\"\",L23,M23)*N23)/T20)","v":0},{"$f":"SUM(O21:O23)","v":0}]
[null,null,null,null,null,null,null,1,null,{"$f":"IF(I21=\"\",0,OFFSET($N$108,1+MATCH(IF(M21=\"\",L21,M21),$N$109:$N$129,1),0))","v":0},null,{"$f":"IF(K21=\"\",I21*$R$103,K21*0.85)","v":0},null,{"$f":"IF(I21=\"\",0,LOOKUP(IF(K21=\"\",J21,K21),$N$109:$N$129,$O$109:$O$129))","v":0},{"$f":"IF(K21=\"\",J21,K21)*0.03*0.746","v":0},null,"Make-Up Air",{"$f":"MIN(R20,SUM(I25:I27))","v":0},{"$f":"IF(K25=\"\",J25,K25)+IF(K26=\"\",J26,K26)+IF(K27=\"\",J27,K27)","v":0},{"$f":"IF(M25=\"\",L25,M25)+IF(M26=\"\",L26,M26)+IF(M27=\"\",L27,M27)","v":0},{"$f":"IF(R21=0,0,(IF(M25=\"\",L25,M25)*N25+IF(M26=\"\",L26,M26)*N26+IF(M27=\"\",L27,M27)*N27)/T21)","v":0},{"$f":"SUM(O25:O27)","v":0}]
["Custom Incentive Rates",null,null,null,null,null,null,2,null,{"$f":"IF(I22=\"\",0,OFFSET($N$108,1+MATCH(IF(M22=\"\",L22,M22),$N$109:$N$129,1),0))","v":0},null,{"$f":"IF(K22=\"\",I22*$R$103,K22*0.85)","v":0},null,{"$f":"IF(I22=\"\",0,LOOKUP(IF(K22=\"\",J22,K22),$N$109:$N$129,$O$109:$O$129))","v":0},{"$f":"IF(K22=\"\",J22,K22)*0.03*0.746","v":0},null,{"$f":"IF(R20>5000,\"System Not Eligible For Savings/Incentives\",\"\")","v":""}]
[null,null,"Rate","Unit",null,null,null,3,null,{"$f":"IF(I23=\"\",0,OFFSET($N$108,1+MATCH(IF(M23=\"\",L23,M23),$N$109:$N$129,1),0))","v":0},null,{"$f":"IF(K23=\"\",I23*$R$103,K23*0.85)","v":0},null,{"$f":"IF(I23=\"\",0,LOOKUP(IF(K23=\"\",J23,K23),$N$109:$N$129,$O$109:$O$129))","v":0},{"$f":"IF(K23=\"\",J23,K23)*0.03*0.746","v":0},null,{"$f":"IF(R20>5000,\"Variable Flow Control required for kitchens with total hood exhaust > 5,000 CFM\",\"\")","v":""}]
["Electric",null,{"$f":"'ECM Summary'!$J$31","v":0.28000000000000003},"kWh",null,null,"MAKE-UP AIR FANS"]
[{"$f":"'ECM Summary'!$H$32","v":0},null,{"$f":"'ECM Summary'!$J$32","v":0},{"$f":"'ECM Summary'!$K$32","v":{"$error":"#N/A"}},null,null,null,1,null,{"$f":"IF(I25=\"\",0,OFFSET($N$108,1+MATCH(IF(M25=\"\",L25,M25),$N$109:$N$129,1),0))","v":0},null,{"$f":"IF(K25=\"\",I25*$R$102,K25*0.85)","v":0},null,{"$f":"IF(I25=\"\",0,LOOKUP(IF(K25=\"\",J25,K25),$N$109:$N$129,$O$109:$O$129))","v":0},{"$f":"IF(K25=\"\",J25,K25)*0.03*0.746","v":0}]
[null,null,null,null,null,null,null,2,null,{"$f":"IF(I26=\"\",0,OFFSET($N$108,1+MATCH(IF(M26=\"\",L26,M26),$N$109:$N$129,1),0))","v":0},null,{"$f":"IF(K26=\"\",I26*$R$102,K26*0.85)","v":0},null,{"$f":"IF(I26=\"\",0,LOOKUP(IF(K26=\"\",J26,K26),$N$109:$N$129,$O$109:$O$129))","v":0},{"$f":"IF(K26=\"\",J26,K26)*0.03*0.746","v":0}]
["Fossil Fuel",null,{"$f":"'Project Info'!C21","v":0},null,null,null,null,3,null,{"$f":"IF(I27=\"\",0,OFFSET($N$108,1+MATCH(IF(M27=\"\",L27,M27),$N$109:$N$129,1),0))","v":0},null,{"$f":"IF(K27=\"\",I27*$R$102,K27*0.85)","v":0},null,{"$f":"IF(I27=\"\",0,LOOKUP(IF(K27=\"\",J27,K27),$N$109:$N$129,$O$109:$O$129))","v":0},{"$f":"IF(K27=\"\",J27,K27)*0.03*0.746","v":0}]
["Fuel Conversion",null,{"$f":"LOOKUP(C27,'Project Info'!X102:X104,'Project Info'!Z102:Z104)","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,"Table 2: Heating & Cooling Performance",null,null,null,"Table 3: Kitchen Hood Use Profile"]
[null,null,null,null,null,null,"Heating Fuel",null,null,null,null,"Breakfast","Lunch","Dinner","Late Night"]
[null,null,null,null,null,null,"Fossil Fuel Baseline Eff (%)",null,null,null,"Weekdays"]
[null,null,null,null,null,null,"Elec Heat Baseline COP",null,null,null,"Saturday"]
[null,null,null,null,null,null,"Cooling Included?",null,null,null,"Sunday"]
[null,null,null,null,null,null,"Cooling Baseline IEER or IPLV"]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,"Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown",null,null,null,null,null,null,null,"Baseline System Operation",null,null,null,null,null,null,null,null,null,null,null,"PROPOSED System Operation",null,null,null,null,null,null,null,null,null,null,null,"Elec Demand Savings",null,null,null,"Gas"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Hood/Bldg","Avg.","Motor","Exhaust","Make-Up","Exhaust","Make-Up","Make-Up","Cooling","Heating","Cooling","Heating","Heating","Avg.","Motor","Exhaust","Make-Up","Exhaust","Make-Up","Make-Up","Cooling","Heating","Cooling","Heating","Heating","Fan","Cooling","Heating","Total","Demand"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Hours","% Flow","BHP","Motor","Motor","Fan","Fan","Flow","Load","Load","Demand","Demand","Demand","% Flow","BHP","Motor","Motor","Fan","Fan","Flow","Load","Load","Demand","Demand","Demand","Savings","Savings","Savings","Savings","Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","Ratio","%","%","Eff %","Eff %","kW","kW","CFM","MBH","MBH","kW","kW","MBH","%","%","Eff %","Eff %","kW","kW","CFM","MBH","MBH","kW","kW","MBH","kW","kW","kW","kW","MBH"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A44","v":100},{"$f":"'Project Info'!B44","v":105},{"$f":"'Project Info'!C44","v":102},{"$f":"'Project Info'!D44","v":76},{"$f":"'Project Info'!E44","v":40},{"$f":"'Project Info'!F44","v":0},{"$f":"'Project Info'!G44","v":0},{"$f":"'Project Info'!H44","v":0},{"$f":"'Project Info'!I44","v":0},{"$f":"'Project Info'!J44","v":0},{"$f":"'Project Info'!K44","v":0},{"$f":"'Project Info'!L44","v":0},{"$f":"$K$126","v":{"$error":"#DIV/0!"}},{"$f":"IF($R$20<=5000,$L$125,AF45)","v":1},{"$f":"$S$124*T45+(1-$S$124)*T45^3","v":1},{"$f":"$U$20*TREND(OFFSET($Q$107,MATCH(U45,$Q$108:$Q$115,1),1,2,1),OFFSET($Q$107,MATCH(U45,$Q$108:$Q$115,1),0,2,1),U45)","v":0},{"$f":"$U$21*TREND(OFFSET($Q$107,MATCH(U45,$Q$108:$Q$115,1),1,2,1),OFFSET($Q$107,MATCH(U45,$Q$108:$Q$115,1),0,2,1),U45)","v":0},{"$f":"IF(V45=0,0,$T$20*U45*0.746/V45)","v":0},{"$f":"IF(W45=0,0,$T$21*U45*0.746/W45)","v":0},{"$f":"IF($R$21=0,$R$20,$R$21)*T45","v":0},{"$f":"($I$33=\"Yes\")*($I45>$S$123)*(MAX(0,4.45*Z45*($K45-$S$121)/1000+Y45*3.412))","v":0},{"$f":"($I45<$S$123)*(MAX(0,1.08*Z45*($R$120-$I45)/1000-Y45*3.412))","v":0},{"$f":"IF(AA45>0,AA45/$I$34,0)","v":0},{"$f":"IF($I$30=$J$102,AB45/$I$32/3.412,0)","v":0},{"$f":"IF($I$30=$J$101,AB45/$I$31,0)","v":0},{"$f":"$K$125","v":0},{"$f":"$S$124*AF45+(1-$S$124)*AF45^3","v":0},{"$f":"$U$20*TREND(OFFSET($Q$107,MATCH(AG45,$Q$108:$Q$115,1),1,2,1),OFFSET($Q$107,MATCH(AG45,$Q$108:$Q$115,1),0,2,1),AG45)","v":0},{"$f":"$U$21*TREND(OFFSET($Q$107,MATCH(AG45,$Q$108:$Q$115,1),1,2,1),OFFSET($Q$107,MATCH(AG45,$Q$108:$Q$115,1),0,2,1),AG45)","v":0},{"$f":"IF(AH45=0,0,$T$20*AG45*0.746/AH45)","v":0},{"$f":"IF(AI45=0,0,$T$21*AG45*0.746/AI45)","v":0},{"$f":"IF($R$21=0,$R$20,$R$21)*AF45","v":0},{"$f":"($I$33=\"Yes\")*($I45>$S$123)*(MAX(0,4.45*AL45*($K45-$S$121)/1000+AK45*3.412))","v":0},{"$f":"($I45<$S$123)*(MAX(0,1.08*AL45*($R$120-$I45)/1000-AK45*3.412))","v":0},{"$f":"IF(AM45>0,AM45/$I$34,0)","v":0},{"$f":"IF($I$30=$J$102,AN45/$I$32/3.412,0)","v":0},{"$f":"IF($I$30=$J$101,AN45/$I$31,0)","v":0},{"$f":"(X45+Y45)-(AJ45+AK45)","v":0},{"$f":"(AC45-AO45)","v":0},{"$f":"(AD45-AP45)","v":0},{"$f":"SUM(AR45:AT45)","v":0},{"$f":"(AE45-AQ45)","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A45","v":95},{"$f":"'Project Info'!B45","v":100},{"$f":"'Project Info'!C45","v":95.219272727272724},{"$f":"'Project Info'!D45","v":74.534025272781079},{"$f":"'Project Info'!E45","v":37.923296058061368},{"$f":"'Project Info'!F45","v":0},{"$f":"'Project Info'!G45","v":0},{"$f":"'Project Info'!H45","v":0},{"$f":"'Project Info'!I45","v":0},{"$f":"'Project Info'!J45","v":0},{"$f":"'Project Info'!K45","v":0},{"$f":"'Project Info'!L45","v":0},{"$error":"#DIV/0!"},1,1,{"$f":"$U$20*TREND(OFFSET($Q$107,MATCH(U46,$Q$108:$Q$115,1),1,2,1),OFFSET($Q$107,MATCH(U46,$Q$108:$Q$115,1),0,2,1),U46)","v":0},0,{"$f":"IF(V46=0,0,$T$20*U46*0.746/V46)","v":0},{"$f":"IF(W46=0,0,$T$21*U46*0.746/W46)","v":0},{"$f":"IF($R$21=0,$R$20,$R$21)*T46","v":0},0,0,0,0,0,{"$f":"$K$125","v":0},0,0,0,{"$f":"IF(AH46=0,0,$T$20*AG46*0.746/AH46)","v":0},{"$f":"IF(AI46=0,0,$T$21*AG46*0.746/AI46)","v":0},{"$f":"IF($R$21=0,$R$20,$R$21)*AF46","v":0},0,0,0,0,0,{"$f":"(X46+Y46)-(AJ46+AK46)","v":0},{"$f":"(AC46-AO46)","v":0},{"$f":"(AD46-AP46)","v":0},{"$f":"SUM(AR46:AT46)","v":0},{"$f":"(AE46-AQ46)","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A46","v":90},{"$f":"'Project Info'!B46","v":95},{"$f":"'Project Info'!C46","v":92.016049160256074},{"$f":"'Project Info'!D46","v":72.911561930607689},{"$f":"'Project Info'!E46","v":36.467095439351091},{"$f":"'Project Info'!F46","v":0},{"$f":"'Project Info'!G46","v":0},{"$f":"'Project Info'!H46","v":0},{"$f":"'Project Info'!I46","v":0},{"$f":"'Project Info'!J46","v":0},{"$f":"'Project Info'!K46","v":0},{"$f":"'Project Info'!L46","v":0},{"$error":"#DIV/0!"},1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A47","v":85},{"$f":"'Project Info'!B47","v":90},{"$f":"'Project Info'!C47","v":87.457811360655285},{"$f":"'Project Info'!D47","v":70.80538329449476},{"$f":"'Project Info'!E47","v":34.679413213566804},{"$f":"'Project Info'!F47","v":0},{"$f":"'Project Info'!G47","v":0},{"$f":"'Project Info'!H47","v":0},{"$f":"'Project Info'!I47","v":0},{"$f":"'Project Info'!J47","v":0},{"$f":"'Project Info'!K47","v":0},{"$f":"'Project Info'!L47","v":0},{"$error":"#DIV/0!"},1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A48","v":80},{"$f":"'Project Info'!B48","v":85},{"$f":"'Project Info'!C48","v":82.136788830239965},{"$f":"'Project Info'!D48","v":67.872393622439333},{"$f":"'Project Info'!E48","v":32.296248223809314},{"$f":"'Project Info'!F48","v":0},{"$f":"'Project Info'!G48","v":0},{"$f":"'Project Info'!H48","v":0},{"$f":"'Project Info'!I48","v":0},{"$f":"'Project Info'!J48","v":0},{"$f":"'Project Info'!K48","v":0},{"$f":"'Project Info'!L48","v":0},{"$error":"#DIV/0!"},1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A49","v":75},{"$f":"'Project Info'!B49","v":80},{"$f":"'Project Info'!C49","v":76.988400157585886},{"$f":"'Project Info'!D49","v":65.129261896908645},{"$f":"'Project Info'!E49","v":30.190476812806729},{"$f":"'Project Info'!F49","v":0},{"$f":"'Project Info'!G49","v":0},{"$f":"'Project Info'!H49","v":0},{"$f":"'Project Info'!I49","v":0},{"$f":"'Project Info'!J49","v":0},{"$f":"'Project Info'!K49","v":0},{"$f":"'Project Info'!L49","v":0},{"$error":"#DIV/0!"},1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A50","v":70},{"$f":"'Project Info'!B50","v":75},{"$f":"'Project Info'!C50","v":72.457982050814195},{"$f":"'Project Info'!D50","v":63.604425012889301},{"$f":"'Project Info'!E50","v":29.088683095945193},{"$f":"'Project Info'!F50","v":0},{"$f":"'Project Info'!G50","v":0},{"$f":"'Project Info'!H50","v":0},{"$f":"'Project Info'!I50","v":0},{"$f":"'Project Info'!J50","v":0},{"$f":"'Project Info'!K50","v":0},{"$f":"'Project Info'!L50","v":0},{"$error":"#DIV/0!"},1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A51","v":65},{"$f":"'Project Info'!B51","v":70},{"$f":"'Project Info'!C51","v":67.815831070966169},{"$f":"'Project Info'!D51","v":61.631331368130574},{"$f":"'Project Info'!E51","v":27.661514889731574},{"$f":"'Project Info'!F51","v":0},{"$f":"'Project Info'!G51","v":0},{"$f":"'Project Info'!H51","v":0},{"$f":"'Project Info'!I51","v":0},{"$f":"'Project Info'!J51","v":0},{"$f":"'Project Info'!K51","v":0},{"$f":"'Project Info'!L51","v":0},{"$error":"#DIV/0!"},1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A52","v":60},{"$f":"'Project Info'!B52","v":65},{"$f":"'Project Info'!C52","v":62.535961472271332},{"$f":"'Project Info'!D52","v":57.135476922863582},{"$f":"'Project Info'!E52","v":24.623037157728302},{"$f":"'Project Info'!F52","v":0},{"$f":"'Project Info'!G52","v":0},{"$f":"'Project Info'!H52","v":0},{"$f":"'Project Info'!I52","v":0},{"$f":"'Project Info'!J52","v":0},{"$f":"'Project Info'!K52","v":0},{"$f":"'Project Info'!L52","v":0},{"$error":"#DIV/0!"},1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A53","v":55},{"$f":"'Project Info'!B53","v":60},{"$f":"'Project Info'!C53","v":57.125792270740902},{"$f":"'Project Info'!D53","v":52.596971157053673},{"$f":"'Project Info'!E53","v":21.818001539159841},{"$f":"'Project Info'!F53","v":0},{"$f":"'Project Info'!G53","v":0},{"$f":"'Project Info'!H53","v":0},{"$f":"'Project Info'!I53","v":0},{"$f":"'Project Info'!J53","v":0},{"$f":"'Project Info'!K53","v":0},{"$f":"'Project Info'!L53","v":0},{"$error":"#DIV/0!"},1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A54","v":50},{"$f":"'Project Info'!B54","v":55},{"$f":"'Project Info'!C54","v":52.235698854337961},{"$f":"'Project Info'!D54","v":48.022768090099298},{"$f":"'Project Info'!E54","v":19.246640192796217},{"$f":"'Project Info'!F54","v":0},{"$f":"'Project Info'!G54","v":0},{"$f":"'Project Info'!H54","v":0},{"$f":"'Project Info'!I54","v":0},{"$f":"'Project Info'!J54","v":0},{"$f":"'Project Info'!K54","v":0},{"$f":"'Project Info'!L54","v":0},{"$error":"#DIV/0!"},1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A55","v":45},{"$f":"'Project Info'!B55","v":50},{"$f":"'Project Info'!C55","v":47.459170258371508},{"$f":"'Project Info'!D55","v":43.465397050422162},{"$f":"'Project Info'!E55","v":16.894183241713304},{"$f":"'Project Info'!F55","v":0},{"$f":"'Project Info'!G55","v":0},{"$f":"'Project Info'!H55","v":0},{"$f":"'Project Info'!I55","v":0},{"$f":"'Project Info'!J55","v":0},{"$f":"'Project Info'!K55","v":0},{"$f":"'Project Info'!L55","v":0},{"$error":"#DIV/0!"},1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A56","v":40},{"$f":"'Project Info'!B56","v":45},{"$f":"'Project Info'!C56","v":42.677030404888129},{"$f":"'Project Info'!D56","v":38.812544504634097},{"$f":"'Project Info'!E56","v":14.690265649465921},{"$f":"'Project Info'!F56","v":0},{"$f":"'Project Info'!G56","v":0},{"$f":"'Project Info'!H56","v":0},{"$f":"'Project Info'!I56","v":0},{"$f":"'Project Info'!J56","v":0},{"$f":"'Project Info'!K56","v":0},{"$f":"'Project Info'!L56","v":0},{"$error":"#DIV/0!"},1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A57","v":35},{"$f":"'Project Info'!B57","v":40},{"$f":"'Project Info'!C57","v":37.333046773755832},{"$f":"'Project Info'!D57","v":33.904706919479686},{"$f":"'Project Info'!E57","v":12.53841602318813},{"$f":"'Project Info'!F57","v":0},{"$f":"'Project Info'!G57","v":0},{"$f":"'Project Info'!H57","v":0},{"$f":"'Project Info'!I57","v":0},{"$f":"'Project Info'!J57","v":0},{"$f":"'Project Info'!K57","v":0},{"$f":"'Project Info'!L57","v":0},{"$error":"#DIV/0!"},1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A58","v":30},{"$f":"'Project Info'!B58","v":35},{"$f":"'Project Info'!C58","v":32.638179845662044},{"$f":"'Project Info'!D58","v":29.547170928664851},{"$f":"'Project Info'!E58","v":10.728972818165861},{"$f":"'Project Info'!F58","v":0},{"$f":"'Project Info'!G58","v":0},{"$f":"'Project Info'!H58","v":0},{"$f":"'Project Info'!I58","v":0},{"$f":"'Project Info'!J58","v":0},{"$f":"'Project Info'!K58","v":0},{"$f":"'Project Info'!L58","v":0},{"$error":"#DIV/0!"},1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A59","v":25},{"$f":"'Project Info'!B59","v":30},{"$f":"'Project Info'!C59","v":27.529264646850947},{"$f":"'Project Info'!D59","v":24.652717392657845},{"$f":"'Project Info'!E59","v":8.8041305482613303},{"$f":"'Project Info'!F59","v":0},{"$f":"'Project Info'!G59","v":0},{"$f":"'Project Info'!H59","v":0},{"$f":"'Project Info'!I59","v":0},{"$f":"'Project Info'!J59","v":0},{"$f":"'Project Info'!K59","v":0},{"$f":"'Project Info'!L59","v":0},{"$error":"#DIV/0!"},1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A60","v":20},{"$f":"'Project Info'!B60","v":25},{"$f":"'Project Info'!C60","v":22.998111483544687},{"$f":"'Project Info'!D60","v":20.383306659827422},{"$f":"'Project Info'!E60","v":7.246164547543378},{"$f":"'Project Info'!F60","v":0},{"$f":"'Project Info'!G60","v":0},{"$f":"'Project Info'!H60","v":0},{"$f":"'Project Info'!I60","v":0},{"$f":"'Project Info'!J60","v":0},{"$f":"'Project Info'!K60","v":0},{"$f":"'Project Info'!L60","v":0},{"$error":"#DIV/0!"},1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A61","v":15},{"$f":"'Project Info'!B61","v":20},{"$f":"'Project Info'!C61","v":17.808510327474309},{"$f":"'Project Info'!D61","v":15.420865796304254},{"$f":"'Project Info'!E61","v":5.5490484131518292},{"$f":"'Project Info'!F61","v":0},{"$f":"'Project Info'!G61","v":0},{"$f":"'Project Info'!H61","v":0},{"$f":"'Project Info'!I61","v":0},{"$f":"'Project Info'!J61","v":0},{"$f":"'Project Info'!K61","v":0},{"$f":"'Project Info'!L61","v":0},{"$error":"#DIV/0!"},1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A62","v":10},{"$f":"'Project Info'!B62","v":15},{"$f":"'Project Info'!C62","v":12.269931130346862},{"$f":"'Project Info'!D62","v":10.318264913023604},{"$f":"'Project Info'!E62","v":3.9082824916941998},{"$f":"'Project Info'!F62","v":0},{"$f":"'Project Info'!G62","v":0},{"$f":"'Project Info'!H62","v":0},{"$f":"'Project Info'!I62","v":0},{"$f":"'Project Info'!J62","v":0},{"$f":"'Project Info'!K62","v":0},{"$f":"'Project Info'!L62","v":0},{"$error":"#DIV/0!"},1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A63","v":5},{"$f":"'Project Info'!B63","v":10},{"$f":"'Project Info'!C63","v":7.3137581369917548},{"$f":"'Project Info'!D63","v":5.7052382449247707},{"$f":"'Project Info'!E63","v":2.5019418419888937},{"$f":"'Project Info'!F63","v":0},{"$f":"'Project Info'!G63","v":0},{"$f":"'Project Info'!H63","v":0},{"$f":"'Project Info'!I63","v":0},{"$f":"'Project Info'!J63","v":0},{"$f":"'Project Info'!K63","v":0},{"$f":"'Project Info'!L63","v":0},{"$error":"#DIV/0!"},1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A64","v":0},{"$f":"'Project Info'!B64","v":5},{"$f":"'Project Info'!C64","v":2.6119461836144886},{"$f":"'Project Info'!D64","v":1.2699770062067783},{"$f":"'Project Info'!E64","v":1.2046477897733283},{"$f":"'Project Info'!F64","v":0},{"$f":"'Project Info'!G64","v":0},{"$f":"'Project Info'!H64","v":0},{"$f":"'Project Info'!I64","v":0},{"$f":"'Project Info'!J64","v":0},{"$f":"'Project Info'!K64","v":0},{"$f":"'Project Info'!L64","v":0},{"$error":"#DIV/0!"},1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A65","v":-5},{"$f":"'Project Info'!B65","v":0},{"$f":"'Project Info'!C65","v":-1.6731398516793925},{"$f":"'Project Info'!D65","v":-2.7083318773557807},{"$f":"'Project Info'!E65","v":7.9391832815876459E-2},{"$f":"'Project Info'!F65","v":0},{"$f":"'Project Info'!G65","v":0},{"$f":"'Project Info'!H65","v":0},{"$f":"'Project Info'!I65","v":0},{"$f":"'Project Info'!J65","v":0},{"$f":"'Project Info'!K65","v":0},{"$f":"'Project Info'!L65","v":0},{"$error":"#DIV/0!"},1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A66","v":-10},{"$f":"'Project Info'!B66","v":-5},{"$f":"'Project Info'!C66","v":-6.5729865085377277},{"$f":"'Project Info'!D66","v":-7.2465935998252222},{"$f":"'Project Info'!E66","v":-1.168423365310433},{"$f":"'Project Info'!F66","v":0},{"$f":"'Project Info'!G66","v":0},{"$f":"'Project Info'!H66","v":0},{"$f":"'Project Info'!I66","v":0},{"$f":"'Project Info'!J66","v":0},{"$f":"'Project Info'!K66","v":0},{"$f":"'Project Info'!L66","v":0},{"$error":"#DIV/0!"},1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A67","v":-15},{"$f":"'Project Info'!B67","v":-10},{"$f":"'Project Info'!C67","v":-15.32570353422995},{"$f":"'Project Info'!D67","v":-15.707838211108999},{"$f":"'Project Info'!E67","v":-3.4051318156661381},{"$f":"'Project Info'!F67","v":0},{"$f":"'Project Info'!G67","v":0},{"$f":"'Project Info'!H67","v":0},{"$f":"'Project Info'!I67","v":0},{"$f":"'Project Info'!J67","v":0},{"$f":"'Project Info'!K67","v":0},{"$f":"'Project Info'!L67","v":0},{"$error":"#DIV/0!"},1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[]
[null,null,null,null,null,null,"Unoccupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A74","v":100},{"$f":"'Project Info'!B74","v":105},{"$f":"'Project Info'!C74","v":102},{"$f":"'Project Info'!D74","v":76},{"$f":"'Project Info'!E74","v":40},{"$f":"'Project Info'!F74","v":0},{"$f":"'Project Info'!G74","v":0},{"$f":"'Project Info'!H74","v":0},{"$f":"'Project Info'!I74","v":0},{"$f":"'Project Info'!J74","v":0},{"$f":"'Project Info'!K74","v":0},{"$f":"'Project Info'!L74","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A75","v":95},{"$f":"'Project Info'!B75","v":100},{"$f":"'Project Info'!C75","v":95.219272727272724},{"$f":"'Project Info'!D75","v":74.534025272781079},{"$f":"'Project Info'!E75","v":37.923296058061368},{"$f":"'Project Info'!F75","v":0},{"$f":"'Project Info'!G75","v":0},{"$f":"'Project Info'!H75","v":0},{"$f":"'Project Info'!I75","v":0},{"$f":"'Project Info'!J75","v":0},{"$f":"'Project Info'!K75","v":0},{"$f":"'Project Info'!L75","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A76","v":90},{"$f":"'Project Info'!B76","v":95},{"$f":"'Project Info'!C76","v":92.016049160256074},{"$f":"'Project Info'!D76","v":72.911561930607689},{"$f":"'Project Info'!E76","v":36.467095439351091},{"$f":"'Project Info'!F76","v":0},{"$f":"'Project Info'!G76","v":0},{"$f":"'Project Info'!H76","v":0},{"$f":"'Project Info'!I76","v":0},{"$f":"'Project Info'!J76","v":0},{"$f":"'Project Info'!K76","v":0},{"$f":"'Project Info'!L76","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A77","v":85},{"$f":"'Project Info'!B77","v":90},{"$f":"'Project Info'!C77","v":87.457811360655285},{"$f":"'Project Info'!D77","v":70.80538329449476},{"$f":"'Project Info'!E77","v":34.679413213566804},{"$f":"'Project Info'!F77","v":0},{"$f":"'Project Info'!G77","v":0},{"$f":"'Project Info'!H77","v":0},{"$f":"'Project Info'!I77","v":0},{"$f":"'Project Info'!J77","v":0},{"$f":"'Project Info'!K77","v":0},{"$f":"'Project Info'!L77","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A78","v":80},{"$f":"'Project Info'!B78","v":85},{"$f":"'Project Info'!C78","v":82.136788830239965},{"$f":"'Project Info'!D78","v":67.872393622439333},{"$f":"'Project Info'!E78","v":32.296248223809314},{"$f":"'Project Info'!F78","v":0},{"$f":"'Project Info'!G78","v":0},{"$f":"'Project Info'!H78","v":0},{"$f":"'Project Info'!I78","v":0},{"$f":"'Project Info'!J78","v":0},{"$f":"'Project Info'!K78","v":0},{"$f":"'Project Info'!L78","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A79","v":75},{"$f":"'Project Info'!B79","v":80},{"$f":"'Project Info'!C79","v":76.988400157585886},{"$f":"'Project Info'!D79","v":65.129261896908645},{"$f":"'Project Info'!E79","v":30.190476812806729},{"$f":"'Project Info'!F79","v":0},{"$f":"'Project Info'!G79","v":0},{"$f":"'Project Info'!H79","v":0},{"$f":"'Project Info'!I79","v":0},{"$f":"'Project Info'!J79","v":0},{"$f":"'Project Info'!K79","v":0},{"$f":"'Project Info'!L79","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A80","v":70},{"$f":"'Project Info'!B80","v":75},{"$f":"'Project Info'!C80","v":72.457982050814195},{"$f":"'Project Info'!D80","v":63.604425012889301},{"$f":"'Project Info'!E80","v":29.088683095945193},{"$f":"'Project Info'!F80","v":0},{"$f":"'Project Info'!G80","v":0},{"$f":"'Project Info'!H80","v":0},{"$f":"'Project Info'!I80","v":0},{"$f":"'Project Info'!J80","v":0},{"$f":"'Project Info'!K80","v":0},{"$f":"'Project Info'!L80","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A81","v":65},{"$f":"'Project Info'!B81","v":70},{"$f":"'Project Info'!C81","v":67.815831070966169},{"$f":"'Project Info'!D81","v":61.631331368130574},{"$f":"'Project Info'!E81","v":27.661514889731574},{"$f":"'Project Info'!F81","v":0},{"$f":"'Project Info'!G81","v":0},{"$f":"'Project Info'!H81","v":0},{"$f":"'Project Info'!I81","v":0},{"$f":"'Project Info'!J81","v":0},{"$f":"'Project Info'!K81","v":0},{"$f":"'Project Info'!L81","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A82","v":60},{"$f":"'Project Info'!B82","v":65},{"$f":"'Project Info'!C82","v":62.535961472271332},{"$f":"'Project Info'!D82","v":57.135476922863582},{"$f":"'Project Info'!E82","v":24.623037157728302},{"$f":"'Project Info'!F82","v":0},{"$f":"'Project Info'!G82","v":0},{"$f":"'Project Info'!H82","v":0},{"$f":"'Project Info'!I82","v":0},{"$f":"'Project Info'!J82","v":0},{"$f":"'Project Info'!K82","v":0},{"$f":"'Project Info'!L82","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A83","v":55},{"$f":"'Project Info'!B83","v":60},{"$f":"'Project Info'!C83","v":57.125792270740902},{"$f":"'Project Info'!D83","v":52.596971157053673},{"$f":"'Project Info'!E83","v":21.818001539159841},{"$f":"'Project Info'!F83","v":0},{"$f":"'Project Info'!G83","v":0},{"$f":"'Project Info'!H83","v":0},{"$f":"'Project Info'!I83","v":0},{"$f":"'Project Info'!J83","v":0},{"$f":"'Project Info'!K83","v":0},{"$f":"'Project Info'!L83","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A84","v":50},{"$f":"'Project Info'!B84","v":55},{"$f":"'Project Info'!C84","v":52.235698854337961},{"$f":"'Project Info'!D84","v":48.022768090099298},{"$f":"'Project Info'!E84","v":19.246640192796217},{"$f":"'Project Info'!F84","v":0},{"$f":"'Project Info'!G84","v":0},{"$f":"'Project Info'!H84","v":0},{"$f":"'Project Info'!I84","v":0},{"$f":"'Project Info'!J84","v":0},{"$f":"'Project Info'!K84","v":0},{"$f":"'Project Info'!L84","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A85","v":45},{"$f":"'Project Info'!B85","v":50},{"$f":"'Project Info'!C85","v":47.459170258371508},{"$f":"'Project Info'!D85","v":43.465397050422162},{"$f":"'Project Info'!E85","v":16.894183241713304},{"$f":"'Project Info'!F85","v":0},{"$f":"'Project Info'!G85","v":0},{"$f":"'Project Info'!H85","v":0},{"$f":"'Project Info'!I85","v":0},{"$f":"'Project Info'!J85","v":0},{"$f":"'Project Info'!K85","v":0},{"$f":"'Project Info'!L85","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A86","v":40},{"$f":"'Project Info'!B86","v":45},{"$f":"'Project Info'!C86","v":42.677030404888129},{"$f":"'Project Info'!D86","v":38.812544504634097},{"$f":"'Project Info'!E86","v":14.690265649465921},{"$f":"'Project Info'!F86","v":0},{"$f":"'Project Info'!G86","v":0},{"$f":"'Project Info'!H86","v":0},{"$f":"'Project Info'!I86","v":0},{"$f":"'Project Info'!J86","v":0},{"$f":"'Project Info'!K86","v":0},{"$f":"'Project Info'!L86","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A87","v":35},{"$f":"'Project Info'!B87","v":40},{"$f":"'Project Info'!C87","v":37.333046773755832},{"$f":"'Project Info'!D87","v":33.904706919479686},{"$f":"'Project Info'!E87","v":12.53841602318813},{"$f":"'Project Info'!F87","v":0},{"$f":"'Project Info'!G87","v":0},{"$f":"'Project Info'!H87","v":0},{"$f":"'Project Info'!I87","v":0},{"$f":"'Project Info'!J87","v":0},{"$f":"'Project Info'!K87","v":0},{"$f":"'Project Info'!L87","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A88","v":30},{"$f":"'Project Info'!B88","v":35},{"$f":"'Project Info'!C88","v":32.638179845662044},{"$f":"'Project Info'!D88","v":29.547170928664851},{"$f":"'Project Info'!E88","v":10.728972818165861},{"$f":"'Project Info'!F88","v":0},{"$f":"'Project Info'!G88","v":0},{"$f":"'Project Info'!H88","v":0},{"$f":"'Project Info'!I88","v":0},{"$f":"'Project Info'!J88","v":0},{"$f":"'Project Info'!K88","v":0},{"$f":"'Project Info'!L88","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A89","v":25},{"$f":"'Project Info'!B89","v":30},{"$f":"'Project Info'!C89","v":27.529264646850947},{"$f":"'Project Info'!D89","v":24.652717392657845},{"$f":"'Project Info'!E89","v":8.8041305482613303},{"$f":"'Project Info'!F89","v":0},{"$f":"'Project Info'!G89","v":0},{"$f":"'Project Info'!H89","v":0},{"$f":"'Project Info'!I89","v":0},{"$f":"'Project Info'!J89","v":0},{"$f":"'Project Info'!K89","v":0},{"$f":"'Project Info'!L89","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A90","v":20},{"$f":"'Project Info'!B90","v":25},{"$f":"'Project Info'!C90","v":22.998111483544687},{"$f":"'Project Info'!D90","v":20.383306659827422},{"$f":"'Project Info'!E90","v":7.246164547543378},{"$f":"'Project Info'!F90","v":0},{"$f":"'Project Info'!G90","v":0},{"$f":"'Project Info'!H90","v":0},{"$f":"'Project Info'!I90","v":0},{"$f":"'Project Info'!J90","v":0},{"$f":"'Project Info'!K90","v":0},{"$f":"'Project Info'!L90","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A91","v":15},{"$f":"'Project Info'!B91","v":20},{"$f":"'Project Info'!C91","v":17.808510327474309},{"$f":"'Project Info'!D91","v":15.420865796304254},{"$f":"'Project Info'!E91","v":5.5490484131518292},{"$f":"'Project Info'!F91","v":0},{"$f":"'Project Info'!G91","v":0},{"$f":"'Project Info'!H91","v":0},{"$f":"'Project Info'!I91","v":0},{"$f":"'Project Info'!J91","v":0},{"$f":"'Project Info'!K91","v":0},{"$f":"'Project Info'!L91","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A92","v":10},{"$f":"'Project Info'!B92","v":15},{"$f":"'Project Info'!C92","v":12.269931130346862},{"$f":"'Project Info'!D92","v":10.318264913023604},{"$f":"'Project Info'!E92","v":3.9082824916941998},{"$f":"'Project Info'!F92","v":0},{"$f":"'Project Info'!G92","v":0},{"$f":"'Project Info'!H92","v":0},{"$f":"'Project Info'!I92","v":0},{"$f":"'Project Info'!J92","v":0},{"$f":"'Project Info'!K92","v":0},{"$f":"'Project Info'!L92","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A93","v":5},{"$f":"'Project Info'!B93","v":10},{"$f":"'Project Info'!C93","v":7.3137581369917548},{"$f":"'Project Info'!D93","v":5.7052382449247707},{"$f":"'Project Info'!E93","v":2.5019418419888937},{"$f":"'Project Info'!F93","v":0},{"$f":"'Project Info'!G93","v":0},{"$f":"'Project Info'!H93","v":0},{"$f":"'Project Info'!I93","v":0},{"$f":"'Project Info'!J93","v":0},{"$f":"'Project Info'!K93","v":0},{"$f":"'Project Info'!L93","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A94","v":0},{"$f":"'Project Info'!B94","v":5},{"$f":"'Project Info'!C94","v":2.6119461836144886},{"$f":"'Project Info'!D94","v":1.2699770062067783},{"$f":"'Project Info'!E94","v":1.2046477897733283},{"$f":"'Project Info'!F94","v":8760},{"$f":"'Project Info'!G94","v":2672},{"$f":"'Project Info'!H94","v":3160},{"$f":"'Project Info'!I94","v":1344},{"$f":"'Project Info'!J94","v":1584},{"$f":"'Project Info'!K94","v":88},{"$f":"'Project Info'!L94","v":264}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A95","v":-5},{"$f":"'Project Info'!B95","v":0},{"$f":"'Project Info'!C95","v":-1.6731398516793925},{"$f":"'Project Info'!D95","v":-2.7083318773557807},{"$f":"'Project Info'!E95","v":7.9391832815876459E-2},{"$f":"'Project Info'!F95","v":0},{"$f":"'Project Info'!G95","v":0},{"$f":"'Project Info'!H95","v":0},{"$f":"'Project Info'!I95","v":0},{"$f":"'Project Info'!J95","v":0},{"$f":"'Project Info'!K95","v":0},{"$f":"'Project Info'!L95","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A96","v":-10},{"$f":"'Project Info'!B96","v":-5},{"$f":"'Project Info'!C96","v":-6.5729865085377277},{"$f":"'Project Info'!D96","v":-7.2465935998252222},{"$f":"'Project Info'!E96","v":-1.168423365310433},{"$f":"'Project Info'!F96","v":0},{"$f":"'Project Info'!G96","v":0},{"$f":"'Project Info'!H96","v":0},{"$f":"'Project Info'!I96","v":0},{"$f":"'Project Info'!J96","v":0},{"$f":"'Project Info'!K96","v":0},{"$f":"'Project Info'!L96","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A97","v":-15},{"$f":"'Project Info'!B97","v":-10},{"$f":"'Project Info'!C97","v":-15.32570353422995},{"$f":"'Project Info'!D97","v":-15.707838211108999},{"$f":"'Project Info'!E97","v":-3.4051318156661381},{"$f":"'Project Info'!F97","v":0},{"$f":"'Project Info'!G97","v":0},{"$f":"'Project Info'!H97","v":0},{"$f":"'Project Info'!I97","v":0},{"$f":"'Project Info'!J97","v":0},{"$f":"'Project Info'!K97","v":0},{"$f":"'Project Info'!L97","v":0}]
[]
[null,null,null,null,null,null,"Yes/No",null,null,"Heating Fuels",null,null,"Exhaust Flow Threshold for Code Requirement",null,null,null,5000,"CFM"]
[null,null,null,null,null,null,"Yes",null,null,"Fossil Fuel"]
[null,null,null,null,null,null,"No",null,null,"Elec",null,null,"Sample MAU Fan BHP/CFM (from Westport MS/HS 100% CD)",null,null,null,null,{"$f":"2.84/4735","v":5.9978880675818367E-4},"BHP/CFM"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Sample Hood Exhaust Fan BHP/CFM (from Westport MS/HS 100% CD)",null,null,null,null,{"$f":"3/4935","v":6.0790273556231007E-4},"BHP/CFM"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Max Allowable Input BHP/CFM",null,null,null,null,1E-3,"BHP/CFM"]
[null,null,null,null,null,null,"Building Type",null,{"$f":"'Project Info'!C18","v":0},null,null,null,null,"NEMA Premium"]
[null,null,null,null,null,null,"Building Hours of Operation",null,null,null,null,null,null,"Motor Efficiency",null,null,"Motor %of FL Eff vs %BHP"]
[null,null,null,null,null,null,null,null,"Start","End","Weekly Hrs",null,null,null,"1800 rpm",null,"% BHP","% of FL Eff"]
[null,null,null,null,null,null,"Weekdays",null,{"$f":"'Project Info'!I15","v":0},{"$f":"'Project Info'!J15","v":0},{"$f":"(J108-I108)*5","v":0},null,null,"HP","Eff",null,0,0.05]
[null,null,null,null,null,null,"Saturday",null,{"$f":"'Project Info'!I16","v":0},{"$f":"'Project Info'!J16","v":0},{"$f":"J109-I109","v":0},null,null,0,0,null,0.1,0.4]
[null,null,null,null,null,null,"Sunday",null,{"$f":"'Project Info'!I17","v":0},{"$f":"'Project Info'!J17","v":0},{"$f":"J110-I110","v":0},null,null,0.5,0.85,null,0.2,0.6]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,0.85499999999999998,null,0.4,0.92]
[null,null,null,null,null,null,"Hood Run Hours and % Flow by Meal (Same assuption used for all projects)",null,null,null,null,null,null,1.5,0.86499999999999999,null,0.6,0.98]
[null,null,null,null,null,null,null,"Breakfast","Lunch","Dinner","Late Night",null,null,2,0.86499999999999999,null,0.8,1]
[null,null,null,null,null,null,"Hours",4,5,6,3,null,null,3,0.89500000000000002,null,1,1]
[null,null,null,null,null,null,"Avg. % Flow",0.65,0.7,0.75,0.6,null,null,5,0.89500000000000002,null,1.1000000000000001,0.97]
[null,null,null,null,null,null,null,null,null,null,null,null,null,7.5,0.91]
[null,null,null,null,null,null,"Site Specific  Hood Operating Hours Based on User Inputs",null,null,null,null,null,null,10,0.91700000000000004,null,"Make-Up Air Discharge Temp Setpoint"]
[null,null,null,null,null,null,null,"Breakfast","Lunch","Dinner","Late Night","Week Total",null,15,0.93,null,null,"DAT","DAH"]
[null,null,null,null,null,null,"Weekdays",{"$f":"H$114*(L31=$G$101)","v":0},0,0,0,{"$f":"SUM(H119:K119)*5","v":0},null,20,0.93,null,null,"°F","Btu/lb"]
[null,null,null,null,null,null,"Saturdays",0,0,0,0,{"$f":"SUM(H120:K120)","v":0},null,25,0.93599999999999994,null,"Heating",68]
[null,null,null,null,null,null,"Sundays",0,0,0,0,{"$f":"SUM(H121:K121)","v":0},null,30,0.94099999999999995,null,"Cooling",null,25]
[null,null,null,null,null,null,"Week Total",{"$f":"5*H119+H120+H121","v":0},{"$f":"5*I119+I120+I121","v":0},{"$f":"5*J119+J120+J121","v":0},{"$f":"5*K119+K120+K121","v":0},null,null,40,0.94099999999999995]
[null,null,null,null,null,null,null,null,null,null,null,null,null,50,0.94499999999999995,null,null,"OAT Heat/Cool Switch",60,"°F"]
[null,null,null,null,null,null,null,null,null,null,"Proposed","Base",null,60,0.95,null,null,"SP Control Ratio",0.3,"for modified cube law calc"]
[null,null,null,null,null,null,null,null,null,"Hood Average Operating % Flow (% of Design CFM)",{"$f":"IFERROR(SUMPRODUCT(H122:K122,H115:K115)/SUM(H122:K122),0)","v":0},1,null,75,0.95]
[null,null,null,null,null,null,null,null,null,"Hood Operating Hours as % of Total Building Occ Hours",{"$f":"SUM(L119:L121)/SUM(K108:K110)","v":{"$error":"#DIV/0!"}},null,null,100,0.95400000000000007,null,"Incremental Cost Estimates"]
[null,null,null,null,null,null,null,null,null,"% of Savings During On Peak",{"$f":"IFERROR(5*SUM(H119:J119)/SUM(H122:K122),0)","v":0},null,null,125,0.95400000000000007,null,null,null,"Units","Qty","$/unit","Total $"]
[null,null,null,null,null,null,null,null,null,"Savings During Summer Demand Peak?",{"$f":"M31","v":0},null,null,150,0.95799999999999996,null,"Controls Package Cost per CFM",null,"CFM",{"$f":"R20","v":0},1.5,{"$f":"U128*T128","v":0}]
[null,null,null,null,null,null,null,null,null,"Savings During Winter Demand Peak?",{"$f":"N31","v":0},null,null,200,0.95799999999999996,null,"Controls Base Cost",null,null,null,null,10000]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Cost",{"$f":"SUM(V128:V129)*(R20>0)","v":0}]
[null,null,null,null,null,null,null,null,null,null,0.5,0.22]
[null,null,null,null,null,null,null,null,null,null,0.7,0.66]

{"sheet":"Condensing Boilers","index":17,"n_rows":132,"n_cols":50,"rows_kept":132,"cut":false,"hidden":true,"merged":[[1,19,11,27],[15,13,15,14],[15,15,15,16],[15,17,15,18],[27,13,27,14],[27,15,27,16],[27,17,27,18],[1,10,4,17],[9,11,9,12]]}
["Savings Summary",null,null,null,null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,null,null,"Notes (Optional)"]
["Annual kWh Savings",null,null,{"$f":"SUM(A14:D14)","v":0},null,null,null,"Value","Unit",null,"This measure considers savings from installing high performance condensing boilers that exceed the baseline boiler efficiency requirements. Note: ONLY condensing boilers are considered in this measure (not non-condensing high efficiency boilers). Non-condensing boilers that exceed baseline efficiency must be analyzed as a separate user-defined measure.\n"]
["% On Peak",null,null,{"$f":"IF(D2<=0,0,MIN(1,A15+C15))","v":0},null,"Annual Electric Savings",null,{"$f":"D2","v":0},"kWh"]
["Max kW",null,null,{"$f":"MAX(AX35:AX58,AX65:AX88)","v":0},null,"Annual Fuel Savings",null,{"$f":"D7*C28","v":{"$error":"#N/A"}},{"$f":"D20","v":{"$error":"#N/A"}}]
["Summer kW",null,null,{"$f":"(SUMPRODUCT(AX35:AX58,R35:R58)+SUMPRODUCT(AX65:AX88,R65:R88))/SUM(R35:R58,R65:R88)","v":0},null,"Incremental","Default Calc",{"$f":"SUM($AI$103:$AI$105)","v":0},"$"]
["Winter kW",null,null,{"$f":"(SUMPRODUCT(AX35:AX58,Q35:Q58)+SUMPRODUCT(AX65:AX88,Q65:Q88))/SUM(Q35:Q58,Q65:Q88)","v":0},null,"Cost","Project Specific",null,"$ (Optional)"]
["Annual Fuel Savings (MMBtu)",null,null,{"$f":"(SUMPRODUCT($L$35:$L$58,AW35:AW58)+SUMPRODUCT($L$65:$L$88,AW65:AW88))/1000","v":0},null,"Estimated Incentive",null,{"$f":"O27+Q27*(Q15=\"Yes\")+S27*(S15=\"Yes\")","v":0},"$"]
["Incremental Cost (Default Calc)",null,null,{"$f":"SUM($AI$103:$AI$105)","v":0}]
["Incremental Cost (for Summary)",null,null,{"$f":"IF(H6>0,H6,D8)","v":0},null,"Project Information Summary"]
["kWh Savings by Peak Period",null,null,null,null,null,"STATE",{"$f":"'Project Info'!C15","v":"NH"},null,null,"Project Type","New Construction"]
["Winter","Winter","Summer","Summer",null,null,"Program Year",{"$f":"'Project Info'!C19","v":0},null,null,null,"Existing Building","> For replace on failure or end of life replacement of equipment in an existing building."]
["On-Peak","Off-Peak","On-Peak","Off-Peak",null,null,"Code IECC Version",{"$f":"MID('Project Info'!C20,1,4)","v":"2018"},null,null,null,"New Constructin","> For equipment in a ground-up new construction project."]
["kWh","kWh","kWh","kWh",null,null,"Electric PA",{"$f":"'Project Info'!F3","v":0}]
[{"$f":"SUMPRODUCT($AX$35:$AX$58,M35:M58)+SUMPRODUCT($AX$65:$AX$88,M65:M88)","v":0},{"$f":"SUMPRODUCT($AX$35:$AX$58,N35:N58)+SUMPRODUCT($AX$65:$AX$88,N65:N88)","v":0},{"$f":"SUMPRODUCT($AX$35:$AX$58,O35:O58)+SUMPRODUCT($AX$65:$AX$88,O65:O88)","v":0},{"$f":"SUMPRODUCT($AX$35:$AX$58,P35:P58)+SUMPRODUCT($AX$65:$AX$88,P65:P88)","v":0},null,null,"Gas PA",{"$f":"'Project Info'!I3","v":0},null,null,"Table 1: Boiler/Loop Parameters",null,null,null,null,"Optional: System #2",null,"Optional: System #3",null,null,"Baseline vs. Proposed Assumptions Summary"]
[{"$f":"ROUND(IF(A14<=0,0,A14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(B14<=0,0,B14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(C14<=0,0,C14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"IF(SUM(A14:D14)=0,0,1-SUM(A15:C15))","v":0},null,"*NOTE: Baseline values are automated and cannot be changed.",null,null,null,null,null,null,null,"System #1",null,"Include?","No","Include?","No",null,null,"Baseline Eff (%)",null,"Proposed Eff (%)",null,"EFLH"]
[null,null,null,null,null,null,null,null,null,null,"System Load Profile",null,null,null,null,null,null,null,null,null,null,"Min","Max","Min","Max","Heating"]
["Utility Rates",null,null,null,null,null,null,null,null,null,"Boiler Quantity",null,null,null,null,null,null,null,null,null,"System 1",{"$f":"MIN(V35:V58,V65:V88)","v":0.99},{"$f":"MAX(V35:V58,V65:V88)","v":0.99},{"$f":"MIN(X35:X58,X65:X88)","v":0.99},{"$f":"MAX(X35:X58,X65:X88)","v":0.99},{"$f":"IF(ISERROR(Y103),0,Y103)","v":0}]
[null,null,"Rate","Unit",null,null,null,null,null,null,"Output Capacity MBH (per Boiler)",null,null,null,null,null,null,null,null,null,"System 2",{"$f":"MIN(AF35:AF58,AF65:AF88)*($Q$15=\"Yes\")","v":0},{"$f":"MAX(AF35:AF58,AF65:AF88)*($Q$15=\"Yes\")","v":0},{"$f":"MIN(AH35:AH58,AH65:AH88)*($Q$15=\"Yes\")","v":0},{"$f":"MAX(AH35:AH58,AH65:AH88)*($Q$15=\"Yes\")","v":0},{"$f":"IF(ISERROR(Y104),0,Y104)","v":0}]
["Electric",null,{"$f":"'ECM Summary'!$E$31","v":0.1593},"kWh",null,null,null,null,null,null,"Max # of Operating Boilers",null,null,null,{"$f":"MAX(1,N17-1)*(N17>0)","v":0},null,{"$f":"MAX(1,P17-1)*(P17>0)","v":0},null,{"$f":"MAX(1,R17-1)*(R17>0)","v":0},null,"System 3",{"$f":"MIN(AP35:AP58,AP65:AP88)*($S$15=\"Yes\")","v":0},{"$f":"MAX(AP35:AP58,AP65:AP88)*($S$15=\"Yes\")","v":0},{"$f":"MIN(AR35:AR58,AR65:AR88)*($S$15=\"Yes\")","v":0},{"$f":"MAX(AR35:AR58,AR65:AR88)*($S$15=\"Yes\")","v":0},{"$f":"IF(ISERROR(Y105),0,Y105)","v":0}]
[{"$f":"'ECM Summary'!$C$32","v":0},null,{"$f":"'ECM Summary'!$E$32","v":{"$error":"#N/A"}},{"$f":"'ECM Summary'!$F$32","v":{"$error":"#N/A"}},null,null,null,null,null,null,"Peak Load % of Max Op. Cap",null,null,null,0.85,null,0.85,null,0.85]
[null,null,null,null,null,null,null,null,null,null,"Design Supply HW Temp. (°F)"]
["Custom Incentive Rates",null,null,null,null,null,null,null,null,null,"Design HW Loop dT (°F)"]
[null,null,"Rate","Unit",null,null,null,null,null,null,null,null,null,"Outside Air","HW Supply","Outside Air","HW Supply","Outside Air","HW Supply"]
["Electric",null,{"$f":"'ECM Summary'!$J$31","v":0.28000000000000003},"kWh",null,null,null,null,null,null,"HW Outside Air",null,null,"Temp (°F)","Temp (°F)","Temp (°F)","Temp (°F)","Temp (°F)","Temp (°F)"]
[{"$f":"'ECM Summary'!$H$32","v":0},null,{"$f":"'ECM Summary'!$J$32","v":0},{"$f":"'ECM Summary'!$K$32","v":{"$error":"#N/A"}},null,null,null,null,null,null,"Reset Range",null,"OA Low | HW High"]
[null,null,null,null,null,null,null,null,null,null,null,null,"OA High | HW Low"]
["Fossil Fuel",null,{"$f":"'Project Info'!C21","v":0},null,null,null,null,null,null,null,"Incentive ($)",null,null,null,{"$f":"AH103","v":0},null,{"$f":"AH104","v":0},null,{"$f":"AH105","v":0}]
["Fuel Conversion",null,{"$f":"LOOKUP(C27,'Project Info'!X102:X104,'Project Info'!Z102:Z104)","v":{"$error":"#N/A"}},null,null,null,null,null,null,null,"Manufacturer & Model (Optional)"]
[null,null,null,null,null,null,null,null,null,null,"*Savings are based on custom calculation; Incentives are based on prescriptive rates."]
[]
[null,null,null,null,null,null,"Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown",null,null,null,null,null,null,"SYSTEM 1 ANALYSIS",null,null,null,null,null,null,null,null,null,"SYSTEM 2 ANALYSIS",null,null,null,null,null,null,null,null,null,"SYSTEM 3 ANALYSIS",null,null,null,null,null,null,null,null,null,"Total Combined"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Heating","Heating","Base Return","Base","Prop Return","Proposed","Base","Design","Demand","Demand","Heating","Heating","Base Return","Base","Prop Return","Proposed","Base","Design","Demand","Demand","Heating","Heating","Base Return","Base","Prop Return","Proposed","Base","Design","Demand","Demand","Demand"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Load","Load","HWT","Eff.","HWT","Eff.","Demand","Demand","Savings","Savings","Load","Load","HWT","Eff.","HWT","Eff.","Demand","Demand","Savings","Savings","Load","Load","HWT","Eff.","HWT","Eff.","Demand","Demand","Savings","Savings","Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","%","MBH","°F","%","°F","%","MBH","MBH","MBH","kW","%","MBH","°F","%","°F","%","MBH","MBH","MBH","kW","%","MBH","°F","%","°F","%","MBH","MBH","MBH","kW","MBH","kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A44","v":100},{"$f":"'Project Info'!B44","v":105},{"$f":"'Project Info'!C44","v":102},{"$f":"'Project Info'!D44","v":76},{"$f":"'Project Info'!E44","v":40},{"$f":"'Project Info'!F44","v":0},{"$f":"'Project Info'!G44","v":0},{"$f":"'Project Info'!H44","v":0},{"$f":"'Project Info'!I44","v":0},{"$f":"'Project Info'!J44","v":0},{"$f":"'Project Info'!K44","v":0},{"$f":"'Project Info'!L44","v":0},{"$f":"IFERROR(MAX(0,MIN(1,TREND($S$103:$T$103,$Q$103:$R$103,$I35)))*($I35<=$Q$103),0)","v":0},{"$f":"S35*$J$103*$K$103","v":0},{"$f":"IF($I35>=$AA$103,$AE$103,IF($I35<=$Z$103,$AB$103,TREND($AD$103:$AE$103,$Z$103:$AA$103,$I35)))","v":0},{"$f":"IF($L$103<90%,$L$103,MAX($Q$132,MIN($Q$124,TREND(OFFSET($P$123,MATCH(U35,$P$124:$P$132,1),1,2,1),OFFSET($P$123,MATCH(U35,$P$124:$P$132,1),0,2,1),U35))))","v":0.99},{"$f":"IF($I35>=$AA$103,$AC$103,IF($I35<=$Z$103,$AB$103,TREND($AB$103:$AC$103,$Z$103:$AA$103,$I35)))","v":0},{"$f":"MAX($Q$132,MIN($Q$124,TREND(OFFSET($P$123,MATCH(W35,$P$124:$P$132,1),1,2,1),OFFSET($P$123,MATCH(W35,$P$124:$P$132,1),0,2,1),W35)))","v":0.99},{"$f":"T35/V35","v":0},{"$f":"T35/X35","v":0},{"$f":"Y35-Z35","v":0},0,{"$f":"IFERROR(IF($Q$15<>$G$92,0,MAX(0,MIN(1,TREND($S$104:$T$104,$Q$104:$R$104,$I35)))*($I35<=$Q$104)),0)","v":0},{"$f":"AC35*$J$104*$K$104","v":0},{"$f":"IF($I35>=$AA$104,$AE$104,IF($I35<=$Z$104,$AB$104,TREND($AD$104:$AE$104,$Z$104:$AA$104,$I35)))","v":0},{"$f":"IF($L$104<=90%,$L$104,MAX($Q$132,MIN($Q$124,TREND(OFFSET($P$123,MATCH(AE35,$P$124:$P$132,1),1,2,1),OFFSET($P$123,MATCH(AE35,$P$124:$P$132,1),0,2,1),AE35))))","v":0.99},{"$f":"IF($I35>=$AA$104,$AC$104,IF($I35<=$Z$104,$AB$104,TREND($AB$104:$AC$104,$Z$104:$AA$104,$I35)))","v":0},{"$f":"MAX($Q$132,MIN($Q$124,TREND(OFFSET($P$123,MATCH(AG35,$P$124:$P$132,1),1,2,1),OFFSET($P$123,MATCH(AG35,$P$124:$P$132,1),0,2,1),AG35)))","v":0.99},{"$f":"AD35/AF35","v":0},{"$f":"AD35/AH35","v":0},{"$f":"AI35-AJ35","v":0},0,{"$f":"IFERROR(IF($S$15<>$G$92,0,MAX(0,MIN(1,TREND($S$105:$T$105,$Q$105:$R$105,$I35)))*($I35<=$Q$105)),0)","v":0},{"$f":"AM35*$J$105*$K$105","v":0},{"$f":"IF($I35>=$AA$105,$AE$105,IF($I35<=$Z$105,$AB$105,TREND($AD$105:$AE$105,$Z$105:$AA$105,$I35)))","v":0},{"$f":"IF($L$105<=90%,$L$105,MAX($Q$132,MIN($Q$124,TREND(OFFSET($P$123,MATCH(AO35,$P$124:$P$132,1),1,2,1),OFFSET($P$123,MATCH(AO35,$P$124:$P$132,1),0,2,1),AO35))))","v":0.99},{"$f":"IF($I35>=$AA$105,$AC$105,IF($I35<=$Z$105,$AB$105,TREND($AB$105:$AC$105,$Z$105:$AA$105,$I35)))","v":0},{"$f":"MAX($Q$132,MIN($Q$124,TREND(OFFSET($P$123,MATCH(AQ35,$P$124:$P$132,1),1,2,1),OFFSET($P$123,MATCH(AQ35,$P$124:$P$132,1),0,2,1),AQ35)))","v":0.99},{"$f":"AN35/AP35","v":0},{"$f":"AN35/AR35","v":0},{"$f":"AS35-AT35","v":0},0,{"$f":"AA35+AK35+AU35","v":0},{"$f":"AB35+AL35+AV35","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A45","v":95},{"$f":"'Project Info'!B45","v":100},{"$f":"'Project Info'!C45","v":95.219272727272724},{"$f":"'Project Info'!D45","v":74.534025272781079},{"$f":"'Project Info'!E45","v":37.923296058061368},{"$f":"'Project Info'!F45","v":0},{"$f":"'Project Info'!G45","v":0},{"$f":"'Project Info'!H45","v":0},{"$f":"'Project Info'!I45","v":0},{"$f":"'Project Info'!J45","v":0},{"$f":"'Project Info'!K45","v":0},{"$f":"'Project Info'!L45","v":0},{"$f":"IFERROR(MAX(0,MIN(1,TREND($S$103:$T$103,$Q$103:$R$103,$I36)))*($I36<=$Q$103),0)","v":0},{"$f":"S36*$J$103*$K$103","v":0},{"$f":"IF($I36>=$AA$103,$AE$103,IF($I36<=$Z$103,$AB$103,TREND($AD$103:$AE$103,$Z$103:$AA$103,$I36)))","v":0},{"$f":"IF($L$103<90%,$L$103,MAX($Q$132,MIN($Q$124,TREND(OFFSET($P$123,MATCH(U36,$P$124:$P$132,1),1,2,1),OFFSET($P$123,MATCH(U36,$P$124:$P$132,1),0,2,1),U36))))","v":0.99},0,0.99,0,0,{"$f":"Y36-Z36","v":0},0,0,{"$f":"AC36*$J$104*$K$104","v":0},{"$f":"IF($I36>=$AA$104,$AE$104,IF($I36<=$Z$104,$AB$104,TREND($AD$104:$AE$104,$Z$104:$AA$104,$I36)))","v":0},{"$f":"IF($L$104<=90%,$L$104,MAX($Q$132,MIN($Q$124,TREND(OFFSET($P$123,MATCH(AE36,$P$124:$P$132,1),1,2,1),OFFSET($P$123,MATCH(AE36,$P$124:$P$132,1),0,2,1),AE36))))","v":0.99},0,0.99,0,0,{"$f":"AI36-AJ36","v":0},0,{"$f":"IFERROR(IF($S$15<>$G$92,0,MAX(0,MIN(1,TREND($S$105:$T$105,$Q$105:$R$105,$I36)))*($I36<=$Q$105)),0)","v":0},{"$f":"AM36*$J$105*$K$105","v":0},{"$f":"IF($I36>=$AA$105,$AE$105,IF($I36<=$Z$105,$AB$105,TREND($AD$105:$AE$105,$Z$105:$AA$105,$I36)))","v":0},{"$f":"IF($L$105<=90%,$L$105,MAX($Q$132,MIN($Q$124,TREND(OFFSET($P$123,MATCH(AO36,$P$124:$P$132,1),1,2,1),OFFSET($P$123,MATCH(AO36,$P$124:$P$132,1),0,2,1),AO36))))","v":0.99},0,0.99,0,0,{"$f":"AS36-AT36","v":0},0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A46","v":90},{"$f":"'Project Info'!B46","v":95},{"$f":"'Project Info'!C46","v":92.016049160256074},{"$f":"'Project Info'!D46","v":72.911561930607689},{"$f":"'Project Info'!E46","v":36.467095439351091},{"$f":"'Project Info'!F46","v":0},{"$f":"'Project Info'!G46","v":0},{"$f":"'Project Info'!H46","v":0},{"$f":"'Project Info'!I46","v":0},{"$f":"'Project Info'!J46","v":0},{"$f":"'Project Info'!K46","v":0},{"$f":"'Project Info'!L46","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A47","v":85},{"$f":"'Project Info'!B47","v":90},{"$f":"'Project Info'!C47","v":87.457811360655285},{"$f":"'Project Info'!D47","v":70.80538329449476},{"$f":"'Project Info'!E47","v":34.679413213566804},{"$f":"'Project Info'!F47","v":0},{"$f":"'Project Info'!G47","v":0},{"$f":"'Project Info'!H47","v":0},{"$f":"'Project Info'!I47","v":0},{"$f":"'Project Info'!J47","v":0},{"$f":"'Project Info'!K47","v":0},{"$f":"'Project Info'!L47","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A48","v":80},{"$f":"'Project Info'!B48","v":85},{"$f":"'Project Info'!C48","v":82.136788830239965},{"$f":"'Project Info'!D48","v":67.872393622439333},{"$f":"'Project Info'!E48","v":32.296248223809314},{"$f":"'Project Info'!F48","v":0},{"$f":"'Project Info'!G48","v":0},{"$f":"'Project Info'!H48","v":0},{"$f":"'Project Info'!I48","v":0},{"$f":"'Project Info'!J48","v":0},{"$f":"'Project Info'!K48","v":0},{"$f":"'Project Info'!L48","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A49","v":75},{"$f":"'Project Info'!B49","v":80},{"$f":"'Project Info'!C49","v":76.988400157585886},{"$f":"'Project Info'!D49","v":65.129261896908645},{"$f":"'Project Info'!E49","v":30.190476812806729},{"$f":"'Project Info'!F49","v":0},{"$f":"'Project Info'!G49","v":0},{"$f":"'Project Info'!H49","v":0},{"$f":"'Project Info'!I49","v":0},{"$f":"'Project Info'!J49","v":0},{"$f":"'Project Info'!K49","v":0},{"$f":"'Project Info'!L49","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A50","v":70},{"$f":"'Project Info'!B50","v":75},{"$f":"'Project Info'!C50","v":72.457982050814195},{"$f":"'Project Info'!D50","v":63.604425012889301},{"$f":"'Project Info'!E50","v":29.088683095945193},{"$f":"'Project Info'!F50","v":0},{"$f":"'Project Info'!G50","v":0},{"$f":"'Project Info'!H50","v":0},{"$f":"'Project Info'!I50","v":0},{"$f":"'Project Info'!J50","v":0},{"$f":"'Project Info'!K50","v":0},{"$f":"'Project Info'!L50","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A51","v":65},{"$f":"'Project Info'!B51","v":70},{"$f":"'Project Info'!C51","v":67.815831070966169},{"$f":"'Project Info'!D51","v":61.631331368130574},{"$f":"'Project Info'!E51","v":27.661514889731574},{"$f":"'Project Info'!F51","v":0},{"$f":"'Project Info'!G51","v":0},{"$f":"'Project Info'!H51","v":0},{"$f":"'Project Info'!I51","v":0},{"$f":"'Project Info'!J51","v":0},{"$f":"'Project Info'!K51","v":0},{"$f":"'Project Info'!L51","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A52","v":60},{"$f":"'Project Info'!B52","v":65},{"$f":"'Project Info'!C52","v":62.535961472271332},{"$f":"'Project Info'!D52","v":57.135476922863582},{"$f":"'Project Info'!E52","v":24.623037157728302},{"$f":"'Project Info'!F52","v":0},{"$f":"'Project Info'!G52","v":0},{"$f":"'Project Info'!H52","v":0},{"$f":"'Project Info'!I52","v":0},{"$f":"'Project Info'!J52","v":0},{"$f":"'Project Info'!K52","v":0},{"$f":"'Project Info'!L52","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A53","v":55},{"$f":"'Project Info'!B53","v":60},{"$f":"'Project Info'!C53","v":57.125792270740902},{"$f":"'Project Info'!D53","v":52.596971157053673},{"$f":"'Project Info'!E53","v":21.818001539159841},{"$f":"'Project Info'!F53","v":0},{"$f":"'Project Info'!G53","v":0},{"$f":"'Project Info'!H53","v":0},{"$f":"'Project Info'!I53","v":0},{"$f":"'Project Info'!J53","v":0},{"$f":"'Project Info'!K53","v":0},{"$f":"'Project Info'!L53","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A54","v":50},{"$f":"'Project Info'!B54","v":55},{"$f":"'Project Info'!C54","v":52.235698854337961},{"$f":"'Project Info'!D54","v":48.022768090099298},{"$f":"'Project Info'!E54","v":19.246640192796217},{"$f":"'Project Info'!F54","v":0},{"$f":"'Project Info'!G54","v":0},{"$f":"'Project Info'!H54","v":0},{"$f":"'Project Info'!I54","v":0},{"$f":"'Project Info'!J54","v":0},{"$f":"'Project Info'!K54","v":0},{"$f":"'Project Info'!L54","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A55","v":45},{"$f":"'Project Info'!B55","v":50},{"$f":"'Project Info'!C55","v":47.459170258371508},{"$f":"'Project Info'!D55","v":43.465397050422162},{"$f":"'Project Info'!E55","v":16.894183241713304},{"$f":"'Project Info'!F55","v":0},{"$f":"'Project Info'!G55","v":0},{"$f":"'Project Info'!H55","v":0},{"$f":"'Project Info'!I55","v":0},{"$f":"'Project Info'!J55","v":0},{"$f":"'Project Info'!K55","v":0},{"$f":"'Project Info'!L55","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A56","v":40},{"$f":"'Project Info'!B56","v":45},{"$f":"'Project Info'!C56","v":42.677030404888129},{"$f":"'Project Info'!D56","v":38.812544504634097},{"$f":"'Project Info'!E56","v":14.690265649465921},{"$f":"'Project Info'!F56","v":0},{"$f":"'Project Info'!G56","v":0},{"$f":"'Project Info'!H56","v":0},{"$f":"'Project Info'!I56","v":0},{"$f":"'Project Info'!J56","v":0},{"$f":"'Project Info'!K56","v":0},{"$f":"'Project Info'!L56","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A57","v":35},{"$f":"'Project Info'!B57","v":40},{"$f":"'Project Info'!C57","v":37.333046773755832},{"$f":"'Project Info'!D57","v":33.904706919479686},{"$f":"'Project Info'!E57","v":12.53841602318813},{"$f":"'Project Info'!F57","v":0},{"$f":"'Project Info'!G57","v":0},{"$f":"'Project Info'!H57","v":0},{"$f":"'Project Info'!I57","v":0},{"$f":"'Project Info'!J57","v":0},{"$f":"'Project Info'!K57","v":0},{"$f":"'Project Info'!L57","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A58","v":30},{"$f":"'Project Info'!B58","v":35},{"$f":"'Project Info'!C58","v":32.638179845662044},{"$f":"'Project Info'!D58","v":29.547170928664851},{"$f":"'Project Info'!E58","v":10.728972818165861},{"$f":"'Project Info'!F58","v":0},{"$f":"'Project Info'!G58","v":0},{"$f":"'Project Info'!H58","v":0},{"$f":"'Project Info'!I58","v":0},{"$f":"'Project Info'!J58","v":0},{"$f":"'Project Info'!K58","v":0},{"$f":"'Project Info'!L58","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A59","v":25},{"$f":"'Project Info'!B59","v":30},{"$f":"'Project Info'!C59","v":27.529264646850947},{"$f":"'Project Info'!D59","v":24.652717392657845},{"$f":"'Project Info'!E59","v":8.8041305482613303},{"$f":"'Project Info'!F59","v":0},{"$f":"'Project Info'!G59","v":0},{"$f":"'Project Info'!H59","v":0},{"$f":"'Project Info'!I59","v":0},{"$f":"'Project Info'!J59","v":0},{"$f":"'Project Info'!K59","v":0},{"$f":"'Project Info'!L59","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A60","v":20},{"$f":"'Project Info'!B60","v":25},{"$f":"'Project Info'!C60","v":22.998111483544687},{"$f":"'Project Info'!D60","v":20.383306659827422},{"$f":"'Project Info'!E60","v":7.246164547543378},{"$f":"'Project Info'!F60","v":0},{"$f":"'Project Info'!G60","v":0},{"$f":"'Project Info'!H60","v":0},{"$f":"'Project Info'!I60","v":0},{"$f":"'Project Info'!J60","v":0},{"$f":"'Project Info'!K60","v":0},{"$f":"'Project Info'!L60","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A61","v":15},{"$f":"'Project Info'!B61","v":20},{"$f":"'Project Info'!C61","v":17.808510327474309},{"$f":"'Project Info'!D61","v":15.420865796304254},{"$f":"'Project Info'!E61","v":5.5490484131518292},{"$f":"'Project Info'!F61","v":0},{"$f":"'Project Info'!G61","v":0},{"$f":"'Project Info'!H61","v":0},{"$f":"'Project Info'!I61","v":0},{"$f":"'Project Info'!J61","v":0},{"$f":"'Project Info'!K61","v":0},{"$f":"'Project Info'!L61","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A62","v":10},{"$f":"'Project Info'!B62","v":15},{"$f":"'Project Info'!C62","v":12.269931130346862},{"$f":"'Project Info'!D62","v":10.318264913023604},{"$f":"'Project Info'!E62","v":3.9082824916941998},{"$f":"'Project Info'!F62","v":0},{"$f":"'Project Info'!G62","v":0},{"$f":"'Project Info'!H62","v":0},{"$f":"'Project Info'!I62","v":0},{"$f":"'Project Info'!J62","v":0},{"$f":"'Project Info'!K62","v":0},{"$f":"'Project Info'!L62","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A63","v":5},{"$f":"'Project Info'!B63","v":10},{"$f":"'Project Info'!C63","v":7.3137581369917548},{"$f":"'Project Info'!D63","v":5.7052382449247707},{"$f":"'Project Info'!E63","v":2.5019418419888937},{"$f":"'Project Info'!F63","v":0},{"$f":"'Project Info'!G63","v":0},{"$f":"'Project Info'!H63","v":0},{"$f":"'Project Info'!I63","v":0},{"$f":"'Project Info'!J63","v":0},{"$f":"'Project Info'!K63","v":0},{"$f":"'Project Info'!L63","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A64","v":0},{"$f":"'Project Info'!B64","v":5},{"$f":"'Project Info'!C64","v":2.6119461836144886},{"$f":"'Project Info'!D64","v":1.2699770062067783},{"$f":"'Project Info'!E64","v":1.2046477897733283},{"$f":"'Project Info'!F64","v":0},{"$f":"'Project Info'!G64","v":0},{"$f":"'Project Info'!H64","v":0},{"$f":"'Project Info'!I64","v":0},{"$f":"'Project Info'!J64","v":0},{"$f":"'Project Info'!K64","v":0},{"$f":"'Project Info'!L64","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A65","v":-5},{"$f":"'Project Info'!B65","v":0},{"$f":"'Project Info'!C65","v":-1.6731398516793925},{"$f":"'Project Info'!D65","v":-2.7083318773557807},{"$f":"'Project Info'!E65","v":7.9391832815876459E-2},{"$f":"'Project Info'!F65","v":0},{"$f":"'Project Info'!G65","v":0},{"$f":"'Project Info'!H65","v":0},{"$f":"'Project Info'!I65","v":0},{"$f":"'Project Info'!J65","v":0},{"$f":"'Project Info'!K65","v":0},{"$f":"'Project Info'!L65","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A66","v":-10},{"$f":"'Project Info'!B66","v":-5},{"$f":"'Project Info'!C66","v":-6.5729865085377277},{"$f":"'Project Info'!D66","v":-7.2465935998252222},{"$f":"'Project Info'!E66","v":-1.168423365310433},{"$f":"'Project Info'!F66","v":0},{"$f":"'Project Info'!G66","v":0},{"$f":"'Project Info'!H66","v":0},{"$f":"'Project Info'!I66","v":0},{"$f":"'Project Info'!J66","v":0},{"$f":"'Project Info'!K66","v":0},{"$f":"'Project Info'!L66","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A67","v":-15},{"$f":"'Project Info'!B67","v":-10},{"$f":"'Project Info'!C67","v":-15.32570353422995},{"$f":"'Project Info'!D67","v":-15.707838211108999},{"$f":"'Project Info'!E67","v":-3.4051318156661381},{"$f":"'Project Info'!F67","v":0},{"$f":"'Project Info'!G67","v":0},{"$f":"'Project Info'!H67","v":0},{"$f":"'Project Info'!I67","v":0},{"$f":"'Project Info'!J67","v":0},{"$f":"'Project Info'!K67","v":0},{"$f":"'Project Info'!L67","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[]
[]
[null,null,null,null,null,null,"Unoccupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown",null,null,null,null,null,null,"SYSTEM 1 ANALYSIS",null,null,null,null,null,null,null,null,null,"SYSTEM 2 ANALYSIS",null,null,null,null,null,null,null,null,null,"SYSTEM 3 ANALYSIS",null,null,null,null,null,null,null,null,null,"Total Combined"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Heating","Heating","Base Return","Base","Prop Return","Proposed","Base","Design","Demand","Demand","Heating","Heating","Base Return","Base","Prop Return","Proposed","Base","Design","Demand","Demand","Heating","Heating","Base Return","Base","Prop Return","Proposed","Base","Design","Demand","Demand","Demand"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Load","Load","HWT","Eff.","HWT","Eff.","Demand","Demand","Savings","Savings","Load","Load","HWT","Eff.","HWT","Eff.","Demand","Demand","Savings","Savings","Load","Load","HWT","Eff.","HWT","Eff.","Demand","Demand","Savings","Savings","Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","%","MBH","°F","%","°F","%","MBH","MBH","MBH","kW","%","MBH","°F","%","°F","%","MBH","MBH","MBH","kW","%","MBH","°F","%","°F","%","MBH","MBH","MBH","kW","MBH","kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A74","v":100},{"$f":"'Project Info'!B74","v":105},{"$f":"'Project Info'!C74","v":102},{"$f":"'Project Info'!D74","v":76},{"$f":"'Project Info'!E74","v":40},{"$f":"'Project Info'!F74","v":0},{"$f":"'Project Info'!G74","v":0},{"$f":"'Project Info'!H74","v":0},{"$f":"'Project Info'!I74","v":0},{"$f":"'Project Info'!J74","v":0},{"$f":"'Project Info'!K74","v":0},{"$f":"'Project Info'!L74","v":0},{"$f":"IFERROR(MAX(0,MIN(1,TREND($W$103:$X$103,$U$103:$V$103,$I65)))*($I65<=$U$103),0)","v":0},{"$f":"S65*$J$103*$K$103","v":0},{"$f":"IF($I65>=$AA$103,$AE$103,IF($I65<=$Z$103,$AB$103,TREND($AD$103:$AE$103,$Z$103:$AA$103,$I65)))","v":0},{"$f":"IF($L$103<90%,$L$103,MAX($Q$132,MIN($Q$124,TREND(OFFSET($P$123,MATCH(U65,$P$124:$P$132,1),1,2,1),OFFSET($P$123,MATCH(U65,$P$124:$P$132,1),0,2,1),U65))))","v":0.99},{"$f":"IF($I65>=$AA$103,$AC$103,IF($I65<=$Z$103,$AB$103,TREND($AB$103:$AC$103,$Z$103:$AA$103,$I65)))","v":0},{"$f":"MAX($Q$132,MIN($Q$124,TREND(OFFSET($P$123,MATCH(W65,$P$124:$P$132,1),1,2,1),OFFSET($P$123,MATCH(W65,$P$124:$P$132,1),0,2,1),W65)))","v":0.99},{"$f":"T65/V65","v":0},{"$f":"T65/X65","v":0},{"$f":"Y65-Z65","v":0},0,{"$f":"IFERROR(IF($Q$15<>$G$92,0,MAX(0,MIN(1,TREND($W$104:$X$104,$U$104:$V$104,$I65)))*($I65<=$U$104)),0)","v":0},{"$f":"AC65*$J$104*$K$104","v":0},{"$f":"IF($I65>=$AA$104,$AE$104,IF($I65<=$Z$104,$AB$104,TREND($AD$104:$AE$104,$Z$104:$AA$104,$I65)))","v":0},{"$f":"IF($L$104<=90%,$L$104,MAX($Q$132,MIN($Q$124,TREND(OFFSET($P$123,MATCH(AE65,$P$124:$P$132,1),1,2,1),OFFSET($P$123,MATCH(AE65,$P$124:$P$132,1),0,2,1),AE65))))","v":0.99},{"$f":"IF($I65>=$AA$104,$AC$104,IF($I65<=$Z$104,$AB$104,TREND($AB$104:$AC$104,$Z$104:$AA$104,$I65)))","v":0},{"$f":"MAX($Q$132,MIN($Q$124,TREND(OFFSET($P$123,MATCH(AG65,$P$124:$P$132,1),1,2,1),OFFSET($P$123,MATCH(AG65,$P$124:$P$132,1),0,2,1),AG65)))","v":0.99},{"$f":"AD65/AF65","v":0},{"$f":"AD65/AH65","v":0},{"$f":"AI65-AJ65","v":0},0,{"$f":"IFERROR(IF($S$15<>$G$92,0,MAX(0,MIN(1,TREND($W$105:$X$105,$U$105:$V$105,$I65)))*($I65<=$U$105)),0)","v":0},{"$f":"AM65*$J$105*$K$105","v":0},{"$f":"IF($I65>=$AA$105,$AE$105,IF($I65<=$Z$105,$AB$105,TREND($AD$105:$AE$105,$Z$105:$AA$105,$I65)))","v":0},{"$f":"IF($L$105<=90%,$L$105,MAX($Q$132,MIN($Q$124,TREND(OFFSET($P$123,MATCH(AO65,$P$124:$P$132,1),1,2,1),OFFSET($P$123,MATCH(AO65,$P$124:$P$132,1),0,2,1),AO65))))","v":0.99},{"$f":"IF($I65>=$AA$105,$AC$105,IF($I65<=$Z$105,$AB$105,TREND($AB$105:$AC$105,$Z$105:$AA$105,$I65)))","v":0},{"$f":"MAX($Q$132,MIN($Q$124,TREND(OFFSET($P$123,MATCH(AQ65,$P$124:$P$132,1),1,2,1),OFFSET($P$123,MATCH(AQ65,$P$124:$P$132,1),0,2,1),AQ65)))","v":0.99},{"$f":"AN65/AP65","v":0},{"$f":"AN65/AR65","v":0},{"$f":"AS65-AT65","v":0},0,{"$f":"AA65+AK65+AU65","v":0},{"$f":"AB65+AL65+AV65","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A75","v":95},{"$f":"'Project Info'!B75","v":100},{"$f":"'Project Info'!C75","v":95.219272727272724},{"$f":"'Project Info'!D75","v":74.534025272781079},{"$f":"'Project Info'!E75","v":37.923296058061368},{"$f":"'Project Info'!F75","v":0},{"$f":"'Project Info'!G75","v":0},{"$f":"'Project Info'!H75","v":0},{"$f":"'Project Info'!I75","v":0},{"$f":"'Project Info'!J75","v":0},{"$f":"'Project Info'!K75","v":0},{"$f":"'Project Info'!L75","v":0},{"$f":"IFERROR(MAX(0,MIN(1,TREND($W$103:$X$103,$U$103:$V$103,$I66)))*($I66<=$U$103),0)","v":0},{"$f":"S66*$J$103*$K$103","v":0},{"$f":"IF($I66>=$AA$103,$AE$103,IF($I66<=$Z$103,$AB$103,TREND($AD$103:$AE$103,$Z$103:$AA$103,$I66)))","v":0},{"$f":"IF($L$103<90%,$L$103,MAX($Q$132,MIN($Q$124,TREND(OFFSET($P$123,MATCH(U66,$P$124:$P$132,1),1,2,1),OFFSET($P$123,MATCH(U66,$P$124:$P$132,1),0,2,1),U66))))","v":0.99},0,0.99,0,0,{"$f":"Y66-Z66","v":0},0,0,{"$f":"AC66*$J$104*$K$104","v":0},{"$f":"IF($I66>=$AA$104,$AE$104,IF($I66<=$Z$104,$AB$104,TREND($AD$104:$AE$104,$Z$104:$AA$104,$I66)))","v":0},{"$f":"IF($L$104<=90%,$L$104,MAX($Q$132,MIN($Q$124,TREND(OFFSET($P$123,MATCH(AE66,$P$124:$P$132,1),1,2,1),OFFSET($P$123,MATCH(AE66,$P$124:$P$132,1),0,2,1),AE66))))","v":0.99},0,0.99,0,0,{"$f":"AI66-AJ66","v":0},0,{"$f":"IFERROR(IF($S$15<>$G$92,0,MAX(0,MIN(1,TREND($W$105:$X$105,$U$105:$V$105,$I66)))*($I66<=$U$105)),0)","v":0},{"$f":"AM66*$J$105*$K$105","v":0},{"$f":"IF($I66>=$AA$105,$AE$105,IF($I66<=$Z$105,$AB$105,TREND($AD$105:$AE$105,$Z$105:$AA$105,$I66)))","v":0},{"$f":"IF($L$105<=90%,$L$105,MAX($Q$132,MIN($Q$124,TREND(OFFSET($P$123,MATCH(AO66,$P$124:$P$132,1),1,2,1),OFFSET($P$123,MATCH(AO66,$P$124:$P$132,1),0,2,1),AO66))))","v":0.99},0,0.99,0,0,{"$f":"AS66-AT66","v":0},0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A76","v":90},{"$f":"'Project Info'!B76","v":95},{"$f":"'Project Info'!C76","v":92.016049160256074},{"$f":"'Project Info'!D76","v":72.911561930607689},{"$f":"'Project Info'!E76","v":36.467095439351091},{"$f":"'Project Info'!F76","v":0},{"$f":"'Project Info'!G76","v":0},{"$f":"'Project Info'!H76","v":0},{"$f":"'Project Info'!I76","v":0},{"$f":"'Project Info'!J76","v":0},{"$f":"'Project Info'!K76","v":0},{"$f":"'Project Info'!L76","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A77","v":85},{"$f":"'Project Info'!B77","v":90},{"$f":"'Project Info'!C77","v":87.457811360655285},{"$f":"'Project Info'!D77","v":70.80538329449476},{"$f":"'Project Info'!E77","v":34.679413213566804},{"$f":"'Project Info'!F77","v":0},{"$f":"'Project Info'!G77","v":0},{"$f":"'Project Info'!H77","v":0},{"$f":"'Project Info'!I77","v":0},{"$f":"'Project Info'!J77","v":0},{"$f":"'Project Info'!K77","v":0},{"$f":"'Project Info'!L77","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A78","v":80},{"$f":"'Project Info'!B78","v":85},{"$f":"'Project Info'!C78","v":82.136788830239965},{"$f":"'Project Info'!D78","v":67.872393622439333},{"$f":"'Project Info'!E78","v":32.296248223809314},{"$f":"'Project Info'!F78","v":0},{"$f":"'Project Info'!G78","v":0},{"$f":"'Project Info'!H78","v":0},{"$f":"'Project Info'!I78","v":0},{"$f":"'Project Info'!J78","v":0},{"$f":"'Project Info'!K78","v":0},{"$f":"'Project Info'!L78","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A79","v":75},{"$f":"'Project Info'!B79","v":80},{"$f":"'Project Info'!C79","v":76.988400157585886},{"$f":"'Project Info'!D79","v":65.129261896908645},{"$f":"'Project Info'!E79","v":30.190476812806729},{"$f":"'Project Info'!F79","v":0},{"$f":"'Project Info'!G79","v":0},{"$f":"'Project Info'!H79","v":0},{"$f":"'Project Info'!I79","v":0},{"$f":"'Project Info'!J79","v":0},{"$f":"'Project Info'!K79","v":0},{"$f":"'Project Info'!L79","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A80","v":70},{"$f":"'Project Info'!B80","v":75},{"$f":"'Project Info'!C80","v":72.457982050814195},{"$f":"'Project Info'!D80","v":63.604425012889301},{"$f":"'Project Info'!E80","v":29.088683095945193},{"$f":"'Project Info'!F80","v":0},{"$f":"'Project Info'!G80","v":0},{"$f":"'Project Info'!H80","v":0},{"$f":"'Project Info'!I80","v":0},{"$f":"'Project Info'!J80","v":0},{"$f":"'Project Info'!K80","v":0},{"$f":"'Project Info'!L80","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A81","v":65},{"$f":"'Project Info'!B81","v":70},{"$f":"'Project Info'!C81","v":67.815831070966169},{"$f":"'Project Info'!D81","v":61.631331368130574},{"$f":"'Project Info'!E81","v":27.661514889731574},{"$f":"'Project Info'!F81","v":0},{"$f":"'Project Info'!G81","v":0},{"$f":"'Project Info'!H81","v":0},{"$f":"'Project Info'!I81","v":0},{"$f":"'Project Info'!J81","v":0},{"$f":"'Project Info'!K81","v":0},{"$f":"'Project Info'!L81","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A82","v":60},{"$f":"'Project Info'!B82","v":65},{"$f":"'Project Info'!C82","v":62.535961472271332},{"$f":"'Project Info'!D82","v":57.135476922863582},{"$f":"'Project Info'!E82","v":24.623037157728302},{"$f":"'Project Info'!F82","v":0},{"$f":"'Project Info'!G82","v":0},{"$f":"'Project Info'!H82","v":0},{"$f":"'Project Info'!I82","v":0},{"$f":"'Project Info'!J82","v":0},{"$f":"'Project Info'!K82","v":0},{"$f":"'Project Info'!L82","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A83","v":55},{"$f":"'Project Info'!B83","v":60},{"$f":"'Project Info'!C83","v":57.125792270740902},{"$f":"'Project Info'!D83","v":52.596971157053673},{"$f":"'Project Info'!E83","v":21.818001539159841},{"$f":"'Project Info'!F83","v":0},{"$f":"'Project Info'!G83","v":0},{"$f":"'Project Info'!H83","v":0},{"$f":"'Project Info'!I83","v":0},{"$f":"'Project Info'!J83","v":0},{"$f":"'Project Info'!K83","v":0},{"$f":"'Project Info'!L83","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A84","v":50},{"$f":"'Project Info'!B84","v":55},{"$f":"'Project Info'!C84","v":52.235698854337961},{"$f":"'Project Info'!D84","v":48.022768090099298},{"$f":"'Project Info'!E84","v":19.246640192796217},{"$f":"'Project Info'!F84","v":0},{"$f":"'Project Info'!G84","v":0},{"$f":"'Project Info'!H84","v":0},{"$f":"'Project Info'!I84","v":0},{"$f":"'Project Info'!J84","v":0},{"$f":"'Project Info'!K84","v":0},{"$f":"'Project Info'!L84","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A85","v":45},{"$f":"'Project Info'!B85","v":50},{"$f":"'Project Info'!C85","v":47.459170258371508},{"$f":"'Project Info'!D85","v":43.465397050422162},{"$f":"'Project Info'!E85","v":16.894183241713304},{"$f":"'Project Info'!F85","v":0},{"$f":"'Project Info'!G85","v":0},{"$f":"'Project Info'!H85","v":0},{"$f":"'Project Info'!I85","v":0},{"$f":"'Project Info'!J85","v":0},{"$f":"'Project Info'!K85","v":0},{"$f":"'Project Info'!L85","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A86","v":40},{"$f":"'Project Info'!B86","v":45},{"$f":"'Project Info'!C86","v":42.677030404888129},{"$f":"'Project Info'!D86","v":38.812544504634097},{"$f":"'Project Info'!E86","v":14.690265649465921},{"$f":"'Project Info'!F86","v":0},{"$f":"'Project Info'!G86","v":0},{"$f":"'Project Info'!H86","v":0},{"$f":"'Project Info'!I86","v":0},{"$f":"'Project Info'!J86","v":0},{"$f":"'Project Info'!K86","v":0},{"$f":"'Project Info'!L86","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A87","v":35},{"$f":"'Project Info'!B87","v":40},{"$f":"'Project Info'!C87","v":37.333046773755832},{"$f":"'Project Info'!D87","v":33.904706919479686},{"$f":"'Project Info'!E87","v":12.53841602318813},{"$f":"'Project Info'!F87","v":0},{"$f":"'Project Info'!G87","v":0},{"$f":"'Project Info'!H87","v":0},{"$f":"'Project Info'!I87","v":0},{"$f":"'Project Info'!J87","v":0},{"$f":"'Project Info'!K87","v":0},{"$f":"'Project Info'!L87","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A88","v":30},{"$f":"'Project Info'!B88","v":35},{"$f":"'Project Info'!C88","v":32.638179845662044},{"$f":"'Project Info'!D88","v":29.547170928664851},{"$f":"'Project Info'!E88","v":10.728972818165861},{"$f":"'Project Info'!F88","v":0},{"$f":"'Project Info'!G88","v":0},{"$f":"'Project Info'!H88","v":0},{"$f":"'Project Info'!I88","v":0},{"$f":"'Project Info'!J88","v":0},{"$f":"'Project Info'!K88","v":0},{"$f":"'Project Info'!L88","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A89","v":25},{"$f":"'Project Info'!B89","v":30},{"$f":"'Project Info'!C89","v":27.529264646850947},{"$f":"'Project Info'!D89","v":24.652717392657845},{"$f":"'Project Info'!E89","v":8.8041305482613303},{"$f":"'Project Info'!F89","v":0},{"$f":"'Project Info'!G89","v":0},{"$f":"'Project Info'!H89","v":0},{"$f":"'Project Info'!I89","v":0},{"$f":"'Project Info'!J89","v":0},{"$f":"'Project Info'!K89","v":0},{"$f":"'Project Info'!L89","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A90","v":20},{"$f":"'Project Info'!B90","v":25},{"$f":"'Project Info'!C90","v":22.998111483544687},{"$f":"'Project Info'!D90","v":20.383306659827422},{"$f":"'Project Info'!E90","v":7.246164547543378},{"$f":"'Project Info'!F90","v":0},{"$f":"'Project Info'!G90","v":0},{"$f":"'Project Info'!H90","v":0},{"$f":"'Project Info'!I90","v":0},{"$f":"'Project Info'!J90","v":0},{"$f":"'Project Info'!K90","v":0},{"$f":"'Project Info'!L90","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A91","v":15},{"$f":"'Project Info'!B91","v":20},{"$f":"'Project Info'!C91","v":17.808510327474309},{"$f":"'Project Info'!D91","v":15.420865796304254},{"$f":"'Project Info'!E91","v":5.5490484131518292},{"$f":"'Project Info'!F91","v":0},{"$f":"'Project Info'!G91","v":0},{"$f":"'Project Info'!H91","v":0},{"$f":"'Project Info'!I91","v":0},{"$f":"'Project Info'!J91","v":0},{"$f":"'Project Info'!K91","v":0},{"$f":"'Project Info'!L91","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A92","v":10},{"$f":"'Project Info'!B92","v":15},{"$f":"'Project Info'!C92","v":12.269931130346862},{"$f":"'Project Info'!D92","v":10.318264913023604},{"$f":"'Project Info'!E92","v":3.9082824916941998},{"$f":"'Project Info'!F92","v":0},{"$f":"'Project Info'!G92","v":0},{"$f":"'Project Info'!H92","v":0},{"$f":"'Project Info'!I92","v":0},{"$f":"'Project Info'!J92","v":0},{"$f":"'Project Info'!K92","v":0},{"$f":"'Project Info'!L92","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A93","v":5},{"$f":"'Project Info'!B93","v":10},{"$f":"'Project Info'!C93","v":7.3137581369917548},{"$f":"'Project Info'!D93","v":5.7052382449247707},{"$f":"'Project Info'!E93","v":2.5019418419888937},{"$f":"'Project Info'!F93","v":0},{"$f":"'Project Info'!G93","v":0},{"$f":"'Project Info'!H93","v":0},{"$f":"'Project Info'!I93","v":0},{"$f":"'Project Info'!J93","v":0},{"$f":"'Project Info'!K93","v":0},{"$f":"'Project Info'!L93","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A94","v":0},{"$f":"'Project Info'!B94","v":5},{"$f":"'Project Info'!C94","v":2.6119461836144886},{"$f":"'Project Info'!D94","v":1.2699770062067783},{"$f":"'Project Info'!E94","v":1.2046477897733283},{"$f":"'Project Info'!F94","v":8760},{"$f":"'Project Info'!G94","v":2672},{"$f":"'Project Info'!H94","v":3160},{"$f":"'Project Info'!I94","v":1344},{"$f":"'Project Info'!J94","v":1584},{"$f":"'Project Info'!K94","v":88},{"$f":"'Project Info'!L94","v":264},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A95","v":-5},{"$f":"'Project Info'!B95","v":0},{"$f":"'Project Info'!C95","v":-1.6731398516793925},{"$f":"'Project Info'!D95","v":-2.7083318773557807},{"$f":"'Project Info'!E95","v":7.9391832815876459E-2},{"$f":"'Project Info'!F95","v":0},{"$f":"'Project Info'!G95","v":0},{"$f":"'Project Info'!H95","v":0},{"$f":"'Project Info'!I95","v":0},{"$f":"'Project Info'!J95","v":0},{"$f":"'Project Info'!K95","v":0},{"$f":"'Project Info'!L95","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A96","v":-10},{"$f":"'Project Info'!B96","v":-5},{"$f":"'Project Info'!C96","v":-6.5729865085377277},{"$f":"'Project Info'!D96","v":-7.2465935998252222},{"$f":"'Project Info'!E96","v":-1.168423365310433},{"$f":"'Project Info'!F96","v":0},{"$f":"'Project Info'!G96","v":0},{"$f":"'Project Info'!H96","v":0},{"$f":"'Project Info'!I96","v":0},{"$f":"'Project Info'!J96","v":0},{"$f":"'Project Info'!K96","v":0},{"$f":"'Project Info'!L96","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A97","v":-15},{"$f":"'Project Info'!B97","v":-10},{"$f":"'Project Info'!C97","v":-15.32570353422995},{"$f":"'Project Info'!D97","v":-15.707838211108999},{"$f":"'Project Info'!E97","v":-3.4051318156661381},{"$f":"'Project Info'!F97","v":0},{"$f":"'Project Info'!G97","v":0},{"$f":"'Project Info'!H97","v":0},{"$f":"'Project Info'!I97","v":0},{"$f":"'Project Info'!J97","v":0},{"$f":"'Project Info'!K97","v":0},{"$f":"'Project Info'!L97","v":0},0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0,0,0.99,0,0.99,0,0,0,0,0,0]
[]
[null,null,null,null,null,null,"Added Systems Included?",null,null,null,null,"Boiler Plant Heating Load Profile"]
[null,null,null,null,null,null,"No",null,null,null,null,"Occupied Profile",null,null,null,"Unocc Profile"]
[null,null,null,null,null,null,"Yes",null,null,null,null,"Max OAT","Min OAT","% Load @","%Load @","Max OAT","Min OAT","% Load @","%Load @"]
[null,null,null,null,null,null,null,null,null,"System Load Profile",null,"°F","°F","Max OAT","Min OAT","°F","°F","Max OAT","Min OAT"]
[null,null,null,null,null,null,"Incentive Type",null,null,"1-HVAC/Comfort",null,60,0,0.1,1,60,0,0,0.5]
[null,null,null,null,null,null,"Custom",null,null,"2-Constant/Process",null,110,-10,1,1,110,-10,1,1]
[null,null,null,null,null,null,"Prescriptive",null,null,"3-Snow Melt",null,40,-10,0.5,1,40,-10,0.5,1]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Modeled System Heating Load Profiles based on User Inputs and System Type Profiles"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Occupied Profile",null,null,null,"Unocc Profile",null,null,null,null,"HW Reset Schedules",null,null,null,null,null,"Annual","Custom","Prescr.",null,null,"Modeled","Tiered Incent"]
[null,null,null,null,null,null,null,null,"Boiler","Max Boilers","Per Boiler","Base","Peak Plant Load",null,null,null,"Max OAT","Min OAT","% Load @","%Load @","Max OAT","Min OAT","% Load @","%Load @","Heating","Min","Max","Max","Prop. Min","Base Max","Base Min","Savings","Incentive","Incentive","Incr.",null,"Avg. Boiler","if Boilers"]
[null,null,null,null,null,null,null,"Included?","Quantity","Operating","MBH","Efficiency","%","MBH","System Load Profile",null,"°F","°F","Max OAT","Min OAT","°F","°F","Max OAT","Min OAT","EFLH","OAT","OAT","HW Ret","HW Ret","HW Ret","HW Ret",{"$f":"D20","v":{"$error":"#N/A"}},"$","$","Cost",null,"Eff (%)","< 300 MBH"]
[null,null,null,null,null,null,"System 1",1,{"$f":"N17","v":0},{"$f":"IF($N$19=\"\",$O$19,$N$19)","v":0},{"$f":"N18","v":0},{"$f":"IF(K103<$H$110,$L$110,IF(K103<=$H$111,$L$111,$L$112))","v":0.92},{"$f":"IF(N20=\"\",O20,N20)","v":0.85},{"$f":"J103*K103*M103","v":0},{"$f":"N16","v":0},null,{"$f":"LOOKUP($O103,$J$94:$J$96,$L$94:$L$96)","v":{"$error":"#N/A"}},{"$f":"LOOKUP($O103,$J$94:$J$96,$M$94:$M$96)","v":{"$error":"#N/A"}},{"$f":"M103*LOOKUP($O103,$J$94:$J$96,$N$94:$N$96)","v":{"$error":"#N/A"}},{"$f":"M103*LOOKUP($O103,$J$94:$J$96,$O$94:$O$96)","v":{"$error":"#N/A"}},{"$f":"LOOKUP($O103,$J$94:$J$96,$P$94:$P$96)","v":{"$error":"#N/A"}},{"$f":"LOOKUP($O103,$J$94:$J$96,$Q$94:$Q$96)","v":{"$error":"#N/A"}},{"$f":"M103*LOOKUP($O103,$J$94:$J$96,$R$94:$R$96)","v":{"$error":"#N/A"}},{"$f":"M103*LOOKUP($O103,$J$94:$J$96,$S$94:$S$96)","v":{"$error":"#N/A"}},{"$f":"IFERROR((SUMPRODUCT($L$35:$L$58,T35:T58)+SUMPRODUCT($L$65:$L$88,T65:T88))/(J103*K103),0)","v":0},{"$f":"N25","v":0},{"$f":"N26","v":0},{"$f":"O25-N22","v":0},{"$f":"O26-N22","v":0},{"$f":"AB103","v":0},{"$f":"AB103-0.25*$N$22","v":0},{"$f":"(SUMPRODUCT($L$35:$L$58,AA35:AA58)+SUMPRODUCT($L$65:$L$88,AA65:AA88))/1000*$C$28","v":{"$error":"#N/A"}},{"$f":"AF103*$C$25","v":{"$error":"#N/A"}},{"$f":"IF(K103<=$U$115,J103*AL103,IF(K103>$U$111,MAX(J103*$V$110,AG103),J103*OFFSET($U$109,MATCH(K103,$U$110:$U$115,-1),1)))","v":0},{"$f":"I103*K103*H103*$J$121","v":0},null,{"$f":"IFERROR((SUMPRODUCT($X$35:$X$58,$S$35:$S$58,$L$35:$L$58)+SUMPRODUCT($X$65:$X$88,$S$65:$S$88,$L$65:$L$88))/(SUMPRODUCT($L$35:$L$58,$S$35:$S$58)+SUMPRODUCT($L$65:$L$88,$S$65:$S$88)),0)","v":0},{"$f":"IF(AK103>=$W$116,$V$116,$V$115)","v":1000}]
[null,null,null,null,null,null,"System 2",{"$f":"1*(Q15=\"Yes\")","v":0},{"$f":"P17*H104","v":0},{"$f":"IF($P$19=\"\",$Q$19,$P$19)*H104","v":0},{"$f":"P18*H104","v":0},{"$f":"IF(K104<$H$110,$L$110,IF(K104<=$H$111,$L$111,$L$112))","v":0.92},{"$f":"IF(P20=\"\",Q20,P20)*H104","v":0},{"$f":"J104*K104*M104","v":0},{"$f":"P16","v":0},null,{"$f":"LOOKUP($O104,$J$94:$J$96,$L$94:$L$96)","v":{"$error":"#N/A"}},{"$f":"LOOKUP($O104,$J$94:$J$96,$M$94:$M$96)","v":{"$error":"#N/A"}},{"$f":"M104*LOOKUP($O104,$J$94:$J$96,$N$94:$N$96)","v":{"$error":"#N/A"}},{"$f":"M104*LOOKUP($O104,$J$94:$J$96,$O$94:$O$96)","v":{"$error":"#N/A"}},{"$f":"LOOKUP($O104,$J$94:$J$96,$P$94:$P$96)","v":{"$error":"#N/A"}},{"$f":"LOOKUP($O104,$J$94:$J$96,$Q$94:$Q$96)","v":{"$error":"#N/A"}},{"$f":"M104*LOOKUP($O104,$J$94:$J$96,$R$94:$R$96)","v":{"$error":"#N/A"}},{"$f":"M104*LOOKUP($O104,$J$94:$J$96,$S$94:$S$96)","v":{"$error":"#N/A"}},{"$f":"IFERROR((SUMPRODUCT($L$35:$L$58,$AD$35:$AD$58)+SUMPRODUCT($L$65:$L$88,$AD$65:$AD$88))/(J104*K104),0)","v":0},{"$f":"P25","v":0},{"$f":"P26","v":0},{"$f":"Q25-P22","v":0},{"$f":"Q26-P22","v":0},{"$f":"AB104","v":0},{"$f":"AB104-0.25*$P$22","v":0},{"$f":"(SUMPRODUCT($L$35:$L$58,AK35:AK58)+SUMPRODUCT($L$65:$L$88,AK65:AK88))/1000*$C$28","v":{"$error":"#N/A"}},{"$f":"AF104*$C$25","v":{"$error":"#N/A"}},{"$f":"IF(K104<=$U$115,J104*AL104,IF(K104>$U$111,MAX(J104*$V$110,AG104),J104*OFFSET($U$109,MATCH(K104,$U$110:$U$115,-1),1)))","v":0},{"$f":"I104*K104*H104*$J$121","v":0},null,{"$f":"IFERROR((SUMPRODUCT($AH$35:$AH$58,$AC$35:$AC$58,$L$35:$L$58)+SUMPRODUCT($AH$65:$AH$88,$AC$65:$AC$88,$L$65:$L$88))/(SUMPRODUCT($L$35:$L$58,$AC$35:$AC$58)+SUMPRODUCT($L$65:$L$88,$AC$65:$AC$88)),0)","v":0},{"$f":"IF(AK104>=$W$116,$V$116,$V$115)","v":1000}]
[null,null,null,null,null,null,"System 3",{"$f":"1*(S15=\"Yes\")","v":0},{"$f":"R17*H105","v":0},{"$f":"IF($R$19=\"\",$S$19,$R$19)*H105","v":0},{"$f":"R18*H105","v":0},0.92,{"$f":"IF(R20=\"\",S20,R20)*H105","v":0},{"$f":"J105*K105*M105","v":0},{"$f":"R16","v":0},null,{"$f":"LOOKUP($O105,$J$94:$J$96,$L$94:$L$96)","v":{"$error":"#N/A"}},{"$f":"LOOKUP($O105,$J$94:$J$96,$M$94:$M$96)","v":{"$error":"#N/A"}},{"$f":"M105*LOOKUP($O105,$J$94:$J$96,$N$94:$N$96)","v":{"$error":"#N/A"}},{"$f":"M105*LOOKUP($O105,$J$94:$J$96,$O$94:$O$96)","v":{"$error":"#N/A"}},{"$f":"LOOKUP($O105,$J$94:$J$96,$P$94:$P$96)","v":{"$error":"#N/A"}},{"$f":"LOOKUP($O105,$J$94:$J$96,$Q$94:$Q$96)","v":{"$error":"#N/A"}},{"$f":"M105*LOOKUP($O105,$J$94:$J$96,$R$94:$R$96)","v":{"$error":"#N/A"}},{"$f":"M105*LOOKUP($O105,$J$94:$J$96,$S$94:$S$96)","v":{"$error":"#N/A"}},{"$f":"IFERROR((SUMPRODUCT($L$35:$L$58,$AN$35:$AN$58)+SUMPRODUCT($L$65:$L$88,$AN$65:$AN$88))/(J105*K105),0)","v":0},{"$f":"R25","v":0},{"$f":"R26","v":0},{"$f":"S25-R22","v":0},{"$f":"S26-R22","v":0},0,{"$f":"AB105-0.25*$R$22","v":0},{"$f":"(SUMPRODUCT($L$35:$L$58,AU35:AU58)+SUMPRODUCT($L$65:$L$88,AU65:AU88))/1000*$C$28","v":{"$error":"#N/A"}},{"$f":"AF105*$C$25","v":{"$error":"#N/A"}},{"$f":"IF(K105<=$U$115,J105*AL105,IF(K105>$U$111,MAX(J105*$V$110,AG105),J105*OFFSET($U$109,MATCH(K105,$U$110:$U$115,-1),1)))","v":0},{"$f":"I105*K105*H105*$J$121","v":0},null,{"$f":"IFERROR((SUMPRODUCT($AR$35:$AR$58,$AM$35:$AM$58,$L$35:$L$58)+SUMPRODUCT($AR$65:$AR$88,$AM$65:$AM$88,$L$65:$L$88))/(SUMPRODUCT($L$35:$L$58,$AM$35:$AM$58)+SUMPRODUCT($L$65:$L$88,$AM$65:$AM$88)),0)","v":0},{"$f":"IF(AK105>=$W$116,$V$116,$V$115)","v":1000}]
[]
[null,null,null,null,null,null,"Baseline Boiler Efficiency by Capacity",null,null,null,null,null,null,null,null,null,null,null,null,"Project Incentive Rate"]
[null,null,null,null,null,null,"Input",null,"Rated","Existing Building","New Construction","Current Project",null,null,null,"HW Reset",null,null,null,"Capacity Range (MBH)",null,"NH"]
[null,null,null,null,null,null,"MBH",null,"Ec","Et","Et","Et",null,null,null,"OAT","Prop Return","Base Return",null,"Min","Max","Incentive"]
[null,null,null,null,null,null,"<",300,null,0.82,0.92,{"$f":"IF($L$10=$J$108,J110,K110)","v":0.92},null,null,null,"°F","°F","°F",null,2001,100000,10000]
[null,null,null,null,null,null,"≤",2500,null,0.8,0.92,{"$f":"IF($L$10=$J$108,J111,K111)","v":0.92},null,null,null,{"$f":"N25","v":0},{"$f":"O25-$N$22","v":0},{"$f":"O25-$N$22","v":0},null,1701,2000,10000]
[null,null,null,null,null,null,">",2500,0.82,0.8,0.8,0.8,null,null,null,{"$f":"N26","v":0},{"$f":"O26-$N$22","v":0},{"$f":"R111-0.25*$N$22","v":0},null,1000,1700,7500]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,500,999,4000]
[null,null,null,null,null,null,"Incremental Cost Estimates",null,null,null,null,null,null,null,null,"Annual EFLH Modeled",null,null,null,301,499,2000]
[null,null,null,null,null,null,"Incremental Cost Estimate - per vendor budget pricing",null,null,null,null,null,null,null,null,"System 1",{"$f":"SUMPRODUCT(S35:S58,L35:L58)+SUMPRODUCT(S65:S88,L65:L88)","v":0},null,null,0,300,1000,0.9,"<Min AFUE for this Tier incentive when boilers are ≤ 300 MBH"]
[null,null,null,null,null,null,null,null,"MBH","$",null,null,null,null,null,"System 2",{"$f":"SUMPRODUCT(AC35:AC58,L35:L58)+SUMPRODUCT(AC65:AC88,L65:L88)","v":0},null,null,0,300,1500,0.95,"<Min AFUE for this Tier incentive when boilers are ≤ 300 MBH"]
[null,null,null,null,null,null,"Burnham 85% Eff",null,3000,16000,null,null,null,null,null,"System 3",{"$f":"SUMPRODUCT(AM35:AM58,L35:L58)+SUMPRODUCT(AM65:AM88,L65:L88)","v":0}]
[null,null,null,null,null,null,"Burnham 95% Eff",null,3000,47000,null,null,null,null,null,null,null,null,null,"Two Incentive Levels for Boilers up to 300 MBH"]
[null,null,null,null,null,null,"Incremental Cost",null,null,{"$f":"J118-J117","v":31000},null,null,null,null,null,"Boiler Efficiency",null,null,null,"Efficiency (AFUE)",null,"NH"]
[null,null,null,null,null,null,"Incremental Cost w O&P 20%",null,null,{"$f":"J119*1.2","v":37200},null,null,null,null,null,"vs. HW Return Temp",null,null,null,"AFUE ≥",0.9,1000]
[null,null,null,null,null,null,"Incremental Cost/MBH",null,null,{"$f":"J120/I117","v":12.4},null,null,null,null,null,"Return","Cond Blr","Std Blr",null,"AFUE ≥",0.95,1500]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Water ","Eff","Eff"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"°F","%","%"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,0.99,{"$f":"$L$103","v":0.92}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,60,0.99,0.92]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,80,0.97499999999999998,0.92]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,100,0.95,0.92]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,120,0.91,0.92]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,140,0.87,0.92]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,150,0.86,0.92]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,160,0.86,0.92]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,186,0.85,0.92]

{"sheet":"DHW Heaters","index":18,"n_rows":150,"n_cols":25,"rows_kept":150,"cut":false,"hidden":true,"merged":[[14,13,14,14],[15,13,15,14],[22,13,22,14],[1,19,11,27],[1,10,4,17]]}
["Savings Summary",null,null,null,null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,null,null,"Notes (Optional)"]
["Annual kWh Savings",null,null,{"$f":"SUM(A14:D14)","v":0},null,null,null,"Value","Unit",null,"This measure considers savings from installing high performance domestic hot water heaters that exceed the baseline efficiency requirements.  Two types of DHW heaters are considered for savings: gas-fired condensing heaters or electric heat pump heaters."]
["% On Peak",null,null,{"$f":"IF(D2<=0,0,MIN(1,A15+C15))","v":0},null,"Annual Electric Savings",null,{"$f":"D2","v":0},"kWh"]
["Max kW",null,null,{"$f":"MAX(Y33:Y56,Y63:Y86)","v":0},null,"Annual Fuel Savings",null,{"$f":"D7*C28","v":{"$error":"#N/A"}},{"$f":"D20","v":{"$error":"#N/A"}}]
["Summer kW",null,null,{"$f":"(SUMPRODUCT(Y33:Y56,R33:R56)+SUMPRODUCT(Y63:Y86,R63:R86))/SUM(R33:R56,R63:R86)","v":0},null,"Incremental","Default Calc",{"$f":"$V$105*$N$17*$N$19","v":0},"$"]
["Winter kW",null,null,{"$f":"(SUMPRODUCT(Y33:Y56,Q33:Q56)+SUMPRODUCT(Y63:Y86,Q63:Q86))/SUM(Q33:Q56,Q63:Q86)","v":0},null,"Cost","Project Specific",null,"$ (Optional)"]
["Annual Fuel Savings (MMBtu)",null,null,{"$f":"(SUMPRODUCT($L$33:$L$56,$X$33:$X$56)+SUMPRODUCT($L$63:$L$86,$X$63:$X$86))/1000","v":0},null,"Estimated Incentive",null,{"$f":"IF(AND($C$24>=0,$C$25>=0),MAX(0,H3)*C24+MAX(0,H4)*C25,\"TBD\")","v":{"$error":"#N/A"}},"$"]
["Incremental Cost (Default Calc)",null,null,{"$f":"$V$105*$N$17*$N$19","v":0}]
["Incremental Cost (for Summary)",null,null,{"$f":"IF(H6>0,H6,D8)","v":0},null,"Project Information Summary"]
["kWh Savings by Peak Period",null,null,null,null,null,"STATE",{"$f":"'Project Info'!C15","v":"NH"}]
["Winter","Winter","Summer","Summer",null,null,"Program Year",{"$f":"'Project Info'!C19","v":0}]
["On-Peak","Off-Peak","On-Peak","Off-Peak",null,null,"Code IECC Version",{"$f":"MID('Project Info'!C20,1,4)","v":"2018"}]
["kWh","kWh","kWh","kWh",null,null,"Electric PA",{"$f":"'Project Info'!F3","v":0}]
[{"$f":"SUMPRODUCT(M33:M56,$Y$33:$Y$56)+SUMPRODUCT(M63:M86,$Y$63:$Y$86)","v":0},{"$f":"SUMPRODUCT(N33:N56,$Y$33:$Y$56)+SUMPRODUCT(N63:N86,$Y$63:$Y$86)","v":0},{"$f":"SUMPRODUCT(O33:O56,$Y$33:$Y$56)+SUMPRODUCT(O63:O86,$Y$63:$Y$86)","v":0},{"$f":"SUMPRODUCT(P33:P56,$Y$33:$Y$56)+SUMPRODUCT(P63:P86,$Y$63:$Y$86)","v":0},null,null,"Gas PA",{"$f":"'Project Info'!I3","v":0},null,null,"Table 1: Hot Water Heater Parameters",null,null,null,null,null,"Building Avg. Daily DHW Consumption"]
[{"$f":"ROUND(IF(A14<=0,0,A14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(B14<=0,0,B14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(C14<=0,0,C14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"IF(SUM(A14:D14)=0,0,1-SUM(A15:C15))","v":0},null,"Building Type",null,{"$f":"'Project Info'!C18","v":0},null,null,"Water Heater Type",null,null,null,null,null,"Building Type",null,null,{"$f":"H15","v":0}]
[null,null,null,null,null,"Building Area (ft²)",null,{"$f":"'Project Info'!C17","v":0},null,null,"Storage Type",null,null,null,null,null,"Estimated DHW gallons/day per ft²",null,null,{"$f":"LOOKUP($H$15,$G$92:$G$133,$M$92:$M$133)","v":{"$error":"#N/A"}}]
["Utility Rates",null,null,null,null,"*NOTE: Baseline values are automated and cannot be changed.",null,null,null,null,"Capacity, MBH (per heater)",null,null,null,null,null,"DHW gallons per day - Calculated",null,null,{"$f":"T16*H16","v":{"$error":"#N/A"}}]
[null,null,"Rate","Unit",null,null,null,null,null,null,"Storage, gallons (per heater)",null,null,null,null,null,"DHW gallons per day - Optional Override"]
["Electric",null,{"$f":"'ECM Summary'!$E$31","v":0.1593},"kWh",null,null,null,null,null,null,"Heater Quantity"]
[{"$f":"'ECM Summary'!$C$32","v":0},null,{"$f":"'ECM Summary'!$E$32","v":{"$error":"#N/A"}},{"$f":"'ECM Summary'!$F$32","v":{"$error":"#N/A"}},null,null,null,null,null,null,null,null,null,{"$f":"IFERROR(IF(N15=$O$96,VLOOKUP($N$16,$P$91:$R$93,3,FALSE),\"\"),\"\")","v":""},"COP (Elec)"]
[null,null,null,null,null,null,null,null,null,null,"Proposed Rated Performance",null,null,0.85,2.2000000000000002]
["Custom Incentive Rates",null,null,null,null,null,null,null,null,null,"Base Performance",null,null,{"$f":"IFERROR(IF(N15=$O$96,VLOOKUP($N$16,$P$91:$Q$93,2,FALSE),\"\"),\"\")","v":""},{"$f":"IF(N15=$O$97,OFFSET($T$91,MATCH(N18,$T$92:$T$94,1),1),\"\")","v":""}]
[null,null,"Rate","Unit",null,null,null,null,null,null,"Manufacturer & Model (Optional)"]
["Electric",null,{"$f":"'ECM Summary'!$J$31","v":0.28000000000000003},"kWh"]
[{"$f":"'ECM Summary'!$H$32","v":0},null,{"$f":"'ECM Summary'!$J$32","v":0},{"$f":"'ECM Summary'!$K$32","v":{"$error":"#N/A"}}]
[]
["Fossil Fuel",null,{"$f":"'Project Info'!C21","v":0}]
["Fuel Conversion",null,{"$f":"LOOKUP(C27,'Project Info'!X102:X104,'Project Info'!Z102:Z104)","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,"Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown",null,null,null,null,null,null,null,{"$f":"(SUMPRODUCT($L$33:$L$56,T33:T56)+SUMPRODUCT($L$63:$L$86,T63:T86))/100","v":0},{"$f":"(SUMPRODUCT($L$33:$L$56,U33:U56)+SUMPRODUCT($L$63:$L$86,U63:U86))/100","v":0}]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","DHW"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Load","Base","Proposed","Base","Proposed","Demand Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","MBH","MBH","MBH","kW","kW","MBH","kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A44","v":100},{"$f":"'Project Info'!B44","v":105},{"$f":"'Project Info'!C44","v":102},{"$f":"'Project Info'!D44","v":76},{"$f":"'Project Info'!E44","v":40},{"$f":"'Project Info'!F44","v":0},{"$f":"'Project Info'!G44","v":0},{"$f":"'Project Info'!H44","v":0},{"$f":"'Project Info'!I44","v":0},{"$f":"'Project Info'!J44","v":0},{"$f":"'Project Info'!K44","v":0},{"$f":"'Project Info'!L44","v":0},{"$f":"$R$117+$W$116/1000","v":{"$error":"#N/A"}},{"$f":"IF($N$15=$O$96,S33/$N$22,0)","v":0},{"$f":"IF($N$15=$O$96,S33/$N$21,0)","v":0},{"$f":"IF($N$15=$O$97,S33/$O$22/3.412,0)","v":0},{"$f":"IF($N$15=$O$97,S33/$O$21/3.412,0)","v":0},{"$f":"(T33-U33)","v":0},{"$f":"(V33-W33)","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A45","v":95},{"$f":"'Project Info'!B45","v":100},{"$f":"'Project Info'!C45","v":95.219272727272724},{"$f":"'Project Info'!D45","v":74.534025272781079},{"$f":"'Project Info'!E45","v":37.923296058061368},{"$f":"'Project Info'!F45","v":0},{"$f":"'Project Info'!G45","v":0},{"$f":"'Project Info'!H45","v":0},{"$f":"'Project Info'!I45","v":0},{"$f":"'Project Info'!J45","v":0},{"$f":"'Project Info'!K45","v":0},{"$f":"'Project Info'!L45","v":0},{"$error":"#N/A"},0,0,0,0,{"$f":"(T34-U34)","v":0},{"$f":"(V34-W34)","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A46","v":90},{"$f":"'Project Info'!B46","v":95},{"$f":"'Project Info'!C46","v":92.016049160256074},{"$f":"'Project Info'!D46","v":72.911561930607689},{"$f":"'Project Info'!E46","v":36.467095439351091},{"$f":"'Project Info'!F46","v":0},{"$f":"'Project Info'!G46","v":0},{"$f":"'Project Info'!H46","v":0},{"$f":"'Project Info'!I46","v":0},{"$f":"'Project Info'!J46","v":0},{"$f":"'Project Info'!K46","v":0},{"$f":"'Project Info'!L46","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A47","v":85},{"$f":"'Project Info'!B47","v":90},{"$f":"'Project Info'!C47","v":87.457811360655285},{"$f":"'Project Info'!D47","v":70.80538329449476},{"$f":"'Project Info'!E47","v":34.679413213566804},{"$f":"'Project Info'!F47","v":0},{"$f":"'Project Info'!G47","v":0},{"$f":"'Project Info'!H47","v":0},{"$f":"'Project Info'!I47","v":0},{"$f":"'Project Info'!J47","v":0},{"$f":"'Project Info'!K47","v":0},{"$f":"'Project Info'!L47","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A48","v":80},{"$f":"'Project Info'!B48","v":85},{"$f":"'Project Info'!C48","v":82.136788830239965},{"$f":"'Project Info'!D48","v":67.872393622439333},{"$f":"'Project Info'!E48","v":32.296248223809314},{"$f":"'Project Info'!F48","v":0},{"$f":"'Project Info'!G48","v":0},{"$f":"'Project Info'!H48","v":0},{"$f":"'Project Info'!I48","v":0},{"$f":"'Project Info'!J48","v":0},{"$f":"'Project Info'!K48","v":0},{"$f":"'Project Info'!L48","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A49","v":75},{"$f":"'Project Info'!B49","v":80},{"$f":"'Project Info'!C49","v":76.988400157585886},{"$f":"'Project Info'!D49","v":65.129261896908645},{"$f":"'Project Info'!E49","v":30.190476812806729},{"$f":"'Project Info'!F49","v":0},{"$f":"'Project Info'!G49","v":0},{"$f":"'Project Info'!H49","v":0},{"$f":"'Project Info'!I49","v":0},{"$f":"'Project Info'!J49","v":0},{"$f":"'Project Info'!K49","v":0},{"$f":"'Project Info'!L49","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A50","v":70},{"$f":"'Project Info'!B50","v":75},{"$f":"'Project Info'!C50","v":72.457982050814195},{"$f":"'Project Info'!D50","v":63.604425012889301},{"$f":"'Project Info'!E50","v":29.088683095945193},{"$f":"'Project Info'!F50","v":0},{"$f":"'Project Info'!G50","v":0},{"$f":"'Project Info'!H50","v":0},{"$f":"'Project Info'!I50","v":0},{"$f":"'Project Info'!J50","v":0},{"$f":"'Project Info'!K50","v":0},{"$f":"'Project Info'!L50","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A51","v":65},{"$f":"'Project Info'!B51","v":70},{"$f":"'Project Info'!C51","v":67.815831070966169},{"$f":"'Project Info'!D51","v":61.631331368130574},{"$f":"'Project Info'!E51","v":27.661514889731574},{"$f":"'Project Info'!F51","v":0},{"$f":"'Project Info'!G51","v":0},{"$f":"'Project Info'!H51","v":0},{"$f":"'Project Info'!I51","v":0},{"$f":"'Project Info'!J51","v":0},{"$f":"'Project Info'!K51","v":0},{"$f":"'Project Info'!L51","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A52","v":60},{"$f":"'Project Info'!B52","v":65},{"$f":"'Project Info'!C52","v":62.535961472271332},{"$f":"'Project Info'!D52","v":57.135476922863582},{"$f":"'Project Info'!E52","v":24.623037157728302},{"$f":"'Project Info'!F52","v":0},{"$f":"'Project Info'!G52","v":0},{"$f":"'Project Info'!H52","v":0},{"$f":"'Project Info'!I52","v":0},{"$f":"'Project Info'!J52","v":0},{"$f":"'Project Info'!K52","v":0},{"$f":"'Project Info'!L52","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A53","v":55},{"$f":"'Project Info'!B53","v":60},{"$f":"'Project Info'!C53","v":57.125792270740902},{"$f":"'Project Info'!D53","v":52.596971157053673},{"$f":"'Project Info'!E53","v":21.818001539159841},{"$f":"'Project Info'!F53","v":0},{"$f":"'Project Info'!G53","v":0},{"$f":"'Project Info'!H53","v":0},{"$f":"'Project Info'!I53","v":0},{"$f":"'Project Info'!J53","v":0},{"$f":"'Project Info'!K53","v":0},{"$f":"'Project Info'!L53","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A54","v":50},{"$f":"'Project Info'!B54","v":55},{"$f":"'Project Info'!C54","v":52.235698854337961},{"$f":"'Project Info'!D54","v":48.022768090099298},{"$f":"'Project Info'!E54","v":19.246640192796217},{"$f":"'Project Info'!F54","v":0},{"$f":"'Project Info'!G54","v":0},{"$f":"'Project Info'!H54","v":0},{"$f":"'Project Info'!I54","v":0},{"$f":"'Project Info'!J54","v":0},{"$f":"'Project Info'!K54","v":0},{"$f":"'Project Info'!L54","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A55","v":45},{"$f":"'Project Info'!B55","v":50},{"$f":"'Project Info'!C55","v":47.459170258371508},{"$f":"'Project Info'!D55","v":43.465397050422162},{"$f":"'Project Info'!E55","v":16.894183241713304},{"$f":"'Project Info'!F55","v":0},{"$f":"'Project Info'!G55","v":0},{"$f":"'Project Info'!H55","v":0},{"$f":"'Project Info'!I55","v":0},{"$f":"'Project Info'!J55","v":0},{"$f":"'Project Info'!K55","v":0},{"$f":"'Project Info'!L55","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A56","v":40},{"$f":"'Project Info'!B56","v":45},{"$f":"'Project Info'!C56","v":42.677030404888129},{"$f":"'Project Info'!D56","v":38.812544504634097},{"$f":"'Project Info'!E56","v":14.690265649465921},{"$f":"'Project Info'!F56","v":0},{"$f":"'Project Info'!G56","v":0},{"$f":"'Project Info'!H56","v":0},{"$f":"'Project Info'!I56","v":0},{"$f":"'Project Info'!J56","v":0},{"$f":"'Project Info'!K56","v":0},{"$f":"'Project Info'!L56","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A57","v":35},{"$f":"'Project Info'!B57","v":40},{"$f":"'Project Info'!C57","v":37.333046773755832},{"$f":"'Project Info'!D57","v":33.904706919479686},{"$f":"'Project Info'!E57","v":12.53841602318813},{"$f":"'Project Info'!F57","v":0},{"$f":"'Project Info'!G57","v":0},{"$f":"'Project Info'!H57","v":0},{"$f":"'Project Info'!I57","v":0},{"$f":"'Project Info'!J57","v":0},{"$f":"'Project Info'!K57","v":0},{"$f":"'Project Info'!L57","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A58","v":30},{"$f":"'Project Info'!B58","v":35},{"$f":"'Project Info'!C58","v":32.638179845662044},{"$f":"'Project Info'!D58","v":29.547170928664851},{"$f":"'Project Info'!E58","v":10.728972818165861},{"$f":"'Project Info'!F58","v":0},{"$f":"'Project Info'!G58","v":0},{"$f":"'Project Info'!H58","v":0},{"$f":"'Project Info'!I58","v":0},{"$f":"'Project Info'!J58","v":0},{"$f":"'Project Info'!K58","v":0},{"$f":"'Project Info'!L58","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A59","v":25},{"$f":"'Project Info'!B59","v":30},{"$f":"'Project Info'!C59","v":27.529264646850947},{"$f":"'Project Info'!D59","v":24.652717392657845},{"$f":"'Project Info'!E59","v":8.8041305482613303},{"$f":"'Project Info'!F59","v":0},{"$f":"'Project Info'!G59","v":0},{"$f":"'Project Info'!H59","v":0},{"$f":"'Project Info'!I59","v":0},{"$f":"'Project Info'!J59","v":0},{"$f":"'Project Info'!K59","v":0},{"$f":"'Project Info'!L59","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A60","v":20},{"$f":"'Project Info'!B60","v":25},{"$f":"'Project Info'!C60","v":22.998111483544687},{"$f":"'Project Info'!D60","v":20.383306659827422},{"$f":"'Project Info'!E60","v":7.246164547543378},{"$f":"'Project Info'!F60","v":0},{"$f":"'Project Info'!G60","v":0},{"$f":"'Project Info'!H60","v":0},{"$f":"'Project Info'!I60","v":0},{"$f":"'Project Info'!J60","v":0},{"$f":"'Project Info'!K60","v":0},{"$f":"'Project Info'!L60","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A61","v":15},{"$f":"'Project Info'!B61","v":20},{"$f":"'Project Info'!C61","v":17.808510327474309},{"$f":"'Project Info'!D61","v":15.420865796304254},{"$f":"'Project Info'!E61","v":5.5490484131518292},{"$f":"'Project Info'!F61","v":0},{"$f":"'Project Info'!G61","v":0},{"$f":"'Project Info'!H61","v":0},{"$f":"'Project Info'!I61","v":0},{"$f":"'Project Info'!J61","v":0},{"$f":"'Project Info'!K61","v":0},{"$f":"'Project Info'!L61","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A62","v":10},{"$f":"'Project Info'!B62","v":15},{"$f":"'Project Info'!C62","v":12.269931130346862},{"$f":"'Project Info'!D62","v":10.318264913023604},{"$f":"'Project Info'!E62","v":3.9082824916941998},{"$f":"'Project Info'!F62","v":0},{"$f":"'Project Info'!G62","v":0},{"$f":"'Project Info'!H62","v":0},{"$f":"'Project Info'!I62","v":0},{"$f":"'Project Info'!J62","v":0},{"$f":"'Project Info'!K62","v":0},{"$f":"'Project Info'!L62","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A63","v":5},{"$f":"'Project Info'!B63","v":10},{"$f":"'Project Info'!C63","v":7.3137581369917548},{"$f":"'Project Info'!D63","v":5.7052382449247707},{"$f":"'Project Info'!E63","v":2.5019418419888937},{"$f":"'Project Info'!F63","v":0},{"$f":"'Project Info'!G63","v":0},{"$f":"'Project Info'!H63","v":0},{"$f":"'Project Info'!I63","v":0},{"$f":"'Project Info'!J63","v":0},{"$f":"'Project Info'!K63","v":0},{"$f":"'Project Info'!L63","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A64","v":0},{"$f":"'Project Info'!B64","v":5},{"$f":"'Project Info'!C64","v":2.6119461836144886},{"$f":"'Project Info'!D64","v":1.2699770062067783},{"$f":"'Project Info'!E64","v":1.2046477897733283},{"$f":"'Project Info'!F64","v":0},{"$f":"'Project Info'!G64","v":0},{"$f":"'Project Info'!H64","v":0},{"$f":"'Project Info'!I64","v":0},{"$f":"'Project Info'!J64","v":0},{"$f":"'Project Info'!K64","v":0},{"$f":"'Project Info'!L64","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A65","v":-5},{"$f":"'Project Info'!B65","v":0},{"$f":"'Project Info'!C65","v":-1.6731398516793925},{"$f":"'Project Info'!D65","v":-2.7083318773557807},{"$f":"'Project Info'!E65","v":7.9391832815876459E-2},{"$f":"'Project Info'!F65","v":0},{"$f":"'Project Info'!G65","v":0},{"$f":"'Project Info'!H65","v":0},{"$f":"'Project Info'!I65","v":0},{"$f":"'Project Info'!J65","v":0},{"$f":"'Project Info'!K65","v":0},{"$f":"'Project Info'!L65","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A66","v":-10},{"$f":"'Project Info'!B66","v":-5},{"$f":"'Project Info'!C66","v":-6.5729865085377277},{"$f":"'Project Info'!D66","v":-7.2465935998252222},{"$f":"'Project Info'!E66","v":-1.168423365310433},{"$f":"'Project Info'!F66","v":0},{"$f":"'Project Info'!G66","v":0},{"$f":"'Project Info'!H66","v":0},{"$f":"'Project Info'!I66","v":0},{"$f":"'Project Info'!J66","v":0},{"$f":"'Project Info'!K66","v":0},{"$f":"'Project Info'!L66","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A67","v":-15},{"$f":"'Project Info'!B67","v":-10},{"$f":"'Project Info'!C67","v":-15.32570353422995},{"$f":"'Project Info'!D67","v":-15.707838211108999},{"$f":"'Project Info'!E67","v":-3.4051318156661381},{"$f":"'Project Info'!F67","v":0},{"$f":"'Project Info'!G67","v":0},{"$f":"'Project Info'!H67","v":0},{"$f":"'Project Info'!I67","v":0},{"$f":"'Project Info'!J67","v":0},{"$f":"'Project Info'!K67","v":0},{"$f":"'Project Info'!L67","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[]
[]
[null,null,null,null,null,null,"Unoccupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","DHW"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Load","Base","Proposed","Base","Proposed","Demand Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","MBH","MBH","MBH","kW","kW","MBH","kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A74","v":100},{"$f":"'Project Info'!B74","v":105},{"$f":"'Project Info'!C74","v":102},{"$f":"'Project Info'!D74","v":76},{"$f":"'Project Info'!E74","v":40},{"$f":"'Project Info'!F74","v":0},{"$f":"'Project Info'!G74","v":0},{"$f":"'Project Info'!H74","v":0},{"$f":"'Project Info'!I74","v":0},{"$f":"'Project Info'!J74","v":0},{"$f":"'Project Info'!K74","v":0},{"$f":"'Project Info'!L74","v":0},{"$f":"$R$118+$W$116/1000","v":{"$error":"#N/A"}},{"$f":"IF($N$15=$O$96,S63/$N$22,0)","v":0},{"$f":"IF($N$15=$O$96,S63/$N$21,0)","v":0},{"$f":"IF($N$15=$O$97,S63/$O$22/3.412,0)","v":0},{"$f":"IF($N$15=$O$97,S63/$O$21/3.412,0)","v":0},{"$f":"(T63-U63)","v":0},{"$f":"(V63-W63)","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A75","v":95},{"$f":"'Project Info'!B75","v":100},{"$f":"'Project Info'!C75","v":95.219272727272724},{"$f":"'Project Info'!D75","v":74.534025272781079},{"$f":"'Project Info'!E75","v":37.923296058061368},{"$f":"'Project Info'!F75","v":0},{"$f":"'Project Info'!G75","v":0},{"$f":"'Project Info'!H75","v":0},{"$f":"'Project Info'!I75","v":0},{"$f":"'Project Info'!J75","v":0},{"$f":"'Project Info'!K75","v":0},{"$f":"'Project Info'!L75","v":0},{"$error":"#N/A"},0,0,0,0,{"$f":"(T64-U64)","v":0},{"$f":"(V64-W64)","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A76","v":90},{"$f":"'Project Info'!B76","v":95},{"$f":"'Project Info'!C76","v":92.016049160256074},{"$f":"'Project Info'!D76","v":72.911561930607689},{"$f":"'Project Info'!E76","v":36.467095439351091},{"$f":"'Project Info'!F76","v":0},{"$f":"'Project Info'!G76","v":0},{"$f":"'Project Info'!H76","v":0},{"$f":"'Project Info'!I76","v":0},{"$f":"'Project Info'!J76","v":0},{"$f":"'Project Info'!K76","v":0},{"$f":"'Project Info'!L76","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A77","v":85},{"$f":"'Project Info'!B77","v":90},{"$f":"'Project Info'!C77","v":87.457811360655285},{"$f":"'Project Info'!D77","v":70.80538329449476},{"$f":"'Project Info'!E77","v":34.679413213566804},{"$f":"'Project Info'!F77","v":0},{"$f":"'Project Info'!G77","v":0},{"$f":"'Project Info'!H77","v":0},{"$f":"'Project Info'!I77","v":0},{"$f":"'Project Info'!J77","v":0},{"$f":"'Project Info'!K77","v":0},{"$f":"'Project Info'!L77","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A78","v":80},{"$f":"'Project Info'!B78","v":85},{"$f":"'Project Info'!C78","v":82.136788830239965},{"$f":"'Project Info'!D78","v":67.872393622439333},{"$f":"'Project Info'!E78","v":32.296248223809314},{"$f":"'Project Info'!F78","v":0},{"$f":"'Project Info'!G78","v":0},{"$f":"'Project Info'!H78","v":0},{"$f":"'Project Info'!I78","v":0},{"$f":"'Project Info'!J78","v":0},{"$f":"'Project Info'!K78","v":0},{"$f":"'Project Info'!L78","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A79","v":75},{"$f":"'Project Info'!B79","v":80},{"$f":"'Project Info'!C79","v":76.988400157585886},{"$f":"'Project Info'!D79","v":65.129261896908645},{"$f":"'Project Info'!E79","v":30.190476812806729},{"$f":"'Project Info'!F79","v":0},{"$f":"'Project Info'!G79","v":0},{"$f":"'Project Info'!H79","v":0},{"$f":"'Project Info'!I79","v":0},{"$f":"'Project Info'!J79","v":0},{"$f":"'Project Info'!K79","v":0},{"$f":"'Project Info'!L79","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A80","v":70},{"$f":"'Project Info'!B80","v":75},{"$f":"'Project Info'!C80","v":72.457982050814195},{"$f":"'Project Info'!D80","v":63.604425012889301},{"$f":"'Project Info'!E80","v":29.088683095945193},{"$f":"'Project Info'!F80","v":0},{"$f":"'Project Info'!G80","v":0},{"$f":"'Project Info'!H80","v":0},{"$f":"'Project Info'!I80","v":0},{"$f":"'Project Info'!J80","v":0},{"$f":"'Project Info'!K80","v":0},{"$f":"'Project Info'!L80","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A81","v":65},{"$f":"'Project Info'!B81","v":70},{"$f":"'Project Info'!C81","v":67.815831070966169},{"$f":"'Project Info'!D81","v":61.631331368130574},{"$f":"'Project Info'!E81","v":27.661514889731574},{"$f":"'Project Info'!F81","v":0},{"$f":"'Project Info'!G81","v":0},{"$f":"'Project Info'!H81","v":0},{"$f":"'Project Info'!I81","v":0},{"$f":"'Project Info'!J81","v":0},{"$f":"'Project Info'!K81","v":0},{"$f":"'Project Info'!L81","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A82","v":60},{"$f":"'Project Info'!B82","v":65},{"$f":"'Project Info'!C82","v":62.535961472271332},{"$f":"'Project Info'!D82","v":57.135476922863582},{"$f":"'Project Info'!E82","v":24.623037157728302},{"$f":"'Project Info'!F82","v":0},{"$f":"'Project Info'!G82","v":0},{"$f":"'Project Info'!H82","v":0},{"$f":"'Project Info'!I82","v":0},{"$f":"'Project Info'!J82","v":0},{"$f":"'Project Info'!K82","v":0},{"$f":"'Project Info'!L82","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A83","v":55},{"$f":"'Project Info'!B83","v":60},{"$f":"'Project Info'!C83","v":57.125792270740902},{"$f":"'Project Info'!D83","v":52.596971157053673},{"$f":"'Project Info'!E83","v":21.818001539159841},{"$f":"'Project Info'!F83","v":0},{"$f":"'Project Info'!G83","v":0},{"$f":"'Project Info'!H83","v":0},{"$f":"'Project Info'!I83","v":0},{"$f":"'Project Info'!J83","v":0},{"$f":"'Project Info'!K83","v":0},{"$f":"'Project Info'!L83","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A84","v":50},{"$f":"'Project Info'!B84","v":55},{"$f":"'Project Info'!C84","v":52.235698854337961},{"$f":"'Project Info'!D84","v":48.022768090099298},{"$f":"'Project Info'!E84","v":19.246640192796217},{"$f":"'Project Info'!F84","v":0},{"$f":"'Project Info'!G84","v":0},{"$f":"'Project Info'!H84","v":0},{"$f":"'Project Info'!I84","v":0},{"$f":"'Project Info'!J84","v":0},{"$f":"'Project Info'!K84","v":0},{"$f":"'Project Info'!L84","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A85","v":45},{"$f":"'Project Info'!B85","v":50},{"$f":"'Project Info'!C85","v":47.459170258371508},{"$f":"'Project Info'!D85","v":43.465397050422162},{"$f":"'Project Info'!E85","v":16.894183241713304},{"$f":"'Project Info'!F85","v":0},{"$f":"'Project Info'!G85","v":0},{"$f":"'Project Info'!H85","v":0},{"$f":"'Project Info'!I85","v":0},{"$f":"'Project Info'!J85","v":0},{"$f":"'Project Info'!K85","v":0},{"$f":"'Project Info'!L85","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A86","v":40},{"$f":"'Project Info'!B86","v":45},{"$f":"'Project Info'!C86","v":42.677030404888129},{"$f":"'Project Info'!D86","v":38.812544504634097},{"$f":"'Project Info'!E86","v":14.690265649465921},{"$f":"'Project Info'!F86","v":0},{"$f":"'Project Info'!G86","v":0},{"$f":"'Project Info'!H86","v":0},{"$f":"'Project Info'!I86","v":0},{"$f":"'Project Info'!J86","v":0},{"$f":"'Project Info'!K86","v":0},{"$f":"'Project Info'!L86","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A87","v":35},{"$f":"'Project Info'!B87","v":40},{"$f":"'Project Info'!C87","v":37.333046773755832},{"$f":"'Project Info'!D87","v":33.904706919479686},{"$f":"'Project Info'!E87","v":12.53841602318813},{"$f":"'Project Info'!F87","v":0},{"$f":"'Project Info'!G87","v":0},{"$f":"'Project Info'!H87","v":0},{"$f":"'Project Info'!I87","v":0},{"$f":"'Project Info'!J87","v":0},{"$f":"'Project Info'!K87","v":0},{"$f":"'Project Info'!L87","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A88","v":30},{"$f":"'Project Info'!B88","v":35},{"$f":"'Project Info'!C88","v":32.638179845662044},{"$f":"'Project Info'!D88","v":29.547170928664851},{"$f":"'Project Info'!E88","v":10.728972818165861},{"$f":"'Project Info'!F88","v":0},{"$f":"'Project Info'!G88","v":0},{"$f":"'Project Info'!H88","v":0},{"$f":"'Project Info'!I88","v":0},{"$f":"'Project Info'!J88","v":0},{"$f":"'Project Info'!K88","v":0},{"$f":"'Project Info'!L88","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A89","v":25},{"$f":"'Project Info'!B89","v":30},{"$f":"'Project Info'!C89","v":27.529264646850947},{"$f":"'Project Info'!D89","v":24.652717392657845},{"$f":"'Project Info'!E89","v":8.8041305482613303},{"$f":"'Project Info'!F89","v":0},{"$f":"'Project Info'!G89","v":0},{"$f":"'Project Info'!H89","v":0},{"$f":"'Project Info'!I89","v":0},{"$f":"'Project Info'!J89","v":0},{"$f":"'Project Info'!K89","v":0},{"$f":"'Project Info'!L89","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A90","v":20},{"$f":"'Project Info'!B90","v":25},{"$f":"'Project Info'!C90","v":22.998111483544687},{"$f":"'Project Info'!D90","v":20.383306659827422},{"$f":"'Project Info'!E90","v":7.246164547543378},{"$f":"'Project Info'!F90","v":0},{"$f":"'Project Info'!G90","v":0},{"$f":"'Project Info'!H90","v":0},{"$f":"'Project Info'!I90","v":0},{"$f":"'Project Info'!J90","v":0},{"$f":"'Project Info'!K90","v":0},{"$f":"'Project Info'!L90","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A91","v":15},{"$f":"'Project Info'!B91","v":20},{"$f":"'Project Info'!C91","v":17.808510327474309},{"$f":"'Project Info'!D91","v":15.420865796304254},{"$f":"'Project Info'!E91","v":5.5490484131518292},{"$f":"'Project Info'!F91","v":0},{"$f":"'Project Info'!G91","v":0},{"$f":"'Project Info'!H91","v":0},{"$f":"'Project Info'!I91","v":0},{"$f":"'Project Info'!J91","v":0},{"$f":"'Project Info'!K91","v":0},{"$f":"'Project Info'!L91","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A92","v":10},{"$f":"'Project Info'!B92","v":15},{"$f":"'Project Info'!C92","v":12.269931130346862},{"$f":"'Project Info'!D92","v":10.318264913023604},{"$f":"'Project Info'!E92","v":3.9082824916941998},{"$f":"'Project Info'!F92","v":0},{"$f":"'Project Info'!G92","v":0},{"$f":"'Project Info'!H92","v":0},{"$f":"'Project Info'!I92","v":0},{"$f":"'Project Info'!J92","v":0},{"$f":"'Project Info'!K92","v":0},{"$f":"'Project Info'!L92","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A93","v":5},{"$f":"'Project Info'!B93","v":10},{"$f":"'Project Info'!C93","v":7.3137581369917548},{"$f":"'Project Info'!D93","v":5.7052382449247707},{"$f":"'Project Info'!E93","v":2.5019418419888937},{"$f":"'Project Info'!F93","v":0},{"$f":"'Project Info'!G93","v":0},{"$f":"'Project Info'!H93","v":0},{"$f":"'Project Info'!I93","v":0},{"$f":"'Project Info'!J93","v":0},{"$f":"'Project Info'!K93","v":0},{"$f":"'Project Info'!L93","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A94","v":0},{"$f":"'Project Info'!B94","v":5},{"$f":"'Project Info'!C94","v":2.6119461836144886},{"$f":"'Project Info'!D94","v":1.2699770062067783},{"$f":"'Project Info'!E94","v":1.2046477897733283},{"$f":"'Project Info'!F94","v":8760},{"$f":"'Project Info'!G94","v":2672},{"$f":"'Project Info'!H94","v":3160},{"$f":"'Project Info'!I94","v":1344},{"$f":"'Project Info'!J94","v":1584},{"$f":"'Project Info'!K94","v":88},{"$f":"'Project Info'!L94","v":264},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A95","v":-5},{"$f":"'Project Info'!B95","v":0},{"$f":"'Project Info'!C95","v":-1.6731398516793925},{"$f":"'Project Info'!D95","v":-2.7083318773557807},{"$f":"'Project Info'!E95","v":7.9391832815876459E-2},{"$f":"'Project Info'!F95","v":0},{"$f":"'Project Info'!G95","v":0},{"$f":"'Project Info'!H95","v":0},{"$f":"'Project Info'!I95","v":0},{"$f":"'Project Info'!J95","v":0},{"$f":"'Project Info'!K95","v":0},{"$f":"'Project Info'!L95","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A96","v":-10},{"$f":"'Project Info'!B96","v":-5},{"$f":"'Project Info'!C96","v":-6.5729865085377277},{"$f":"'Project Info'!D96","v":-7.2465935998252222},{"$f":"'Project Info'!E96","v":-1.168423365310433},{"$f":"'Project Info'!F96","v":0},{"$f":"'Project Info'!G96","v":0},{"$f":"'Project Info'!H96","v":0},{"$f":"'Project Info'!I96","v":0},{"$f":"'Project Info'!J96","v":0},{"$f":"'Project Info'!K96","v":0},{"$f":"'Project Info'!L96","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A97","v":-15},{"$f":"'Project Info'!B97","v":-10},{"$f":"'Project Info'!C97","v":-15.32570353422995},{"$f":"'Project Info'!D97","v":-15.707838211108999},{"$f":"'Project Info'!E97","v":-3.4051318156661381},{"$f":"'Project Info'!F97","v":0},{"$f":"'Project Info'!G97","v":0},{"$f":"'Project Info'!H97","v":0},{"$f":"'Project Info'!I97","v":0},{"$f":"'Project Info'!J97","v":0},{"$f":"'Project Info'!K97","v":0},{"$f":"'Project Info'!L97","v":0},{"$error":"#N/A"},0,0,0,0,0,0]
[]
[]
[null,null,null,null,null,null,null,null,null,"Occ","DHW","DHW","DHW",null,"Baseline for Fossil Fuel Water Heater",null,null,null,null,"Baseline for HP Water Heater"]
[null,null,null,null,null,null,"Bldg",null,null,"Density","gal/day","Use","gal/day",null,null,"Type","Base Eff.","Base Unit",null,"Min Storage","Base"]
[null,null,null,null,null,null,"Type",null,null,"ft²/person","per person","Category","per ft²",null,null,"Storage",0.8,"Eff (%)",null,"Gal","COP"]
[null,null,null,null,null,null,{"$f":"'Project Info'!E102","v":"Automotive facility"},null,null,500,1,2,{"$f":"LOOKUP(L92,$G$147:$G$150,$I$147:$I$150)","v":0.02},null,null,"Tankless (On-Demand)",0.61,"EF (%)",null,0,0.95]
[null,null,null,null,null,null,{"$f":"'Project Info'!E103","v":"Convention center"},null,null,10,0.25,2,0.02,null,null,"Indirect/Boiler-Fed",0.78,"Rec. Eff (%)",null,55,1.94]
[null,null,null,null,null,null,{"$f":"'Project Info'!E104","v":"Courthouse"},null,null,15,0.25,1,0.01,null,null,null,null,null,null,80,1.98]
[null,null,null,null,null,null,{"$f":"'Project Info'!E105","v":"Daycare"},null,null,null,null,2,0.02,null,"Water Heater Types (Eligible Types)"]
[null,null,null,null,null,null,{"$f":"'Project Info'!E106","v":"Dining: bar/lounge/leisure"},null,null,{"$f":"1000/100","v":10},2.5,2,0.02,null,"Fossil Fuel"]
[null,null,null,null,null,null,{"$f":"'Project Info'!E107","v":"Dining: Cafeteria/Fast Food"},null,null,{"$f":"1000/10","v":100},2.5,2,0.02,null,"Heat Pump (Elec)"]
[null,null,null,null,null,null,{"$f":"'Project Info'!E108","v":"Dining: Family"},null,null,15,2.5,2,0.02]
[null,null,null,null,null,null,{"$f":"'Project Info'!E109","v":"Dormitory"},null,null,{"$f":"1000/20","v":50},12,4,0.04,null,"Incentive Type"]
[null,null,null,null,null,null,{"$f":"'Project Info'!E110","v":"Education - College/University"},null,null,null,null,1,{"$f":"LOOKUP(L100,$G$147:$G$150,$I$147:$I$150)","v":0.01},null,"Custom",null,null,null,null,"Incremental Cost Estimate"]
[null,null,null,null,null,null,{"$f":"'Project Info'!E111","v":"Education - Community College"},null,null,null,null,1,{"$f":"LOOKUP(L101,$G$147:$G$150,$I$147:$I$150)","v":0.01},null,"Upstream",null,null,null,null,"Data from Supply.com"]
[null,null,null,null,null,null,{"$f":"'Project Info'!E112","v":"Education - K-12 School"},null,null,null,null,1,{"$f":"LOOKUP(L102,$G$147:$G$150,$I$147:$I$150)","v":0.01},null,null,null,null,null,null,"Type","MBH","$"]
[null,null,null,null,null,null,{"$f":"'Project Info'!E113","v":"Exercise center"},null,null,50,0.5,3,{"$f":"LOOKUP(L103,$G$147:$G$150,$I$147:$I$150)","v":0.03},null,"Building Occupied Hours from Project Info",null,null,null,null,"Gas Condensing",200,6095]
[null,null,null,null,null,null,{"$f":"'Project Info'!E114","v":"Fire station"},null,null,400,1,1,0.01,null,"Weekday Occ Hours",null,{"$f":"'Project Info'!J15-'Project Info'!I15","v":0},null,null,"Gas Standard",200,4675]
[null,null,null,null,null,null,{"$f":"'Project Info'!E115","v":"Grocery"},null,null,null,null,2,0.02,null,"Saturday Occ Hour",null,{"$f":"'Project Info'!J16-'Project Info'!I16","v":0},null,null,"Incr Cost per MBH",null,{"$f":"(V103-V104)/U103","v":7.1}]
[null,null,null,null,null,null,{"$f":"'Project Info'!E116","v":"Gymnasium"},null,null,50,0.25,2,0.02,null,"Sunday Occ Hours",null,{"$f":"'Project Info'!J17-'Project Info'!I17","v":0},null,null,"Est Incr. Cost per MBH",null,10]
[null,null,null,null,null,null,{"$f":"'Project Info'!E117","v":"Health/Medical - Clinic"},null,null,300,0.25,1,0.01,null,"Avg. Daily Occ Hrs",null,{"$f":"(5*Q104+Q105+Q106)/7","v":0},null,null,"(with venting)"]
[null,null,null,null,null,null,{"$f":"'Project Info'!E118","v":"Hospital"},null,null,200,5,2,0.02]
[null,null,null,null,null,null,{"$f":"'Project Info'!E119","v":"Hotel/Motel/Lodging"},null,null,{"$f":"1000/10","v":100},12,3,0.03,null,"DHW gallons per day",null,null,{"$f":"IF(T18>0,T18,T17)","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,{"$f":"'Project Info'!E120","v":"Industrial/Manufacturing - 1 Shift"},null,null,null,null,1,{"$f":"LOOKUP(L110,$G$147:$G$150,$I$147:$I$150)","v":0.01},null,"Avg Daily Occ Hrs",null,null,{"$f":"Q107","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!E121","v":"Industrial/Manufacturing - 2 Shifts"},null,null,250,1,2,{"$f":"LOOKUP(L111,$G$147:$G$150,$I$147:$I$150)","v":0.02},null,"DHW Loads"]
[null,null,null,null,null,null,{"$f":"'Project Info'!E122","v":"Industrial/Manufacturing - 3 Shifts"},null,null,null,null,2,{"$f":"LOOKUP(L112,$G$147:$G$150,$I$147:$I$150)","v":0.02},null,"Avg Occupied DHW Gal/hr",null,null,{"$f":"R109/R110","v":{"$error":"#N/A"}},null,"Standby Losses"]
[null,null,null,null,null,null,{"$f":"'Project Info'!E123","v":"Library"},null,null,500,0.25,1,{"$f":"LOOKUP(L113,$G$147:$G$150,$I$147:$I$150)","v":0.01},null,"Annual Occupied DHW gallons",null,null,{"$f":"R112*SUM(L33:L56)","v":{"$error":"#N/A"}},null,"Total Heaters",null,null,{"$f":"N19","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!E124","v":"Motion picture theater"},null,null,15,0.25,1,0.01,null,"Entering Water Temp (°F)",null,null,55,null,"Max Input Rate (Btu/h)",null,null,{"$f":"W113*N17*1000","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!E125","v":"Multifamily"},null,null,200,15,4,0.04,null,"Leaving Water Temp (°F)",null,null,130,null,"Total Storage (gal)",null,null,{"$f":"W113*N18*(N16<>\"Instantaneous\")","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!E126","v":"Museum"},null,null,500,0.25,1,0.01,null,"Annual Occupied DHW Load (kBTU)",null,null,{"$f":"8.33*R113*(R115-R114)/1000","v":{"$error":"#N/A"}},null,"Standby Loss Rate (Btu/h)",null,null,{"$f":"W114/800+110*SQRT(W115)","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!E127","v":"Nursing Home"},null,null,null,null,4,0.04,null,"Avg Occ Input Load (MBH)",null,null,{"$f":"MIN(R116/SUM(L33:L56),W114/1000)","v":{"$error":"#N/A"}},null,"Annual Standby Loss Load (kBTU)",null,null,{"$f":"W116*8760/1000","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!E128","v":"Office - Medium/Large ( > 20,000 ft²)"},null,null,200,1,1,0.01,null,"Avg Unocc Input Load (MBH)",null,null,{"$f":"0.1*R117","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,{"$f":"'Project Info'!E129","v":"Office - Small ( < 20,000 ft²)"},null,null,null,null,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E130","v":"Parking garage"},null,null,1000,0.25,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E131","v":"Penitentiary"},null,null,{"$f":"1000/25","v":40},15,4,0.04]
[null,null,null,null,null,null,{"$f":"'Project Info'!E132","v":"Performing arts theater"},null,null,15,0.25,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E133","v":"Police station"},null,null,1000,1,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E134","v":"Post office"},null,null,1000,0.25,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E135","v":"Religious Worship/Church"},null,null,10,0.1,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E136","v":"Retail"},null,null,1000,0.1,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E137","v":"Sports arena"},null,null,10,0.1,2,0.02]
[null,null,null,null,null,null,{"$f":"'Project Info'!E138","v":"Storage Facility"},null,null,null,null,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E139","v":"Town hall"},null,null,1000,1,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E140","v":"Transportation"},null,null,1000,0.5,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E141","v":"Warehouse - Distribution Center"},null,null,10000,1,2,0.02]
[null,null,null,null,null,null,{"$f":"'Project Info'!E142","v":"Warehouse - Inactive Storage"},null,null,null,null,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E143","v":"Workshop"},null,null,1000,2,1,0.01]
[]
[null,null,null,null,null,null,"Estimate of Daily DHW Gallons per ft² by Building Type per ASHRAE Handbook DHW Use Data"]
[null,null,null,null,null,null,"Bldg Type",null,"Avg Daily","Daily gal/unit","ft²/unit","Daily gal/ft²","Source of ft² per unit estimate"]
[null,null,null,null,null,null,"Dormitories",null,"gal/student",12.8,{"$f":"52000/165","v":315.15151515151513},{"$f":"J137/K137","v":4.0615384615384623E-2},"IMC"]
[null,null,null,null,null,null,"Hotel/Motel",null,"gal/room",16,{"$f":"105000/175","v":600},{"$f":"J138/K138","v":2.6666666666666668E-2},"Aloft Hotel Providence"]
[null,null,null,null,null,null,"Nursing Home",null,"gal/bed",18.399999999999999,{"$f":"42000/54","v":777.77777777777783},2.3657142857142852E-2,"Bridges at Lexington"]
[null,null,null,null,null,null,"Office",null,"gal/person",1,100,0.01,"52 Dunham Rd"]
[null,null,null,null,null,null,"Dining",null,"gal/daily meals",2.4,{"$f":"225000/1500","v":150},1.6E-2,"1500 daily meal per 225,000 ft² (Pentucket MS/HS)"]
[null,null,null,null,null,null,"Multifamily",null,"gal/apt",38,1000,3.7999999999999999E-2,"Waterside Place"]
[null,null,null,null,null,null,"Elementary School",null,"gal/student",1,235,4.2553191489361703E-3,"Amesbury Elem"]
[null,null,null,null,null,null,"Jr/Sr High School",null,"gal/student",1.8,{"$f":"225000/1000","v":225},8.0000000000000002E-3,"Pentucket MS/HS"]
[]
[null,null,null,null,null,null,"DHW Load Category",null,"Daily gal/ft²","Ex. Bldg Type"]
[null,null,null,null,null,null,1,"Minimal",0.01,"Office/School"]
[null,null,null,null,null,null,2,"Light",0.02,"Dining"]
[null,null,null,null,null,null,3,"Moderate",0.03,"Hotel"]
[null,null,null,null,null,null,4,"Heavy",0.04,"Dorm/Multifamily"]

{"sheet":"Low Flow DHW Fixtures","index":19,"n_rows":150,"n_cols":26,"rows_kept":150,"cut":false,"hidden":true,"merged":[[1,19,11,27],[1,10,4,17]]}
["Savings Summary",null,null,null,null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,null,null,"Notes (Optional)"]
["Annual kWh Savings",null,null,{"$f":"SUM(A14:D14)","v":0},null,null,null,"Value","Unit",null,"This measure considers savings from installing low flow hot water fixtures to reduce DHW heating demand and water use.\nThe baseline reflects the LEED v4 baseline fixture flow ratings, which are assume to be consistent with Federal standards.\n"]
["% On Peak",null,null,{"$f":"IF(D2<=0,0,MIN(1,A15+C15))","v":0},null,"Annual Electric Savings",null,{"$f":"D2","v":0},"kWh"]
["Max kW",null,null,{"$f":"MAX(Z33:Z56,Z63:Z86)","v":0},null,"Annual Fuel Savings",null,{"$f":"D7*C28","v":{"$error":"#N/A"}},{"$f":"D20","v":{"$error":"#N/A"}}]
["Summer kW",null,null,{"$f":"(SUMPRODUCT(Z33:Z56,R33:R56)+SUMPRODUCT(Z63:Z86,R63:R86))/SUM(R33:R56,R63:R86)","v":0},null,"Incremental","Default Calc",{"$f":"$U$94*(($M$17-$N$17)*$P$17+($M$18-$N$18)*$P$18+($M$19-$N$19)*$P$19+($M$20-$N$20)*$P$20)","v":0},"$"]
["Winter kW",null,null,{"$f":"(SUMPRODUCT(Z33:Z56,Q33:Q56)+SUMPRODUCT(Z63:Z86,Q63:Q86))/SUM(Q33:Q56,Q63:Q86)","v":0},null,"Cost","Project Specific",null,"$ (Optional)"]
["Annual Fuel Savings (MMBtu)",null,null,{"$f":"(SUMPRODUCT($L$33:$L$56,$Y$33:$Y$56)+SUMPRODUCT($L$63:$L$86,$Y$63:$Y$86))/1000","v":0},null,"Estimated Incentive",null,{"$f":"IF(AND($C$24>=0,$C$25>=0),MAX(0,H3)*C24+MAX(0,H4)*C25,\"TBD\")","v":{"$error":"#N/A"}},"$"]
["Incremental Cost (Default Calc)",null,null,{"$f":"$U$94*(($M$17-$N$17)*$P$17+($M$18-$N$18)*$P$18+($M$19-$N$19)*$P$19+($M$20-$N$20)*$P$20)","v":0}]
["Incremental Cost (for Summary)",null,null,{"$f":"IF(H6>0,H6,D8)","v":0},null,"Project Information Summary"]
["kWh Savings by Peak Period",null,null,null,null,null,"STATE",{"$f":"'Project Info'!C15","v":"NH"}]
["Winter","Winter","Summer","Summer",null,null,"Program Year",{"$f":"'Project Info'!C19","v":0}]
["On-Peak","Off-Peak","On-Peak","Off-Peak",null,null,"Code IECC Version",{"$f":"MID('Project Info'!C20,1,4)","v":"2018"}]
["kWh","kWh","kWh","kWh",null,null,"Electric PA",{"$f":"'Project Info'!F3","v":0}]
[{"$f":"SUMPRODUCT(M33:M56,$Z$33:$Z$56)+SUMPRODUCT(M63:M86,$Z$63:$Z$86)","v":0},{"$f":"SUMPRODUCT(N33:N56,$Z$33:$Z$56)+SUMPRODUCT(N63:N86,$Z$63:$Z$86)","v":0},{"$f":"SUMPRODUCT(O33:O56,$Z$33:$Z$56)+SUMPRODUCT(O63:O86,$Z$63:$Z$86)","v":0},{"$f":"SUMPRODUCT(P33:P56,$Z$33:$Z$56)+SUMPRODUCT(P63:P86,$Z$63:$Z$86)","v":0},null,null,"Gas PA",{"$f":"'Project Info'!I3","v":0},null,null,"Table 1: Hot Water Fixture Flow Rates",null,null,null,null,null,null,"User Inputs - Heater Performance"]
[{"$f":"ROUND(IF(A14<=0,0,A14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(B14<=0,0,B14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(C14<=0,0,C14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"IF(SUM(A14:D14)=0,0,1-SUM(A15:C15))","v":0},null,"Building Type",null,{"$f":"'Project Info'!C18","v":0},null,null,null,null,"Base","Design","Fixture % of","Fixture Qty",null,"Water Heater Type"]
[null,null,null,null,null,"Building Area (ft²)",null,{"$f":"'Project Info'!C17","v":0},null,null,"Fixture Type",null,"gpm","gpm","Total DHW Use","(For Incr. Cost)",null,"Fossil Fuel Design Eff. (%)"]
["Utility Rates",null,null,null,null,"*NOTE: Baseline values are automated and cannot be changed.",null,null,null,null,"Public Restroom Faucet",null,0.5,null,null,null,null,"Electric Design COP"]
[null,null,"Rate","Unit",null,null,null,null,null,null,"Private Restroom Faucet",null,2.2000000000000002]
["Electric",null,{"$f":"'ECM Summary'!$E$31","v":0.1593},"kWh",null,null,null,null,null,null,"Kitchen Sink Faucet",null,2.2000000000000002,null,null,null,null,"Building Avg. Daily DHW Consumption"]
[{"$f":"'ECM Summary'!$C$32","v":0},null,{"$f":"'ECM Summary'!$E$32","v":{"$error":"#N/A"}},{"$f":"'ECM Summary'!$F$32","v":{"$error":"#N/A"}},null,null,null,null,null,null,"Showerhead",null,2.5,null,null,null,null,"Building Type",null,null,{"$f":"H15","v":0}]
[null,null,null,null,null,null,null,null,null,null,"Other Fixtures/Equip. (Not Impacted by Low Flow Fixtures)",null,null,null,{"$f":"1-SUM(O17:O20)","v":1},null,null,"Estimated DHW gallons/day per ft²",null,null,{"$f":"LOOKUP($H$15,$G$92:$G$133,$M$92:$M$133)","v":{"$error":"#N/A"}}]
["Custom Incentive Rates",null,null,null,null,null,null,null,null,null,null,null,"Baseline","Proposed",null,null,null,"DHW gallons per day - Calculated",null,null,{"$f":"U21*H16","v":{"$error":"#N/A"}}]
[null,null,"Rate","Unit",null,null,null,null,null,null,"Avg. gpm from Impacted Load",null,{"$f":"IF(SUM($O$17:$O$20)=0,0,SUMPRODUCT(M17:M20,$O$17:$O$20)/SUM($O$17:$O$20))","v":0},{"$f":"IF(SUM($O$17:$O$20)=0,0,SUMPRODUCT(N17:N20,$O$17:$O$20)/SUM($O$17:$O$20))","v":0},null,null,null,"DHW gallons per day - Optional Override"]
["Electric",null,{"$f":"'ECM Summary'!$J$31","v":0.28000000000000003},"kWh",null,null,null,null,null,null,"Impacted Load % of Total Use",null,{"$f":"SUM(O17:O20)","v":0}]
[{"$f":"'ECM Summary'!$H$32","v":0},null,{"$f":"'ECM Summary'!$J$32","v":0},{"$f":"'ECM Summary'!$K$32","v":{"$error":"#N/A"}},null,null,null,null,null,null,"% Reduction in Avg. DHW Flow",null,{"$f":"(1-(N23/M23))*M24+0*O21","v":{"$error":"#DIV/0!"}}]
[]
["Fossil Fuel",null,{"$f":"'Project Info'!C21","v":0}]
["Fuel Conversion",null,{"$f":"LOOKUP(C27,'Project Info'!X102:X104,'Project Info'!Z102:Z104)","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,"Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown",null,null,null,null,null,null,null,null,{"$f":"(SUMPRODUCT($L$33:$L$56,U33:U56)+SUMPRODUCT($L$63:$L$86,U63:U86))/100","v":0},{"$f":"(SUMPRODUCT($L$33:$L$56,V33:V56)+SUMPRODUCT($L$63:$L$86,V63:V86))/100","v":0}]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","DHW Avg. Load"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Base","Design","Base","Proposed","Base","Proposed","Demand Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","MBH","MBH","MBH","MBH","kW","kW","MBH","kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A44","v":100},{"$f":"'Project Info'!B44","v":105},{"$f":"'Project Info'!C44","v":102},{"$f":"'Project Info'!D44","v":76},{"$f":"'Project Info'!E44","v":40},{"$f":"'Project Info'!F44","v":0},{"$f":"'Project Info'!G44","v":0},{"$f":"'Project Info'!H44","v":0},{"$f":"'Project Info'!I44","v":0},{"$f":"'Project Info'!J44","v":0},{"$f":"'Project Info'!K44","v":0},{"$f":"'Project Info'!L44","v":0},{"$f":"$R$108","v":{"$error":"#N/A"}},{"$f":"$R$108*(1-$M$25)","v":{"$error":"#N/A"}},{"$f":"IF($T$15=$S$90,S33/$T$16,0)","v":0},{"$f":"IF($T$15=$S$90,T33/$T$16,0)","v":0},{"$f":"IF($T$15=$S$91,S33/$T$17/3.412,0)","v":0},{"$f":"IF($T$15=$S$91,T33/$T$17/3.412,0)","v":0},{"$f":"(U33-V33)","v":0},{"$f":"(W33-X33)","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A45","v":95},{"$f":"'Project Info'!B45","v":100},{"$f":"'Project Info'!C45","v":95.219272727272724},{"$f":"'Project Info'!D45","v":74.534025272781079},{"$f":"'Project Info'!E45","v":37.923296058061368},{"$f":"'Project Info'!F45","v":0},{"$f":"'Project Info'!G45","v":0},{"$f":"'Project Info'!H45","v":0},{"$f":"'Project Info'!I45","v":0},{"$f":"'Project Info'!J45","v":0},{"$f":"'Project Info'!K45","v":0},{"$f":"'Project Info'!L45","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,{"$f":"(U34-V34)","v":0},{"$f":"(W34-X34)","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A46","v":90},{"$f":"'Project Info'!B46","v":95},{"$f":"'Project Info'!C46","v":92.016049160256074},{"$f":"'Project Info'!D46","v":72.911561930607689},{"$f":"'Project Info'!E46","v":36.467095439351091},{"$f":"'Project Info'!F46","v":0},{"$f":"'Project Info'!G46","v":0},{"$f":"'Project Info'!H46","v":0},{"$f":"'Project Info'!I46","v":0},{"$f":"'Project Info'!J46","v":0},{"$f":"'Project Info'!K46","v":0},{"$f":"'Project Info'!L46","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A47","v":85},{"$f":"'Project Info'!B47","v":90},{"$f":"'Project Info'!C47","v":87.457811360655285},{"$f":"'Project Info'!D47","v":70.80538329449476},{"$f":"'Project Info'!E47","v":34.679413213566804},{"$f":"'Project Info'!F47","v":0},{"$f":"'Project Info'!G47","v":0},{"$f":"'Project Info'!H47","v":0},{"$f":"'Project Info'!I47","v":0},{"$f":"'Project Info'!J47","v":0},{"$f":"'Project Info'!K47","v":0},{"$f":"'Project Info'!L47","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A48","v":80},{"$f":"'Project Info'!B48","v":85},{"$f":"'Project Info'!C48","v":82.136788830239965},{"$f":"'Project Info'!D48","v":67.872393622439333},{"$f":"'Project Info'!E48","v":32.296248223809314},{"$f":"'Project Info'!F48","v":0},{"$f":"'Project Info'!G48","v":0},{"$f":"'Project Info'!H48","v":0},{"$f":"'Project Info'!I48","v":0},{"$f":"'Project Info'!J48","v":0},{"$f":"'Project Info'!K48","v":0},{"$f":"'Project Info'!L48","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A49","v":75},{"$f":"'Project Info'!B49","v":80},{"$f":"'Project Info'!C49","v":76.988400157585886},{"$f":"'Project Info'!D49","v":65.129261896908645},{"$f":"'Project Info'!E49","v":30.190476812806729},{"$f":"'Project Info'!F49","v":0},{"$f":"'Project Info'!G49","v":0},{"$f":"'Project Info'!H49","v":0},{"$f":"'Project Info'!I49","v":0},{"$f":"'Project Info'!J49","v":0},{"$f":"'Project Info'!K49","v":0},{"$f":"'Project Info'!L49","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A50","v":70},{"$f":"'Project Info'!B50","v":75},{"$f":"'Project Info'!C50","v":72.457982050814195},{"$f":"'Project Info'!D50","v":63.604425012889301},{"$f":"'Project Info'!E50","v":29.088683095945193},{"$f":"'Project Info'!F50","v":0},{"$f":"'Project Info'!G50","v":0},{"$f":"'Project Info'!H50","v":0},{"$f":"'Project Info'!I50","v":0},{"$f":"'Project Info'!J50","v":0},{"$f":"'Project Info'!K50","v":0},{"$f":"'Project Info'!L50","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A51","v":65},{"$f":"'Project Info'!B51","v":70},{"$f":"'Project Info'!C51","v":67.815831070966169},{"$f":"'Project Info'!D51","v":61.631331368130574},{"$f":"'Project Info'!E51","v":27.661514889731574},{"$f":"'Project Info'!F51","v":0},{"$f":"'Project Info'!G51","v":0},{"$f":"'Project Info'!H51","v":0},{"$f":"'Project Info'!I51","v":0},{"$f":"'Project Info'!J51","v":0},{"$f":"'Project Info'!K51","v":0},{"$f":"'Project Info'!L51","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A52","v":60},{"$f":"'Project Info'!B52","v":65},{"$f":"'Project Info'!C52","v":62.535961472271332},{"$f":"'Project Info'!D52","v":57.135476922863582},{"$f":"'Project Info'!E52","v":24.623037157728302},{"$f":"'Project Info'!F52","v":0},{"$f":"'Project Info'!G52","v":0},{"$f":"'Project Info'!H52","v":0},{"$f":"'Project Info'!I52","v":0},{"$f":"'Project Info'!J52","v":0},{"$f":"'Project Info'!K52","v":0},{"$f":"'Project Info'!L52","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A53","v":55},{"$f":"'Project Info'!B53","v":60},{"$f":"'Project Info'!C53","v":57.125792270740902},{"$f":"'Project Info'!D53","v":52.596971157053673},{"$f":"'Project Info'!E53","v":21.818001539159841},{"$f":"'Project Info'!F53","v":0},{"$f":"'Project Info'!G53","v":0},{"$f":"'Project Info'!H53","v":0},{"$f":"'Project Info'!I53","v":0},{"$f":"'Project Info'!J53","v":0},{"$f":"'Project Info'!K53","v":0},{"$f":"'Project Info'!L53","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A54","v":50},{"$f":"'Project Info'!B54","v":55},{"$f":"'Project Info'!C54","v":52.235698854337961},{"$f":"'Project Info'!D54","v":48.022768090099298},{"$f":"'Project Info'!E54","v":19.246640192796217},{"$f":"'Project Info'!F54","v":0},{"$f":"'Project Info'!G54","v":0},{"$f":"'Project Info'!H54","v":0},{"$f":"'Project Info'!I54","v":0},{"$f":"'Project Info'!J54","v":0},{"$f":"'Project Info'!K54","v":0},{"$f":"'Project Info'!L54","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A55","v":45},{"$f":"'Project Info'!B55","v":50},{"$f":"'Project Info'!C55","v":47.459170258371508},{"$f":"'Project Info'!D55","v":43.465397050422162},{"$f":"'Project Info'!E55","v":16.894183241713304},{"$f":"'Project Info'!F55","v":0},{"$f":"'Project Info'!G55","v":0},{"$f":"'Project Info'!H55","v":0},{"$f":"'Project Info'!I55","v":0},{"$f":"'Project Info'!J55","v":0},{"$f":"'Project Info'!K55","v":0},{"$f":"'Project Info'!L55","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A56","v":40},{"$f":"'Project Info'!B56","v":45},{"$f":"'Project Info'!C56","v":42.677030404888129},{"$f":"'Project Info'!D56","v":38.812544504634097},{"$f":"'Project Info'!E56","v":14.690265649465921},{"$f":"'Project Info'!F56","v":0},{"$f":"'Project Info'!G56","v":0},{"$f":"'Project Info'!H56","v":0},{"$f":"'Project Info'!I56","v":0},{"$f":"'Project Info'!J56","v":0},{"$f":"'Project Info'!K56","v":0},{"$f":"'Project Info'!L56","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A57","v":35},{"$f":"'Project Info'!B57","v":40},{"$f":"'Project Info'!C57","v":37.333046773755832},{"$f":"'Project Info'!D57","v":33.904706919479686},{"$f":"'Project Info'!E57","v":12.53841602318813},{"$f":"'Project Info'!F57","v":0},{"$f":"'Project Info'!G57","v":0},{"$f":"'Project Info'!H57","v":0},{"$f":"'Project Info'!I57","v":0},{"$f":"'Project Info'!J57","v":0},{"$f":"'Project Info'!K57","v":0},{"$f":"'Project Info'!L57","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A58","v":30},{"$f":"'Project Info'!B58","v":35},{"$f":"'Project Info'!C58","v":32.638179845662044},{"$f":"'Project Info'!D58","v":29.547170928664851},{"$f":"'Project Info'!E58","v":10.728972818165861},{"$f":"'Project Info'!F58","v":0},{"$f":"'Project Info'!G58","v":0},{"$f":"'Project Info'!H58","v":0},{"$f":"'Project Info'!I58","v":0},{"$f":"'Project Info'!J58","v":0},{"$f":"'Project Info'!K58","v":0},{"$f":"'Project Info'!L58","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A59","v":25},{"$f":"'Project Info'!B59","v":30},{"$f":"'Project Info'!C59","v":27.529264646850947},{"$f":"'Project Info'!D59","v":24.652717392657845},{"$f":"'Project Info'!E59","v":8.8041305482613303},{"$f":"'Project Info'!F59","v":0},{"$f":"'Project Info'!G59","v":0},{"$f":"'Project Info'!H59","v":0},{"$f":"'Project Info'!I59","v":0},{"$f":"'Project Info'!J59","v":0},{"$f":"'Project Info'!K59","v":0},{"$f":"'Project Info'!L59","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A60","v":20},{"$f":"'Project Info'!B60","v":25},{"$f":"'Project Info'!C60","v":22.998111483544687},{"$f":"'Project Info'!D60","v":20.383306659827422},{"$f":"'Project Info'!E60","v":7.246164547543378},{"$f":"'Project Info'!F60","v":0},{"$f":"'Project Info'!G60","v":0},{"$f":"'Project Info'!H60","v":0},{"$f":"'Project Info'!I60","v":0},{"$f":"'Project Info'!J60","v":0},{"$f":"'Project Info'!K60","v":0},{"$f":"'Project Info'!L60","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A61","v":15},{"$f":"'Project Info'!B61","v":20},{"$f":"'Project Info'!C61","v":17.808510327474309},{"$f":"'Project Info'!D61","v":15.420865796304254},{"$f":"'Project Info'!E61","v":5.5490484131518292},{"$f":"'Project Info'!F61","v":0},{"$f":"'Project Info'!G61","v":0},{"$f":"'Project Info'!H61","v":0},{"$f":"'Project Info'!I61","v":0},{"$f":"'Project Info'!J61","v":0},{"$f":"'Project Info'!K61","v":0},{"$f":"'Project Info'!L61","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A62","v":10},{"$f":"'Project Info'!B62","v":15},{"$f":"'Project Info'!C62","v":12.269931130346862},{"$f":"'Project Info'!D62","v":10.318264913023604},{"$f":"'Project Info'!E62","v":3.9082824916941998},{"$f":"'Project Info'!F62","v":0},{"$f":"'Project Info'!G62","v":0},{"$f":"'Project Info'!H62","v":0},{"$f":"'Project Info'!I62","v":0},{"$f":"'Project Info'!J62","v":0},{"$f":"'Project Info'!K62","v":0},{"$f":"'Project Info'!L62","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A63","v":5},{"$f":"'Project Info'!B63","v":10},{"$f":"'Project Info'!C63","v":7.3137581369917548},{"$f":"'Project Info'!D63","v":5.7052382449247707},{"$f":"'Project Info'!E63","v":2.5019418419888937},{"$f":"'Project Info'!F63","v":0},{"$f":"'Project Info'!G63","v":0},{"$f":"'Project Info'!H63","v":0},{"$f":"'Project Info'!I63","v":0},{"$f":"'Project Info'!J63","v":0},{"$f":"'Project Info'!K63","v":0},{"$f":"'Project Info'!L63","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A64","v":0},{"$f":"'Project Info'!B64","v":5},{"$f":"'Project Info'!C64","v":2.6119461836144886},{"$f":"'Project Info'!D64","v":1.2699770062067783},{"$f":"'Project Info'!E64","v":1.2046477897733283},{"$f":"'Project Info'!F64","v":0},{"$f":"'Project Info'!G64","v":0},{"$f":"'Project Info'!H64","v":0},{"$f":"'Project Info'!I64","v":0},{"$f":"'Project Info'!J64","v":0},{"$f":"'Project Info'!K64","v":0},{"$f":"'Project Info'!L64","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A65","v":-5},{"$f":"'Project Info'!B65","v":0},{"$f":"'Project Info'!C65","v":-1.6731398516793925},{"$f":"'Project Info'!D65","v":-2.7083318773557807},{"$f":"'Project Info'!E65","v":7.9391832815876459E-2},{"$f":"'Project Info'!F65","v":0},{"$f":"'Project Info'!G65","v":0},{"$f":"'Project Info'!H65","v":0},{"$f":"'Project Info'!I65","v":0},{"$f":"'Project Info'!J65","v":0},{"$f":"'Project Info'!K65","v":0},{"$f":"'Project Info'!L65","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A66","v":-10},{"$f":"'Project Info'!B66","v":-5},{"$f":"'Project Info'!C66","v":-6.5729865085377277},{"$f":"'Project Info'!D66","v":-7.2465935998252222},{"$f":"'Project Info'!E66","v":-1.168423365310433},{"$f":"'Project Info'!F66","v":0},{"$f":"'Project Info'!G66","v":0},{"$f":"'Project Info'!H66","v":0},{"$f":"'Project Info'!I66","v":0},{"$f":"'Project Info'!J66","v":0},{"$f":"'Project Info'!K66","v":0},{"$f":"'Project Info'!L66","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A67","v":-15},{"$f":"'Project Info'!B67","v":-10},{"$f":"'Project Info'!C67","v":-15.32570353422995},{"$f":"'Project Info'!D67","v":-15.707838211108999},{"$f":"'Project Info'!E67","v":-3.4051318156661381},{"$f":"'Project Info'!F67","v":0},{"$f":"'Project Info'!G67","v":0},{"$f":"'Project Info'!H67","v":0},{"$f":"'Project Info'!I67","v":0},{"$f":"'Project Info'!J67","v":0},{"$f":"'Project Info'!K67","v":0},{"$f":"'Project Info'!L67","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[]
[]
[null,null,null,null,null,null,"Unoccupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","DHW Avg. Load"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Base","Design","Base","Proposed","Base","Proposed","Demand Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","MBH","MBH","MBH","MBH","kW","kW","MBH","kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A74","v":100},{"$f":"'Project Info'!B74","v":105},{"$f":"'Project Info'!C74","v":102},{"$f":"'Project Info'!D74","v":76},{"$f":"'Project Info'!E74","v":40},{"$f":"'Project Info'!F74","v":0},{"$f":"'Project Info'!G74","v":0},{"$f":"'Project Info'!H74","v":0},{"$f":"'Project Info'!I74","v":0},{"$f":"'Project Info'!J74","v":0},{"$f":"'Project Info'!K74","v":0},{"$f":"'Project Info'!L74","v":0},{"$f":"$R$109","v":{"$error":"#N/A"}},{"$f":"$R$109*(1-$M$25)","v":{"$error":"#N/A"}},{"$f":"IF($T$15=$S$90,S63/$T$16,0)","v":0},{"$f":"IF($T$15=$S$90,T63/$T$16,0)","v":0},{"$f":"IF($T$15=$S$91,S63/$T$17/3.412,0)","v":0},{"$f":"IF($T$15=$S$91,T63/$T$17/3.412,0)","v":0},{"$f":"(U63-V63)","v":0},{"$f":"(W63-X63)","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A75","v":95},{"$f":"'Project Info'!B75","v":100},{"$f":"'Project Info'!C75","v":95.219272727272724},{"$f":"'Project Info'!D75","v":74.534025272781079},{"$f":"'Project Info'!E75","v":37.923296058061368},{"$f":"'Project Info'!F75","v":0},{"$f":"'Project Info'!G75","v":0},{"$f":"'Project Info'!H75","v":0},{"$f":"'Project Info'!I75","v":0},{"$f":"'Project Info'!J75","v":0},{"$f":"'Project Info'!K75","v":0},{"$f":"'Project Info'!L75","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,{"$f":"(U64-V64)","v":0},{"$f":"(W64-X64)","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A76","v":90},{"$f":"'Project Info'!B76","v":95},{"$f":"'Project Info'!C76","v":92.016049160256074},{"$f":"'Project Info'!D76","v":72.911561930607689},{"$f":"'Project Info'!E76","v":36.467095439351091},{"$f":"'Project Info'!F76","v":0},{"$f":"'Project Info'!G76","v":0},{"$f":"'Project Info'!H76","v":0},{"$f":"'Project Info'!I76","v":0},{"$f":"'Project Info'!J76","v":0},{"$f":"'Project Info'!K76","v":0},{"$f":"'Project Info'!L76","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A77","v":85},{"$f":"'Project Info'!B77","v":90},{"$f":"'Project Info'!C77","v":87.457811360655285},{"$f":"'Project Info'!D77","v":70.80538329449476},{"$f":"'Project Info'!E77","v":34.679413213566804},{"$f":"'Project Info'!F77","v":0},{"$f":"'Project Info'!G77","v":0},{"$f":"'Project Info'!H77","v":0},{"$f":"'Project Info'!I77","v":0},{"$f":"'Project Info'!J77","v":0},{"$f":"'Project Info'!K77","v":0},{"$f":"'Project Info'!L77","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A78","v":80},{"$f":"'Project Info'!B78","v":85},{"$f":"'Project Info'!C78","v":82.136788830239965},{"$f":"'Project Info'!D78","v":67.872393622439333},{"$f":"'Project Info'!E78","v":32.296248223809314},{"$f":"'Project Info'!F78","v":0},{"$f":"'Project Info'!G78","v":0},{"$f":"'Project Info'!H78","v":0},{"$f":"'Project Info'!I78","v":0},{"$f":"'Project Info'!J78","v":0},{"$f":"'Project Info'!K78","v":0},{"$f":"'Project Info'!L78","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A79","v":75},{"$f":"'Project Info'!B79","v":80},{"$f":"'Project Info'!C79","v":76.988400157585886},{"$f":"'Project Info'!D79","v":65.129261896908645},{"$f":"'Project Info'!E79","v":30.190476812806729},{"$f":"'Project Info'!F79","v":0},{"$f":"'Project Info'!G79","v":0},{"$f":"'Project Info'!H79","v":0},{"$f":"'Project Info'!I79","v":0},{"$f":"'Project Info'!J79","v":0},{"$f":"'Project Info'!K79","v":0},{"$f":"'Project Info'!L79","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A80","v":70},{"$f":"'Project Info'!B80","v":75},{"$f":"'Project Info'!C80","v":72.457982050814195},{"$f":"'Project Info'!D80","v":63.604425012889301},{"$f":"'Project Info'!E80","v":29.088683095945193},{"$f":"'Project Info'!F80","v":0},{"$f":"'Project Info'!G80","v":0},{"$f":"'Project Info'!H80","v":0},{"$f":"'Project Info'!I80","v":0},{"$f":"'Project Info'!J80","v":0},{"$f":"'Project Info'!K80","v":0},{"$f":"'Project Info'!L80","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A81","v":65},{"$f":"'Project Info'!B81","v":70},{"$f":"'Project Info'!C81","v":67.815831070966169},{"$f":"'Project Info'!D81","v":61.631331368130574},{"$f":"'Project Info'!E81","v":27.661514889731574},{"$f":"'Project Info'!F81","v":0},{"$f":"'Project Info'!G81","v":0},{"$f":"'Project Info'!H81","v":0},{"$f":"'Project Info'!I81","v":0},{"$f":"'Project Info'!J81","v":0},{"$f":"'Project Info'!K81","v":0},{"$f":"'Project Info'!L81","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A82","v":60},{"$f":"'Project Info'!B82","v":65},{"$f":"'Project Info'!C82","v":62.535961472271332},{"$f":"'Project Info'!D82","v":57.135476922863582},{"$f":"'Project Info'!E82","v":24.623037157728302},{"$f":"'Project Info'!F82","v":0},{"$f":"'Project Info'!G82","v":0},{"$f":"'Project Info'!H82","v":0},{"$f":"'Project Info'!I82","v":0},{"$f":"'Project Info'!J82","v":0},{"$f":"'Project Info'!K82","v":0},{"$f":"'Project Info'!L82","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A83","v":55},{"$f":"'Project Info'!B83","v":60},{"$f":"'Project Info'!C83","v":57.125792270740902},{"$f":"'Project Info'!D83","v":52.596971157053673},{"$f":"'Project Info'!E83","v":21.818001539159841},{"$f":"'Project Info'!F83","v":0},{"$f":"'Project Info'!G83","v":0},{"$f":"'Project Info'!H83","v":0},{"$f":"'Project Info'!I83","v":0},{"$f":"'Project Info'!J83","v":0},{"$f":"'Project Info'!K83","v":0},{"$f":"'Project Info'!L83","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A84","v":50},{"$f":"'Project Info'!B84","v":55},{"$f":"'Project Info'!C84","v":52.235698854337961},{"$f":"'Project Info'!D84","v":48.022768090099298},{"$f":"'Project Info'!E84","v":19.246640192796217},{"$f":"'Project Info'!F84","v":0},{"$f":"'Project Info'!G84","v":0},{"$f":"'Project Info'!H84","v":0},{"$f":"'Project Info'!I84","v":0},{"$f":"'Project Info'!J84","v":0},{"$f":"'Project Info'!K84","v":0},{"$f":"'Project Info'!L84","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A85","v":45},{"$f":"'Project Info'!B85","v":50},{"$f":"'Project Info'!C85","v":47.459170258371508},{"$f":"'Project Info'!D85","v":43.465397050422162},{"$f":"'Project Info'!E85","v":16.894183241713304},{"$f":"'Project Info'!F85","v":0},{"$f":"'Project Info'!G85","v":0},{"$f":"'Project Info'!H85","v":0},{"$f":"'Project Info'!I85","v":0},{"$f":"'Project Info'!J85","v":0},{"$f":"'Project Info'!K85","v":0},{"$f":"'Project Info'!L85","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A86","v":40},{"$f":"'Project Info'!B86","v":45},{"$f":"'Project Info'!C86","v":42.677030404888129},{"$f":"'Project Info'!D86","v":38.812544504634097},{"$f":"'Project Info'!E86","v":14.690265649465921},{"$f":"'Project Info'!F86","v":0},{"$f":"'Project Info'!G86","v":0},{"$f":"'Project Info'!H86","v":0},{"$f":"'Project Info'!I86","v":0},{"$f":"'Project Info'!J86","v":0},{"$f":"'Project Info'!K86","v":0},{"$f":"'Project Info'!L86","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A87","v":35},{"$f":"'Project Info'!B87","v":40},{"$f":"'Project Info'!C87","v":37.333046773755832},{"$f":"'Project Info'!D87","v":33.904706919479686},{"$f":"'Project Info'!E87","v":12.53841602318813},{"$f":"'Project Info'!F87","v":0},{"$f":"'Project Info'!G87","v":0},{"$f":"'Project Info'!H87","v":0},{"$f":"'Project Info'!I87","v":0},{"$f":"'Project Info'!J87","v":0},{"$f":"'Project Info'!K87","v":0},{"$f":"'Project Info'!L87","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A88","v":30},{"$f":"'Project Info'!B88","v":35},{"$f":"'Project Info'!C88","v":32.638179845662044},{"$f":"'Project Info'!D88","v":29.547170928664851},{"$f":"'Project Info'!E88","v":10.728972818165861},{"$f":"'Project Info'!F88","v":0},{"$f":"'Project Info'!G88","v":0},{"$f":"'Project Info'!H88","v":0},{"$f":"'Project Info'!I88","v":0},{"$f":"'Project Info'!J88","v":0},{"$f":"'Project Info'!K88","v":0},{"$f":"'Project Info'!L88","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A89","v":25},{"$f":"'Project Info'!B89","v":30},{"$f":"'Project Info'!C89","v":27.529264646850947},{"$f":"'Project Info'!D89","v":24.652717392657845},{"$f":"'Project Info'!E89","v":8.8041305482613303},{"$f":"'Project Info'!F89","v":0},{"$f":"'Project Info'!G89","v":0},{"$f":"'Project Info'!H89","v":0},{"$f":"'Project Info'!I89","v":0},{"$f":"'Project Info'!J89","v":0},{"$f":"'Project Info'!K89","v":0},{"$f":"'Project Info'!L89","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A90","v":20},{"$f":"'Project Info'!B90","v":25},{"$f":"'Project Info'!C90","v":22.998111483544687},{"$f":"'Project Info'!D90","v":20.383306659827422},{"$f":"'Project Info'!E90","v":7.246164547543378},{"$f":"'Project Info'!F90","v":0},{"$f":"'Project Info'!G90","v":0},{"$f":"'Project Info'!H90","v":0},{"$f":"'Project Info'!I90","v":0},{"$f":"'Project Info'!J90","v":0},{"$f":"'Project Info'!K90","v":0},{"$f":"'Project Info'!L90","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A91","v":15},{"$f":"'Project Info'!B91","v":20},{"$f":"'Project Info'!C91","v":17.808510327474309},{"$f":"'Project Info'!D91","v":15.420865796304254},{"$f":"'Project Info'!E91","v":5.5490484131518292},{"$f":"'Project Info'!F91","v":0},{"$f":"'Project Info'!G91","v":0},{"$f":"'Project Info'!H91","v":0},{"$f":"'Project Info'!I91","v":0},{"$f":"'Project Info'!J91","v":0},{"$f":"'Project Info'!K91","v":0},{"$f":"'Project Info'!L91","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A92","v":10},{"$f":"'Project Info'!B92","v":15},{"$f":"'Project Info'!C92","v":12.269931130346862},{"$f":"'Project Info'!D92","v":10.318264913023604},{"$f":"'Project Info'!E92","v":3.9082824916941998},{"$f":"'Project Info'!F92","v":0},{"$f":"'Project Info'!G92","v":0},{"$f":"'Project Info'!H92","v":0},{"$f":"'Project Info'!I92","v":0},{"$f":"'Project Info'!J92","v":0},{"$f":"'Project Info'!K92","v":0},{"$f":"'Project Info'!L92","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A93","v":5},{"$f":"'Project Info'!B93","v":10},{"$f":"'Project Info'!C93","v":7.3137581369917548},{"$f":"'Project Info'!D93","v":5.7052382449247707},{"$f":"'Project Info'!E93","v":2.5019418419888937},{"$f":"'Project Info'!F93","v":0},{"$f":"'Project Info'!G93","v":0},{"$f":"'Project Info'!H93","v":0},{"$f":"'Project Info'!I93","v":0},{"$f":"'Project Info'!J93","v":0},{"$f":"'Project Info'!K93","v":0},{"$f":"'Project Info'!L93","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A94","v":0},{"$f":"'Project Info'!B94","v":5},{"$f":"'Project Info'!C94","v":2.6119461836144886},{"$f":"'Project Info'!D94","v":1.2699770062067783},{"$f":"'Project Info'!E94","v":1.2046477897733283},{"$f":"'Project Info'!F94","v":8760},{"$f":"'Project Info'!G94","v":2672},{"$f":"'Project Info'!H94","v":3160},{"$f":"'Project Info'!I94","v":1344},{"$f":"'Project Info'!J94","v":1584},{"$f":"'Project Info'!K94","v":88},{"$f":"'Project Info'!L94","v":264},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A95","v":-5},{"$f":"'Project Info'!B95","v":0},{"$f":"'Project Info'!C95","v":-1.6731398516793925},{"$f":"'Project Info'!D95","v":-2.7083318773557807},{"$f":"'Project Info'!E95","v":7.9391832815876459E-2},{"$f":"'Project Info'!F95","v":0},{"$f":"'Project Info'!G95","v":0},{"$f":"'Project Info'!H95","v":0},{"$f":"'Project Info'!I95","v":0},{"$f":"'Project Info'!J95","v":0},{"$f":"'Project Info'!K95","v":0},{"$f":"'Project Info'!L95","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A96","v":-10},{"$f":"'Project Info'!B96","v":-5},{"$f":"'Project Info'!C96","v":-6.5729865085377277},{"$f":"'Project Info'!D96","v":-7.2465935998252222},{"$f":"'Project Info'!E96","v":-1.168423365310433},{"$f":"'Project Info'!F96","v":0},{"$f":"'Project Info'!G96","v":0},{"$f":"'Project Info'!H96","v":0},{"$f":"'Project Info'!I96","v":0},{"$f":"'Project Info'!J96","v":0},{"$f":"'Project Info'!K96","v":0},{"$f":"'Project Info'!L96","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A97","v":-15},{"$f":"'Project Info'!B97","v":-10},{"$f":"'Project Info'!C97","v":-15.32570353422995},{"$f":"'Project Info'!D97","v":-15.707838211108999},{"$f":"'Project Info'!E97","v":-3.4051318156661381},{"$f":"'Project Info'!F97","v":0},{"$f":"'Project Info'!G97","v":0},{"$f":"'Project Info'!H97","v":0},{"$f":"'Project Info'!I97","v":0},{"$f":"'Project Info'!J97","v":0},{"$f":"'Project Info'!K97","v":0},{"$f":"'Project Info'!L97","v":0},{"$error":"#N/A"},{"$error":"#N/A"},0,0,0,0,0,0]
[]
[]
[null,null,null,null,null,null,null,null,null,"Occ","DHW","DHW","DHW",null,null,null,null,null,"Water Heater Types (Eligible Types)"]
[null,null,null,null,null,null,"Bldg",null,null,"Density","gal/day","Use","gal/day",null,null,null,null,null,"Fossil Fuel"]
[null,null,null,null,null,null,"Type",null,null,"ft²/person","per person","Category","per ft²",null,null,null,null,null,"Electric"]
[null,null,null,null,null,null,{"$f":"'Project Info'!E102","v":"Automotive facility"},null,null,500,1,2,{"$f":"LOOKUP(L92,$G$147:$G$150,$I$147:$I$150)","v":0.02}]
[null,null,null,null,null,null,{"$f":"'Project Info'!E103","v":"Convention center"},null,null,10,0.25,2,0.02,null,null,null,null,null,"Incremental Cost"]
[null,null,null,null,null,null,{"$f":"'Project Info'!E104","v":"Courthouse"},null,null,15,0.25,1,0.01,null,"Building Occupied Hours from Project Info",null,null,null,"$/reduction in rated gpm",null,60,"per fixture"]
[null,null,null,null,null,null,{"$f":"'Project Info'!E105","v":"Daycare"},null,null,null,null,2,0.02,null,"Weekday Occ Hours",null,{"$f":"'Project Info'!J15-'Project Info'!I15","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!E106","v":"Dining: bar/lounge/leisure"},null,null,10,2.5,2,0.02,null,"Saturday Occ Hour",null,{"$f":"'Project Info'!J16-'Project Info'!I16","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!E107","v":"Dining: Cafeteria/Fast Food"},null,null,100,2.5,2,0.02,null,"Sunday Occ Hours",null,{"$f":"'Project Info'!J17-'Project Info'!I17","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!E108","v":"Dining: Family"},null,null,15,2.5,2,0.02,null,"Avg. Daily Occ Hrs",null,{"$f":"(5*Q95+Q96+Q97)/7","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!E109","v":"Dormitory"},null,null,50,12,4,0.04]
[null,null,null,null,null,null,{"$f":"'Project Info'!E110","v":"Education - College/University"},null,null,null,null,1,0.01,null,"DHW gallons per day",null,null,{"$f":"IF(U23>0,U23,U22)","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,{"$f":"'Project Info'!E111","v":"Education - Community College"},null,null,null,null,1,0.01,null,"Avg Daily Occ Hrs",null,null,{"$f":"Q98","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!E112","v":"Education - K-12 School"},null,null,null,null,1,0.01,null,"DHW Loads"]
[null,null,null,null,null,null,{"$f":"'Project Info'!E113","v":"Exercise center"},null,null,50,0.5,3,0.03,null,"Avg Occupied DHW Gal/hr",null,null,{"$f":"R100/R101","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,{"$f":"'Project Info'!E114","v":"Fire station"},null,null,400,1,1,0.01,null,"Annual Occupied DHW gallons",null,null,{"$f":"R103*SUM(L33:L56)","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,{"$f":"'Project Info'!E115","v":"Grocery"},null,null,null,null,2,0.02,null,"Entering Water Temp (°F)",null,null,55]
[null,null,null,null,null,null,{"$f":"'Project Info'!E116","v":"Gymnasium"},null,null,50,0.25,2,0.02,null,"Leaving Water Temp (°F)",null,null,130]
[null,null,null,null,null,null,{"$f":"'Project Info'!E117","v":"Health/Medical - Clinic"},null,null,300,0.25,1,0.01,null,"Annual Occupied DHW Load (kBTU)",null,null,{"$f":"8.33*R104*(R106-R105)/1000","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,{"$f":"'Project Info'!E118","v":"Hospital"},null,null,200,5,2,0.02,null,"Avg Occ Input Load (MBH)",null,null,{"$f":"R107/SUM(L33:L56)","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,{"$f":"'Project Info'!E119","v":"Hotel/Motel/Lodging"},null,null,100,12,3,0.03,null,"Avg Unocc Input Load (MBH)",null,null,{"$f":"0.1*R108","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,{"$f":"'Project Info'!E120","v":"Industrial/Manufacturing - 1 Shift"},null,null,null,null,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E121","v":"Industrial/Manufacturing - 2 Shifts"},null,null,250,1,2,0.02]
[null,null,null,null,null,null,{"$f":"'Project Info'!E122","v":"Industrial/Manufacturing - 3 Shifts"},null,null,null,null,2,0.02]
[null,null,null,null,null,null,{"$f":"'Project Info'!E123","v":"Library"},null,null,500,0.25,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E124","v":"Motion picture theater"},null,null,15,0.25,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E125","v":"Multifamily"},null,null,200,15,4,0.04]
[null,null,null,null,null,null,{"$f":"'Project Info'!E126","v":"Museum"},null,null,500,0.25,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E127","v":"Nursing Home"},null,null,null,null,4,0.04]
[null,null,null,null,null,null,{"$f":"'Project Info'!E128","v":"Office - Medium/Large ( > 20,000 ft²)"},null,null,200,1,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E129","v":"Office - Small ( < 20,000 ft²)"},null,null,null,null,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E130","v":"Parking garage"},null,null,1000,0.25,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E131","v":"Penitentiary"},null,null,40,15,4,0.04]
[null,null,null,null,null,null,{"$f":"'Project Info'!E132","v":"Performing arts theater"},null,null,15,0.25,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E133","v":"Police station"},null,null,1000,1,1,{"$f":"LOOKUP(L123,$G$147:$G$150,$I$147:$I$150)","v":0.01}]
[null,null,null,null,null,null,{"$f":"'Project Info'!E134","v":"Post office"},null,null,1000,0.25,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E135","v":"Religious Worship/Church"},null,null,10,0.1,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E136","v":"Retail"},null,null,1000,0.1,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E137","v":"Sports arena"},null,null,10,0.1,2,0.02]
[null,null,null,null,null,null,{"$f":"'Project Info'!E138","v":"Storage Facility"},null,null,null,null,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E139","v":"Town hall"},null,null,1000,1,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E140","v":"Transportation"},null,null,1000,0.5,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E141","v":"Warehouse - Distribution Center"},null,null,10000,1,2,0.02]
[null,null,null,null,null,null,{"$f":"'Project Info'!E142","v":"Warehouse - Inactive Storage"},null,null,null,null,1,0.01]
[null,null,null,null,null,null,{"$f":"'Project Info'!E143","v":"Workshop"},null,null,1000,2,1,{"$f":"LOOKUP(L133,$G$147:$G$150,$I$147:$I$150)","v":0.01}]
[]
[null,null,null,null,null,null,"Estimate of Daily DHW Gallons per ft² by Building Type per ASHRAE Handbook DHW Use Data"]
[null,null,null,null,null,null,"Bldg Type",null,"Avg Daily","Daily gal/unit","ft²/unit","Daily gal/ft²","Source of ft² per unit estimate"]
[null,null,null,null,null,null,"Dormitories",null,"gal/student",12.8,{"$f":"52000/165","v":315.15151515151513},{"$f":"J137/K137","v":4.0615384615384623E-2},"IMC"]
[null,null,null,null,null,null,"Hotel/Motel",null,"gal/room",16,{"$f":"105000/175","v":600},{"$f":"J138/K138","v":2.6666666666666668E-2},"Aloft Hotel Providence"]
[null,null,null,null,null,null,"Nursing Home",null,"gal/bed",18.399999999999999,{"$f":"42000/54","v":777.77777777777783},2.3657142857142852E-2,"Bridges at Lexington"]
[null,null,null,null,null,null,"Office",null,"gal/person",1,100,0.01,"52 Dunham Rd"]
[null,null,null,null,null,null,"Dining",null,"gal/daily meals",2.4,{"$f":"225000/1500","v":150},1.6E-2,"1500 daily meal per 225,000 ft² (Pentucket MS/HS)"]
[null,null,null,null,null,null,"Multifamily",null,"gal/apt",38,1000,3.7999999999999999E-2,"Waterside Place"]
[null,null,null,null,null,null,"Elementary School",null,"gal/student",1,235,4.2553191489361703E-3,"Amesbury Elem"]
[null,null,null,null,null,null,"Jr/Sr High School",null,"gal/student",1.8,{"$f":"225000/1000","v":225},8.0000000000000002E-3,"Pentucket MS/HS"]
[]
[null,null,null,null,null,null,"DHW Load Category",null,"Daily gal/ft²","Ex. Bldg Type"]
[null,null,null,null,null,null,1,"Minimal",0.01,"Office/School"]
[null,null,null,null,null,null,2,"Light",0.02,"Dining"]
[null,null,null,null,null,null,3,"Moderate",0.03,"Hotel"]
[null,null,null,null,null,null,4,"Heavy",0.04,"Dorm/Multifamily"]

{"sheet":"17","index":20,"n_rows":109,"n_cols":27,"rows_kept":109,"cut":false,"hidden":true,"merged":[]}
["Savings Summary",null,null,null,null,"Measure Summary",null,null,null,null,"Measure Description"]
["Annual kWh Savings",null,null,{"$f":"SUM(A14:D14)","v":0},null,null,null,"Value","Unit"]
["% On Peak",null,null,{"$f":"IF(D2<=0,0,MIN(1,A15+C15))","v":0},null,"Annual Electric Savings",null,{"$f":"D2","v":0},"kWh"]
["Max kW",null,null,{"$f":"MAX(AC41:AC64,AC71:AC94)","v":0},null,"Annual Fuel Savings",null,{"$f":"D7*C28","v":{"$error":"#DIV/0!"}},{"$f":"D20","v":{"$error":"#N/A"}}]
["Summer kW",null,null,{"$f":"(SUMPRODUCT(AC41:AC64,R33:R56)+SUMPRODUCT(AC71:AC94,R63:R86))/SUM(R33:R56,R63:R86)","v":0},null,"Incremental Cost",null,45000,"$",null,"Measure Instructions"]
["Winter kW",null,null,{"$f":"(SUMPRODUCT(AC41:AC64,Q33:Q56)+SUMPRODUCT(AC71:AC94,Q63:Q86))/SUM(Q33:Q56,Q63:Q86)","v":0},null,"Estimated Incentive",null,{"$f":"IF(AND($C$24>0,$C$25>0),MIN(H5,H3*C24+H4*C25),\"TBD\")","v":"TBD"},"$"]
["Annual Fuel Savings (MMBtu)",null,null,{"$f":"(SUMPRODUCT($L$33:$L$56,Z33:Z56)+SUMPRODUCT($L$63:$L$86,Z63:Z86))/1000","v":{"$error":"#DIV/0!"}},null,"Custom Payback",null,null,"years"]
["Incremental Cost",null,null,45000]
[]
["kWh Savings by Peak Period"]
["Winter","Winter","Summer","Summer"]
["On-Peak","Off-Peak","On-Peak","Off-Peak"]
["kWh","kWh","kWh","kWh"]
[{"$f":"SUMPRODUCT($AA$33:$AA$56,M33:M56)+SUMPRODUCT($AA$63:$AA$86,M63:M86)","v":0},{"$f":"SUMPRODUCT($AA$33:$AA$56,N33:N56)+SUMPRODUCT($AA$63:$AA$86,N63:N86)","v":0},{"$f":"SUMPRODUCT($AA$33:$AA$56,O33:O56)+SUMPRODUCT($AA$63:$AA$86,O63:O86)","v":0},{"$f":"SUMPRODUCT($AA$33:$AA$56,P33:P56)+SUMPRODUCT($AA$63:$AA$86,P63:P86)","v":0}]
[{"$f":"IF(A14<=0,0,A14/SUMIF($A$14:$D$14,\">0\"))","v":0},{"$f":"IF(B14<=0,0,B14/SUMIF($A$14:$D$14,\">0\"))","v":0},{"$f":"IF(C14<=0,0,C14/SUMIF($A$14:$D$14,\">0\"))","v":0},{"$f":"IF(D14<=0,0,D14/SUMIF($A$14:$D$14,\">0\"))","v":0}]
[]
["Utility Rates"]
[null,null,"Rate","Unit"]
["Electric",null,{"$f":"'ECM Summary'!$E$31","v":0.1593},"kWh"]
[{"$f":"'ECM Summary'!$C$32","v":0},null,{"$f":"'ECM Summary'!$E$32","v":{"$error":"#N/A"}},{"$f":"'ECM Summary'!$F$32","v":{"$error":"#N/A"}}]
[]
["Custom Incentive Rates"]
[null,null,"Rate","Unit"]
["Electric",null,{"$f":"'ECM Summary'!$J$31","v":0.28000000000000003},"kWh"]
[{"$f":"'ECM Summary'!$H$32","v":0},null,{"$f":"'ECM Summary'!$J$32","v":0},{"$f":"'ECM Summary'!$K$32","v":{"$error":"#N/A"}}]
[]
["Fossil Fuel",null,{"$f":"'Project Info'!C21","v":0}]
["Fuel Conversion",null,{"$f":"LOOKUP(C27,'Project Info'!X102:X104,'Project Info'!Z102:Z104)","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,"Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Heating","Heating","Base","Return","Proposed","Base","Design","Demand","Demand"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Load","Load","Eff.","HWT","Eff.","Demand","Demand","Savings","Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","%","MBH","%","°F","%","MBH","MBH","MBH","kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A44","v":100},{"$f":"'Project Info'!B44","v":105},{"$f":"'Project Info'!C44","v":102},{"$f":"'Project Info'!D44","v":76},{"$f":"'Project Info'!E44","v":40},{"$f":"'Project Info'!F44","v":0},{"$f":"'Project Info'!G44","v":0},{"$f":"'Project Info'!H44","v":0},{"$f":"'Project Info'!I44","v":0},{"$f":"'Project Info'!J44","v":0},{"$f":"'Project Info'!K44","v":0},{"$f":"'Project Info'!L44","v":0},{"$f":"MAX($U$93,MIN(1,TREND($U$93:$V$93,$S$93:$T$93,I33)))","v":0.1},{"$f":"S33*$U$103","v":{"$error":"#DIV/0!"}},{"$f":"$V$100","v":0.82450000000000001},{"$f":"IF(I33>$T$109,$U$109,IF(I33<$T$108,$U$108,$U$108+(I33*(($U$108-$U$109)/($T$108-$T$109)))))","v":0},{"$f":"MAX($Y$106,MIN($Y$100,TREND(OFFSET($X$99,MATCH(V33,$X$100:$X$106,1),1,2,1),OFFSET($X$99,MATCH(V33,$X$100:$X$106,1),0,2,1),V33)))","v":{"$error":"#N/A"}},{"$f":"T33/U33","v":{"$error":"#DIV/0!"}},{"$f":"T33/W33","v":{"$error":"#DIV/0!"}},{"$f":"X33-Y33","v":{"$error":"#DIV/0!"}},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A45","v":95},{"$f":"'Project Info'!B45","v":100},{"$f":"'Project Info'!C45","v":95.219272727272724},{"$f":"'Project Info'!D45","v":74.534025272781079},{"$f":"'Project Info'!E45","v":37.923296058061368},{"$f":"'Project Info'!F45","v":0},{"$f":"'Project Info'!G45","v":0},{"$f":"'Project Info'!H45","v":0},{"$f":"'Project Info'!I45","v":0},{"$f":"'Project Info'!J45","v":0},{"$f":"'Project Info'!K45","v":0},{"$f":"'Project Info'!L45","v":0},0.1,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$f":"T34/U34","v":{"$error":"#DIV/0!"}},{"$f":"T34/W34","v":{"$error":"#DIV/0!"}},{"$f":"X34-Y34","v":{"$error":"#DIV/0!"}},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A46","v":90},{"$f":"'Project Info'!B46","v":95},{"$f":"'Project Info'!C46","v":92.016049160256074},{"$f":"'Project Info'!D46","v":72.911561930607689},{"$f":"'Project Info'!E46","v":36.467095439351091},{"$f":"'Project Info'!F46","v":0},{"$f":"'Project Info'!G46","v":0},{"$f":"'Project Info'!H46","v":0},{"$f":"'Project Info'!I46","v":0},{"$f":"'Project Info'!J46","v":0},{"$f":"'Project Info'!K46","v":0},{"$f":"'Project Info'!L46","v":0},0.1,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A47","v":85},{"$f":"'Project Info'!B47","v":90},{"$f":"'Project Info'!C47","v":87.457811360655285},{"$f":"'Project Info'!D47","v":70.80538329449476},{"$f":"'Project Info'!E47","v":34.679413213566804},{"$f":"'Project Info'!F47","v":0},{"$f":"'Project Info'!G47","v":0},{"$f":"'Project Info'!H47","v":0},{"$f":"'Project Info'!I47","v":0},{"$f":"'Project Info'!J47","v":0},{"$f":"'Project Info'!K47","v":0},{"$f":"'Project Info'!L47","v":0},0.1,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A48","v":80},{"$f":"'Project Info'!B48","v":85},{"$f":"'Project Info'!C48","v":82.136788830239965},{"$f":"'Project Info'!D48","v":67.872393622439333},{"$f":"'Project Info'!E48","v":32.296248223809314},{"$f":"'Project Info'!F48","v":0},{"$f":"'Project Info'!G48","v":0},{"$f":"'Project Info'!H48","v":0},{"$f":"'Project Info'!I48","v":0},{"$f":"'Project Info'!J48","v":0},{"$f":"'Project Info'!K48","v":0},{"$f":"'Project Info'!L48","v":0},0.1,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A49","v":75},{"$f":"'Project Info'!B49","v":80},{"$f":"'Project Info'!C49","v":76.988400157585886},{"$f":"'Project Info'!D49","v":65.129261896908645},{"$f":"'Project Info'!E49","v":30.190476812806729},{"$f":"'Project Info'!F49","v":0},{"$f":"'Project Info'!G49","v":0},{"$f":"'Project Info'!H49","v":0},{"$f":"'Project Info'!I49","v":0},{"$f":"'Project Info'!J49","v":0},{"$f":"'Project Info'!K49","v":0},{"$f":"'Project Info'!L49","v":0},0.1,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A50","v":70},{"$f":"'Project Info'!B50","v":75},{"$f":"'Project Info'!C50","v":72.457982050814195},{"$f":"'Project Info'!D50","v":63.604425012889301},{"$f":"'Project Info'!E50","v":29.088683095945193},{"$f":"'Project Info'!F50","v":0},{"$f":"'Project Info'!G50","v":0},{"$f":"'Project Info'!H50","v":0},{"$f":"'Project Info'!I50","v":0},{"$f":"'Project Info'!J50","v":0},{"$f":"'Project Info'!K50","v":0},{"$f":"'Project Info'!L50","v":0},0.1,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A51","v":65},{"$f":"'Project Info'!B51","v":70},{"$f":"'Project Info'!C51","v":67.815831070966169},{"$f":"'Project Info'!D51","v":61.631331368130574},{"$f":"'Project Info'!E51","v":27.661514889731574},{"$f":"'Project Info'!F51","v":0},{"$f":"'Project Info'!G51","v":0},{"$f":"'Project Info'!H51","v":0},{"$f":"'Project Info'!I51","v":0},{"$f":"'Project Info'!J51","v":0},{"$f":"'Project Info'!K51","v":0},{"$f":"'Project Info'!L51","v":0},0.1,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A52","v":60},{"$f":"'Project Info'!B52","v":65},{"$f":"'Project Info'!C52","v":62.535961472271332},{"$f":"'Project Info'!D52","v":57.135476922863582},{"$f":"'Project Info'!E52","v":24.623037157728302},{"$f":"'Project Info'!F52","v":0},{"$f":"'Project Info'!G52","v":0},{"$f":"'Project Info'!H52","v":0},{"$f":"'Project Info'!I52","v":0},{"$f":"'Project Info'!J52","v":0},{"$f":"'Project Info'!K52","v":0},{"$f":"'Project Info'!L52","v":0},0.1,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A53","v":55},{"$f":"'Project Info'!B53","v":60},{"$f":"'Project Info'!C53","v":57.125792270740902},{"$f":"'Project Info'!D53","v":52.596971157053673},{"$f":"'Project Info'!E53","v":21.818001539159841},{"$f":"'Project Info'!F53","v":0},{"$f":"'Project Info'!G53","v":0},{"$f":"'Project Info'!H53","v":0},{"$f":"'Project Info'!I53","v":0},{"$f":"'Project Info'!J53","v":0},{"$f":"'Project Info'!K53","v":0},{"$f":"'Project Info'!L53","v":0},0.1,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A54","v":50},{"$f":"'Project Info'!B54","v":55},{"$f":"'Project Info'!C54","v":52.235698854337961},{"$f":"'Project Info'!D54","v":48.022768090099298},{"$f":"'Project Info'!E54","v":19.246640192796217},{"$f":"'Project Info'!F54","v":0},{"$f":"'Project Info'!G54","v":0},{"$f":"'Project Info'!H54","v":0},{"$f":"'Project Info'!I54","v":0},{"$f":"'Project Info'!J54","v":0},{"$f":"'Project Info'!K54","v":0},{"$f":"'Project Info'!L54","v":0},0.13769501562266417,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A55","v":45},{"$f":"'Project Info'!B55","v":50},{"$f":"'Project Info'!C55","v":47.459170258371508},{"$f":"'Project Info'!D55","v":43.465397050422162},{"$f":"'Project Info'!E55","v":16.894183241713304},{"$f":"'Project Info'!F55","v":0},{"$f":"'Project Info'!G55","v":0},{"$f":"'Project Info'!H55","v":0},{"$f":"'Project Info'!I55","v":0},{"$f":"'Project Info'!J55","v":0},{"$f":"'Project Info'!K55","v":0},{"$f":"'Project Info'!L55","v":0},0.20282949647675219,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A56","v":40},{"$f":"'Project Info'!B56","v":45},{"$f":"'Project Info'!C56","v":42.677030404888129},{"$f":"'Project Info'!D56","v":38.812544504634097},{"$f":"'Project Info'!E56","v":14.690265649465921},{"$f":"'Project Info'!F56","v":0},{"$f":"'Project Info'!G56","v":0},{"$f":"'Project Info'!H56","v":0},{"$f":"'Project Info'!I56","v":0},{"$f":"'Project Info'!J56","v":0},{"$f":"'Project Info'!K56","v":0},{"$f":"'Project Info'!L56","v":0},0.26804049447879819,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A57","v":35},{"$f":"'Project Info'!B57","v":40},{"$f":"'Project Info'!C57","v":37.333046773755832},{"$f":"'Project Info'!D57","v":33.904706919479686},{"$f":"'Project Info'!E57","v":12.53841602318813},{"$f":"'Project Info'!F57","v":0},{"$f":"'Project Info'!G57","v":0},{"$f":"'Project Info'!H57","v":0},{"$f":"'Project Info'!I57","v":0},{"$f":"'Project Info'!J57","v":0},{"$f":"'Project Info'!K57","v":0},{"$f":"'Project Info'!L57","v":0},0.34091299853969315,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A58","v":30},{"$f":"'Project Info'!B58","v":35},{"$f":"'Project Info'!C58","v":32.638179845662044},{"$f":"'Project Info'!D58","v":29.547170928664851},{"$f":"'Project Info'!E58","v":10.728972818165861},{"$f":"'Project Info'!F58","v":0},{"$f":"'Project Info'!G58","v":0},{"$f":"'Project Info'!H58","v":0},{"$f":"'Project Info'!I58","v":0},{"$f":"'Project Info'!J58","v":0},{"$f":"'Project Info'!K58","v":0},{"$f":"'Project Info'!L58","v":0},0.40493391119551753,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A59","v":25},{"$f":"'Project Info'!B59","v":30},{"$f":"'Project Info'!C59","v":27.529264646850947},{"$f":"'Project Info'!D59","v":24.652717392657845},{"$f":"'Project Info'!E59","v":8.8041305482613303},{"$f":"'Project Info'!F59","v":0},{"$f":"'Project Info'!G59","v":0},{"$f":"'Project Info'!H59","v":0},{"$f":"'Project Info'!I59","v":0},{"$f":"'Project Info'!J59","v":0},{"$f":"'Project Info'!K59","v":0},{"$f":"'Project Info'!L59","v":0},0.47460093663385067,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A60","v":20},{"$f":"'Project Info'!B60","v":25},{"$f":"'Project Info'!C60","v":22.998111483544687},{"$f":"'Project Info'!D60","v":20.383306659827422},{"$f":"'Project Info'!E60","v":7.246164547543378},{"$f":"'Project Info'!F60","v":0},{"$f":"'Project Info'!G60","v":0},{"$f":"'Project Info'!H60","v":0},{"$f":"'Project Info'!I60","v":0},{"$f":"'Project Info'!J60","v":0},{"$f":"'Project Info'!K60","v":0},{"$f":"'Project Info'!L60","v":0},0.53638938886075427,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A61","v":15},{"$f":"'Project Info'!B61","v":20},{"$f":"'Project Info'!C61","v":17.808510327474309},{"$f":"'Project Info'!D61","v":15.420865796304254},{"$f":"'Project Info'!E61","v":5.5490484131518292},{"$f":"'Project Info'!F61","v":0},{"$f":"'Project Info'!G61","v":0},{"$f":"'Project Info'!H61","v":0},{"$f":"'Project Info'!I61","v":0},{"$f":"'Project Info'!J61","v":0},{"$f":"'Project Info'!K61","v":0},{"$f":"'Project Info'!L61","v":0},0.60715667735262291,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A62","v":10},{"$f":"'Project Info'!B62","v":15},{"$f":"'Project Info'!C62","v":12.269931130346862},{"$f":"'Project Info'!D62","v":10.318264913023604},{"$f":"'Project Info'!E62","v":3.9082824916941998},{"$f":"'Project Info'!F62","v":0},{"$f":"'Project Info'!G62","v":0},{"$f":"'Project Info'!H62","v":0},{"$f":"'Project Info'!I62","v":0},{"$f":"'Project Info'!J62","v":0},{"$f":"'Project Info'!K62","v":0},{"$f":"'Project Info'!L62","v":0},0.68268275731345174,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A63","v":5},{"$f":"'Project Info'!B63","v":10},{"$f":"'Project Info'!C63","v":7.3137581369917548},{"$f":"'Project Info'!D63","v":5.7052382449247707},{"$f":"'Project Info'!E63","v":2.5019418419888937},{"$f":"'Project Info'!F63","v":0},{"$f":"'Project Info'!G63","v":0},{"$f":"'Project Info'!H63","v":0},{"$f":"'Project Info'!I63","v":0},{"$f":"'Project Info'!J63","v":0},{"$f":"'Project Info'!K63","v":0},{"$f":"'Project Info'!L63","v":0},0.75026693449556681,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A64","v":0},{"$f":"'Project Info'!B64","v":5},{"$f":"'Project Info'!C64","v":2.6119461836144886},{"$f":"'Project Info'!D64","v":1.2699770062067783},{"$f":"'Project Info'!E64","v":1.2046477897733283},{"$f":"'Project Info'!F64","v":0},{"$f":"'Project Info'!G64","v":0},{"$f":"'Project Info'!H64","v":0},{"$f":"'Project Info'!I64","v":0},{"$f":"'Project Info'!J64","v":0},{"$f":"'Project Info'!K64","v":0},{"$f":"'Project Info'!L64","v":0},0.81438255204162047,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A65","v":-5},{"$f":"'Project Info'!B65","v":0},{"$f":"'Project Info'!C65","v":-1.6731398516793925},{"$f":"'Project Info'!D65","v":-2.7083318773557807},{"$f":"'Project Info'!E65","v":7.9391832815876459E-2},{"$f":"'Project Info'!F65","v":0},{"$f":"'Project Info'!G65","v":0},{"$f":"'Project Info'!H65","v":0},{"$f":"'Project Info'!I65","v":0},{"$f":"'Project Info'!J65","v":0},{"$f":"'Project Info'!K65","v":0},{"$f":"'Project Info'!L65","v":0},0.87281554343199153,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A66","v":-10},{"$f":"'Project Info'!B66","v":-5},{"$f":"'Project Info'!C66","v":-6.5729865085377277},{"$f":"'Project Info'!D66","v":-7.2465935998252222},{"$f":"'Project Info'!E66","v":-1.168423365310433},{"$f":"'Project Info'!F66","v":0},{"$f":"'Project Info'!G66","v":0},{"$f":"'Project Info'!H66","v":0},{"$f":"'Project Info'!I66","v":0},{"$f":"'Project Info'!J66","v":0},{"$f":"'Project Info'!K66","v":0},{"$f":"'Project Info'!L66","v":0},0.93963163420733253,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A67","v":-15},{"$f":"'Project Info'!B67","v":-10},{"$f":"'Project Info'!C67","v":-15.32570353422995},{"$f":"'Project Info'!D67","v":-15.707838211108999},{"$f":"'Project Info'!E67","v":-3.4051318156661381},{"$f":"'Project Info'!F67","v":0},{"$f":"'Project Info'!G67","v":0},{"$f":"'Project Info'!H67","v":0},{"$f":"'Project Info'!I67","v":0},{"$f":"'Project Info'!J67","v":0},{"$f":"'Project Info'!K67","v":0},{"$f":"'Project Info'!L67","v":0},1,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[]
[]
[null,null,null,null,null,null,"Unoccupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Heating","Heating","Base","Return","Proposed","Base","Design","Demand","Demand"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Load","Load","Eff.","HWT","Eff.","Demand","Demand","Savings","Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","%","MBH","%","°F","%","MBH","MBH","MBH","kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A74","v":100},{"$f":"'Project Info'!B74","v":105},{"$f":"'Project Info'!C74","v":102},{"$f":"'Project Info'!D74","v":76},{"$f":"'Project Info'!E74","v":40},{"$f":"'Project Info'!F74","v":0},{"$f":"'Project Info'!G74","v":0},{"$f":"'Project Info'!H74","v":0},{"$f":"'Project Info'!I74","v":0},{"$f":"'Project Info'!J74","v":0},{"$f":"'Project Info'!K74","v":0},{"$f":"'Project Info'!L74","v":0},{"$f":"MAX($Y$93,MIN(1,TREND($Y$93:$Z$93,$W$93:$X$93,I63)))","v":0},{"$f":"S63*$U$103","v":{"$error":"#DIV/0!"}},{"$f":"$V$100","v":0.82450000000000001},{"$f":"IF(I63>$T$109,$U$109,IF(I63<$T$108,$U$108,$U$108+(I63*(($U$108-$U$109)/($T$108-$T$109)))))","v":0},{"$f":"MAX($Y$106,MIN($Y$100,TREND(OFFSET($X$99,MATCH(V63,$X$100:$X$106,1),1,2,1),OFFSET($X$99,MATCH(V63,$X$100:$X$106,1),0,2,1),V63)))","v":{"$error":"#N/A"}},{"$f":"T63/U63","v":{"$error":"#DIV/0!"}},{"$f":"T63/W63","v":{"$error":"#DIV/0!"}},{"$f":"X63-Y63","v":{"$error":"#DIV/0!"}},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A75","v":95},{"$f":"'Project Info'!B75","v":100},{"$f":"'Project Info'!C75","v":95.219272727272724},{"$f":"'Project Info'!D75","v":74.534025272781079},{"$f":"'Project Info'!E75","v":37.923296058061368},{"$f":"'Project Info'!F75","v":0},{"$f":"'Project Info'!G75","v":0},{"$f":"'Project Info'!H75","v":0},{"$f":"'Project Info'!I75","v":0},{"$f":"'Project Info'!J75","v":0},{"$f":"'Project Info'!K75","v":0},{"$f":"'Project Info'!L75","v":0},0,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$f":"T64/U64","v":{"$error":"#DIV/0!"}},{"$f":"T64/W64","v":{"$error":"#DIV/0!"}},{"$f":"X64-Y64","v":{"$error":"#DIV/0!"}},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A76","v":90},{"$f":"'Project Info'!B76","v":95},{"$f":"'Project Info'!C76","v":92.016049160256074},{"$f":"'Project Info'!D76","v":72.911561930607689},{"$f":"'Project Info'!E76","v":36.467095439351091},{"$f":"'Project Info'!F76","v":0},{"$f":"'Project Info'!G76","v":0},{"$f":"'Project Info'!H76","v":0},{"$f":"'Project Info'!I76","v":0},{"$f":"'Project Info'!J76","v":0},{"$f":"'Project Info'!K76","v":0},{"$f":"'Project Info'!L76","v":0},0,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A77","v":85},{"$f":"'Project Info'!B77","v":90},{"$f":"'Project Info'!C77","v":87.457811360655285},{"$f":"'Project Info'!D77","v":70.80538329449476},{"$f":"'Project Info'!E77","v":34.679413213566804},{"$f":"'Project Info'!F77","v":0},{"$f":"'Project Info'!G77","v":0},{"$f":"'Project Info'!H77","v":0},{"$f":"'Project Info'!I77","v":0},{"$f":"'Project Info'!J77","v":0},{"$f":"'Project Info'!K77","v":0},{"$f":"'Project Info'!L77","v":0},0,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A78","v":80},{"$f":"'Project Info'!B78","v":85},{"$f":"'Project Info'!C78","v":82.136788830239965},{"$f":"'Project Info'!D78","v":67.872393622439333},{"$f":"'Project Info'!E78","v":32.296248223809314},{"$f":"'Project Info'!F78","v":0},{"$f":"'Project Info'!G78","v":0},{"$f":"'Project Info'!H78","v":0},{"$f":"'Project Info'!I78","v":0},{"$f":"'Project Info'!J78","v":0},{"$f":"'Project Info'!K78","v":0},{"$f":"'Project Info'!L78","v":0},0,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A79","v":75},{"$f":"'Project Info'!B79","v":80},{"$f":"'Project Info'!C79","v":76.988400157585886},{"$f":"'Project Info'!D79","v":65.129261896908645},{"$f":"'Project Info'!E79","v":30.190476812806729},{"$f":"'Project Info'!F79","v":0},{"$f":"'Project Info'!G79","v":0},{"$f":"'Project Info'!H79","v":0},{"$f":"'Project Info'!I79","v":0},{"$f":"'Project Info'!J79","v":0},{"$f":"'Project Info'!K79","v":0},{"$f":"'Project Info'!L79","v":0},0,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A80","v":70},{"$f":"'Project Info'!B80","v":75},{"$f":"'Project Info'!C80","v":72.457982050814195},{"$f":"'Project Info'!D80","v":63.604425012889301},{"$f":"'Project Info'!E80","v":29.088683095945193},{"$f":"'Project Info'!F80","v":0},{"$f":"'Project Info'!G80","v":0},{"$f":"'Project Info'!H80","v":0},{"$f":"'Project Info'!I80","v":0},{"$f":"'Project Info'!J80","v":0},{"$f":"'Project Info'!K80","v":0},{"$f":"'Project Info'!L80","v":0},0,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A81","v":65},{"$f":"'Project Info'!B81","v":70},{"$f":"'Project Info'!C81","v":67.815831070966169},{"$f":"'Project Info'!D81","v":61.631331368130574},{"$f":"'Project Info'!E81","v":27.661514889731574},{"$f":"'Project Info'!F81","v":0},{"$f":"'Project Info'!G81","v":0},{"$f":"'Project Info'!H81","v":0},{"$f":"'Project Info'!I81","v":0},{"$f":"'Project Info'!J81","v":0},{"$f":"'Project Info'!K81","v":0},{"$f":"'Project Info'!L81","v":0},0,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A82","v":60},{"$f":"'Project Info'!B82","v":65},{"$f":"'Project Info'!C82","v":62.535961472271332},{"$f":"'Project Info'!D82","v":57.135476922863582},{"$f":"'Project Info'!E82","v":24.623037157728302},{"$f":"'Project Info'!F82","v":0},{"$f":"'Project Info'!G82","v":0},{"$f":"'Project Info'!H82","v":0},{"$f":"'Project Info'!I82","v":0},{"$f":"'Project Info'!J82","v":0},{"$f":"'Project Info'!K82","v":0},{"$f":"'Project Info'!L82","v":0},0,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A83","v":55},{"$f":"'Project Info'!B83","v":60},{"$f":"'Project Info'!C83","v":57.125792270740902},{"$f":"'Project Info'!D83","v":52.596971157053673},{"$f":"'Project Info'!E83","v":21.818001539159841},{"$f":"'Project Info'!F83","v":0},{"$f":"'Project Info'!G83","v":0},{"$f":"'Project Info'!H83","v":0},{"$f":"'Project Info'!I83","v":0},{"$f":"'Project Info'!J83","v":0},{"$f":"'Project Info'!K83","v":0},{"$f":"'Project Info'!L83","v":0},3.1137250400306904E-2,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A84","v":50},{"$f":"'Project Info'!B84","v":55},{"$f":"'Project Info'!C84","v":52.235698854337961},{"$f":"'Project Info'!D84","v":48.022768090099298},{"$f":"'Project Info'!E84","v":19.246640192796217},{"$f":"'Project Info'!F84","v":0},{"$f":"'Project Info'!G84","v":0},{"$f":"'Project Info'!H84","v":0},{"$f":"'Project Info'!I84","v":0},{"$f":"'Project Info'!J84","v":0},{"$f":"'Project Info'!K84","v":0},{"$f":"'Project Info'!L84","v":0},8.4113262411338763E-2,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A85","v":45},{"$f":"'Project Info'!B85","v":50},{"$f":"'Project Info'!C85","v":47.459170258371508},{"$f":"'Project Info'!D85","v":43.465397050422162},{"$f":"'Project Info'!E85","v":16.894183241713304},{"$f":"'Project Info'!F85","v":0},{"$f":"'Project Info'!G85","v":0},{"$f":"'Project Info'!H85","v":0},{"$f":"'Project Info'!I85","v":0},{"$f":"'Project Info'!J85","v":0},{"$f":"'Project Info'!K85","v":0},{"$f":"'Project Info'!L85","v":0},0.13585898886764203,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A86","v":40},{"$f":"'Project Info'!B86","v":45},{"$f":"'Project Info'!C86","v":42.677030404888129},{"$f":"'Project Info'!D86","v":38.812544504634097},{"$f":"'Project Info'!E86","v":14.690265649465921},{"$f":"'Project Info'!F86","v":0},{"$f":"'Project Info'!G86","v":0},{"$f":"'Project Info'!H86","v":0},{"$f":"'Project Info'!I86","v":0},{"$f":"'Project Info'!J86","v":0},{"$f":"'Project Info'!K86","v":0},{"$f":"'Project Info'!L86","v":0},0.18766550394704523,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A87","v":35},{"$f":"'Project Info'!B87","v":40},{"$f":"'Project Info'!C87","v":37.333046773755832},{"$f":"'Project Info'!D87","v":33.904706919479686},{"$f":"'Project Info'!E87","v":12.53841602318813},{"$f":"'Project Info'!F87","v":0},{"$f":"'Project Info'!G87","v":0},{"$f":"'Project Info'!H87","v":0},{"$f":"'Project Info'!I87","v":0},{"$f":"'Project Info'!J87","v":0},{"$f":"'Project Info'!K87","v":0},{"$f":"'Project Info'!L87","v":0},0.24555865995097842,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A88","v":30},{"$f":"'Project Info'!B88","v":35},{"$f":"'Project Info'!C88","v":32.638179845662044},{"$f":"'Project Info'!D88","v":29.547170928664851},{"$f":"'Project Info'!E88","v":10.728972818165861},{"$f":"'Project Info'!F88","v":0},{"$f":"'Project Info'!G88","v":0},{"$f":"'Project Info'!H88","v":0},{"$f":"'Project Info'!I88","v":0},{"$f":"'Project Info'!J88","v":0},{"$f":"'Project Info'!K88","v":0},{"$f":"'Project Info'!L88","v":0},0.29641971833866115,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A89","v":25},{"$f":"'Project Info'!B89","v":30},{"$f":"'Project Info'!C89","v":27.529264646850947},{"$f":"'Project Info'!D89","v":24.652717392657845},{"$f":"'Project Info'!E89","v":8.8041305482613303},{"$f":"'Project Info'!F89","v":0},{"$f":"'Project Info'!G89","v":0},{"$f":"'Project Info'!H89","v":0},{"$f":"'Project Info'!I89","v":0},{"$f":"'Project Info'!J89","v":0},{"$f":"'Project Info'!K89","v":0},{"$f":"'Project Info'!L89","v":0},0.35176629965911471,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A90","v":20},{"$f":"'Project Info'!B90","v":25},{"$f":"'Project Info'!C90","v":22.998111483544687},{"$f":"'Project Info'!D90","v":20.383306659827422},{"$f":"'Project Info'!E90","v":7.246164547543378},{"$f":"'Project Info'!F90","v":0},{"$f":"'Project Info'!G90","v":0},{"$f":"'Project Info'!H90","v":0},{"$f":"'Project Info'!I90","v":0},{"$f":"'Project Info'!J90","v":0},{"$f":"'Project Info'!K90","v":0},{"$f":"'Project Info'!L90","v":0},0.40085379226159917,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A91","v":15},{"$f":"'Project Info'!B91","v":20},{"$f":"'Project Info'!C91","v":17.808510327474309},{"$f":"'Project Info'!D91","v":15.420865796304254},{"$f":"'Project Info'!E91","v":5.5490484131518292},{"$f":"'Project Info'!F91","v":0},{"$f":"'Project Info'!G91","v":0},{"$f":"'Project Info'!H91","v":0},{"$f":"'Project Info'!I91","v":0},{"$f":"'Project Info'!J91","v":0},{"$f":"'Project Info'!K91","v":0},{"$f":"'Project Info'!L91","v":0},0.45707447145236157,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A92","v":10},{"$f":"'Project Info'!B92","v":15},{"$f":"'Project Info'!C92","v":12.269931130346862},{"$f":"'Project Info'!D92","v":10.318264913023604},{"$f":"'Project Info'!E92","v":3.9082824916941998},{"$f":"'Project Info'!F92","v":0},{"$f":"'Project Info'!G92","v":0},{"$f":"'Project Info'!H92","v":0},{"$f":"'Project Info'!I92","v":0},{"$f":"'Project Info'!J92","v":0},{"$f":"'Project Info'!K92","v":0},{"$f":"'Project Info'!L92","v":0},0.51707574608790896,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A93","v":5},{"$f":"'Project Info'!B93","v":10},{"$f":"'Project Info'!C93","v":7.3137581369917548},{"$f":"'Project Info'!D93","v":5.7052382449247707},{"$f":"'Project Info'!E93","v":2.5019418419888937},{"$f":"'Project Info'!F93","v":0},{"$f":"'Project Info'!G93","v":0},{"$f":"'Project Info'!H93","v":0},{"$f":"'Project Info'!I93","v":0},{"$f":"'Project Info'!J93","v":0},{"$f":"'Project Info'!K93","v":0},{"$f":"'Project Info'!L93","v":0},0.5707676201825892,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A94","v":0},{"$f":"'Project Info'!B94","v":5},{"$f":"'Project Info'!C94","v":2.6119461836144886},{"$f":"'Project Info'!D94","v":1.2699770062067783},{"$f":"'Project Info'!E94","v":1.2046477897733283},{"$f":"'Project Info'!F94","v":8760},{"$f":"'Project Info'!G94","v":2672},{"$f":"'Project Info'!H94","v":3160},{"$f":"'Project Info'!I94","v":1344},{"$f":"'Project Info'!J94","v":1584},{"$f":"'Project Info'!K94","v":88},{"$f":"'Project Info'!L94","v":264},0.62170391634417632,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A95","v":-5},{"$f":"'Project Info'!B95","v":0},{"$f":"'Project Info'!C95","v":-1.6731398516793925},{"$f":"'Project Info'!D95","v":-2.7083318773557807},{"$f":"'Project Info'!E95","v":7.9391832815876459E-2},{"$f":"'Project Info'!F95","v":0},{"$f":"'Project Info'!G95","v":0},{"$f":"'Project Info'!H95","v":0},{"$f":"'Project Info'!I95","v":0},{"$f":"'Project Info'!J95","v":0},{"$f":"'Project Info'!K95","v":0},{"$f":"'Project Info'!L95","v":0},0.66812568172652664,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A96","v":-10},{"$f":"'Project Info'!B96","v":-5},{"$f":"'Project Info'!C96","v":-6.5729865085377277},{"$f":"'Project Info'!D96","v":-7.2465935998252222},{"$f":"'Project Info'!E96","v":-1.168423365310433},{"$f":"'Project Info'!F96","v":0},{"$f":"'Project Info'!G96","v":0},{"$f":"'Project Info'!H96","v":0},{"$f":"'Project Info'!I96","v":0},{"$f":"'Project Info'!J96","v":0},{"$f":"'Project Info'!K96","v":0},{"$f":"'Project Info'!L96","v":0},0.72120735384249191,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A97","v":-15},{"$f":"'Project Info'!B97","v":-10},{"$f":"'Project Info'!C97","v":-15.32570353422995},{"$f":"'Project Info'!D97","v":-15.707838211108999},{"$f":"'Project Info'!E97","v":-3.4051318156661381},{"$f":"'Project Info'!F97","v":0},{"$f":"'Project Info'!G97","v":0},{"$f":"'Project Info'!H97","v":0},{"$f":"'Project Info'!I97","v":0},{"$f":"'Project Info'!J97","v":0},{"$f":"'Project Info'!K97","v":0},{"$f":"'Project Info'!L97","v":0},0.81602845495415766,{"$error":"#DIV/0!"},0.82450000000000001,0,{"$error":"#N/A"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},0]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Boiler Plant Heating Load Profile"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Occupied Profile",null,null,null,"Unocc Profile"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Max OAT","Min OAT","% Load @","%Load @","Max OAT","Min OAT","% Load @","%Load @"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"°F","°F","Max OAT","Min OAT","°F","°F","Max OAT","Min OAT"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,55,0,0.1,0.85,60,0,0,0.65]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Baseline Boiler Efficiency",null,null,null,null,"Boiler Efficiency"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Input",null,"Rated","Avg. Op.",null,"vs. HW Return Temp"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"MBH",null,"Ec","Et",null,"Return","Cond Blr","Std Blr"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"≤",2500,0.85,{"$f":"0.97*U98","v":0.82450000000000001},null,"Water ","Eff","Eff"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,">",2500,0.82,{"$f":"0.96*U99","v":0.7871999999999999},null,"°F","%","%"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Base Eff. per design capacity",null,null,{"$f":"IF($N$16<=$T$98,V98,V99)","v":0.82450000000000001},null,68,0.96099999999999997,{"$f":"$V$100","v":0.82450000000000001}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,86,0.94799999999999995,0.82450000000000001]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Peak Plant Load",null,null,null,null,104,0.92800000000000005,0.82450000000000001]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Peak Plant MBH",null,{"$f":"N16/N18","v":{"$error":"#DIV/0!"}},null,null,122,0.90900000000000003,0.82450000000000001]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,140,0.88,0.82450000000000001]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"HW Reset",null,null,null,150,0.87,0.82450000000000001]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"OAT","Return",null,null,160,0.87,0.82450000000000001]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"°F","°F"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"M23","v":0},{"$f":"N23-$N$20","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"M24","v":0},{"$f":"N24-$N$20","v":0}]

{"sheet":"18","index":21,"n_rows":109,"n_cols":27,"rows_kept":109,"cut":false,"hidden":true,"merged":[]}
["Savings Summary",null,null,null,null,"Measure Summary",null,null,null,null,"Measure Description"]
["Annual kWh Savings",null,null,{"$f":"SUM(A14:D14)","v":0},null,null,null,"Value","Unit"]
["% On Peak",null,null,{"$f":"IF(D2<=0,0,MIN(1,A15+C15))","v":0},null,"Annual Electric Savings",null,{"$f":"D2","v":0},"kWh"]
["Max kW",null,null,{"$f":"MAX(AC41:AC64,AC71:AC94)","v":0},null,"Annual Fuel Savings",null,{"$f":"D7*C28","v":{"$error":"#N/A"}},{"$f":"D20","v":{"$error":"#N/A"}}]
["Summer kW",null,null,{"$f":"(SUMPRODUCT(AC41:AC64,R33:R56)+SUMPRODUCT(AC71:AC94,R63:R86))/SUM(R33:R56,R63:R86)","v":0},null,"Incremental Cost",null,45000,"$",null,"Measure Instructions"]
["Winter kW",null,null,{"$f":"(SUMPRODUCT(AC41:AC64,Q33:Q56)+SUMPRODUCT(AC71:AC94,Q63:Q86))/SUM(Q33:Q56,Q63:Q86)","v":0},null,"Estimated Incentive",null,{"$f":"IF(AND($C$24>0,$C$25>0),MIN(H5,H3*C24+H4*C25),\"TBD\")","v":"TBD"},"$"]
["Annual Fuel Savings (MMBtu)",null,null,{"$f":"(SUMPRODUCT($L$33:$L$56,Z33:Z56)+SUMPRODUCT($L$63:$L$86,Z63:Z86))/100","v":58259.609579071992},null,"Custom Payback",null,null,"years"]
["Incremental Cost",null,null,45000]
[]
["kWh Savings by Peak Period"]
["Winter","Winter","Summer","Summer"]
["On-Peak","Off-Peak","On-Peak","Off-Peak"]
["kWh","kWh","kWh","kWh"]
[{"$f":"SUMPRODUCT($AA$33:$AA$56,M33:M56)+SUMPRODUCT($AA$63:$AA$86,M63:M86)","v":0},{"$f":"SUMPRODUCT($AA$33:$AA$56,N33:N56)+SUMPRODUCT($AA$63:$AA$86,N63:N86)","v":0},{"$f":"SUMPRODUCT($AA$33:$AA$56,O33:O56)+SUMPRODUCT($AA$63:$AA$86,O63:O86)","v":0},{"$f":"SUMPRODUCT($AA$33:$AA$56,P33:P56)+SUMPRODUCT($AA$63:$AA$86,P63:P86)","v":0},null,null,null,null,null,null,"User Inputs - Boiler/Loop Parameters"]
[{"$f":"IF(A14<=0,0,A14/SUMIF($A$14:$D$14,\">0\"))","v":0},{"$f":"IF(B14<=0,0,B14/SUMIF($A$14:$D$14,\">0\"))","v":0},{"$f":"IF(C14<=0,0,C14/SUMIF($A$14:$D$14,\">0\"))","v":0},{"$f":"IF(D14<=0,0,D14/SUMIF($A$14:$D$14,\">0\"))","v":0},null,null,null,null,null,null,"Boiler Quantity",null,null,3]
[null,null,null,null,null,null,null,null,null,null,"Output MBH (per Boiler)",null,null,4392]
["Utility Rates",null,null,null,null,null,null,null,null,null,"Max # of Operating Boilers",null,null,2]
[null,null,"Rate","Unit",null,null,null,null,null,null,"Design Capacity Ratio*",null,null,0.55000000000000004]
["Electric",null,{"$f":"'ECM Summary'!$E$31","v":0.1593},"kWh",null,null,null,null,null,null,"Design HW Temperature",null,null,160]
[{"$f":"'ECM Summary'!$C$32","v":0},null,{"$f":"'ECM Summary'!$E$32","v":{"$error":"#N/A"}},{"$f":"'ECM Summary'!$F$32","v":{"$error":"#N/A"}},null,null,null,null,null,null,"Design HW Loop dT",null,null,20]
[null,null,null,null,null,null,null,null,null,null,null,null,"OAT","HW Temp"]
["Custom Incentive Rates",null,null,null,null,null,null,null,null,null,null,null,"°F","°F"]
[null,null,"Rate","Unit",null,null,null,null,null,null,"Reset Max Supply T",null,20,160]
["Electric",null,{"$f":"'ECM Summary'!$J$31","v":0.28000000000000003},"kWh",null,null,null,null,null,null,"Reset Min Supply T",null,60,120]
[{"$f":"'ECM Summary'!$H$32","v":0},null,{"$f":"'ECM Summary'!$J$32","v":0},{"$f":"'ECM Summary'!$K$32","v":{"$error":"#N/A"}},null,null,null,null,null,null,"*Cap Ratio = % of Peak Load from 1 boiler"]
[]
["Fossil Fuel",null,{"$f":"'Project Info'!C21","v":0}]
["Fuel Conversion",null,{"$f":"LOOKUP(C27,'Project Info'!X102:X104,'Project Info'!Z102:Z104)","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,"Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Heating","Heating","Base","Return","Proposed","Base","Design","Demand","Demand"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Load","Load","Eff.","HWT","Eff.","Demand","Demand","Savings","Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","%","MBH","%","°F","%","MBH","MBH","MBH","kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A44","v":100},{"$f":"'Project Info'!B44","v":105},{"$f":"'Project Info'!C44","v":102},{"$f":"'Project Info'!D44","v":76},{"$f":"'Project Info'!E44","v":40},{"$f":"'Project Info'!F44","v":0},{"$f":"'Project Info'!G44","v":0},{"$f":"'Project Info'!H44","v":0},{"$f":"'Project Info'!I44","v":0},{"$f":"'Project Info'!J44","v":0},{"$f":"'Project Info'!K44","v":0},{"$f":"'Project Info'!L44","v":0},{"$f":"MAX($U$93,MIN(1,TREND($U$93:$V$93,$S$93:$T$93,I33)))","v":0.1},{"$f":"S33*$U$103","v":798.5454545454545},{"$f":"$V$100","v":0.7871999999999999},{"$f":"IF(I33>$T$109,$U$109,IF(I33<$T$108,$U$108,$U$108+(I33*(($U$108-$U$109)/($T$108-$T$109)))))","v":100},{"$f":"MAX($Y$106,MIN($Y$100,TREND(OFFSET($X$99,MATCH(V33,$X$100:$X$106,1),1,2,1),OFFSET($X$99,MATCH(V33,$X$100:$X$106,1),0,2,1),V33)))","v":0.9324444444444443},{"$f":"T33/U33","v":1014.4124168514413},{"$f":"T33/W33","v":856.40003466504902},{"$f":"X33-Y33","v":158.0123821863923},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A45","v":95},{"$f":"'Project Info'!B45","v":100},{"$f":"'Project Info'!C45","v":95.219272727272724},{"$f":"'Project Info'!D45","v":74.534025272781079},{"$f":"'Project Info'!E45","v":37.923296058061368},{"$f":"'Project Info'!F45","v":0},{"$f":"'Project Info'!G45","v":0},{"$f":"'Project Info'!H45","v":0},{"$f":"'Project Info'!I45","v":0},{"$f":"'Project Info'!J45","v":0},{"$f":"'Project Info'!K45","v":0},{"$f":"'Project Info'!L45","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,{"$f":"T34/U34","v":1014.4124168514413},{"$f":"T34/W34","v":856.40003466504902},{"$f":"X34-Y34","v":158.0123821863923},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A46","v":90},{"$f":"'Project Info'!B46","v":95},{"$f":"'Project Info'!C46","v":92.016049160256074},{"$f":"'Project Info'!D46","v":72.911561930607689},{"$f":"'Project Info'!E46","v":36.467095439351091},{"$f":"'Project Info'!F46","v":0},{"$f":"'Project Info'!G46","v":0},{"$f":"'Project Info'!H46","v":0},{"$f":"'Project Info'!I46","v":0},{"$f":"'Project Info'!J46","v":0},{"$f":"'Project Info'!K46","v":0},{"$f":"'Project Info'!L46","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,1014.4124168514413,856.40003466504902,158.0123821863923,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A47","v":85},{"$f":"'Project Info'!B47","v":90},{"$f":"'Project Info'!C47","v":87.457811360655285},{"$f":"'Project Info'!D47","v":70.80538329449476},{"$f":"'Project Info'!E47","v":34.679413213566804},{"$f":"'Project Info'!F47","v":0},{"$f":"'Project Info'!G47","v":0},{"$f":"'Project Info'!H47","v":0},{"$f":"'Project Info'!I47","v":0},{"$f":"'Project Info'!J47","v":0},{"$f":"'Project Info'!K47","v":0},{"$f":"'Project Info'!L47","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,1014.4124168514413,856.40003466504902,158.0123821863923,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A48","v":80},{"$f":"'Project Info'!B48","v":85},{"$f":"'Project Info'!C48","v":82.136788830239965},{"$f":"'Project Info'!D48","v":67.872393622439333},{"$f":"'Project Info'!E48","v":32.296248223809314},{"$f":"'Project Info'!F48","v":0},{"$f":"'Project Info'!G48","v":0},{"$f":"'Project Info'!H48","v":0},{"$f":"'Project Info'!I48","v":0},{"$f":"'Project Info'!J48","v":0},{"$f":"'Project Info'!K48","v":0},{"$f":"'Project Info'!L48","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,1014.4124168514413,856.40003466504902,158.0123821863923,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A49","v":75},{"$f":"'Project Info'!B49","v":80},{"$f":"'Project Info'!C49","v":76.988400157585886},{"$f":"'Project Info'!D49","v":65.129261896908645},{"$f":"'Project Info'!E49","v":30.190476812806729},{"$f":"'Project Info'!F49","v":0},{"$f":"'Project Info'!G49","v":0},{"$f":"'Project Info'!H49","v":0},{"$f":"'Project Info'!I49","v":0},{"$f":"'Project Info'!J49","v":0},{"$f":"'Project Info'!K49","v":0},{"$f":"'Project Info'!L49","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,1014.4124168514413,856.40003466504902,158.0123821863923,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A50","v":70},{"$f":"'Project Info'!B50","v":75},{"$f":"'Project Info'!C50","v":72.457982050814195},{"$f":"'Project Info'!D50","v":63.604425012889301},{"$f":"'Project Info'!E50","v":29.088683095945193},{"$f":"'Project Info'!F50","v":0},{"$f":"'Project Info'!G50","v":0},{"$f":"'Project Info'!H50","v":0},{"$f":"'Project Info'!I50","v":0},{"$f":"'Project Info'!J50","v":0},{"$f":"'Project Info'!K50","v":0},{"$f":"'Project Info'!L50","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,1014.4124168514413,856.40003466504902,158.0123821863923,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A51","v":65},{"$f":"'Project Info'!B51","v":70},{"$f":"'Project Info'!C51","v":67.815831070966169},{"$f":"'Project Info'!D51","v":61.631331368130574},{"$f":"'Project Info'!E51","v":27.661514889731574},{"$f":"'Project Info'!F51","v":0},{"$f":"'Project Info'!G51","v":0},{"$f":"'Project Info'!H51","v":0},{"$f":"'Project Info'!I51","v":0},{"$f":"'Project Info'!J51","v":0},{"$f":"'Project Info'!K51","v":0},{"$f":"'Project Info'!L51","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,1014.4124168514413,856.40003466504902,158.0123821863923,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A52","v":60},{"$f":"'Project Info'!B52","v":65},{"$f":"'Project Info'!C52","v":62.535961472271332},{"$f":"'Project Info'!D52","v":57.135476922863582},{"$f":"'Project Info'!E52","v":24.623037157728302},{"$f":"'Project Info'!F52","v":0},{"$f":"'Project Info'!G52","v":0},{"$f":"'Project Info'!H52","v":0},{"$f":"'Project Info'!I52","v":0},{"$f":"'Project Info'!J52","v":0},{"$f":"'Project Info'!K52","v":0},{"$f":"'Project Info'!L52","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,1014.4124168514413,856.40003466504902,158.0123821863923,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A53","v":55},{"$f":"'Project Info'!B53","v":60},{"$f":"'Project Info'!C53","v":57.125792270740902},{"$f":"'Project Info'!D53","v":52.596971157053673},{"$f":"'Project Info'!E53","v":21.818001539159841},{"$f":"'Project Info'!F53","v":0},{"$f":"'Project Info'!G53","v":0},{"$f":"'Project Info'!H53","v":0},{"$f":"'Project Info'!I53","v":0},{"$f":"'Project Info'!J53","v":0},{"$f":"'Project Info'!K53","v":0},{"$f":"'Project Info'!L53","v":0},0.1,798.5454545454545,0.7871999999999999,82.874207729259098,0.95025751663997937,1014.4124168514413,840.34636986512419,174.06604698631713,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A54","v":50},{"$f":"'Project Info'!B54","v":55},{"$f":"'Project Info'!C54","v":52.235698854337961},{"$f":"'Project Info'!D54","v":48.022768090099298},{"$f":"'Project Info'!E54","v":19.246640192796217},{"$f":"'Project Info'!F54","v":0},{"$f":"'Project Info'!G54","v":0},{"$f":"'Project Info'!H54","v":0},{"$f":"'Project Info'!I54","v":0},{"$f":"'Project Info'!J54","v":0},{"$f":"'Project Info'!K54","v":0},{"$f":"'Project Info'!L54","v":0},0.13769501562266417,1099.5572883904383,0.7871999999999999,87.764301145662046,0.94603966539370865,1396.7953358618374,1162.2739813270314,234.52135453480605,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A55","v":45},{"$f":"'Project Info'!B55","v":50},{"$f":"'Project Info'!C55","v":47.459170258371508},{"$f":"'Project Info'!D55","v":43.465397050422162},{"$f":"'Project Info'!E55","v":16.894183241713304},{"$f":"'Project Info'!F55","v":0},{"$f":"'Project Info'!G55","v":0},{"$f":"'Project Info'!H55","v":0},{"$f":"'Project Info'!I55","v":0},{"$f":"'Project Info'!J55","v":0},{"$f":"'Project Info'!K55","v":0},{"$f":"'Project Info'!L55","v":0},0.20282949647675219,1619.6857245925373,0.7871999999999999,92.5408297416285,0.94073241139819042,2057.5275972974309,1721.7284160383431,335.79918125908785,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A56","v":40},{"$f":"'Project Info'!B56","v":45},{"$f":"'Project Info'!C56","v":42.677030404888129},{"$f":"'Project Info'!D56","v":38.812544504634097},{"$f":"'Project Info'!E56","v":14.690265649465921},{"$f":"'Project Info'!F56","v":0},{"$f":"'Project Info'!G56","v":0},{"$f":"'Project Info'!H56","v":0},{"$f":"'Project Info'!I56","v":0},{"$f":"'Project Info'!J56","v":0},{"$f":"'Project Info'!K56","v":0},{"$f":"'Project Info'!L56","v":0},0.26804049447879819,2140.425185001603,0.7871999999999999,97.322969595111871,0.93541892267209781,2719.0360581829309,2288.1995789515463,430.8364792313846,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A57","v":35},{"$f":"'Project Info'!B57","v":40},{"$f":"'Project Info'!C57","v":37.333046773755832},{"$f":"'Project Info'!D57","v":33.904706919479686},{"$f":"'Project Info'!E57","v":12.53841602318813},{"$f":"'Project Info'!F57","v":0},{"$f":"'Project Info'!G57","v":0},{"$f":"'Project Info'!H57","v":0},{"$f":"'Project Info'!I57","v":0},{"$f":"'Project Info'!J57","v":0},{"$f":"'Project Info'!K57","v":0},{"$f":"'Project Info'!L57","v":0},0.34091299853969315,2722.3452537933313,0.7871999999999999,102.66695322624417,0.92948116308195083,3458.2637878472201,2928.8869553489881,529.37683249823203,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A58","v":30},{"$f":"'Project Info'!B58","v":35},{"$f":"'Project Info'!C58","v":32.638179845662044},{"$f":"'Project Info'!D58","v":29.547170928664851},{"$f":"'Project Info'!E58","v":10.728972818165861},{"$f":"'Project Info'!F58","v":0},{"$f":"'Project Info'!G58","v":0},{"$f":"'Project Info'!H58","v":0},{"$f":"'Project Info'!I58","v":0},{"$f":"'Project Info'!J58","v":0},{"$f":"'Project Info'!K58","v":0},{"$f":"'Project Info'!L58","v":0},0.40493391119551753,3233.5813417649324,0.7871999999999999,107.36182015433795,0.92445141205930992,4107.6998752095187,3497.8380687004415,609.86180650907727,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A59","v":25},{"$f":"'Project Info'!B59","v":30},{"$f":"'Project Info'!C59","v":27.529264646850947},{"$f":"'Project Info'!D59","v":24.652717392657845},{"$f":"'Project Info'!E59","v":8.8041305482613303},{"$f":"'Project Info'!F59","v":0},{"$f":"'Project Info'!G59","v":0},{"$f":"'Project Info'!H59","v":0},{"$f":"'Project Info'!I59","v":0},{"$f":"'Project Info'!J59","v":0},{"$f":"'Project Info'!K59","v":0},{"$f":"'Project Info'!L59","v":0},0.47460093663385067,3789.9042067197674,0.7871999999999999,112.47073535314905,0.9190586682383427,4814.4108317070222,4123.6803891793752,690.73044252764703,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A60","v":20},{"$f":"'Project Info'!B60","v":25},{"$f":"'Project Info'!C60","v":22.998111483544687},{"$f":"'Project Info'!D60","v":20.383306659827422},{"$f":"'Project Info'!E60","v":7.246164547543378},{"$f":"'Project Info'!F60","v":0},{"$f":"'Project Info'!G60","v":0},{"$f":"'Project Info'!H60","v":0},{"$f":"'Project Info'!I60","v":0},{"$f":"'Project Info'!J60","v":0},{"$f":"'Project Info'!K60","v":0},{"$f":"'Project Info'!L60","v":0},0.53638938886075427,4283.3130834116955,0.7871999999999999,117.00188851645531,0.91427578434374157,5441.2005632770533,4684.9245673571204,756.27599591993294,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A61","v":15},{"$f":"'Project Info'!B61","v":20},{"$f":"'Project Info'!C61","v":17.808510327474309},{"$f":"'Project Info'!D61","v":15.420865796304254},{"$f":"'Project Info'!E61","v":5.5490484131518292},{"$f":"'Project Info'!F61","v":0},{"$f":"'Project Info'!G61","v":0},{"$f":"'Project Info'!H61","v":0},{"$f":"'Project Info'!I61","v":0},{"$f":"'Project Info'!J61","v":0},{"$f":"'Project Info'!K61","v":0},{"$f":"'Project Info'!L61","v":0},0.60715667735262291,4848.4220489685813,0.7871999999999999,140,0.87999999999999989,6159.07272480765,5509.5705101915701,649.50221461607998,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A62","v":10},{"$f":"'Project Info'!B62","v":15},{"$f":"'Project Info'!C62","v":12.269931130346862},{"$f":"'Project Info'!D62","v":10.318264913023604},{"$f":"'Project Info'!E62","v":3.9082824916941998},{"$f":"'Project Info'!F62","v":0},{"$f":"'Project Info'!G62","v":0},{"$f":"'Project Info'!H62","v":0},{"$f":"'Project Info'!I62","v":0},{"$f":"'Project Info'!J62","v":0},{"$f":"'Project Info'!K62","v":0},{"$f":"'Project Info'!L62","v":0},0.68268275731345174,5451.5321274921453,0.7871999999999999,140,0.87999999999999989,6925.2186578914452,6194.9228721501659,730.29578574127936,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A63","v":5},{"$f":"'Project Info'!B63","v":10},{"$f":"'Project Info'!C63","v":7.3137581369917548},{"$f":"'Project Info'!D63","v":5.7052382449247707},{"$f":"'Project Info'!E63","v":2.5019418419888937},{"$f":"'Project Info'!F63","v":0},{"$f":"'Project Info'!G63","v":0},{"$f":"'Project Info'!H63","v":0},{"$f":"'Project Info'!I63","v":0},{"$f":"'Project Info'!J63","v":0},{"$f":"'Project Info'!K63","v":0},{"$f":"'Project Info'!L63","v":0},0.75026693449556681,5991.2225023718711,0.7871999999999999,140,0.87999999999999989,7610.8009430536986,6808.2073890589454,802.59355399475317,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A64","v":0},{"$f":"'Project Info'!B64","v":5},{"$f":"'Project Info'!C64","v":2.6119461836144886},{"$f":"'Project Info'!D64","v":1.2699770062067783},{"$f":"'Project Info'!E64","v":1.2046477897733283},{"$f":"'Project Info'!F64","v":0},{"$f":"'Project Info'!G64","v":0},{"$f":"'Project Info'!H64","v":0},{"$f":"'Project Info'!I64","v":0},{"$f":"'Project Info'!J64","v":0},{"$f":"'Project Info'!K64","v":0},{"$f":"'Project Info'!L64","v":0},0.81438255204162047,6503.2148519396305,0.7871999999999999,140,0.87999999999999989,8261.1977285818484,7390.0168772041261,871.18085137772232,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A65","v":-5},{"$f":"'Project Info'!B65","v":0},{"$f":"'Project Info'!C65","v":-1.6731398516793925},{"$f":"'Project Info'!D65","v":-2.7083318773557807},{"$f":"'Project Info'!E65","v":7.9391832815876459E-2},{"$f":"'Project Info'!F65","v":0},{"$f":"'Project Info'!G65","v":0},{"$f":"'Project Info'!H65","v":0},{"$f":"'Project Info'!I65","v":0},{"$f":"'Project Info'!J65","v":0},{"$f":"'Project Info'!K65","v":0},{"$f":"'Project Info'!L65","v":0},0.87281554343199153,6969.8288486423753,0.7871999999999999,140,0.87999999999999989,8853.9492487835068,7920.2600552754275,933.68919350807937,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A66","v":-10},{"$f":"'Project Info'!B66","v":-5},{"$f":"'Project Info'!C66","v":-6.5729865085377277},{"$f":"'Project Info'!D66","v":-7.2465935998252222},{"$f":"'Project Info'!E66","v":-1.168423365310433},{"$f":"'Project Info'!F66","v":0},{"$f":"'Project Info'!G66","v":0},{"$f":"'Project Info'!H66","v":0},{"$f":"'Project Info'!I66","v":0},{"$f":"'Project Info'!J66","v":0},{"$f":"'Project Info'!K66","v":0},{"$f":"'Project Info'!L66","v":0},0.93963163420733253,7503.3857044338256,0.7871999999999999,140,0.87999999999999989,9531.7399700632959,8526.5746641293481,1005.1653059339478,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A67","v":-15},{"$f":"'Project Info'!B67","v":-10},{"$f":"'Project Info'!C67","v":-15.32570353422995},{"$f":"'Project Info'!D67","v":-15.707838211108999},{"$f":"'Project Info'!E67","v":-3.4051318156661381},{"$f":"'Project Info'!F67","v":0},{"$f":"'Project Info'!G67","v":0},{"$f":"'Project Info'!H67","v":0},{"$f":"'Project Info'!I67","v":0},{"$f":"'Project Info'!J67","v":0},{"$f":"'Project Info'!K67","v":0},{"$f":"'Project Info'!L67","v":0},1,7985.454545454545,0.7871999999999999,140,0.87999999999999989,10144.124168514412,9074.3801652892562,1069.7440032251561,0]
[]
[]
[null,null,null,null,null,null,"Unoccupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Heating","Heating","Base","Return","Proposed","Base","Design","Demand","Demand"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Load","Load","Eff.","HWT","Eff.","Demand","Demand","Savings","Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","%","MBH","%","°F","%","MBH","MBH","MBH","kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A74","v":100},{"$f":"'Project Info'!B74","v":105},{"$f":"'Project Info'!C74","v":102},{"$f":"'Project Info'!D74","v":76},{"$f":"'Project Info'!E74","v":40},{"$f":"'Project Info'!F74","v":0},{"$f":"'Project Info'!G74","v":0},{"$f":"'Project Info'!H74","v":0},{"$f":"'Project Info'!I74","v":0},{"$f":"'Project Info'!J74","v":0},{"$f":"'Project Info'!K74","v":0},{"$f":"'Project Info'!L74","v":0},{"$f":"MAX($Y$93,MIN(1,TREND($Y$93:$Z$93,$W$93:$X$93,I63)))","v":0},{"$f":"S63*$U$103","v":0},{"$f":"$V$100","v":0.7871999999999999},{"$f":"IF(I63>$T$109,$U$109,IF(I63<$T$108,$U$108,$U$108+(I63*(($U$108-$U$109)/($T$108-$T$109)))))","v":100},{"$f":"MAX($Y$106,MIN($Y$100,TREND(OFFSET($X$99,MATCH(V63,$X$100:$X$106,1),1,2,1),OFFSET($X$99,MATCH(V63,$X$100:$X$106,1),0,2,1),V63)))","v":0.9324444444444443},{"$f":"T63/U63","v":0},{"$f":"T63/W63","v":0},{"$f":"X63-Y63","v":0},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A75","v":95},{"$f":"'Project Info'!B75","v":100},{"$f":"'Project Info'!C75","v":95.219272727272724},{"$f":"'Project Info'!D75","v":74.534025272781079},{"$f":"'Project Info'!E75","v":37.923296058061368},{"$f":"'Project Info'!F75","v":0},{"$f":"'Project Info'!G75","v":0},{"$f":"'Project Info'!H75","v":0},{"$f":"'Project Info'!I75","v":0},{"$f":"'Project Info'!J75","v":0},{"$f":"'Project Info'!K75","v":0},{"$f":"'Project Info'!L75","v":0},0,0,0.7871999999999999,100,0.9324444444444443,{"$f":"T64/U64","v":0},{"$f":"T64/W64","v":0},{"$f":"X64-Y64","v":0},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A76","v":90},{"$f":"'Project Info'!B76","v":95},{"$f":"'Project Info'!C76","v":92.016049160256074},{"$f":"'Project Info'!D76","v":72.911561930607689},{"$f":"'Project Info'!E76","v":36.467095439351091},{"$f":"'Project Info'!F76","v":0},{"$f":"'Project Info'!G76","v":0},{"$f":"'Project Info'!H76","v":0},{"$f":"'Project Info'!I76","v":0},{"$f":"'Project Info'!J76","v":0},{"$f":"'Project Info'!K76","v":0},{"$f":"'Project Info'!L76","v":0},0,0,0.7871999999999999,100,0.9324444444444443,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A77","v":85},{"$f":"'Project Info'!B77","v":90},{"$f":"'Project Info'!C77","v":87.457811360655285},{"$f":"'Project Info'!D77","v":70.80538329449476},{"$f":"'Project Info'!E77","v":34.679413213566804},{"$f":"'Project Info'!F77","v":0},{"$f":"'Project Info'!G77","v":0},{"$f":"'Project Info'!H77","v":0},{"$f":"'Project Info'!I77","v":0},{"$f":"'Project Info'!J77","v":0},{"$f":"'Project Info'!K77","v":0},{"$f":"'Project Info'!L77","v":0},0,0,0.7871999999999999,100,0.9324444444444443,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A78","v":80},{"$f":"'Project Info'!B78","v":85},{"$f":"'Project Info'!C78","v":82.136788830239965},{"$f":"'Project Info'!D78","v":67.872393622439333},{"$f":"'Project Info'!E78","v":32.296248223809314},{"$f":"'Project Info'!F78","v":0},{"$f":"'Project Info'!G78","v":0},{"$f":"'Project Info'!H78","v":0},{"$f":"'Project Info'!I78","v":0},{"$f":"'Project Info'!J78","v":0},{"$f":"'Project Info'!K78","v":0},{"$f":"'Project Info'!L78","v":0},0,0,0.7871999999999999,100,0.9324444444444443,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A79","v":75},{"$f":"'Project Info'!B79","v":80},{"$f":"'Project Info'!C79","v":76.988400157585886},{"$f":"'Project Info'!D79","v":65.129261896908645},{"$f":"'Project Info'!E79","v":30.190476812806729},{"$f":"'Project Info'!F79","v":0},{"$f":"'Project Info'!G79","v":0},{"$f":"'Project Info'!H79","v":0},{"$f":"'Project Info'!I79","v":0},{"$f":"'Project Info'!J79","v":0},{"$f":"'Project Info'!K79","v":0},{"$f":"'Project Info'!L79","v":0},0,0,0.7871999999999999,100,0.9324444444444443,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A80","v":70},{"$f":"'Project Info'!B80","v":75},{"$f":"'Project Info'!C80","v":72.457982050814195},{"$f":"'Project Info'!D80","v":63.604425012889301},{"$f":"'Project Info'!E80","v":29.088683095945193},{"$f":"'Project Info'!F80","v":0},{"$f":"'Project Info'!G80","v":0},{"$f":"'Project Info'!H80","v":0},{"$f":"'Project Info'!I80","v":0},{"$f":"'Project Info'!J80","v":0},{"$f":"'Project Info'!K80","v":0},{"$f":"'Project Info'!L80","v":0},0,0,0.7871999999999999,100,0.9324444444444443,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A81","v":65},{"$f":"'Project Info'!B81","v":70},{"$f":"'Project Info'!C81","v":67.815831070966169},{"$f":"'Project Info'!D81","v":61.631331368130574},{"$f":"'Project Info'!E81","v":27.661514889731574},{"$f":"'Project Info'!F81","v":0},{"$f":"'Project Info'!G81","v":0},{"$f":"'Project Info'!H81","v":0},{"$f":"'Project Info'!I81","v":0},{"$f":"'Project Info'!J81","v":0},{"$f":"'Project Info'!K81","v":0},{"$f":"'Project Info'!L81","v":0},0,0,0.7871999999999999,100,0.9324444444444443,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A82","v":60},{"$f":"'Project Info'!B82","v":65},{"$f":"'Project Info'!C82","v":62.535961472271332},{"$f":"'Project Info'!D82","v":57.135476922863582},{"$f":"'Project Info'!E82","v":24.623037157728302},{"$f":"'Project Info'!F82","v":0},{"$f":"'Project Info'!G82","v":0},{"$f":"'Project Info'!H82","v":0},{"$f":"'Project Info'!I82","v":0},{"$f":"'Project Info'!J82","v":0},{"$f":"'Project Info'!K82","v":0},{"$f":"'Project Info'!L82","v":0},0,0,0.7871999999999999,100,0.9324444444444443,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A83","v":55},{"$f":"'Project Info'!B83","v":60},{"$f":"'Project Info'!C83","v":57.125792270740902},{"$f":"'Project Info'!D83","v":52.596971157053673},{"$f":"'Project Info'!E83","v":21.818001539159841},{"$f":"'Project Info'!F83","v":0},{"$f":"'Project Info'!G83","v":0},{"$f":"'Project Info'!H83","v":0},{"$f":"'Project Info'!I83","v":0},{"$f":"'Project Info'!J83","v":0},{"$f":"'Project Info'!K83","v":0},{"$f":"'Project Info'!L83","v":0},3.1137250400306904E-2,248.64509774208713,0.7871999999999999,82.874207729259098,0.95025751663997937,315.86013432683836,261.66075341479291,54.199380912045456,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A84","v":50},{"$f":"'Project Info'!B84","v":55},{"$f":"'Project Info'!C84","v":52.235698854337961},{"$f":"'Project Info'!D84","v":48.022768090099298},{"$f":"'Project Info'!E84","v":19.246640192796217},{"$f":"'Project Info'!F84","v":0},{"$f":"'Project Info'!G84","v":0},{"$f":"'Project Info'!H84","v":0},{"$f":"'Project Info'!I84","v":0},{"$f":"'Project Info'!J84","v":0},{"$f":"'Project Info'!K84","v":0},{"$f":"'Project Info'!L84","v":0},8.4113262411338763E-2,671.6826336556361,0.7871999999999999,87.764301145662046,0.94603966539370865,853.25537811945651,709.99415587517171,143.2612222442848,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A85","v":45},{"$f":"'Project Info'!B85","v":50},{"$f":"'Project Info'!C85","v":47.459170258371508},{"$f":"'Project Info'!D85","v":43.465397050422162},{"$f":"'Project Info'!E85","v":16.894183241713304},{"$f":"'Project Info'!F85","v":0},{"$f":"'Project Info'!G85","v":0},{"$f":"'Project Info'!H85","v":0},{"$f":"'Project Info'!I85","v":0},{"$f":"'Project Info'!J85","v":0},{"$f":"'Project Info'!K85","v":0},{"$f":"'Project Info'!L85","v":0},0.13585898886764203,1084.8957801939705,0.7871999999999999,92.5408297416285,0.94073241139819042,1378.1704524821782,1153.2458827282385,224.92456975393975,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A86","v":40},{"$f":"'Project Info'!B86","v":45},{"$f":"'Project Info'!C86","v":42.677030404888129},{"$f":"'Project Info'!D86","v":38.812544504634097},{"$f":"'Project Info'!E86","v":14.690265649465921},{"$f":"'Project Info'!F86","v":0},{"$f":"'Project Info'!G86","v":0},{"$f":"'Project Info'!H86","v":0},{"$f":"'Project Info'!I86","v":0},{"$f":"'Project Info'!J86","v":0},{"$f":"'Project Info'!K86","v":0},{"$f":"'Project Info'!L86","v":0},0.18766550394704523,1498.5943515189501,0.7871999999999999,97.322969595111871,0.93541892267209781,1903.7021741856584,1602.0569128942757,301.64526129138267,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A87","v":35},{"$f":"'Project Info'!B87","v":40},{"$f":"'Project Info'!C87","v":37.333046773755832},{"$f":"'Project Info'!D87","v":33.904706919479686},{"$f":"'Project Info'!E87","v":12.53841602318813},{"$f":"'Project Info'!F87","v":0},{"$f":"'Project Info'!G87","v":0},{"$f":"'Project Info'!H87","v":0},{"$f":"'Project Info'!I87","v":0},{"$f":"'Project Info'!J87","v":0},{"$f":"'Project Info'!K87","v":0},{"$f":"'Project Info'!L87","v":0},0.24555865995097842,1960.8975172812675,0.7871999999999999,102.66695322624417,0.92948116308195083,2490.9775371967326,2109.668915483313,381.3086217134196,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A88","v":30},{"$f":"'Project Info'!B88","v":35},{"$f":"'Project Info'!C88","v":32.638179845662044},{"$f":"'Project Info'!D88","v":29.547170928664851},{"$f":"'Project Info'!E88","v":10.728972818165861},{"$f":"'Project Info'!F88","v":0},{"$f":"'Project Info'!G88","v":0},{"$f":"'Project Info'!H88","v":0},{"$f":"'Project Info'!I88","v":0},{"$f":"'Project Info'!J88","v":0},{"$f":"'Project Info'!K88","v":0},{"$f":"'Project Info'!L88","v":0},0.29641971833866115,2367.0461871698176,0.7871999999999999,107.36182015433795,0.92445141205930992,3006.9184288234474,2560.4873942449613,446.43103457848611,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A89","v":25},{"$f":"'Project Info'!B89","v":30},{"$f":"'Project Info'!C89","v":27.529264646850947},{"$f":"'Project Info'!D89","v":24.652717392657845},{"$f":"'Project Info'!E89","v":8.8041305482613303},{"$f":"'Project Info'!F89","v":0},{"$f":"'Project Info'!G89","v":0},{"$f":"'Project Info'!H89","v":0},{"$f":"'Project Info'!I89","v":0},{"$f":"'Project Info'!J89","v":0},{"$f":"'Project Info'!K89","v":0},{"$f":"'Project Info'!L89","v":0},0.35176629965911471,2809.0137965506033,0.7871999999999999,112.47073535314905,0.9190586682383427,3568.3610220409091,3056.4031368475507,511.95788519335838,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A90","v":20},{"$f":"'Project Info'!B90","v":25},{"$f":"'Project Info'!C90","v":22.998111483544687},{"$f":"'Project Info'!D90","v":20.383306659827422},{"$f":"'Project Info'!E90","v":7.246164547543378},{"$f":"'Project Info'!F90","v":0},{"$f":"'Project Info'!G90","v":0},{"$f":"'Project Info'!H90","v":0},{"$f":"'Project Info'!I90","v":0},{"$f":"'Project Info'!J90","v":0},{"$f":"'Project Info'!K90","v":0},{"$f":"'Project Info'!L90","v":0},0.40085379226159917,3200.9997374780792,0.7871999999999999,117.00188851645531,0.91427578434374157,4066.3106421215443,3501.1314882147144,565.17915390682992,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A91","v":15},{"$f":"'Project Info'!B91","v":20},{"$f":"'Project Info'!C91","v":17.808510327474309},{"$f":"'Project Info'!D91","v":15.420865796304254},{"$f":"'Project Info'!E91","v":5.5490484131518292},{"$f":"'Project Info'!F91","v":0},{"$f":"'Project Info'!G91","v":0},{"$f":"'Project Info'!H91","v":0},{"$f":"'Project Info'!I91","v":0},{"$f":"'Project Info'!J91","v":0},{"$f":"'Project Info'!K91","v":0},{"$f":"'Project Info'!L91","v":0},0.45707447145236157,3649.9474156704946,0.7871999999999999,140,0.87999999999999989,4636.6201926708527,4147.667517807381,488.95267486347166,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A92","v":10},{"$f":"'Project Info'!B92","v":15},{"$f":"'Project Info'!C92","v":12.269931130346862},{"$f":"'Project Info'!D92","v":10.318264913023604},{"$f":"'Project Info'!E92","v":3.9082824916941998},{"$f":"'Project Info'!F92","v":0},{"$f":"'Project Info'!G92","v":0},{"$f":"'Project Info'!H92","v":0},{"$f":"'Project Info'!I92","v":0},{"$f":"'Project Info'!J92","v":0},{"$f":"'Project Info'!K92","v":0},{"$f":"'Project Info'!L92","v":0},0.51707574608790896,4129.0848669419929,0.7871999999999999,140,0.87999999999999989,5245.2805728429794,4692.141894252265,553.13867859071433,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A93","v":5},{"$f":"'Project Info'!B93","v":10},{"$f":"'Project Info'!C93","v":7.3137581369917548},{"$f":"'Project Info'!D93","v":5.7052382449247707},{"$f":"'Project Info'!E93","v":2.5019418419888937},{"$f":"'Project Info'!F93","v":0},{"$f":"'Project Info'!G93","v":0},{"$f":"'Project Info'!H93","v":0},{"$f":"'Project Info'!I93","v":0},{"$f":"'Project Info'!J93","v":0},{"$f":"'Project Info'!K93","v":0},{"$f":"'Project Info'!L93","v":0},0.5707676201825892,4557.8388869853306,0.7871999999999999,140,0.87999999999999989,5789.9376104996581,5179.3623715742397,610.57523892541849,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A94","v":0},{"$f":"'Project Info'!B94","v":5},{"$f":"'Project Info'!C94","v":2.6119461836144886},{"$f":"'Project Info'!D94","v":1.2699770062067783},{"$f":"'Project Info'!E94","v":1.2046477897733283},{"$f":"'Project Info'!F94","v":8760},{"$f":"'Project Info'!G94","v":2672},{"$f":"'Project Info'!H94","v":3160},{"$f":"'Project Info'!I94","v":1344},{"$f":"'Project Info'!J94","v":1584},{"$f":"'Project Info'!K94","v":88},{"$f":"'Project Info'!L94","v":264},0.62170391634417632,4964.5883646974953,0.7871999999999999,140,0.87999999999999989,6306.6417234470218,5641.5776871562457,665.06403629077613,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A95","v":-5},{"$f":"'Project Info'!B95","v":0},{"$f":"'Project Info'!C95","v":-1.6731398516793925},{"$f":"'Project Info'!D95","v":-2.7083318773557807},{"$f":"'Project Info'!E95","v":7.9391832815876459E-2},{"$f":"'Project Info'!F95","v":0},{"$f":"'Project Info'!G95","v":0},{"$f":"'Project Info'!H95","v":0},{"$f":"'Project Info'!I95","v":0},{"$f":"'Project Info'!J95","v":0},{"$f":"'Project Info'!K95","v":0},{"$f":"'Project Info'!L95","v":0},0.66812568172652664,5335.287262078009,0.7871999999999999,140,0.87999999999999989,6777.5498756072275,6062.8264341795566,714.72344142767088,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A96","v":-10},{"$f":"'Project Info'!B96","v":-5},{"$f":"'Project Info'!C96","v":-6.5729865085377277},{"$f":"'Project Info'!D96","v":-7.2465935998252222},{"$f":"'Project Info'!E96","v":-1.168423365310433},{"$f":"'Project Info'!F96","v":0},{"$f":"'Project Info'!G96","v":0},{"$f":"'Project Info'!H96","v":0},{"$f":"'Project Info'!I96","v":0},{"$f":"'Project Info'!J96","v":0},{"$f":"'Project Info'!K96","v":0},{"$f":"'Project Info'!L96","v":0},0.72120735384249191,5759.1685419567712,0.7871999999999999,140,0.87999999999999989,7316.0169486239483,6544.5097067690585,771.5072418548898,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A97","v":-15},{"$f":"'Project Info'!B97","v":-10},{"$f":"'Project Info'!C97","v":-15.32570353422995},{"$f":"'Project Info'!D97","v":-15.707838211108999},{"$f":"'Project Info'!E97","v":-3.4051318156661381},{"$f":"'Project Info'!F97","v":0},{"$f":"'Project Info'!G97","v":0},{"$f":"'Project Info'!H97","v":0},{"$f":"'Project Info'!I97","v":0},{"$f":"'Project Info'!J97","v":0},{"$f":"'Project Info'!K97","v":0},{"$f":"'Project Info'!L97","v":0},0.81602845495415766,6516.3581348339276,0.7871999999999999,140,0.87999999999999989,8277.8939720959461,7404.9524259476457,872.9415461483004,0]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Boiler Plant Heating Load Profile"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Occupied Profile",null,null,null,"Unocc Profile"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Max OAT","Min OAT","% Load @","%Load @","Max OAT","Min OAT","% Load @","%Load @"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"°F","°F","Max OAT","Min OAT","°F","°F","Max OAT","Min OAT"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,55,0,0.1,0.85,60,0,0,0.65]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Baseline Boiler Efficiency",null,null,null,null,"Boiler Efficiency"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Input",null,"Rated","Avg. Op.",null,"vs. HW Return Temp"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"MBH",null,"Ec","Et",null,"Return","Cond Blr","Std Blr"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"≤",2500,0.85,{"$f":"0.97*U98","v":0.82450000000000001},null,"Water ","Eff","Eff"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,">",2500,0.82,{"$f":"0.96*U99","v":0.7871999999999999},null,"°F","%","%"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Base Eff. per design capacity",null,null,{"$f":"IF($N$16<=$T$98,V98,V99)","v":0.7871999999999999},null,68,0.96099999999999997,{"$f":"$V$100","v":0.7871999999999999}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,86,0.94799999999999995,0.7871999999999999]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Peak Plant Load",null,null,null,null,104,0.92800000000000005,0.7871999999999999]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Peak Plant MBH",null,{"$f":"N16/N18","v":7985.454545454545},null,null,122,0.90900000000000003,0.7871999999999999]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,140,0.88,0.7871999999999999]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"HW Reset",null,null,null,150,0.87,0.7871999999999999]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"OAT","Return",null,null,160,0.87,0.7871999999999999]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"°F","°F"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"M23","v":20},{"$f":"N23-$N$20","v":140}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"M24","v":60},{"$f":"N24-$N$20","v":100}]

{"sheet":"19","index":22,"n_rows":109,"n_cols":27,"rows_kept":109,"cut":false,"hidden":true,"merged":[]}
["Savings Summary",null,null,null,null,"Measure Summary",null,null,null,null,"Measure Description"]
["Annual kWh Savings",null,null,{"$f":"SUM(A14:D14)","v":0},null,null,null,"Value","Unit"]
["% On Peak",null,null,{"$f":"IF(D2<=0,0,MIN(1,A15+C15))","v":0},null,"Annual Electric Savings",null,{"$f":"D2","v":0},"kWh"]
["Max kW",null,null,{"$f":"MAX(AC41:AC64,AC71:AC94)","v":0},null,"Annual Fuel Savings",null,{"$f":"D7*C28","v":{"$error":"#N/A"}},{"$f":"D20","v":{"$error":"#N/A"}}]
["Summer kW",null,null,{"$f":"(SUMPRODUCT(AC41:AC64,R33:R56)+SUMPRODUCT(AC71:AC94,R63:R86))/SUM(R33:R56,R63:R86)","v":0},null,"Incremental Cost",null,45000,"$",null,"Measure Instructions"]
["Winter kW",null,null,{"$f":"(SUMPRODUCT(AC41:AC64,Q33:Q56)+SUMPRODUCT(AC71:AC94,Q63:Q86))/SUM(Q33:Q56,Q63:Q86)","v":0},null,"Estimated Incentive",null,{"$f":"IF(AND($C$24>0,$C$25>0),MIN(H5,H3*C24+H4*C25),\"TBD\")","v":"TBD"},"$"]
["Annual Fuel Savings (MMBtu)",null,null,{"$f":"(SUMPRODUCT($L$33:$L$56,Z33:Z56)+SUMPRODUCT($L$63:$L$86,Z63:Z86))/100","v":58259.609579071992},null,"Custom Payback",null,null,"years"]
["Incremental Cost",null,null,45000]
[]
["kWh Savings by Peak Period"]
["Winter","Winter","Summer","Summer"]
["On-Peak","Off-Peak","On-Peak","Off-Peak"]
["kWh","kWh","kWh","kWh"]
[{"$f":"SUMPRODUCT($AA$33:$AA$56,M33:M56)+SUMPRODUCT($AA$63:$AA$86,M63:M86)","v":0},{"$f":"SUMPRODUCT($AA$33:$AA$56,N33:N56)+SUMPRODUCT($AA$63:$AA$86,N63:N86)","v":0},{"$f":"SUMPRODUCT($AA$33:$AA$56,O33:O56)+SUMPRODUCT($AA$63:$AA$86,O63:O86)","v":0},{"$f":"SUMPRODUCT($AA$33:$AA$56,P33:P56)+SUMPRODUCT($AA$63:$AA$86,P63:P86)","v":0},null,null,null,null,null,null,"User Inputs - Boiler/Loop Parameters"]
[{"$f":"IF(A14<=0,0,A14/SUMIF($A$14:$D$14,\">0\"))","v":0},{"$f":"IF(B14<=0,0,B14/SUMIF($A$14:$D$14,\">0\"))","v":0},{"$f":"IF(C14<=0,0,C14/SUMIF($A$14:$D$14,\">0\"))","v":0},{"$f":"IF(D14<=0,0,D14/SUMIF($A$14:$D$14,\">0\"))","v":0},null,null,null,null,null,null,"Boiler Quantity",null,null,3]
[null,null,null,null,null,null,null,null,null,null,"Output MBH (per Boiler)",null,null,4392]
["Utility Rates",null,null,null,null,null,null,null,null,null,"Max # of Operating Boilers",null,null,2]
[null,null,"Rate","Unit",null,null,null,null,null,null,"Design Capacity Ratio*",null,null,0.55000000000000004]
["Electric",null,{"$f":"'ECM Summary'!$E$31","v":0.1593},"kWh",null,null,null,null,null,null,"Design HW Temperature",null,null,160]
[{"$f":"'ECM Summary'!$C$32","v":0},null,{"$f":"'ECM Summary'!$E$32","v":{"$error":"#N/A"}},{"$f":"'ECM Summary'!$F$32","v":{"$error":"#N/A"}},null,null,null,null,null,null,"Design HW Loop dT",null,null,20]
[null,null,null,null,null,null,null,null,null,null,null,null,"OAT","HW Temp"]
["Custom Incentive Rates",null,null,null,null,null,null,null,null,null,null,null,"°F","°F"]
[null,null,"Rate","Unit",null,null,null,null,null,null,"Reset Max Supply T",null,20,160]
["Electric",null,{"$f":"'ECM Summary'!$J$31","v":0.28000000000000003},"kWh",null,null,null,null,null,null,"Reset Min Supply T",null,60,120]
[{"$f":"'ECM Summary'!$H$32","v":0},null,{"$f":"'ECM Summary'!$J$32","v":0},{"$f":"'ECM Summary'!$K$32","v":{"$error":"#N/A"}},null,null,null,null,null,null,"*Cap Ratio = % of Peak Load from 1 boiler"]
[]
["Fossil Fuel",null,{"$f":"'Project Info'!C21","v":0}]
["Fuel Conversion",null,{"$f":"LOOKUP(C27,'Project Info'!X102:X104,'Project Info'!Z102:Z104)","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,"Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Heating","Heating","Base","Return","Proposed","Base","Design","Demand","Demand"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Load","Load","Eff.","HWT","Eff.","Demand","Demand","Savings","Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","%","MBH","%","°F","%","MBH","MBH","MBH","kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A44","v":100},{"$f":"'Project Info'!B44","v":105},{"$f":"'Project Info'!C44","v":102},{"$f":"'Project Info'!D44","v":76},{"$f":"'Project Info'!E44","v":40},{"$f":"'Project Info'!F44","v":0},{"$f":"'Project Info'!G44","v":0},{"$f":"'Project Info'!H44","v":0},{"$f":"'Project Info'!I44","v":0},{"$f":"'Project Info'!J44","v":0},{"$f":"'Project Info'!K44","v":0},{"$f":"'Project Info'!L44","v":0},{"$f":"MAX($U$93,MIN(1,TREND($U$93:$V$93,$S$93:$T$93,I33)))","v":0.1},{"$f":"S33*$U$103","v":798.5454545454545},{"$f":"$V$100","v":0.7871999999999999},{"$f":"IF(I33>$T$109,$U$109,IF(I33<$T$108,$U$108,$U$108+(I33*(($U$108-$U$109)/($T$108-$T$109)))))","v":100},{"$f":"MAX($Y$106,MIN($Y$100,TREND(OFFSET($X$99,MATCH(V33,$X$100:$X$106,1),1,2,1),OFFSET($X$99,MATCH(V33,$X$100:$X$106,1),0,2,1),V33)))","v":0.9324444444444443},{"$f":"T33/U33","v":1014.4124168514413},{"$f":"T33/W33","v":856.40003466504902},{"$f":"X33-Y33","v":158.0123821863923},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A45","v":95},{"$f":"'Project Info'!B45","v":100},{"$f":"'Project Info'!C45","v":95.219272727272724},{"$f":"'Project Info'!D45","v":74.534025272781079},{"$f":"'Project Info'!E45","v":37.923296058061368},{"$f":"'Project Info'!F45","v":0},{"$f":"'Project Info'!G45","v":0},{"$f":"'Project Info'!H45","v":0},{"$f":"'Project Info'!I45","v":0},{"$f":"'Project Info'!J45","v":0},{"$f":"'Project Info'!K45","v":0},{"$f":"'Project Info'!L45","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,{"$f":"T34/U34","v":1014.4124168514413},{"$f":"T34/W34","v":856.40003466504902},{"$f":"X34-Y34","v":158.0123821863923},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A46","v":90},{"$f":"'Project Info'!B46","v":95},{"$f":"'Project Info'!C46","v":92.016049160256074},{"$f":"'Project Info'!D46","v":72.911561930607689},{"$f":"'Project Info'!E46","v":36.467095439351091},{"$f":"'Project Info'!F46","v":0},{"$f":"'Project Info'!G46","v":0},{"$f":"'Project Info'!H46","v":0},{"$f":"'Project Info'!I46","v":0},{"$f":"'Project Info'!J46","v":0},{"$f":"'Project Info'!K46","v":0},{"$f":"'Project Info'!L46","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,1014.4124168514413,856.40003466504902,158.0123821863923,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A47","v":85},{"$f":"'Project Info'!B47","v":90},{"$f":"'Project Info'!C47","v":87.457811360655285},{"$f":"'Project Info'!D47","v":70.80538329449476},{"$f":"'Project Info'!E47","v":34.679413213566804},{"$f":"'Project Info'!F47","v":0},{"$f":"'Project Info'!G47","v":0},{"$f":"'Project Info'!H47","v":0},{"$f":"'Project Info'!I47","v":0},{"$f":"'Project Info'!J47","v":0},{"$f":"'Project Info'!K47","v":0},{"$f":"'Project Info'!L47","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,1014.4124168514413,856.40003466504902,158.0123821863923,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A48","v":80},{"$f":"'Project Info'!B48","v":85},{"$f":"'Project Info'!C48","v":82.136788830239965},{"$f":"'Project Info'!D48","v":67.872393622439333},{"$f":"'Project Info'!E48","v":32.296248223809314},{"$f":"'Project Info'!F48","v":0},{"$f":"'Project Info'!G48","v":0},{"$f":"'Project Info'!H48","v":0},{"$f":"'Project Info'!I48","v":0},{"$f":"'Project Info'!J48","v":0},{"$f":"'Project Info'!K48","v":0},{"$f":"'Project Info'!L48","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,1014.4124168514413,856.40003466504902,158.0123821863923,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A49","v":75},{"$f":"'Project Info'!B49","v":80},{"$f":"'Project Info'!C49","v":76.988400157585886},{"$f":"'Project Info'!D49","v":65.129261896908645},{"$f":"'Project Info'!E49","v":30.190476812806729},{"$f":"'Project Info'!F49","v":0},{"$f":"'Project Info'!G49","v":0},{"$f":"'Project Info'!H49","v":0},{"$f":"'Project Info'!I49","v":0},{"$f":"'Project Info'!J49","v":0},{"$f":"'Project Info'!K49","v":0},{"$f":"'Project Info'!L49","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,1014.4124168514413,856.40003466504902,158.0123821863923,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A50","v":70},{"$f":"'Project Info'!B50","v":75},{"$f":"'Project Info'!C50","v":72.457982050814195},{"$f":"'Project Info'!D50","v":63.604425012889301},{"$f":"'Project Info'!E50","v":29.088683095945193},{"$f":"'Project Info'!F50","v":0},{"$f":"'Project Info'!G50","v":0},{"$f":"'Project Info'!H50","v":0},{"$f":"'Project Info'!I50","v":0},{"$f":"'Project Info'!J50","v":0},{"$f":"'Project Info'!K50","v":0},{"$f":"'Project Info'!L50","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,1014.4124168514413,856.40003466504902,158.0123821863923,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A51","v":65},{"$f":"'Project Info'!B51","v":70},{"$f":"'Project Info'!C51","v":67.815831070966169},{"$f":"'Project Info'!D51","v":61.631331368130574},{"$f":"'Project Info'!E51","v":27.661514889731574},{"$f":"'Project Info'!F51","v":0},{"$f":"'Project Info'!G51","v":0},{"$f":"'Project Info'!H51","v":0},{"$f":"'Project Info'!I51","v":0},{"$f":"'Project Info'!J51","v":0},{"$f":"'Project Info'!K51","v":0},{"$f":"'Project Info'!L51","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,1014.4124168514413,856.40003466504902,158.0123821863923,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A52","v":60},{"$f":"'Project Info'!B52","v":65},{"$f":"'Project Info'!C52","v":62.535961472271332},{"$f":"'Project Info'!D52","v":57.135476922863582},{"$f":"'Project Info'!E52","v":24.623037157728302},{"$f":"'Project Info'!F52","v":0},{"$f":"'Project Info'!G52","v":0},{"$f":"'Project Info'!H52","v":0},{"$f":"'Project Info'!I52","v":0},{"$f":"'Project Info'!J52","v":0},{"$f":"'Project Info'!K52","v":0},{"$f":"'Project Info'!L52","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,1014.4124168514413,856.40003466504902,158.0123821863923,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A53","v":55},{"$f":"'Project Info'!B53","v":60},{"$f":"'Project Info'!C53","v":57.125792270740902},{"$f":"'Project Info'!D53","v":52.596971157053673},{"$f":"'Project Info'!E53","v":21.818001539159841},{"$f":"'Project Info'!F53","v":0},{"$f":"'Project Info'!G53","v":0},{"$f":"'Project Info'!H53","v":0},{"$f":"'Project Info'!I53","v":0},{"$f":"'Project Info'!J53","v":0},{"$f":"'Project Info'!K53","v":0},{"$f":"'Project Info'!L53","v":0},0.1,798.5454545454545,0.7871999999999999,82.874207729259098,0.95025751663997937,1014.4124168514413,840.34636986512419,174.06604698631713,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A54","v":50},{"$f":"'Project Info'!B54","v":55},{"$f":"'Project Info'!C54","v":52.235698854337961},{"$f":"'Project Info'!D54","v":48.022768090099298},{"$f":"'Project Info'!E54","v":19.246640192796217},{"$f":"'Project Info'!F54","v":0},{"$f":"'Project Info'!G54","v":0},{"$f":"'Project Info'!H54","v":0},{"$f":"'Project Info'!I54","v":0},{"$f":"'Project Info'!J54","v":0},{"$f":"'Project Info'!K54","v":0},{"$f":"'Project Info'!L54","v":0},0.13769501562266417,1099.5572883904383,0.7871999999999999,87.764301145662046,0.94603966539370865,1396.7953358618374,1162.2739813270314,234.52135453480605,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A55","v":45},{"$f":"'Project Info'!B55","v":50},{"$f":"'Project Info'!C55","v":47.459170258371508},{"$f":"'Project Info'!D55","v":43.465397050422162},{"$f":"'Project Info'!E55","v":16.894183241713304},{"$f":"'Project Info'!F55","v":0},{"$f":"'Project Info'!G55","v":0},{"$f":"'Project Info'!H55","v":0},{"$f":"'Project Info'!I55","v":0},{"$f":"'Project Info'!J55","v":0},{"$f":"'Project Info'!K55","v":0},{"$f":"'Project Info'!L55","v":0},0.20282949647675219,1619.6857245925373,0.7871999999999999,92.5408297416285,0.94073241139819042,2057.5275972974309,1721.7284160383431,335.79918125908785,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A56","v":40},{"$f":"'Project Info'!B56","v":45},{"$f":"'Project Info'!C56","v":42.677030404888129},{"$f":"'Project Info'!D56","v":38.812544504634097},{"$f":"'Project Info'!E56","v":14.690265649465921},{"$f":"'Project Info'!F56","v":0},{"$f":"'Project Info'!G56","v":0},{"$f":"'Project Info'!H56","v":0},{"$f":"'Project Info'!I56","v":0},{"$f":"'Project Info'!J56","v":0},{"$f":"'Project Info'!K56","v":0},{"$f":"'Project Info'!L56","v":0},0.26804049447879819,2140.425185001603,0.7871999999999999,97.322969595111871,0.93541892267209781,2719.0360581829309,2288.1995789515463,430.8364792313846,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A57","v":35},{"$f":"'Project Info'!B57","v":40},{"$f":"'Project Info'!C57","v":37.333046773755832},{"$f":"'Project Info'!D57","v":33.904706919479686},{"$f":"'Project Info'!E57","v":12.53841602318813},{"$f":"'Project Info'!F57","v":0},{"$f":"'Project Info'!G57","v":0},{"$f":"'Project Info'!H57","v":0},{"$f":"'Project Info'!I57","v":0},{"$f":"'Project Info'!J57","v":0},{"$f":"'Project Info'!K57","v":0},{"$f":"'Project Info'!L57","v":0},0.34091299853969315,2722.3452537933313,0.7871999999999999,102.66695322624417,0.92948116308195083,3458.2637878472201,2928.8869553489881,529.37683249823203,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A58","v":30},{"$f":"'Project Info'!B58","v":35},{"$f":"'Project Info'!C58","v":32.638179845662044},{"$f":"'Project Info'!D58","v":29.547170928664851},{"$f":"'Project Info'!E58","v":10.728972818165861},{"$f":"'Project Info'!F58","v":0},{"$f":"'Project Info'!G58","v":0},{"$f":"'Project Info'!H58","v":0},{"$f":"'Project Info'!I58","v":0},{"$f":"'Project Info'!J58","v":0},{"$f":"'Project Info'!K58","v":0},{"$f":"'Project Info'!L58","v":0},0.40493391119551753,3233.5813417649324,0.7871999999999999,107.36182015433795,0.92445141205930992,4107.6998752095187,3497.8380687004415,609.86180650907727,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A59","v":25},{"$f":"'Project Info'!B59","v":30},{"$f":"'Project Info'!C59","v":27.529264646850947},{"$f":"'Project Info'!D59","v":24.652717392657845},{"$f":"'Project Info'!E59","v":8.8041305482613303},{"$f":"'Project Info'!F59","v":0},{"$f":"'Project Info'!G59","v":0},{"$f":"'Project Info'!H59","v":0},{"$f":"'Project Info'!I59","v":0},{"$f":"'Project Info'!J59","v":0},{"$f":"'Project Info'!K59","v":0},{"$f":"'Project Info'!L59","v":0},0.47460093663385067,3789.9042067197674,0.7871999999999999,112.47073535314905,0.9190586682383427,4814.4108317070222,4123.6803891793752,690.73044252764703,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A60","v":20},{"$f":"'Project Info'!B60","v":25},{"$f":"'Project Info'!C60","v":22.998111483544687},{"$f":"'Project Info'!D60","v":20.383306659827422},{"$f":"'Project Info'!E60","v":7.246164547543378},{"$f":"'Project Info'!F60","v":0},{"$f":"'Project Info'!G60","v":0},{"$f":"'Project Info'!H60","v":0},{"$f":"'Project Info'!I60","v":0},{"$f":"'Project Info'!J60","v":0},{"$f":"'Project Info'!K60","v":0},{"$f":"'Project Info'!L60","v":0},0.53638938886075427,4283.3130834116955,0.7871999999999999,117.00188851645531,0.91427578434374157,5441.2005632770533,4684.9245673571204,756.27599591993294,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A61","v":15},{"$f":"'Project Info'!B61","v":20},{"$f":"'Project Info'!C61","v":17.808510327474309},{"$f":"'Project Info'!D61","v":15.420865796304254},{"$f":"'Project Info'!E61","v":5.5490484131518292},{"$f":"'Project Info'!F61","v":0},{"$f":"'Project Info'!G61","v":0},{"$f":"'Project Info'!H61","v":0},{"$f":"'Project Info'!I61","v":0},{"$f":"'Project Info'!J61","v":0},{"$f":"'Project Info'!K61","v":0},{"$f":"'Project Info'!L61","v":0},0.60715667735262291,4848.4220489685813,0.7871999999999999,140,0.87999999999999989,6159.07272480765,5509.5705101915701,649.50221461607998,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A62","v":10},{"$f":"'Project Info'!B62","v":15},{"$f":"'Project Info'!C62","v":12.269931130346862},{"$f":"'Project Info'!D62","v":10.318264913023604},{"$f":"'Project Info'!E62","v":3.9082824916941998},{"$f":"'Project Info'!F62","v":0},{"$f":"'Project Info'!G62","v":0},{"$f":"'Project Info'!H62","v":0},{"$f":"'Project Info'!I62","v":0},{"$f":"'Project Info'!J62","v":0},{"$f":"'Project Info'!K62","v":0},{"$f":"'Project Info'!L62","v":0},0.68268275731345174,5451.5321274921453,0.7871999999999999,140,0.87999999999999989,6925.2186578914452,6194.9228721501659,730.29578574127936,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A63","v":5},{"$f":"'Project Info'!B63","v":10},{"$f":"'Project Info'!C63","v":7.3137581369917548},{"$f":"'Project Info'!D63","v":5.7052382449247707},{"$f":"'Project Info'!E63","v":2.5019418419888937},{"$f":"'Project Info'!F63","v":0},{"$f":"'Project Info'!G63","v":0},{"$f":"'Project Info'!H63","v":0},{"$f":"'Project Info'!I63","v":0},{"$f":"'Project Info'!J63","v":0},{"$f":"'Project Info'!K63","v":0},{"$f":"'Project Info'!L63","v":0},0.75026693449556681,5991.2225023718711,0.7871999999999999,140,0.87999999999999989,7610.8009430536986,6808.2073890589454,802.59355399475317,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A64","v":0},{"$f":"'Project Info'!B64","v":5},{"$f":"'Project Info'!C64","v":2.6119461836144886},{"$f":"'Project Info'!D64","v":1.2699770062067783},{"$f":"'Project Info'!E64","v":1.2046477897733283},{"$f":"'Project Info'!F64","v":0},{"$f":"'Project Info'!G64","v":0},{"$f":"'Project Info'!H64","v":0},{"$f":"'Project Info'!I64","v":0},{"$f":"'Project Info'!J64","v":0},{"$f":"'Project Info'!K64","v":0},{"$f":"'Project Info'!L64","v":0},0.81438255204162047,6503.2148519396305,0.7871999999999999,140,0.87999999999999989,8261.1977285818484,7390.0168772041261,871.18085137772232,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A65","v":-5},{"$f":"'Project Info'!B65","v":0},{"$f":"'Project Info'!C65","v":-1.6731398516793925},{"$f":"'Project Info'!D65","v":-2.7083318773557807},{"$f":"'Project Info'!E65","v":7.9391832815876459E-2},{"$f":"'Project Info'!F65","v":0},{"$f":"'Project Info'!G65","v":0},{"$f":"'Project Info'!H65","v":0},{"$f":"'Project Info'!I65","v":0},{"$f":"'Project Info'!J65","v":0},{"$f":"'Project Info'!K65","v":0},{"$f":"'Project Info'!L65","v":0},0.87281554343199153,6969.8288486423753,0.7871999999999999,140,0.87999999999999989,8853.9492487835068,7920.2600552754275,933.68919350807937,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A66","v":-10},{"$f":"'Project Info'!B66","v":-5},{"$f":"'Project Info'!C66","v":-6.5729865085377277},{"$f":"'Project Info'!D66","v":-7.2465935998252222},{"$f":"'Project Info'!E66","v":-1.168423365310433},{"$f":"'Project Info'!F66","v":0},{"$f":"'Project Info'!G66","v":0},{"$f":"'Project Info'!H66","v":0},{"$f":"'Project Info'!I66","v":0},{"$f":"'Project Info'!J66","v":0},{"$f":"'Project Info'!K66","v":0},{"$f":"'Project Info'!L66","v":0},0.93963163420733253,7503.3857044338256,0.7871999999999999,140,0.87999999999999989,9531.7399700632959,8526.5746641293481,1005.1653059339478,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A67","v":-15},{"$f":"'Project Info'!B67","v":-10},{"$f":"'Project Info'!C67","v":-15.32570353422995},{"$f":"'Project Info'!D67","v":-15.707838211108999},{"$f":"'Project Info'!E67","v":-3.4051318156661381},{"$f":"'Project Info'!F67","v":0},{"$f":"'Project Info'!G67","v":0},{"$f":"'Project Info'!H67","v":0},{"$f":"'Project Info'!I67","v":0},{"$f":"'Project Info'!J67","v":0},{"$f":"'Project Info'!K67","v":0},{"$f":"'Project Info'!L67","v":0},1,7985.454545454545,0.7871999999999999,140,0.87999999999999989,10144.124168514412,9074.3801652892562,1069.7440032251561,0]
[]
[]
[null,null,null,null,null,null,"Unoccupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Heating","Heating","Base","Return","Proposed","Base","Design","Demand","Demand"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Load","Load","Eff.","HWT","Eff.","Demand","Demand","Savings","Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","%","MBH","%","°F","%","MBH","MBH","MBH","kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A74","v":100},{"$f":"'Project Info'!B74","v":105},{"$f":"'Project Info'!C74","v":102},{"$f":"'Project Info'!D74","v":76},{"$f":"'Project Info'!E74","v":40},{"$f":"'Project Info'!F74","v":0},{"$f":"'Project Info'!G74","v":0},{"$f":"'Project Info'!H74","v":0},{"$f":"'Project Info'!I74","v":0},{"$f":"'Project Info'!J74","v":0},{"$f":"'Project Info'!K74","v":0},{"$f":"'Project Info'!L74","v":0},{"$f":"MAX($Y$93,MIN(1,TREND($Y$93:$Z$93,$W$93:$X$93,I63)))","v":0},{"$f":"S63*$U$103","v":0},{"$f":"$V$100","v":0.7871999999999999},{"$f":"IF(I63>$T$109,$U$109,IF(I63<$T$108,$U$108,$U$108+(I63*(($U$108-$U$109)/($T$108-$T$109)))))","v":100},{"$f":"MAX($Y$106,MIN($Y$100,TREND(OFFSET($X$99,MATCH(V63,$X$100:$X$106,1),1,2,1),OFFSET($X$99,MATCH(V63,$X$100:$X$106,1),0,2,1),V63)))","v":0.9324444444444443},{"$f":"T63/U63","v":0},{"$f":"T63/W63","v":0},{"$f":"X63-Y63","v":0},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A75","v":95},{"$f":"'Project Info'!B75","v":100},{"$f":"'Project Info'!C75","v":95.219272727272724},{"$f":"'Project Info'!D75","v":74.534025272781079},{"$f":"'Project Info'!E75","v":37.923296058061368},{"$f":"'Project Info'!F75","v":0},{"$f":"'Project Info'!G75","v":0},{"$f":"'Project Info'!H75","v":0},{"$f":"'Project Info'!I75","v":0},{"$f":"'Project Info'!J75","v":0},{"$f":"'Project Info'!K75","v":0},{"$f":"'Project Info'!L75","v":0},0,0,0.7871999999999999,100,0.9324444444444443,{"$f":"T64/U64","v":0},{"$f":"T64/W64","v":0},{"$f":"X64-Y64","v":0},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A76","v":90},{"$f":"'Project Info'!B76","v":95},{"$f":"'Project Info'!C76","v":92.016049160256074},{"$f":"'Project Info'!D76","v":72.911561930607689},{"$f":"'Project Info'!E76","v":36.467095439351091},{"$f":"'Project Info'!F76","v":0},{"$f":"'Project Info'!G76","v":0},{"$f":"'Project Info'!H76","v":0},{"$f":"'Project Info'!I76","v":0},{"$f":"'Project Info'!J76","v":0},{"$f":"'Project Info'!K76","v":0},{"$f":"'Project Info'!L76","v":0},0,0,0.7871999999999999,100,0.9324444444444443,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A77","v":85},{"$f":"'Project Info'!B77","v":90},{"$f":"'Project Info'!C77","v":87.457811360655285},{"$f":"'Project Info'!D77","v":70.80538329449476},{"$f":"'Project Info'!E77","v":34.679413213566804},{"$f":"'Project Info'!F77","v":0},{"$f":"'Project Info'!G77","v":0},{"$f":"'Project Info'!H77","v":0},{"$f":"'Project Info'!I77","v":0},{"$f":"'Project Info'!J77","v":0},{"$f":"'Project Info'!K77","v":0},{"$f":"'Project Info'!L77","v":0},0,0,0.7871999999999999,100,0.9324444444444443,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A78","v":80},{"$f":"'Project Info'!B78","v":85},{"$f":"'Project Info'!C78","v":82.136788830239965},{"$f":"'Project Info'!D78","v":67.872393622439333},{"$f":"'Project Info'!E78","v":32.296248223809314},{"$f":"'Project Info'!F78","v":0},{"$f":"'Project Info'!G78","v":0},{"$f":"'Project Info'!H78","v":0},{"$f":"'Project Info'!I78","v":0},{"$f":"'Project Info'!J78","v":0},{"$f":"'Project Info'!K78","v":0},{"$f":"'Project Info'!L78","v":0},0,0,0.7871999999999999,100,0.9324444444444443,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A79","v":75},{"$f":"'Project Info'!B79","v":80},{"$f":"'Project Info'!C79","v":76.988400157585886},{"$f":"'Project Info'!D79","v":65.129261896908645},{"$f":"'Project Info'!E79","v":30.190476812806729},{"$f":"'Project Info'!F79","v":0},{"$f":"'Project Info'!G79","v":0},{"$f":"'Project Info'!H79","v":0},{"$f":"'Project Info'!I79","v":0},{"$f":"'Project Info'!J79","v":0},{"$f":"'Project Info'!K79","v":0},{"$f":"'Project Info'!L79","v":0},0,0,0.7871999999999999,100,0.9324444444444443,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A80","v":70},{"$f":"'Project Info'!B80","v":75},{"$f":"'Project Info'!C80","v":72.457982050814195},{"$f":"'Project Info'!D80","v":63.604425012889301},{"$f":"'Project Info'!E80","v":29.088683095945193},{"$f":"'Project Info'!F80","v":0},{"$f":"'Project Info'!G80","v":0},{"$f":"'Project Info'!H80","v":0},{"$f":"'Project Info'!I80","v":0},{"$f":"'Project Info'!J80","v":0},{"$f":"'Project Info'!K80","v":0},{"$f":"'Project Info'!L80","v":0},0,0,0.7871999999999999,100,0.9324444444444443,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A81","v":65},{"$f":"'Project Info'!B81","v":70},{"$f":"'Project Info'!C81","v":67.815831070966169},{"$f":"'Project Info'!D81","v":61.631331368130574},{"$f":"'Project Info'!E81","v":27.661514889731574},{"$f":"'Project Info'!F81","v":0},{"$f":"'Project Info'!G81","v":0},{"$f":"'Project Info'!H81","v":0},{"$f":"'Project Info'!I81","v":0},{"$f":"'Project Info'!J81","v":0},{"$f":"'Project Info'!K81","v":0},{"$f":"'Project Info'!L81","v":0},0,0,0.7871999999999999,100,0.9324444444444443,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A82","v":60},{"$f":"'Project Info'!B82","v":65},{"$f":"'Project Info'!C82","v":62.535961472271332},{"$f":"'Project Info'!D82","v":57.135476922863582},{"$f":"'Project Info'!E82","v":24.623037157728302},{"$f":"'Project Info'!F82","v":0},{"$f":"'Project Info'!G82","v":0},{"$f":"'Project Info'!H82","v":0},{"$f":"'Project Info'!I82","v":0},{"$f":"'Project Info'!J82","v":0},{"$f":"'Project Info'!K82","v":0},{"$f":"'Project Info'!L82","v":0},0,0,0.7871999999999999,100,0.9324444444444443,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A83","v":55},{"$f":"'Project Info'!B83","v":60},{"$f":"'Project Info'!C83","v":57.125792270740902},{"$f":"'Project Info'!D83","v":52.596971157053673},{"$f":"'Project Info'!E83","v":21.818001539159841},{"$f":"'Project Info'!F83","v":0},{"$f":"'Project Info'!G83","v":0},{"$f":"'Project Info'!H83","v":0},{"$f":"'Project Info'!I83","v":0},{"$f":"'Project Info'!J83","v":0},{"$f":"'Project Info'!K83","v":0},{"$f":"'Project Info'!L83","v":0},3.1137250400306904E-2,248.64509774208713,0.7871999999999999,82.874207729259098,0.95025751663997937,315.86013432683836,261.66075341479291,54.199380912045456,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A84","v":50},{"$f":"'Project Info'!B84","v":55},{"$f":"'Project Info'!C84","v":52.235698854337961},{"$f":"'Project Info'!D84","v":48.022768090099298},{"$f":"'Project Info'!E84","v":19.246640192796217},{"$f":"'Project Info'!F84","v":0},{"$f":"'Project Info'!G84","v":0},{"$f":"'Project Info'!H84","v":0},{"$f":"'Project Info'!I84","v":0},{"$f":"'Project Info'!J84","v":0},{"$f":"'Project Info'!K84","v":0},{"$f":"'Project Info'!L84","v":0},8.4113262411338763E-2,671.6826336556361,0.7871999999999999,87.764301145662046,0.94603966539370865,853.25537811945651,709.99415587517171,143.2612222442848,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A85","v":45},{"$f":"'Project Info'!B85","v":50},{"$f":"'Project Info'!C85","v":47.459170258371508},{"$f":"'Project Info'!D85","v":43.465397050422162},{"$f":"'Project Info'!E85","v":16.894183241713304},{"$f":"'Project Info'!F85","v":0},{"$f":"'Project Info'!G85","v":0},{"$f":"'Project Info'!H85","v":0},{"$f":"'Project Info'!I85","v":0},{"$f":"'Project Info'!J85","v":0},{"$f":"'Project Info'!K85","v":0},{"$f":"'Project Info'!L85","v":0},0.13585898886764203,1084.8957801939705,0.7871999999999999,92.5408297416285,0.94073241139819042,1378.1704524821782,1153.2458827282385,224.92456975393975,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A86","v":40},{"$f":"'Project Info'!B86","v":45},{"$f":"'Project Info'!C86","v":42.677030404888129},{"$f":"'Project Info'!D86","v":38.812544504634097},{"$f":"'Project Info'!E86","v":14.690265649465921},{"$f":"'Project Info'!F86","v":0},{"$f":"'Project Info'!G86","v":0},{"$f":"'Project Info'!H86","v":0},{"$f":"'Project Info'!I86","v":0},{"$f":"'Project Info'!J86","v":0},{"$f":"'Project Info'!K86","v":0},{"$f":"'Project Info'!L86","v":0},0.18766550394704523,1498.5943515189501,0.7871999999999999,97.322969595111871,0.93541892267209781,1903.7021741856584,1602.0569128942757,301.64526129138267,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A87","v":35},{"$f":"'Project Info'!B87","v":40},{"$f":"'Project Info'!C87","v":37.333046773755832},{"$f":"'Project Info'!D87","v":33.904706919479686},{"$f":"'Project Info'!E87","v":12.53841602318813},{"$f":"'Project Info'!F87","v":0},{"$f":"'Project Info'!G87","v":0},{"$f":"'Project Info'!H87","v":0},{"$f":"'Project Info'!I87","v":0},{"$f":"'Project Info'!J87","v":0},{"$f":"'Project Info'!K87","v":0},{"$f":"'Project Info'!L87","v":0},0.24555865995097842,1960.8975172812675,0.7871999999999999,102.66695322624417,0.92948116308195083,2490.9775371967326,2109.668915483313,381.3086217134196,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A88","v":30},{"$f":"'Project Info'!B88","v":35},{"$f":"'Project Info'!C88","v":32.638179845662044},{"$f":"'Project Info'!D88","v":29.547170928664851},{"$f":"'Project Info'!E88","v":10.728972818165861},{"$f":"'Project Info'!F88","v":0},{"$f":"'Project Info'!G88","v":0},{"$f":"'Project Info'!H88","v":0},{"$f":"'Project Info'!I88","v":0},{"$f":"'Project Info'!J88","v":0},{"$f":"'Project Info'!K88","v":0},{"$f":"'Project Info'!L88","v":0},0.29641971833866115,2367.0461871698176,0.7871999999999999,107.36182015433795,0.92445141205930992,3006.9184288234474,2560.4873942449613,446.43103457848611,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A89","v":25},{"$f":"'Project Info'!B89","v":30},{"$f":"'Project Info'!C89","v":27.529264646850947},{"$f":"'Project Info'!D89","v":24.652717392657845},{"$f":"'Project Info'!E89","v":8.8041305482613303},{"$f":"'Project Info'!F89","v":0},{"$f":"'Project Info'!G89","v":0},{"$f":"'Project Info'!H89","v":0},{"$f":"'Project Info'!I89","v":0},{"$f":"'Project Info'!J89","v":0},{"$f":"'Project Info'!K89","v":0},{"$f":"'Project Info'!L89","v":0},0.35176629965911471,2809.0137965506033,0.7871999999999999,112.47073535314905,0.9190586682383427,3568.3610220409091,3056.4031368475507,511.95788519335838,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A90","v":20},{"$f":"'Project Info'!B90","v":25},{"$f":"'Project Info'!C90","v":22.998111483544687},{"$f":"'Project Info'!D90","v":20.383306659827422},{"$f":"'Project Info'!E90","v":7.246164547543378},{"$f":"'Project Info'!F90","v":0},{"$f":"'Project Info'!G90","v":0},{"$f":"'Project Info'!H90","v":0},{"$f":"'Project Info'!I90","v":0},{"$f":"'Project Info'!J90","v":0},{"$f":"'Project Info'!K90","v":0},{"$f":"'Project Info'!L90","v":0},0.40085379226159917,3200.9997374780792,0.7871999999999999,117.00188851645531,0.91427578434374157,4066.3106421215443,3501.1314882147144,565.17915390682992,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A91","v":15},{"$f":"'Project Info'!B91","v":20},{"$f":"'Project Info'!C91","v":17.808510327474309},{"$f":"'Project Info'!D91","v":15.420865796304254},{"$f":"'Project Info'!E91","v":5.5490484131518292},{"$f":"'Project Info'!F91","v":0},{"$f":"'Project Info'!G91","v":0},{"$f":"'Project Info'!H91","v":0},{"$f":"'Project Info'!I91","v":0},{"$f":"'Project Info'!J91","v":0},{"$f":"'Project Info'!K91","v":0},{"$f":"'Project Info'!L91","v":0},0.45707447145236157,3649.9474156704946,0.7871999999999999,140,0.87999999999999989,4636.6201926708527,4147.667517807381,488.95267486347166,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A92","v":10},{"$f":"'Project Info'!B92","v":15},{"$f":"'Project Info'!C92","v":12.269931130346862},{"$f":"'Project Info'!D92","v":10.318264913023604},{"$f":"'Project Info'!E92","v":3.9082824916941998},{"$f":"'Project Info'!F92","v":0},{"$f":"'Project Info'!G92","v":0},{"$f":"'Project Info'!H92","v":0},{"$f":"'Project Info'!I92","v":0},{"$f":"'Project Info'!J92","v":0},{"$f":"'Project Info'!K92","v":0},{"$f":"'Project Info'!L92","v":0},0.51707574608790896,4129.0848669419929,0.7871999999999999,140,0.87999999999999989,5245.2805728429794,4692.141894252265,553.13867859071433,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A93","v":5},{"$f":"'Project Info'!B93","v":10},{"$f":"'Project Info'!C93","v":7.3137581369917548},{"$f":"'Project Info'!D93","v":5.7052382449247707},{"$f":"'Project Info'!E93","v":2.5019418419888937},{"$f":"'Project Info'!F93","v":0},{"$f":"'Project Info'!G93","v":0},{"$f":"'Project Info'!H93","v":0},{"$f":"'Project Info'!I93","v":0},{"$f":"'Project Info'!J93","v":0},{"$f":"'Project Info'!K93","v":0},{"$f":"'Project Info'!L93","v":0},0.5707676201825892,4557.8388869853306,0.7871999999999999,140,0.87999999999999989,5789.9376104996581,5179.3623715742397,610.57523892541849,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A94","v":0},{"$f":"'Project Info'!B94","v":5},{"$f":"'Project Info'!C94","v":2.6119461836144886},{"$f":"'Project Info'!D94","v":1.2699770062067783},{"$f":"'Project Info'!E94","v":1.2046477897733283},{"$f":"'Project Info'!F94","v":8760},{"$f":"'Project Info'!G94","v":2672},{"$f":"'Project Info'!H94","v":3160},{"$f":"'Project Info'!I94","v":1344},{"$f":"'Project Info'!J94","v":1584},{"$f":"'Project Info'!K94","v":88},{"$f":"'Project Info'!L94","v":264},0.62170391634417632,4964.5883646974953,0.7871999999999999,140,0.87999999999999989,6306.6417234470218,5641.5776871562457,665.06403629077613,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A95","v":-5},{"$f":"'Project Info'!B95","v":0},{"$f":"'Project Info'!C95","v":-1.6731398516793925},{"$f":"'Project Info'!D95","v":-2.7083318773557807},{"$f":"'Project Info'!E95","v":7.9391832815876459E-2},{"$f":"'Project Info'!F95","v":0},{"$f":"'Project Info'!G95","v":0},{"$f":"'Project Info'!H95","v":0},{"$f":"'Project Info'!I95","v":0},{"$f":"'Project Info'!J95","v":0},{"$f":"'Project Info'!K95","v":0},{"$f":"'Project Info'!L95","v":0},0.66812568172652664,5335.287262078009,0.7871999999999999,140,0.87999999999999989,6777.5498756072275,6062.8264341795566,714.72344142767088,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A96","v":-10},{"$f":"'Project Info'!B96","v":-5},{"$f":"'Project Info'!C96","v":-6.5729865085377277},{"$f":"'Project Info'!D96","v":-7.2465935998252222},{"$f":"'Project Info'!E96","v":-1.168423365310433},{"$f":"'Project Info'!F96","v":0},{"$f":"'Project Info'!G96","v":0},{"$f":"'Project Info'!H96","v":0},{"$f":"'Project Info'!I96","v":0},{"$f":"'Project Info'!J96","v":0},{"$f":"'Project Info'!K96","v":0},{"$f":"'Project Info'!L96","v":0},0.72120735384249191,5759.1685419567712,0.7871999999999999,140,0.87999999999999989,7316.0169486239483,6544.5097067690585,771.5072418548898,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A97","v":-15},{"$f":"'Project Info'!B97","v":-10},{"$f":"'Project Info'!C97","v":-15.32570353422995},{"$f":"'Project Info'!D97","v":-15.707838211108999},{"$f":"'Project Info'!E97","v":-3.4051318156661381},{"$f":"'Project Info'!F97","v":0},{"$f":"'Project Info'!G97","v":0},{"$f":"'Project Info'!H97","v":0},{"$f":"'Project Info'!I97","v":0},{"$f":"'Project Info'!J97","v":0},{"$f":"'Project Info'!K97","v":0},{"$f":"'Project Info'!L97","v":0},0.81602845495415766,6516.3581348339276,0.7871999999999999,140,0.87999999999999989,8277.8939720959461,7404.9524259476457,872.9415461483004,0]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Boiler Plant Heating Load Profile"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Occupied Profile",null,null,null,"Unocc Profile"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Max OAT","Min OAT","% Load @","%Load @","Max OAT","Min OAT","% Load @","%Load @"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"°F","°F","Max OAT","Min OAT","°F","°F","Max OAT","Min OAT"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,55,0,0.1,0.85,60,0,0,0.65]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Baseline Boiler Efficiency",null,null,null,null,"Boiler Efficiency"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Input",null,"Rated","Avg. Op.",null,"vs. HW Return Temp"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"MBH",null,"Ec","Et",null,"Return","Cond Blr","Std Blr"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"≤",2500,0.85,{"$f":"0.97*U98","v":0.82450000000000001},null,"Water ","Eff","Eff"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,">",2500,0.82,{"$f":"0.96*U99","v":0.7871999999999999},null,"°F","%","%"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Base Eff. per design capacity",null,null,{"$f":"IF($N$16<=$T$98,V98,V99)","v":0.7871999999999999},null,68,0.96099999999999997,{"$f":"$V$100","v":0.7871999999999999}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,86,0.94799999999999995,0.7871999999999999]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Peak Plant Load",null,null,null,null,104,0.92800000000000005,0.7871999999999999]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Peak Plant MBH",null,{"$f":"N16/N18","v":7985.454545454545},null,null,122,0.90900000000000003,0.7871999999999999]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,140,0.88,0.7871999999999999]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"HW Reset",null,null,null,150,0.87,0.7871999999999999]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"OAT","Return",null,null,160,0.87,0.7871999999999999]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"°F","°F"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"M23","v":20},{"$f":"N23-$N$20","v":140}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"M24","v":60},{"$f":"N24-$N$20","v":100}]

{"sheet":"20","index":23,"n_rows":109,"n_cols":27,"rows_kept":109,"cut":false,"hidden":true,"merged":[]}
["Savings Summary",null,null,null,null,"Measure Summary",null,null,null,null,"Measure Description"]
["Annual kWh Savings",null,null,{"$f":"SUM(A14:D14)","v":0},null,null,null,"Value","Unit"]
["% On Peak",null,null,{"$f":"IF(D2<=0,0,MIN(1,A15+C15))","v":0},null,"Annual Electric Savings",null,{"$f":"D2","v":0},"kWh"]
["Max kW",null,null,{"$f":"MAX(AC41:AC64,AC71:AC94)","v":0},null,"Annual Fuel Savings",null,{"$f":"D7*C28","v":{"$error":"#N/A"}},{"$f":"D20","v":{"$error":"#N/A"}}]
["Summer kW",null,null,{"$f":"(SUMPRODUCT(AC41:AC64,R33:R56)+SUMPRODUCT(AC71:AC94,R63:R86))/SUM(R33:R56,R63:R86)","v":0},null,"Incremental Cost",null,45000,"$",null,"Measure Instructions"]
["Winter kW",null,null,{"$f":"(SUMPRODUCT(AC41:AC64,Q33:Q56)+SUMPRODUCT(AC71:AC94,Q63:Q86))/SUM(Q33:Q56,Q63:Q86)","v":0},null,"Estimated Incentive",null,{"$f":"IF(AND($C$24>0,$C$25>0),MIN(H5,H3*C24+H4*C25),\"TBD\")","v":"TBD"},"$"]
["Annual Fuel Savings (MMBtu)",null,null,{"$f":"(SUMPRODUCT($L$33:$L$56,Z33:Z56)+SUMPRODUCT($L$63:$L$86,Z63:Z86))/100","v":58259.609579071992},null,"Custom Payback",null,null,"years"]
["Incremental Cost",null,null,45000]
[]
["kWh Savings by Peak Period"]
["Winter","Winter","Summer","Summer"]
["On-Peak","Off-Peak","On-Peak","Off-Peak"]
["kWh","kWh","kWh","kWh"]
[{"$f":"SUMPRODUCT($AA$33:$AA$56,M33:M56)+SUMPRODUCT($AA$63:$AA$86,M63:M86)","v":0},{"$f":"SUMPRODUCT($AA$33:$AA$56,N33:N56)+SUMPRODUCT($AA$63:$AA$86,N63:N86)","v":0},{"$f":"SUMPRODUCT($AA$33:$AA$56,O33:O56)+SUMPRODUCT($AA$63:$AA$86,O63:O86)","v":0},{"$f":"SUMPRODUCT($AA$33:$AA$56,P33:P56)+SUMPRODUCT($AA$63:$AA$86,P63:P86)","v":0},null,null,null,null,null,null,"User Inputs - Boiler/Loop Parameters"]
[{"$f":"IF(A14<=0,0,A14/SUMIF($A$14:$D$14,\">0\"))","v":0},{"$f":"IF(B14<=0,0,B14/SUMIF($A$14:$D$14,\">0\"))","v":0},{"$f":"IF(C14<=0,0,C14/SUMIF($A$14:$D$14,\">0\"))","v":0},{"$f":"IF(D14<=0,0,D14/SUMIF($A$14:$D$14,\">0\"))","v":0},null,null,null,null,null,null,"Boiler Quantity",null,null,3]
[null,null,null,null,null,null,null,null,null,null,"Output MBH (per Boiler)",null,null,4392]
["Utility Rates",null,null,null,null,null,null,null,null,null,"Max # of Operating Boilers",null,null,2]
[null,null,"Rate","Unit",null,null,null,null,null,null,"Design Capacity Ratio*",null,null,0.55000000000000004]
["Electric",null,{"$f":"'ECM Summary'!$E$31","v":0.1593},"kWh",null,null,null,null,null,null,"Design HW Temperature",null,null,160]
[{"$f":"'ECM Summary'!$C$32","v":0},null,{"$f":"'ECM Summary'!$E$32","v":{"$error":"#N/A"}},{"$f":"'ECM Summary'!$F$32","v":{"$error":"#N/A"}},null,null,null,null,null,null,"Design HW Loop dT",null,null,20]
[null,null,null,null,null,null,null,null,null,null,null,null,"OAT","HW Temp"]
["Custom Incentive Rates",null,null,null,null,null,null,null,null,null,null,null,"°F","°F"]
[null,null,"Rate","Unit",null,null,null,null,null,null,"Reset Max Supply T",null,20,160]
["Electric",null,{"$f":"'ECM Summary'!$J$31","v":0.28000000000000003},"kWh",null,null,null,null,null,null,"Reset Min Supply T",null,60,120]
[{"$f":"'ECM Summary'!$H$32","v":0},null,{"$f":"'ECM Summary'!$J$32","v":0},{"$f":"'ECM Summary'!$K$32","v":{"$error":"#N/A"}},null,null,null,null,null,null,"*Cap Ratio = % of Peak Load from 1 boiler"]
[]
["Fossil Fuel",null,{"$f":"'Project Info'!C21","v":0}]
["Fuel Conversion",null,{"$f":"LOOKUP(C27,'Project Info'!X102:X104,'Project Info'!Z102:Z104)","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,"Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Heating","Heating","Base","Return","Proposed","Base","Design","Demand","Demand"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Load","Load","Eff.","HWT","Eff.","Demand","Demand","Savings","Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","%","MBH","%","°F","%","MBH","MBH","MBH","kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A44","v":100},{"$f":"'Project Info'!B44","v":105},{"$f":"'Project Info'!C44","v":102},{"$f":"'Project Info'!D44","v":76},{"$f":"'Project Info'!E44","v":40},{"$f":"'Project Info'!F44","v":0},{"$f":"'Project Info'!G44","v":0},{"$f":"'Project Info'!H44","v":0},{"$f":"'Project Info'!I44","v":0},{"$f":"'Project Info'!J44","v":0},{"$f":"'Project Info'!K44","v":0},{"$f":"'Project Info'!L44","v":0},{"$f":"MAX($U$93,MIN(1,TREND($U$93:$V$93,$S$93:$T$93,I33)))","v":0.1},{"$f":"S33*$U$103","v":798.5454545454545},{"$f":"$V$100","v":0.7871999999999999},{"$f":"IF(I33>$T$109,$U$109,IF(I33<$T$108,$U$108,$U$108+(I33*(($U$108-$U$109)/($T$108-$T$109)))))","v":100},{"$f":"MAX($Y$106,MIN($Y$100,TREND(OFFSET($X$99,MATCH(V33,$X$100:$X$106,1),1,2,1),OFFSET($X$99,MATCH(V33,$X$100:$X$106,1),0,2,1),V33)))","v":0.9324444444444443},{"$f":"T33/U33","v":1014.4124168514413},{"$f":"T33/W33","v":856.40003466504902},{"$f":"X33-Y33","v":158.0123821863923},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A45","v":95},{"$f":"'Project Info'!B45","v":100},{"$f":"'Project Info'!C45","v":95.219272727272724},{"$f":"'Project Info'!D45","v":74.534025272781079},{"$f":"'Project Info'!E45","v":37.923296058061368},{"$f":"'Project Info'!F45","v":0},{"$f":"'Project Info'!G45","v":0},{"$f":"'Project Info'!H45","v":0},{"$f":"'Project Info'!I45","v":0},{"$f":"'Project Info'!J45","v":0},{"$f":"'Project Info'!K45","v":0},{"$f":"'Project Info'!L45","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,{"$f":"T34/U34","v":1014.4124168514413},{"$f":"T34/W34","v":856.40003466504902},{"$f":"X34-Y34","v":158.0123821863923},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A46","v":90},{"$f":"'Project Info'!B46","v":95},{"$f":"'Project Info'!C46","v":92.016049160256074},{"$f":"'Project Info'!D46","v":72.911561930607689},{"$f":"'Project Info'!E46","v":36.467095439351091},{"$f":"'Project Info'!F46","v":0},{"$f":"'Project Info'!G46","v":0},{"$f":"'Project Info'!H46","v":0},{"$f":"'Project Info'!I46","v":0},{"$f":"'Project Info'!J46","v":0},{"$f":"'Project Info'!K46","v":0},{"$f":"'Project Info'!L46","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,1014.4124168514413,856.40003466504902,158.0123821863923,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A47","v":85},{"$f":"'Project Info'!B47","v":90},{"$f":"'Project Info'!C47","v":87.457811360655285},{"$f":"'Project Info'!D47","v":70.80538329449476},{"$f":"'Project Info'!E47","v":34.679413213566804},{"$f":"'Project Info'!F47","v":0},{"$f":"'Project Info'!G47","v":0},{"$f":"'Project Info'!H47","v":0},{"$f":"'Project Info'!I47","v":0},{"$f":"'Project Info'!J47","v":0},{"$f":"'Project Info'!K47","v":0},{"$f":"'Project Info'!L47","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,1014.4124168514413,856.40003466504902,158.0123821863923,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A48","v":80},{"$f":"'Project Info'!B48","v":85},{"$f":"'Project Info'!C48","v":82.136788830239965},{"$f":"'Project Info'!D48","v":67.872393622439333},{"$f":"'Project Info'!E48","v":32.296248223809314},{"$f":"'Project Info'!F48","v":0},{"$f":"'Project Info'!G48","v":0},{"$f":"'Project Info'!H48","v":0},{"$f":"'Project Info'!I48","v":0},{"$f":"'Project Info'!J48","v":0},{"$f":"'Project Info'!K48","v":0},{"$f":"'Project Info'!L48","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,1014.4124168514413,856.40003466504902,158.0123821863923,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A49","v":75},{"$f":"'Project Info'!B49","v":80},{"$f":"'Project Info'!C49","v":76.988400157585886},{"$f":"'Project Info'!D49","v":65.129261896908645},{"$f":"'Project Info'!E49","v":30.190476812806729},{"$f":"'Project Info'!F49","v":0},{"$f":"'Project Info'!G49","v":0},{"$f":"'Project Info'!H49","v":0},{"$f":"'Project Info'!I49","v":0},{"$f":"'Project Info'!J49","v":0},{"$f":"'Project Info'!K49","v":0},{"$f":"'Project Info'!L49","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,1014.4124168514413,856.40003466504902,158.0123821863923,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A50","v":70},{"$f":"'Project Info'!B50","v":75},{"$f":"'Project Info'!C50","v":72.457982050814195},{"$f":"'Project Info'!D50","v":63.604425012889301},{"$f":"'Project Info'!E50","v":29.088683095945193},{"$f":"'Project Info'!F50","v":0},{"$f":"'Project Info'!G50","v":0},{"$f":"'Project Info'!H50","v":0},{"$f":"'Project Info'!I50","v":0},{"$f":"'Project Info'!J50","v":0},{"$f":"'Project Info'!K50","v":0},{"$f":"'Project Info'!L50","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,1014.4124168514413,856.40003466504902,158.0123821863923,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A51","v":65},{"$f":"'Project Info'!B51","v":70},{"$f":"'Project Info'!C51","v":67.815831070966169},{"$f":"'Project Info'!D51","v":61.631331368130574},{"$f":"'Project Info'!E51","v":27.661514889731574},{"$f":"'Project Info'!F51","v":0},{"$f":"'Project Info'!G51","v":0},{"$f":"'Project Info'!H51","v":0},{"$f":"'Project Info'!I51","v":0},{"$f":"'Project Info'!J51","v":0},{"$f":"'Project Info'!K51","v":0},{"$f":"'Project Info'!L51","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,1014.4124168514413,856.40003466504902,158.0123821863923,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A52","v":60},{"$f":"'Project Info'!B52","v":65},{"$f":"'Project Info'!C52","v":62.535961472271332},{"$f":"'Project Info'!D52","v":57.135476922863582},{"$f":"'Project Info'!E52","v":24.623037157728302},{"$f":"'Project Info'!F52","v":0},{"$f":"'Project Info'!G52","v":0},{"$f":"'Project Info'!H52","v":0},{"$f":"'Project Info'!I52","v":0},{"$f":"'Project Info'!J52","v":0},{"$f":"'Project Info'!K52","v":0},{"$f":"'Project Info'!L52","v":0},0.1,798.5454545454545,0.7871999999999999,100,0.9324444444444443,1014.4124168514413,856.40003466504902,158.0123821863923,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A53","v":55},{"$f":"'Project Info'!B53","v":60},{"$f":"'Project Info'!C53","v":57.125792270740902},{"$f":"'Project Info'!D53","v":52.596971157053673},{"$f":"'Project Info'!E53","v":21.818001539159841},{"$f":"'Project Info'!F53","v":0},{"$f":"'Project Info'!G53","v":0},{"$f":"'Project Info'!H53","v":0},{"$f":"'Project Info'!I53","v":0},{"$f":"'Project Info'!J53","v":0},{"$f":"'Project Info'!K53","v":0},{"$f":"'Project Info'!L53","v":0},0.1,798.5454545454545,0.7871999999999999,82.874207729259098,0.95025751663997937,1014.4124168514413,840.34636986512419,174.06604698631713,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A54","v":50},{"$f":"'Project Info'!B54","v":55},{"$f":"'Project Info'!C54","v":52.235698854337961},{"$f":"'Project Info'!D54","v":48.022768090099298},{"$f":"'Project Info'!E54","v":19.246640192796217},{"$f":"'Project Info'!F54","v":0},{"$f":"'Project Info'!G54","v":0},{"$f":"'Project Info'!H54","v":0},{"$f":"'Project Info'!I54","v":0},{"$f":"'Project Info'!J54","v":0},{"$f":"'Project Info'!K54","v":0},{"$f":"'Project Info'!L54","v":0},0.13769501562266417,1099.5572883904383,0.7871999999999999,87.764301145662046,0.94603966539370865,1396.7953358618374,1162.2739813270314,234.52135453480605,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A55","v":45},{"$f":"'Project Info'!B55","v":50},{"$f":"'Project Info'!C55","v":47.459170258371508},{"$f":"'Project Info'!D55","v":43.465397050422162},{"$f":"'Project Info'!E55","v":16.894183241713304},{"$f":"'Project Info'!F55","v":0},{"$f":"'Project Info'!G55","v":0},{"$f":"'Project Info'!H55","v":0},{"$f":"'Project Info'!I55","v":0},{"$f":"'Project Info'!J55","v":0},{"$f":"'Project Info'!K55","v":0},{"$f":"'Project Info'!L55","v":0},0.20282949647675219,1619.6857245925373,0.7871999999999999,92.5408297416285,0.94073241139819042,2057.5275972974309,1721.7284160383431,335.79918125908785,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A56","v":40},{"$f":"'Project Info'!B56","v":45},{"$f":"'Project Info'!C56","v":42.677030404888129},{"$f":"'Project Info'!D56","v":38.812544504634097},{"$f":"'Project Info'!E56","v":14.690265649465921},{"$f":"'Project Info'!F56","v":0},{"$f":"'Project Info'!G56","v":0},{"$f":"'Project Info'!H56","v":0},{"$f":"'Project Info'!I56","v":0},{"$f":"'Project Info'!J56","v":0},{"$f":"'Project Info'!K56","v":0},{"$f":"'Project Info'!L56","v":0},0.26804049447879819,2140.425185001603,0.7871999999999999,97.322969595111871,0.93541892267209781,2719.0360581829309,2288.1995789515463,430.8364792313846,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A57","v":35},{"$f":"'Project Info'!B57","v":40},{"$f":"'Project Info'!C57","v":37.333046773755832},{"$f":"'Project Info'!D57","v":33.904706919479686},{"$f":"'Project Info'!E57","v":12.53841602318813},{"$f":"'Project Info'!F57","v":0},{"$f":"'Project Info'!G57","v":0},{"$f":"'Project Info'!H57","v":0},{"$f":"'Project Info'!I57","v":0},{"$f":"'Project Info'!J57","v":0},{"$f":"'Project Info'!K57","v":0},{"$f":"'Project Info'!L57","v":0},0.34091299853969315,2722.3452537933313,0.7871999999999999,102.66695322624417,0.92948116308195083,3458.2637878472201,2928.8869553489881,529.37683249823203,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A58","v":30},{"$f":"'Project Info'!B58","v":35},{"$f":"'Project Info'!C58","v":32.638179845662044},{"$f":"'Project Info'!D58","v":29.547170928664851},{"$f":"'Project Info'!E58","v":10.728972818165861},{"$f":"'Project Info'!F58","v":0},{"$f":"'Project Info'!G58","v":0},{"$f":"'Project Info'!H58","v":0},{"$f":"'Project Info'!I58","v":0},{"$f":"'Project Info'!J58","v":0},{"$f":"'Project Info'!K58","v":0},{"$f":"'Project Info'!L58","v":0},0.40493391119551753,3233.5813417649324,0.7871999999999999,107.36182015433795,0.92445141205930992,4107.6998752095187,3497.8380687004415,609.86180650907727,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A59","v":25},{"$f":"'Project Info'!B59","v":30},{"$f":"'Project Info'!C59","v":27.529264646850947},{"$f":"'Project Info'!D59","v":24.652717392657845},{"$f":"'Project Info'!E59","v":8.8041305482613303},{"$f":"'Project Info'!F59","v":0},{"$f":"'Project Info'!G59","v":0},{"$f":"'Project Info'!H59","v":0},{"$f":"'Project Info'!I59","v":0},{"$f":"'Project Info'!J59","v":0},{"$f":"'Project Info'!K59","v":0},{"$f":"'Project Info'!L59","v":0},0.47460093663385067,3789.9042067197674,0.7871999999999999,112.47073535314905,0.9190586682383427,4814.4108317070222,4123.6803891793752,690.73044252764703,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A60","v":20},{"$f":"'Project Info'!B60","v":25},{"$f":"'Project Info'!C60","v":22.998111483544687},{"$f":"'Project Info'!D60","v":20.383306659827422},{"$f":"'Project Info'!E60","v":7.246164547543378},{"$f":"'Project Info'!F60","v":0},{"$f":"'Project Info'!G60","v":0},{"$f":"'Project Info'!H60","v":0},{"$f":"'Project Info'!I60","v":0},{"$f":"'Project Info'!J60","v":0},{"$f":"'Project Info'!K60","v":0},{"$f":"'Project Info'!L60","v":0},0.53638938886075427,4283.3130834116955,0.7871999999999999,117.00188851645531,0.91427578434374157,5441.2005632770533,4684.9245673571204,756.27599591993294,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A61","v":15},{"$f":"'Project Info'!B61","v":20},{"$f":"'Project Info'!C61","v":17.808510327474309},{"$f":"'Project Info'!D61","v":15.420865796304254},{"$f":"'Project Info'!E61","v":5.5490484131518292},{"$f":"'Project Info'!F61","v":0},{"$f":"'Project Info'!G61","v":0},{"$f":"'Project Info'!H61","v":0},{"$f":"'Project Info'!I61","v":0},{"$f":"'Project Info'!J61","v":0},{"$f":"'Project Info'!K61","v":0},{"$f":"'Project Info'!L61","v":0},0.60715667735262291,4848.4220489685813,0.7871999999999999,140,0.87999999999999989,6159.07272480765,5509.5705101915701,649.50221461607998,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A62","v":10},{"$f":"'Project Info'!B62","v":15},{"$f":"'Project Info'!C62","v":12.269931130346862},{"$f":"'Project Info'!D62","v":10.318264913023604},{"$f":"'Project Info'!E62","v":3.9082824916941998},{"$f":"'Project Info'!F62","v":0},{"$f":"'Project Info'!G62","v":0},{"$f":"'Project Info'!H62","v":0},{"$f":"'Project Info'!I62","v":0},{"$f":"'Project Info'!J62","v":0},{"$f":"'Project Info'!K62","v":0},{"$f":"'Project Info'!L62","v":0},0.68268275731345174,5451.5321274921453,0.7871999999999999,140,0.87999999999999989,6925.2186578914452,6194.9228721501659,730.29578574127936,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A63","v":5},{"$f":"'Project Info'!B63","v":10},{"$f":"'Project Info'!C63","v":7.3137581369917548},{"$f":"'Project Info'!D63","v":5.7052382449247707},{"$f":"'Project Info'!E63","v":2.5019418419888937},{"$f":"'Project Info'!F63","v":0},{"$f":"'Project Info'!G63","v":0},{"$f":"'Project Info'!H63","v":0},{"$f":"'Project Info'!I63","v":0},{"$f":"'Project Info'!J63","v":0},{"$f":"'Project Info'!K63","v":0},{"$f":"'Project Info'!L63","v":0},0.75026693449556681,5991.2225023718711,0.7871999999999999,140,0.87999999999999989,7610.8009430536986,6808.2073890589454,802.59355399475317,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A64","v":0},{"$f":"'Project Info'!B64","v":5},{"$f":"'Project Info'!C64","v":2.6119461836144886},{"$f":"'Project Info'!D64","v":1.2699770062067783},{"$f":"'Project Info'!E64","v":1.2046477897733283},{"$f":"'Project Info'!F64","v":0},{"$f":"'Project Info'!G64","v":0},{"$f":"'Project Info'!H64","v":0},{"$f":"'Project Info'!I64","v":0},{"$f":"'Project Info'!J64","v":0},{"$f":"'Project Info'!K64","v":0},{"$f":"'Project Info'!L64","v":0},0.81438255204162047,6503.2148519396305,0.7871999999999999,140,0.87999999999999989,8261.1977285818484,7390.0168772041261,871.18085137772232,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A65","v":-5},{"$f":"'Project Info'!B65","v":0},{"$f":"'Project Info'!C65","v":-1.6731398516793925},{"$f":"'Project Info'!D65","v":-2.7083318773557807},{"$f":"'Project Info'!E65","v":7.9391832815876459E-2},{"$f":"'Project Info'!F65","v":0},{"$f":"'Project Info'!G65","v":0},{"$f":"'Project Info'!H65","v":0},{"$f":"'Project Info'!I65","v":0},{"$f":"'Project Info'!J65","v":0},{"$f":"'Project Info'!K65","v":0},{"$f":"'Project Info'!L65","v":0},0.87281554343199153,6969.8288486423753,0.7871999999999999,140,0.87999999999999989,8853.9492487835068,7920.2600552754275,933.68919350807937,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A66","v":-10},{"$f":"'Project Info'!B66","v":-5},{"$f":"'Project Info'!C66","v":-6.5729865085377277},{"$f":"'Project Info'!D66","v":-7.2465935998252222},{"$f":"'Project Info'!E66","v":-1.168423365310433},{"$f":"'Project Info'!F66","v":0},{"$f":"'Project Info'!G66","v":0},{"$f":"'Project Info'!H66","v":0},{"$f":"'Project Info'!I66","v":0},{"$f":"'Project Info'!J66","v":0},{"$f":"'Project Info'!K66","v":0},{"$f":"'Project Info'!L66","v":0},0.93963163420733253,7503.3857044338256,0.7871999999999999,140,0.87999999999999989,9531.7399700632959,8526.5746641293481,1005.1653059339478,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A67","v":-15},{"$f":"'Project Info'!B67","v":-10},{"$f":"'Project Info'!C67","v":-15.32570353422995},{"$f":"'Project Info'!D67","v":-15.707838211108999},{"$f":"'Project Info'!E67","v":-3.4051318156661381},{"$f":"'Project Info'!F67","v":0},{"$f":"'Project Info'!G67","v":0},{"$f":"'Project Info'!H67","v":0},{"$f":"'Project Info'!I67","v":0},{"$f":"'Project Info'!J67","v":0},{"$f":"'Project Info'!K67","v":0},{"$f":"'Project Info'!L67","v":0},1,7985.454545454545,0.7871999999999999,140,0.87999999999999989,10144.124168514412,9074.3801652892562,1069.7440032251561,0]
[]
[]
[null,null,null,null,null,null,"Unoccupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Heating","Heating","Base","Return","Proposed","Base","Design","Demand","Demand"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Load","Load","Eff.","HWT","Eff.","Demand","Demand","Savings","Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","%","MBH","%","°F","%","MBH","MBH","MBH","kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A74","v":100},{"$f":"'Project Info'!B74","v":105},{"$f":"'Project Info'!C74","v":102},{"$f":"'Project Info'!D74","v":76},{"$f":"'Project Info'!E74","v":40},{"$f":"'Project Info'!F74","v":0},{"$f":"'Project Info'!G74","v":0},{"$f":"'Project Info'!H74","v":0},{"$f":"'Project Info'!I74","v":0},{"$f":"'Project Info'!J74","v":0},{"$f":"'Project Info'!K74","v":0},{"$f":"'Project Info'!L74","v":0},{"$f":"MAX($Y$93,MIN(1,TREND($Y$93:$Z$93,$W$93:$X$93,I63)))","v":0},{"$f":"S63*$U$103","v":0},{"$f":"$V$100","v":0.7871999999999999},{"$f":"IF(I63>$T$109,$U$109,IF(I63<$T$108,$U$108,$U$108+(I63*(($U$108-$U$109)/($T$108-$T$109)))))","v":100},{"$f":"MAX($Y$106,MIN($Y$100,TREND(OFFSET($X$99,MATCH(V63,$X$100:$X$106,1),1,2,1),OFFSET($X$99,MATCH(V63,$X$100:$X$106,1),0,2,1),V63)))","v":0.9324444444444443},{"$f":"T63/U63","v":0},{"$f":"T63/W63","v":0},{"$f":"X63-Y63","v":0},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A75","v":95},{"$f":"'Project Info'!B75","v":100},{"$f":"'Project Info'!C75","v":95.219272727272724},{"$f":"'Project Info'!D75","v":74.534025272781079},{"$f":"'Project Info'!E75","v":37.923296058061368},{"$f":"'Project Info'!F75","v":0},{"$f":"'Project Info'!G75","v":0},{"$f":"'Project Info'!H75","v":0},{"$f":"'Project Info'!I75","v":0},{"$f":"'Project Info'!J75","v":0},{"$f":"'Project Info'!K75","v":0},{"$f":"'Project Info'!L75","v":0},0,0,0.7871999999999999,100,0.9324444444444443,{"$f":"T64/U64","v":0},{"$f":"T64/W64","v":0},{"$f":"X64-Y64","v":0},0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A76","v":90},{"$f":"'Project Info'!B76","v":95},{"$f":"'Project Info'!C76","v":92.016049160256074},{"$f":"'Project Info'!D76","v":72.911561930607689},{"$f":"'Project Info'!E76","v":36.467095439351091},{"$f":"'Project Info'!F76","v":0},{"$f":"'Project Info'!G76","v":0},{"$f":"'Project Info'!H76","v":0},{"$f":"'Project Info'!I76","v":0},{"$f":"'Project Info'!J76","v":0},{"$f":"'Project Info'!K76","v":0},{"$f":"'Project Info'!L76","v":0},0,0,0.7871999999999999,100,0.9324444444444443,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A77","v":85},{"$f":"'Project Info'!B77","v":90},{"$f":"'Project Info'!C77","v":87.457811360655285},{"$f":"'Project Info'!D77","v":70.80538329449476},{"$f":"'Project Info'!E77","v":34.679413213566804},{"$f":"'Project Info'!F77","v":0},{"$f":"'Project Info'!G77","v":0},{"$f":"'Project Info'!H77","v":0},{"$f":"'Project Info'!I77","v":0},{"$f":"'Project Info'!J77","v":0},{"$f":"'Project Info'!K77","v":0},{"$f":"'Project Info'!L77","v":0},0,0,0.7871999999999999,100,0.9324444444444443,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A78","v":80},{"$f":"'Project Info'!B78","v":85},{"$f":"'Project Info'!C78","v":82.136788830239965},{"$f":"'Project Info'!D78","v":67.872393622439333},{"$f":"'Project Info'!E78","v":32.296248223809314},{"$f":"'Project Info'!F78","v":0},{"$f":"'Project Info'!G78","v":0},{"$f":"'Project Info'!H78","v":0},{"$f":"'Project Info'!I78","v":0},{"$f":"'Project Info'!J78","v":0},{"$f":"'Project Info'!K78","v":0},{"$f":"'Project Info'!L78","v":0},0,0,0.7871999999999999,100,0.9324444444444443,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A79","v":75},{"$f":"'Project Info'!B79","v":80},{"$f":"'Project Info'!C79","v":76.988400157585886},{"$f":"'Project Info'!D79","v":65.129261896908645},{"$f":"'Project Info'!E79","v":30.190476812806729},{"$f":"'Project Info'!F79","v":0},{"$f":"'Project Info'!G79","v":0},{"$f":"'Project Info'!H79","v":0},{"$f":"'Project Info'!I79","v":0},{"$f":"'Project Info'!J79","v":0},{"$f":"'Project Info'!K79","v":0},{"$f":"'Project Info'!L79","v":0},0,0,0.7871999999999999,100,0.9324444444444443,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A80","v":70},{"$f":"'Project Info'!B80","v":75},{"$f":"'Project Info'!C80","v":72.457982050814195},{"$f":"'Project Info'!D80","v":63.604425012889301},{"$f":"'Project Info'!E80","v":29.088683095945193},{"$f":"'Project Info'!F80","v":0},{"$f":"'Project Info'!G80","v":0},{"$f":"'Project Info'!H80","v":0},{"$f":"'Project Info'!I80","v":0},{"$f":"'Project Info'!J80","v":0},{"$f":"'Project Info'!K80","v":0},{"$f":"'Project Info'!L80","v":0},0,0,0.7871999999999999,100,0.9324444444444443,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A81","v":65},{"$f":"'Project Info'!B81","v":70},{"$f":"'Project Info'!C81","v":67.815831070966169},{"$f":"'Project Info'!D81","v":61.631331368130574},{"$f":"'Project Info'!E81","v":27.661514889731574},{"$f":"'Project Info'!F81","v":0},{"$f":"'Project Info'!G81","v":0},{"$f":"'Project Info'!H81","v":0},{"$f":"'Project Info'!I81","v":0},{"$f":"'Project Info'!J81","v":0},{"$f":"'Project Info'!K81","v":0},{"$f":"'Project Info'!L81","v":0},0,0,0.7871999999999999,100,0.9324444444444443,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A82","v":60},{"$f":"'Project Info'!B82","v":65},{"$f":"'Project Info'!C82","v":62.535961472271332},{"$f":"'Project Info'!D82","v":57.135476922863582},{"$f":"'Project Info'!E82","v":24.623037157728302},{"$f":"'Project Info'!F82","v":0},{"$f":"'Project Info'!G82","v":0},{"$f":"'Project Info'!H82","v":0},{"$f":"'Project Info'!I82","v":0},{"$f":"'Project Info'!J82","v":0},{"$f":"'Project Info'!K82","v":0},{"$f":"'Project Info'!L82","v":0},0,0,0.7871999999999999,100,0.9324444444444443,0,0,0,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A83","v":55},{"$f":"'Project Info'!B83","v":60},{"$f":"'Project Info'!C83","v":57.125792270740902},{"$f":"'Project Info'!D83","v":52.596971157053673},{"$f":"'Project Info'!E83","v":21.818001539159841},{"$f":"'Project Info'!F83","v":0},{"$f":"'Project Info'!G83","v":0},{"$f":"'Project Info'!H83","v":0},{"$f":"'Project Info'!I83","v":0},{"$f":"'Project Info'!J83","v":0},{"$f":"'Project Info'!K83","v":0},{"$f":"'Project Info'!L83","v":0},3.1137250400306904E-2,248.64509774208713,0.7871999999999999,82.874207729259098,0.95025751663997937,315.86013432683836,261.66075341479291,54.199380912045456,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A84","v":50},{"$f":"'Project Info'!B84","v":55},{"$f":"'Project Info'!C84","v":52.235698854337961},{"$f":"'Project Info'!D84","v":48.022768090099298},{"$f":"'Project Info'!E84","v":19.246640192796217},{"$f":"'Project Info'!F84","v":0},{"$f":"'Project Info'!G84","v":0},{"$f":"'Project Info'!H84","v":0},{"$f":"'Project Info'!I84","v":0},{"$f":"'Project Info'!J84","v":0},{"$f":"'Project Info'!K84","v":0},{"$f":"'Project Info'!L84","v":0},8.4113262411338763E-2,671.6826336556361,0.7871999999999999,87.764301145662046,0.94603966539370865,853.25537811945651,709.99415587517171,143.2612222442848,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A85","v":45},{"$f":"'Project Info'!B85","v":50},{"$f":"'Project Info'!C85","v":47.459170258371508},{"$f":"'Project Info'!D85","v":43.465397050422162},{"$f":"'Project Info'!E85","v":16.894183241713304},{"$f":"'Project Info'!F85","v":0},{"$f":"'Project Info'!G85","v":0},{"$f":"'Project Info'!H85","v":0},{"$f":"'Project Info'!I85","v":0},{"$f":"'Project Info'!J85","v":0},{"$f":"'Project Info'!K85","v":0},{"$f":"'Project Info'!L85","v":0},0.13585898886764203,1084.8957801939705,0.7871999999999999,92.5408297416285,0.94073241139819042,1378.1704524821782,1153.2458827282385,224.92456975393975,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A86","v":40},{"$f":"'Project Info'!B86","v":45},{"$f":"'Project Info'!C86","v":42.677030404888129},{"$f":"'Project Info'!D86","v":38.812544504634097},{"$f":"'Project Info'!E86","v":14.690265649465921},{"$f":"'Project Info'!F86","v":0},{"$f":"'Project Info'!G86","v":0},{"$f":"'Project Info'!H86","v":0},{"$f":"'Project Info'!I86","v":0},{"$f":"'Project Info'!J86","v":0},{"$f":"'Project Info'!K86","v":0},{"$f":"'Project Info'!L86","v":0},0.18766550394704523,1498.5943515189501,0.7871999999999999,97.322969595111871,0.93541892267209781,1903.7021741856584,1602.0569128942757,301.64526129138267,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A87","v":35},{"$f":"'Project Info'!B87","v":40},{"$f":"'Project Info'!C87","v":37.333046773755832},{"$f":"'Project Info'!D87","v":33.904706919479686},{"$f":"'Project Info'!E87","v":12.53841602318813},{"$f":"'Project Info'!F87","v":0},{"$f":"'Project Info'!G87","v":0},{"$f":"'Project Info'!H87","v":0},{"$f":"'Project Info'!I87","v":0},{"$f":"'Project Info'!J87","v":0},{"$f":"'Project Info'!K87","v":0},{"$f":"'Project Info'!L87","v":0},0.24555865995097842,1960.8975172812675,0.7871999999999999,102.66695322624417,0.92948116308195083,2490.9775371967326,2109.668915483313,381.3086217134196,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A88","v":30},{"$f":"'Project Info'!B88","v":35},{"$f":"'Project Info'!C88","v":32.638179845662044},{"$f":"'Project Info'!D88","v":29.547170928664851},{"$f":"'Project Info'!E88","v":10.728972818165861},{"$f":"'Project Info'!F88","v":0},{"$f":"'Project Info'!G88","v":0},{"$f":"'Project Info'!H88","v":0},{"$f":"'Project Info'!I88","v":0},{"$f":"'Project Info'!J88","v":0},{"$f":"'Project Info'!K88","v":0},{"$f":"'Project Info'!L88","v":0},0.29641971833866115,2367.0461871698176,0.7871999999999999,107.36182015433795,0.92445141205930992,3006.9184288234474,2560.4873942449613,446.43103457848611,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A89","v":25},{"$f":"'Project Info'!B89","v":30},{"$f":"'Project Info'!C89","v":27.529264646850947},{"$f":"'Project Info'!D89","v":24.652717392657845},{"$f":"'Project Info'!E89","v":8.8041305482613303},{"$f":"'Project Info'!F89","v":0},{"$f":"'Project Info'!G89","v":0},{"$f":"'Project Info'!H89","v":0},{"$f":"'Project Info'!I89","v":0},{"$f":"'Project Info'!J89","v":0},{"$f":"'Project Info'!K89","v":0},{"$f":"'Project Info'!L89","v":0},0.35176629965911471,2809.0137965506033,0.7871999999999999,112.47073535314905,0.9190586682383427,3568.3610220409091,3056.4031368475507,511.95788519335838,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A90","v":20},{"$f":"'Project Info'!B90","v":25},{"$f":"'Project Info'!C90","v":22.998111483544687},{"$f":"'Project Info'!D90","v":20.383306659827422},{"$f":"'Project Info'!E90","v":7.246164547543378},{"$f":"'Project Info'!F90","v":0},{"$f":"'Project Info'!G90","v":0},{"$f":"'Project Info'!H90","v":0},{"$f":"'Project Info'!I90","v":0},{"$f":"'Project Info'!J90","v":0},{"$f":"'Project Info'!K90","v":0},{"$f":"'Project Info'!L90","v":0},0.40085379226159917,3200.9997374780792,0.7871999999999999,117.00188851645531,0.91427578434374157,4066.3106421215443,3501.1314882147144,565.17915390682992,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A91","v":15},{"$f":"'Project Info'!B91","v":20},{"$f":"'Project Info'!C91","v":17.808510327474309},{"$f":"'Project Info'!D91","v":15.420865796304254},{"$f":"'Project Info'!E91","v":5.5490484131518292},{"$f":"'Project Info'!F91","v":0},{"$f":"'Project Info'!G91","v":0},{"$f":"'Project Info'!H91","v":0},{"$f":"'Project Info'!I91","v":0},{"$f":"'Project Info'!J91","v":0},{"$f":"'Project Info'!K91","v":0},{"$f":"'Project Info'!L91","v":0},0.45707447145236157,3649.9474156704946,0.7871999999999999,140,0.87999999999999989,4636.6201926708527,4147.667517807381,488.95267486347166,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A92","v":10},{"$f":"'Project Info'!B92","v":15},{"$f":"'Project Info'!C92","v":12.269931130346862},{"$f":"'Project Info'!D92","v":10.318264913023604},{"$f":"'Project Info'!E92","v":3.9082824916941998},{"$f":"'Project Info'!F92","v":0},{"$f":"'Project Info'!G92","v":0},{"$f":"'Project Info'!H92","v":0},{"$f":"'Project Info'!I92","v":0},{"$f":"'Project Info'!J92","v":0},{"$f":"'Project Info'!K92","v":0},{"$f":"'Project Info'!L92","v":0},0.51707574608790896,4129.0848669419929,0.7871999999999999,140,0.87999999999999989,5245.2805728429794,4692.141894252265,553.13867859071433,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A93","v":5},{"$f":"'Project Info'!B93","v":10},{"$f":"'Project Info'!C93","v":7.3137581369917548},{"$f":"'Project Info'!D93","v":5.7052382449247707},{"$f":"'Project Info'!E93","v":2.5019418419888937},{"$f":"'Project Info'!F93","v":0},{"$f":"'Project Info'!G93","v":0},{"$f":"'Project Info'!H93","v":0},{"$f":"'Project Info'!I93","v":0},{"$f":"'Project Info'!J93","v":0},{"$f":"'Project Info'!K93","v":0},{"$f":"'Project Info'!L93","v":0},0.5707676201825892,4557.8388869853306,0.7871999999999999,140,0.87999999999999989,5789.9376104996581,5179.3623715742397,610.57523892541849,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A94","v":0},{"$f":"'Project Info'!B94","v":5},{"$f":"'Project Info'!C94","v":2.6119461836144886},{"$f":"'Project Info'!D94","v":1.2699770062067783},{"$f":"'Project Info'!E94","v":1.2046477897733283},{"$f":"'Project Info'!F94","v":8760},{"$f":"'Project Info'!G94","v":2672},{"$f":"'Project Info'!H94","v":3160},{"$f":"'Project Info'!I94","v":1344},{"$f":"'Project Info'!J94","v":1584},{"$f":"'Project Info'!K94","v":88},{"$f":"'Project Info'!L94","v":264},0.62170391634417632,4964.5883646974953,0.7871999999999999,140,0.87999999999999989,6306.6417234470218,5641.5776871562457,665.06403629077613,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A95","v":-5},{"$f":"'Project Info'!B95","v":0},{"$f":"'Project Info'!C95","v":-1.6731398516793925},{"$f":"'Project Info'!D95","v":-2.7083318773557807},{"$f":"'Project Info'!E95","v":7.9391832815876459E-2},{"$f":"'Project Info'!F95","v":0},{"$f":"'Project Info'!G95","v":0},{"$f":"'Project Info'!H95","v":0},{"$f":"'Project Info'!I95","v":0},{"$f":"'Project Info'!J95","v":0},{"$f":"'Project Info'!K95","v":0},{"$f":"'Project Info'!L95","v":0},0.66812568172652664,5335.287262078009,0.7871999999999999,140,0.87999999999999989,6777.5498756072275,6062.8264341795566,714.72344142767088,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A96","v":-10},{"$f":"'Project Info'!B96","v":-5},{"$f":"'Project Info'!C96","v":-6.5729865085377277},{"$f":"'Project Info'!D96","v":-7.2465935998252222},{"$f":"'Project Info'!E96","v":-1.168423365310433},{"$f":"'Project Info'!F96","v":0},{"$f":"'Project Info'!G96","v":0},{"$f":"'Project Info'!H96","v":0},{"$f":"'Project Info'!I96","v":0},{"$f":"'Project Info'!J96","v":0},{"$f":"'Project Info'!K96","v":0},{"$f":"'Project Info'!L96","v":0},0.72120735384249191,5759.1685419567712,0.7871999999999999,140,0.87999999999999989,7316.0169486239483,6544.5097067690585,771.5072418548898,0]
[null,null,null,null,null,null,{"$f":"'Project Info'!A97","v":-15},{"$f":"'Project Info'!B97","v":-10},{"$f":"'Project Info'!C97","v":-15.32570353422995},{"$f":"'Project Info'!D97","v":-15.707838211108999},{"$f":"'Project Info'!E97","v":-3.4051318156661381},{"$f":"'Project Info'!F97","v":0},{"$f":"'Project Info'!G97","v":0},{"$f":"'Project Info'!H97","v":0},{"$f":"'Project Info'!I97","v":0},{"$f":"'Project Info'!J97","v":0},{"$f":"'Project Info'!K97","v":0},{"$f":"'Project Info'!L97","v":0},0.81602845495415766,6516.3581348339276,0.7871999999999999,140,0.87999999999999989,8277.8939720959461,7404.9524259476457,872.9415461483004,0]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Boiler Plant Heating Load Profile"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Occupied Profile",null,null,null,"Unocc Profile"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Max OAT","Min OAT","% Load @","%Load @","Max OAT","Min OAT","% Load @","%Load @"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"°F","°F","Max OAT","Min OAT","°F","°F","Max OAT","Min OAT"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,55,0,0.1,0.85,60,0,0,0.65]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Baseline Boiler Efficiency",null,null,null,null,"Boiler Efficiency"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Input",null,"Rated","Avg. Op.",null,"vs. HW Return Temp"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"MBH",null,"Ec","Et",null,"Return","Cond Blr","Std Blr"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"≤",2500,0.85,{"$f":"0.97*U98","v":0.82450000000000001},null,"Water ","Eff","Eff"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,">",2500,0.82,{"$f":"0.96*U99","v":0.7871999999999999},null,"°F","%","%"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Base Eff. per design capacity",null,null,{"$f":"IF($N$16<=$T$98,V98,V99)","v":0.7871999999999999},null,68,0.96099999999999997,{"$f":"$V$100","v":0.7871999999999999}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,86,0.94799999999999995,0.7871999999999999]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Peak Plant Load",null,null,null,null,104,0.92800000000000005,0.7871999999999999]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Peak Plant MBH",null,{"$f":"N16/N18","v":7985.454545454545},null,null,122,0.90900000000000003,0.7871999999999999]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,140,0.88,0.7871999999999999]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"HW Reset",null,null,null,150,0.87,0.7871999999999999]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"OAT","Return",null,null,160,0.87,0.7871999999999999]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"°F","°F"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"M23","v":20},{"$f":"N23-$N$20","v":140}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"M24","v":60},{"$f":"N24-$N$20","v":100}]

{"sheet":"Unitary HVAC (RTU, AC, HP OLD)","index":24,"n_rows":175,"n_cols":51,"rows_kept":175,"cut":false,"hidden":true,"merged":[[23,8,23,9],[23,10,23,11],[23,12,23,13],[24,8,24,9],[24,10,24,11],[24,12,24,13],[25,8,25,9],[25,10,25,11],[25,12,25,13],[26,8,26,9],[26,10,26,11],[26,12,26,13],[27,8,27,9],[27,10,27,11],[27,12,27,13],[28,8,28,9],[28,10,28,11],[28,12,28,13],[29,8,29,9],[29,10,29,11],[29,12,29,13],[30,8,30,9],[30,10,30,11],[30,12,30,13],[31,8,31,9],[31,10,31,11],[31,12,31,13],[32,8,32,9],[32,10,32,11],[32,12,32,13]]}
["Savings Summary",null,null,null,null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,null,null,null,null,null,null,"NOTES"]
["Annual kWh Savings",null,null,{"$f":"SUM(A14:D14)","v":1748.6949632144874},null,null,null,"Value","Unit",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Add HSPF Input for applicable sizes"]
["% On Peak",null,null,{"$f":"IF(D2<=0,0,MIN(1,A15+C15))","v":0.45844748858447487},null,"Annual Electric Savings",null,{"$f":"D2","v":1748.6949632144874},"kWh",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Only make Heat Recovery available for VRF HPs"]
["Max kW",null,null,{"$f":"MAX(AY42:AY65,AY72:AY95)","v":1.6221052393268627},null,"Annual Fuel Savings",null,{"$f":"D7*C28","v":{"$error":"#N/A"}},{"$f":"D20","v":{"$error":"#N/A"}},null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Options for systems with multiple system types (e.g. police, fire, DPW)"]
["Summer kW",null,null,{"$f":"(SUMPRODUCT(R42:R65,AY42:AY65)+SUMPRODUCT(R72:R95,AY72:AY95))/SUM(R42:R65,R72:R95)","v":0.19962271269571774},null,"Incremental Cost",null,45000,"$",null,"Measure Instructions",null,null,null,null,null,null,null,null,null,null,null,null,"Add 2018 Baseline Inputs"]
["Winter kW",null,null,{"$f":"(SUMPRODUCT(Q42:Q65,AY42:AY65)+SUMPRODUCT(Q72:Q95,AY72:AY95))/SUM(Q42:Q65,Q72:Q95)","v":0.19962271269571774},null,"Estimated Incentive",null,{"$f":"IF(AND($C$24>0,$C$25>0),MIN(H5,MAX(0,H3*C24+H4*C25)),\"TBD\")","v":"TBD"},"$"]
["Annual Fuel Savings (MMBtu)",null,null,0,null,"Custom Payback",null,{"$f":"H5/(H3*$C$19+H4*$C$20)","v":{"$error":"#N/A"}},"years"]
["Incremental Cost",null,null,45000]
[]
["kWh Savings by Peak Period",null,null,null,null,null,"STATE (MA or RI)",{"$f":"'Project Info'!C15","v":"NH"}]
["Winter","Winter","Summer","Summer",null,null,"Program Year",{"$f":"'Project Info'!C19","v":0}]
["On-Peak","Off-Peak","On-Peak","Off-Peak",null,null,"Code IECC Version",{"$f":"MID('Project Info'!C20,1,4)","v":"2018"}]
["kWh","kWh","kWh","kWh",null,null,"Electric PA",{"$f":"'Project Info'!F3","v":0}]
[{"$f":"SUMPRODUCT($AY$42:$AY$65,M42:M65)+SUMPRODUCT($AY$72:$AY$95,M72:M95)","v":533.39188832295781},{"$f":"SUMPRODUCT($AY$42:$AY$65,N42:N65)+SUMPRODUCT($AY$72:$AY$95,N72:N95)","v":630.80777211846805},{"$f":"SUMPRODUCT($AY$42:$AY$65,O42:O65)+SUMPRODUCT($AY$72:$AY$95,O72:O95)","v":268.29292586304462},{"$f":"SUMPRODUCT($AY$42:$AY$65,P42:P65)+SUMPRODUCT($AY$72:$AY$95,P72:P95)","v":316.20237691001688},null,null,"Gas PA",{"$f":"'Project Info'!I3","v":0}]
[{"$f":"IF(A14<=0,0,A14/SUMIF($A$14:$D$14,\">0\"))","v":0.30502283105022832},{"$f":"IF(B14<=0,0,B14/SUMIF($A$14:$D$14,\">0\"))","v":0.36073059360730592},{"$f":"IF(C14<=0,0,C14/SUMIF($A$14:$D$14,\">0\"))","v":0.15342465753424656},{"$f":"IF(D14<=0,0,D14/SUMIF($A$14:$D$14,\">0\"))","v":0.18082191780821916}]
[]
["Utility Rates"]
[null,null,"Rate","Unit"]
["Electric",null,{"$f":"'ECM Summary'!$E$31","v":0.1593},"kWh",null,null,"User Inputs"]
[{"$f":"'ECM Summary'!$C$32","v":0},null,{"$f":"'ECM Summary'!$E$32","v":{"$error":"#N/A"}},{"$f":"'ECM Summary'!$F$32","v":{"$error":"#N/A"}},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Proposed/Design Performance",null,null,null,null,"Baseline Performance"]
[null,null,null,null,null,null,null,null,"Unit",null,"Condenser",null,"Primary",null,"Includes",null,"VRF","Cooling","Heating","Cooling",null,"Heating",null,null,"Cooling",null,"Heating"]
["Custom Incentive Rates",null,null,null,null,null,"Line","Unit","Type",null,"Type",null,"Load Profile",null,"Heating",null,"Heat","Capacity","Capacity","Full Load",null,"COP","COP",null,"Full Load",null,"COP","COP"]
[null,null,"Rate","Unit",null,null,"#","Tag/#",null,null,null,null,null,null,"?",null,"Recovery?","MBH","MBH","EER","IEER/SEER","47°F","17°F",null,"EER","IEER","47°F","17°F"]
["Electric",null,{"$f":"'ECM Summary'!$J$31","v":0.28000000000000003},"kWh",null,null,1,"HP-A","VRF AC Only",null,"Air Cooled",null,"Comfort/HVAC",null,"No",null,"Yes",70,100,13,18,3.6,2.2999999999999998,null,{"$f":"IF($I24=\"\",\"\",MAX(0,OFFSET($I$152,MATCH($I24,$F$153:$F$174,0)+MATCH($K24,$H$154:$H$159,0),MATCH($R24,$J$151:$O$151,1))-IF(OR($I24<>$G$101,$R24<$K$152),0,IF($Q24=\"Yes\",0.2,0))))","v":11.2},{"$f":"IF($I24=\"\",\"\",MAX(0,OFFSET($R$152,MATCH($I24,$F$153:$F$174,0)+MATCH($K24,$Q$154:$Q$159,0),MATCH($R24,$S$151:$X$151,1))-IF(OR($I24<>$G$101,$R24<$T$152),0,IF($Q24=\"Yes\",0.2,0))))","v":13.1},{"$f":"IF($I24=\"\",\"\",MAX(0,OFFSET($AA$152,MATCH($I24,$F$153:$F$174,0)+MATCH($K24,$Z$154:$Z$159,0),MATCH($R24,$AB$151:$AG$151,1))))","v":0},{"$f":"IF($I24=\"\",\"\",MAX(0,OFFSET($AJ$152,MATCH($I24,$F$153:$F$174,0)+MATCH($K24,$AI$154:$AI$159,0),MATCH($R24,$AK$151:$AP$151,1))))","v":0}]
[{"$f":"'ECM Summary'!$H$32","v":0},null,{"$f":"'ECM Summary'!$J$32","v":0},{"$f":"'ECM Summary'!$K$32","v":{"$error":"#N/A"}},null,null,2,"HP-B","Heat Pump",null,"Ground Water (HP)",null,"Constant/IT-Elec Rooms",null,"Yes",null,"No",130,60,19,19,4,4,null,18,18,3.7,3.7]
[null,null,null,null,null,null,3,"HP-Ba","VRF AC Only",null,"Air Cooled",null,"Comfort/HVAC",null,"No",null,"Yes",150,66,12,17,3.5,2.5,null,11,12.9,0,0]
["Fossil Fuel",null,{"$f":"'Project Info'!C21","v":0},null,null,null,4,null,"Heat Pump",null,"Ground Water (HP)",null,"Comfort/HVAC",null,"No",null,null,130,100,12,14,null,null,null,18,18,3.7,3.7]
["Fuel Conversion",null,{"$f":"LOOKUP(C27,'Project Info'!X102:X104,'Project Info'!Z102:Z104)","v":{"$error":"#N/A"}},null,null,null,5,null,null,null,null,null,null,null,"No",null,null,null,null,null,null,null,null,null,"","","",""]
[null,null,null,null,null,null,6,null,null,null,null,null,null,null,"No",null,null,null,null,null,null,null,null,null,"","","",""]
[null,null,null,null,null,null,7,null,null,null,null,null,null,null,"No",null,null,null,null,null,null,null,null,null,"","","",""]
[null,null,null,null,null,null,8,null,null,null,null,null,null,null,"No",null,null,null,null,null,null,null,null,null,"","","",""]
[null,null,null,null,null,null,9,null,null,null,null,null,null,null,"No",null,null,null,null,null,null,null,null,null,"","","",""]
[null,null,null,null,null,null,10,null,null,null,null,null,null,null,"No",null,null,null,null,null,null,null,null,null,"","","",""]
[null,null,null,null,null,null,"Comfort/HVAC Systems: Total or Weighted Avg.",null,null,null,null,null,null,null,null,null,null,{"$f":"SUMPRODUCT(R24:R33,1*($M$24:$M$33=$O$102))","v":350},{"$f":"SUMPRODUCT(S24:S33,1*($M$24:$M$33=$O$102),1*($O$24:$O$33=$O$99))","v":0},{"$f":"IF($R34<=0,\"\",SUMPRODUCT(T24:T33,$R$24:$R$33,1*($M$24:$M$33=$O$102))/$R34)","v":12.2},{"$f":"IF($R34<=0,\"\",SUMPRODUCT(U24:U33,$R$24:$R$33,1*($M$24:$M$33=$O$102))/$R34)","v":16.085714285714285},{"$f":"IF($S34<=0,0,SUMPRODUCT(V24:V33,$S$24:$S$33,1*($M$24:$M$33=$O$102),1*($O$24:$O$33=$O$99))/$S34)","v":0},{"$f":"IF($S34<=0,0,SUMPRODUCT(W24:W33,$S$24:$S$33,1*($M$24:$M$33=$O$102),1*($O$24:$O$33=$O$99))/$S34)","v":0},null,{"$f":"IF($R34<=0,\"\",SUMPRODUCT(Y24:Y33,$R$24:$R$33,1*($M$24:$M$33=$O$102))/$R34)","v":13.64},{"$f":"IF($R34<=0,\"\",SUMPRODUCT(Z24:Z33,$R$24:$R$33,1*($M$24:$M$33=$O$102))/$R34)","v":14.834285714285715},{"$f":"IF($S34<=0,0,SUMPRODUCT(AA24:AA33,$S$24:$S$33,1*($M$24:$M$33=$O$102),1*($O$24:$O$33=$O$99))/$S34)","v":0},{"$f":"IF($S34<=0,0,SUMPRODUCT(AB24:AB33,$S$24:$S$33,1*($M$24:$M$33=$O$102),1*($O$24:$O$33=$O$99))/$S34)","v":0}]
[null,null,null,null,null,null,"Constant/IT-Elec Room Systems: Total or Weighted Avg.",null,null,null,null,null,null,null,null,null,null,{"$f":"SUMPRODUCT(R24:R33,1*($M$24:$M$33=$O$103))","v":130},{"$f":"SUMPRODUCT(S24:S33,1*($M$24:$M$33=$O$103),1*($O$24:$O$33=$O$99))","v":60},{"$f":"IF($R35<=0,\"\",SUMPRODUCT(T24:T33,$R$24:$R$33,1*($M$24:$M$33=$O$103))/$R35)","v":19},{"$f":"IF($R35<=0,\"\",SUMPRODUCT(U24:U33,$R$24:$R$33,1*($M$24:$M$33=$O$103))/$R35)","v":19},{"$f":"IF($S35<=0,0,SUMPRODUCT(V24:V33,$S$24:$S$33,1*($M$24:$M$33=$O$103),1*($O$24:$O$33=$O$99))/$S35)","v":4},{"$f":"IF($S35<=0,0,SUMPRODUCT(W24:W33,$S$24:$S$33,1*($M$24:$M$33=$O$103),1*($O$24:$O$33=$O$99))/$S35)","v":4},null,{"$f":"IF($R35<=0,\"\",SUMPRODUCT(Y24:Y33,$R$24:$R$33,1*($M$24:$M$33=$O$103))/$R35)","v":18},{"$f":"IF($R35<=0,\"\",SUMPRODUCT(Z24:Z33,$R$24:$R$33,1*($M$24:$M$33=$O$103))/$R35)","v":18},{"$f":"IF($S35<=0,0,SUMPRODUCT(AA24:AA33,$S$24:$S$33,1*($M$24:$M$33=$O$103),1*($O$24:$O$33=$O$99))/$S35)","v":3.7},{"$f":"IF($S35<=0,0,SUMPRODUCT(AB24:AB33,$S$24:$S$33,1*($M$24:$M$33=$O$103),1*($O$24:$O$33=$O$99))/$S35)","v":3.7}]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Load Profile",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Load Profile"]
[null,null,null,null,null,null,"Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown",null,null,null,null,null,null,"Comfort/HVAC",null,null,null,"Cooling Demand",null,null,null,"Heating Demand",null,null,null,"Demand Savings",null,null,null,"Constant/IT/Elec",null,null,null,"Cooling Demand",null,null,null,"Heating Demand",null,null,null,"Demand Savings",null,null,null,"Overall"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Cooling","Cooling","Heating","Heating","Base","Proposed","Base","Design","Base","Proposed","Base","Design","Cooling","Heating","Total",null,"Cooling","Cooling","Heating","Heating","Base","Proposed","Base","Design","Base","Proposed","Base","Design","Cooling","Heating","Total",null,"Demand"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Load","Load","Load","Load","Perf","Perf","Demand","Demand","Perf","Perf","Demand","Demand","Savings","Savings","Savings",null,"Load","Load","Load","Load","Perf","Perf","Demand","Demand","Perf","Perf","Demand","Demand","Savings","Savings","Savings",null,"Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","%","MBH","%","MBH","EER","EER","kW","kW","COP","COP","kW","kW","kW","kW","kW",null,"%","MBH","%","MBH","EER","EER","kW","kW","COP","COP","kW","kW","kW","kW","kW",null,"kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A44","v":100},{"$f":"'Project Info'!B44","v":105},{"$f":"'Project Info'!C44","v":102},{"$f":"'Project Info'!D44","v":76},{"$f":"'Project Info'!E44","v":40},{"$f":"'Project Info'!F44","v":0},{"$f":"'Project Info'!G44","v":0},{"$f":"'Project Info'!H44","v":0},{"$f":"'Project Info'!I44","v":0},{"$f":"'Project Info'!J44","v":0},{"$f":"'Project Info'!K44","v":0},{"$f":"'Project Info'!L44","v":0},{"$f":"MAX(0,MIN(1,TREND($U$102:$V$102,$S$102:$T$102,$I42)))*($I42>=$T$102)","v":1},{"$f":"$R$34*S42","v":350},{"$f":"MAX(0,MIN(1,TREND($AD$102:$AE$102,$AB$102:$AC$102,$I42)))*($I42<=$AB$102)","v":0},{"$f":"$S$34*U42","v":0},{"$f":"OFFSET($G$122,MATCH($I42,$G$123:$G$133,-1),MATCH(S42,$H$122:$L$122,-1))*(S42>0)","v":13.64},{"$f":"OFFSET($G$135,MATCH($I42,$G$136:$G$146,-1),MATCH(S42,$H$135:$L$135,-1))*(S42>0)","v":12.2},{"$f":"IF(T42>0,T42/W42,0)","v":25.659824046920821},{"$f":"IF(T42>0,T42/X42,0)","v":28.688524590163937},{"$f":"MIN($AB$119,TREND($AB$119:$AC$119,$AB$118:$AC$118,$I42))*(U42>0)","v":0},{"$f":"MIN($AB$120,TREND($AB$120:$AC$120,$AB$118:$AC$118,$I42))*(U42>0)","v":0},{"$f":"IF(V42>0,V42/AA42/3.412,0)","v":0},{"$f":"IF(V42>0,V42/AB42/3.412,0)","v":0},{"$f":"Y42-Z42","v":-3.0287005432431151},{"$f":"AC42-AD42","v":0},{"$f":"AE42+AF42","v":-3.0287005432431151},null,{"$f":"$X$106","v":0.55000000000000004},{"$f":"$R$35*AI42","v":71.5},{"$f":"$Y$106","v":0},{"$f":"$S$35*AK42","v":0},{"$f":"OFFSET($Q$122,MATCH($I42,$Q$123:$Q$133,-1),MATCH(AI42,$R$122:$V$122,-1))*(AI42>0)","v":16.220930232558139},{"$f":"OFFSET($Q$135,MATCH($I42,$Q$136:$Q$146,-1),MATCH(AI42,$R$135:$V$135,-1))*(AI42>0)","v":17.122093023255815},{"$f":"IF(AJ42>0,AJ42/AM42,0)","v":4.4078853046594979},{"$f":"IF(AJ42>0,AJ42/AN42,0)","v":4.1758913412563663},{"$f":"MIN($AB$119,TREND($AB$119:$AC$119,$AB$118:$AC$118,$I42))*(AK42>0)","v":0},{"$f":"MIN($AB$120,TREND($AB$120:$AC$120,$AB$118:$AC$118,$I42))*(AK42>0)","v":0},{"$f":"IF(AL42>0,AL42/AQ42/3.412,0)","v":0},{"$f":"IF(AL42>0,AL42/AR42/3.412,0)","v":0},{"$f":"AO42-AP42","v":0.23199396340313161},{"$f":"AS42-AT42","v":0},{"$f":"AU42+AV42","v":0.23199396340313161},null,{"$f":"AG42+AW42","v":-2.7967065798399835}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A45","v":95},{"$f":"'Project Info'!B45","v":100},{"$f":"'Project Info'!C45","v":95.219272727272724},{"$f":"'Project Info'!D45","v":74.534025272781079},{"$f":"'Project Info'!E45","v":37.923296058061368},{"$f":"'Project Info'!F45","v":0},{"$f":"'Project Info'!G45","v":0},{"$f":"'Project Info'!H45","v":0},{"$f":"'Project Info'!I45","v":0},{"$f":"'Project Info'!J45","v":0},{"$f":"'Project Info'!K45","v":0},{"$f":"'Project Info'!L45","v":0},{"$f":"MAX(0,MIN(1,TREND($U$102:$V$102,$S$102:$T$102,$I43)))*($I43>=$T$102)","v":0.95389818181818165},333.86436363636358,{"$f":"MAX(0,MIN(1,TREND($AD$102:$AE$102,$AB$102:$AC$102,$I43)))*($I43<=$AB$102)","v":0},0,13.64,12.2,{"$f":"IF(T43>0,T43/W43,0)","v":24.476859504132225},{"$f":"IF(T43>0,T43/X43,0)","v":27.365931445603575},0,0,{"$f":"IF(V43>0,V43/AA43/3.412,0)","v":0},{"$f":"IF(V43>0,V43/AB43/3.412,0)","v":0},{"$f":"Y43-Z43","v":-2.8890719414713502},{"$f":"AC43-AD43","v":0},{"$f":"AE43+AF43","v":-2.8890719414713502},null,{"$f":"$X$106","v":0.55000000000000004},71.5,{"$f":"$Y$106","v":0},0,16.220930232558139,17.122093023255815,{"$f":"IF(AJ43>0,AJ43/AM43,0)","v":4.4078853046594979},{"$f":"IF(AJ43>0,AJ43/AN43,0)","v":4.1758913412563663},0,0,{"$f":"IF(AL43>0,AL43/AQ43/3.412,0)","v":0},{"$f":"IF(AL43>0,AL43/AR43/3.412,0)","v":0},{"$f":"AO43-AP43","v":0.23199396340313161},{"$f":"AS43-AT43","v":0},{"$f":"AU43+AV43","v":0.23199396340313161},null,{"$f":"AG43+AW43","v":-2.6570779780682185}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A46","v":90},{"$f":"'Project Info'!B46","v":95},{"$f":"'Project Info'!C46","v":92.016049160256074},{"$f":"'Project Info'!D46","v":72.911561930607689},{"$f":"'Project Info'!E46","v":36.467095439351091},{"$f":"'Project Info'!F46","v":0},{"$f":"'Project Info'!G46","v":0},{"$f":"'Project Info'!H46","v":0},{"$f":"'Project Info'!I46","v":0},{"$f":"'Project Info'!J46","v":0},{"$f":"'Project Info'!K46","v":0},{"$f":"'Project Info'!L46","v":0},0.89695198507121898,313.93319477492662,0,0,13.64,12.2,23.015630115463829,25.73222907991202,0,0,0,0,-2.7165989644481918,0,-2.7165989644481918,null,0.55000000000000004,71.5,0,0,16.220930232558139,17.122093023255815,4.4078853046594979,4.1758913412563663,0,0,0,0,0.23199396340313161,0,0.23199396340313161,null,-2.4846050010450602]
[null,null,null,null,null,null,{"$f":"'Project Info'!A47","v":85},{"$f":"'Project Info'!B47","v":90},{"$f":"'Project Info'!C47","v":87.457811360655285},{"$f":"'Project Info'!D47","v":70.80538329449476},{"$f":"'Project Info'!E47","v":34.679413213566804},{"$f":"'Project Info'!F47","v":0},{"$f":"'Project Info'!G47","v":0},{"$f":"'Project Info'!H47","v":0},{"$f":"'Project Info'!I47","v":0},{"$f":"'Project Info'!J47","v":0},{"$f":"'Project Info'!K47","v":0},{"$f":"'Project Info'!L47","v":0},0.81591664641164952,285.57082624407735,0,0,13.98974358974359,12.512820512820513,20.412870644279721,22.822258654752083,0,0,0,0,-2.4093880104723624,0,-2.4093880104723624,null,0.55000000000000004,71.5,0,0,16.607142857142858,17.529761904761905,4.3053763440860218,4.0787775891341251,0,0,0,0,0.22659875495189663,0,0.22659875495189663,null,-2.1827892555204658]
[null,null,null,null,null,null,{"$f":"'Project Info'!A48","v":80},{"$f":"'Project Info'!B48","v":85},{"$f":"'Project Info'!C48","v":82.136788830239965},{"$f":"'Project Info'!D48","v":67.872393622439333},{"$f":"'Project Info'!E48","v":32.296248223809314},{"$f":"'Project Info'!F48","v":0},{"$f":"'Project Info'!G48","v":0},{"$f":"'Project Info'!H48","v":0},{"$f":"'Project Info'!I48","v":0},{"$f":"'Project Info'!J48","v":0},{"$f":"'Project Info'!K48","v":0},{"$f":"'Project Info'!L48","v":0},0.72132069031537716,252.46224161038199,0,0,14.020209059233451,15.202961672473869,18.007024042492077,16.606122349665874,0,0,0,0,1.4009016928262028,0,1.4009016928262028,null,0.55000000000000004,71.5,0,0,17.012195121951223,17.957317073170735,4.2028673835125439,3.981663837011884,0,0,0,0,0.22120354650065988,0,0.22120354650065988,null,1.6221052393268627]
[null,null,null,null,null,null,{"$f":"'Project Info'!A49","v":75},{"$f":"'Project Info'!B49","v":80},{"$f":"'Project Info'!C49","v":76.988400157585886},{"$f":"'Project Info'!D49","v":65.129261896908645},{"$f":"'Project Info'!E49","v":30.190476812806729},{"$f":"'Project Info'!F49","v":0},{"$f":"'Project Info'!G49","v":0},{"$f":"'Project Info'!H49","v":0},{"$f":"'Project Info'!I49","v":0},{"$f":"'Project Info'!J49","v":0},{"$f":"'Project Info'!K49","v":0},{"$f":"'Project Info'!L49","v":0},0.62979378057930469,220.42782320275663,0,0,14.370714285714287,15.583035714285714,15.33868246353493,14.145371110243937,0,0,0,0,1.1933113532909925,0,1.1933113532909925,null,0.55000000000000004,71.5,0,0,17.4375,18.40625,4.1003584229390677,3.8845500848896433,0,0,0,0,0.21580833804942445,0,0.21580833804942445,null,1.4091196913404169]
[null,null,null,null,null,null,{"$f":"'Project Info'!A50","v":70},{"$f":"'Project Info'!B50","v":75},{"$f":"'Project Info'!C50","v":72.457982050814195},{"$f":"'Project Info'!D50","v":63.604425012889301},{"$f":"'Project Info'!E50","v":29.088683095945193},{"$f":"'Project Info'!F50","v":0},{"$f":"'Project Info'!G50","v":0},{"$f":"'Project Info'!H50","v":0},{"$f":"'Project Info'!I50","v":0},{"$f":"'Project Info'!J50","v":0},{"$f":"'Project Info'!K50","v":0},{"$f":"'Project Info'!L50","v":0},0.54925301423669681,192.23855498284388,0,0,14.739194139194142,15.982600732600732,13.042677446770806,12.027989574357735,0,0,0,0,1.0146878724130719,0,1.0146878724130719,null,0.55000000000000004,71.5,0,0,17.884615384615383,18.878205128205128,3.9978494623655916,3.7874363327674025,0,0,0,0,0.21041312959818903,0,0.21041312959818903,null,1.2251010020112609]
[null,null,null,null,null,null,{"$f":"'Project Info'!A51","v":65},{"$f":"'Project Info'!B51","v":70},{"$f":"'Project Info'!C51","v":67.815831070966169},{"$f":"'Project Info'!D51","v":61.631331368130574},{"$f":"'Project Info'!E51","v":27.661514889731574},{"$f":"'Project Info'!F51","v":0},{"$f":"'Project Info'!G51","v":0},{"$f":"'Project Info'!H51","v":0},{"$f":"'Project Info'!I51","v":0},{"$f":"'Project Info'!J51","v":0},{"$f":"'Project Info'!K51","v":0},{"$f":"'Project Info'!L51","v":0},0.46672588570606532,163.35405999712287,0,0,15.573424603174601,16.887207341269839,10.489283131972371,9.6732429877798491,0,0,0,0,0.81604014419252202,0,0.81604014419252202,null,0.55000000000000004,71.5,0,0,18.355263157894736,19.375,3.895340501792115,3.6903225806451614,0,0,0,0,0.20501792114695361,0,0.20501792114695361,null,1.0210580653394756]
[null,null,null,null,null,null,{"$f":"'Project Info'!A52","v":60},{"$f":"'Project Info'!B52","v":65},{"$f":"'Project Info'!C52","v":62.535961472271332},{"$f":"'Project Info'!D52","v":57.135476922863582},{"$f":"'Project Info'!E52","v":24.623037157728302},{"$f":"'Project Info'!F52","v":0},{"$f":"'Project Info'!G52","v":0},{"$f":"'Project Info'!H52","v":0},{"$f":"'Project Info'!I52","v":0},{"$f":"'Project Info'!J52","v":0},{"$f":"'Project Info'!K52","v":0},{"$f":"'Project Info'!L52","v":0},0.37286153728482374,130.50153804968832,0,0,15.972743182743182,17.320212657712656,8.1702645911618426,7.5346383227908147,0,0,0,0,0.63562626837102787,0,0.63562626837102787,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.83524898106674561]
[null,null,null,null,null,null,{"$f":"'Project Info'!A53","v":55},{"$f":"'Project Info'!B53","v":60},{"$f":"'Project Info'!C53","v":57.125792270740902},{"$f":"'Project Info'!D53","v":52.596971157053673},{"$f":"'Project Info'!E53","v":21.818001539159841},{"$f":"'Project Info'!F53","v":0},{"$f":"'Project Info'!G53","v":0},{"$f":"'Project Info'!H53","v":0},{"$f":"'Project Info'!I53","v":0},{"$f":"'Project Info'!J53","v":0},{"$f":"'Project Info'!K53","v":0},{"$f":"'Project Info'!L53","v":0},0.27668075147983828,96.838263017943405,8.9193741762623957E-2,0,15.972743182743182,17.320212657712656,6.0627195911198681,5.5910550829652497,0,0,0,0,0.47166450815461847,0,0.47166450815461847,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.67128722085033621]
[null,null,null,null,null,null,{"$f":"'Project Info'!A54","v":50},{"$f":"'Project Info'!B54","v":55},{"$f":"'Project Info'!C54","v":52.235698854337961},{"$f":"'Project Info'!D54","v":48.022768090099298},{"$f":"'Project Info'!E54","v":19.246640192796217},{"$f":"'Project Info'!F54","v":0},{"$f":"'Project Info'!G54","v":0},{"$f":"'Project Info'!H54","v":0},{"$f":"'Project Info'!I54","v":0},{"$f":"'Project Info'!J54","v":0},{"$f":"'Project Info'!K54","v":0},{"$f":"'Project Info'!L54","v":0},0.18974575741045285,66.411015093658506,0.15587683380448225,0,16.231438492063489,17.600731646825398,4.0915052061547579,3.7731962753739787,0,0,0,0,0.31830893078077915,0,0.31830893078077915,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.51793164347649689]
[null,null,null,null,null,null,{"$f":"'Project Info'!A55","v":45},{"$f":"'Project Info'!B55","v":50},{"$f":"'Project Info'!C55","v":47.459170258371508},{"$f":"'Project Info'!D55","v":43.465397050422162},{"$f":"'Project Info'!E55","v":16.894183241713304},{"$f":"'Project Info'!F55","v":0},{"$f":"'Project Info'!G55","v":0},{"$f":"'Project Info'!H55","v":0},{"$f":"'Project Info'!I55","v":0},{"$f":"'Project Info'!J55","v":0},{"$f":"'Project Info'!K55","v":0},{"$f":"'Project Info'!L55","v":0},0,0,0.22101131465857027,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A56","v":40},{"$f":"'Project Info'!B56","v":45},{"$f":"'Project Info'!C56","v":42.677030404888129},{"$f":"'Project Info'!D56","v":38.812544504634097},{"$f":"'Project Info'!E56","v":14.690265649465921},{"$f":"'Project Info'!F56","v":0},{"$f":"'Project Info'!G56","v":0},{"$f":"'Project Info'!H56","v":0},{"$f":"'Project Info'!I56","v":0},{"$f":"'Project Info'!J56","v":0},{"$f":"'Project Info'!K56","v":0},{"$f":"'Project Info'!L56","v":0},0,0,0.28622231266061637,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A57","v":35},{"$f":"'Project Info'!B57","v":40},{"$f":"'Project Info'!C57","v":37.333046773755832},{"$f":"'Project Info'!D57","v":33.904706919479686},{"$f":"'Project Info'!E57","v":12.53841602318813},{"$f":"'Project Info'!F57","v":0},{"$f":"'Project Info'!G57","v":0},{"$f":"'Project Info'!H57","v":0},{"$f":"'Project Info'!I57","v":0},{"$f":"'Project Info'!J57","v":0},{"$f":"'Project Info'!K57","v":0},{"$f":"'Project Info'!L57","v":0},0,0,0.35909481672151133,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A58","v":30},{"$f":"'Project Info'!B58","v":35},{"$f":"'Project Info'!C58","v":32.638179845662044},{"$f":"'Project Info'!D58","v":29.547170928664851},{"$f":"'Project Info'!E58","v":10.728972818165861},{"$f":"'Project Info'!F58","v":0},{"$f":"'Project Info'!G58","v":0},{"$f":"'Project Info'!H58","v":0},{"$f":"'Project Info'!I58","v":0},{"$f":"'Project Info'!J58","v":0},{"$f":"'Project Info'!K58","v":0},{"$f":"'Project Info'!L58","v":0},0,0,0.42311572937733577,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A59","v":25},{"$f":"'Project Info'!B59","v":30},{"$f":"'Project Info'!C59","v":27.529264646850947},{"$f":"'Project Info'!D59","v":24.652717392657845},{"$f":"'Project Info'!E59","v":8.8041305482613303},{"$f":"'Project Info'!F59","v":0},{"$f":"'Project Info'!G59","v":0},{"$f":"'Project Info'!H59","v":0},{"$f":"'Project Info'!I59","v":0},{"$f":"'Project Info'!J59","v":0},{"$f":"'Project Info'!K59","v":0},{"$f":"'Project Info'!L59","v":0},0,0,0.49278275481566891,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A60","v":20},{"$f":"'Project Info'!B60","v":25},{"$f":"'Project Info'!C60","v":22.998111483544687},{"$f":"'Project Info'!D60","v":20.383306659827422},{"$f":"'Project Info'!E60","v":7.246164547543378},{"$f":"'Project Info'!F60","v":0},{"$f":"'Project Info'!G60","v":0},{"$f":"'Project Info'!H60","v":0},{"$f":"'Project Info'!I60","v":0},{"$f":"'Project Info'!J60","v":0},{"$f":"'Project Info'!K60","v":0},{"$f":"'Project Info'!L60","v":0},0,0,0.55457120704257257,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A61","v":15},{"$f":"'Project Info'!B61","v":20},{"$f":"'Project Info'!C61","v":17.808510327474309},{"$f":"'Project Info'!D61","v":15.420865796304254},{"$f":"'Project Info'!E61","v":5.5490484131518292},{"$f":"'Project Info'!F61","v":0},{"$f":"'Project Info'!G61","v":0},{"$f":"'Project Info'!H61","v":0},{"$f":"'Project Info'!I61","v":0},{"$f":"'Project Info'!J61","v":0},{"$f":"'Project Info'!K61","v":0},{"$f":"'Project Info'!L61","v":0},0,0,0.62533849553444132,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A62","v":10},{"$f":"'Project Info'!B62","v":15},{"$f":"'Project Info'!C62","v":12.269931130346862},{"$f":"'Project Info'!D62","v":10.318264913023604},{"$f":"'Project Info'!E62","v":3.9082824916941998},{"$f":"'Project Info'!F62","v":0},{"$f":"'Project Info'!G62","v":0},{"$f":"'Project Info'!H62","v":0},{"$f":"'Project Info'!I62","v":0},{"$f":"'Project Info'!J62","v":0},{"$f":"'Project Info'!K62","v":0},{"$f":"'Project Info'!L62","v":0},0,0,0.70086457549527026,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A63","v":5},{"$f":"'Project Info'!B63","v":10},{"$f":"'Project Info'!C63","v":7.3137581369917548},{"$f":"'Project Info'!D63","v":5.7052382449247707},{"$f":"'Project Info'!E63","v":2.5019418419888937},{"$f":"'Project Info'!F63","v":0},{"$f":"'Project Info'!G63","v":0},{"$f":"'Project Info'!H63","v":0},{"$f":"'Project Info'!I63","v":0},{"$f":"'Project Info'!J63","v":0},{"$f":"'Project Info'!K63","v":0},{"$f":"'Project Info'!L63","v":0},0,0,0.76844875267738533,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A64","v":0},{"$f":"'Project Info'!B64","v":5},{"$f":"'Project Info'!C64","v":2.6119461836144886},{"$f":"'Project Info'!D64","v":1.2699770062067783},{"$f":"'Project Info'!E64","v":1.2046477897733283},{"$f":"'Project Info'!F64","v":0},{"$f":"'Project Info'!G64","v":0},{"$f":"'Project Info'!H64","v":0},{"$f":"'Project Info'!I64","v":0},{"$f":"'Project Info'!J64","v":0},{"$f":"'Project Info'!K64","v":0},{"$f":"'Project Info'!L64","v":0},0,0,0.83256437022343899,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A65","v":-5},{"$f":"'Project Info'!B65","v":0},{"$f":"'Project Info'!C65","v":-1.6731398516793925},{"$f":"'Project Info'!D65","v":-2.7083318773557807},{"$f":"'Project Info'!E65","v":7.9391832815876459E-2},{"$f":"'Project Info'!F65","v":0},{"$f":"'Project Info'!G65","v":0},{"$f":"'Project Info'!H65","v":0},{"$f":"'Project Info'!I65","v":0},{"$f":"'Project Info'!J65","v":0},{"$f":"'Project Info'!K65","v":0},{"$f":"'Project Info'!L65","v":0},0,0,0.89099736161381016,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A66","v":-10},{"$f":"'Project Info'!B66","v":-5},{"$f":"'Project Info'!C66","v":-6.5729865085377277},{"$f":"'Project Info'!D66","v":-7.2465935998252222},{"$f":"'Project Info'!E66","v":-1.168423365310433},{"$f":"'Project Info'!F66","v":0},{"$f":"'Project Info'!G66","v":0},{"$f":"'Project Info'!H66","v":0},{"$f":"'Project Info'!I66","v":0},{"$f":"'Project Info'!J66","v":0},{"$f":"'Project Info'!K66","v":0},{"$f":"'Project Info'!L66","v":0},0,0,0.95781345238915105,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A67","v":-15},{"$f":"'Project Info'!B67","v":-10},{"$f":"'Project Info'!C67","v":-15.32570353422995},{"$f":"'Project Info'!D67","v":-15.707838211108999},{"$f":"'Project Info'!E67","v":-3.4051318156661381},{"$f":"'Project Info'!F67","v":0},{"$f":"'Project Info'!G67","v":0},{"$f":"'Project Info'!H67","v":0},{"$f":"'Project Info'!I67","v":0},{"$f":"'Project Info'!J67","v":0},{"$f":"'Project Info'!K67","v":0},{"$f":"'Project Info'!L67","v":0},0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Load Profile",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Load Profile"]
[null,null,null,null,null,null,"Unoccupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown",null,null,null,null,null,null,"Comfort/HVAC",null,null,null,"Cooling Demand",null,null,null,"Heating Demand",null,null,null,"Demand Savings",null,null,null,"Constant/IT/Elec",null,null,null,"Cooling Demand",null,null,null,"Heating Demand",null,null,null,"Demand Savings",null,null,null,"Overall"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Cooling","Cooling","Heating","Heating","Base","Proposed","Base","Design","Base","Proposed","Base","Design","Cooling","Heating","Total",null,"Cooling","Cooling","Heating","Heating","Base","Proposed","Base","Design","Base","Proposed","Base","Design","Cooling","Heating","Total",null,"Demand"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Load","Load","Load","Load","Perf","Perf","Demand","Demand","Perf","Perf","Demand","Demand","Savings","Savings","Savings",null,"Load","Load","Load","Load","Perf","Perf","Demand","Demand","Perf","Perf","Demand","Demand","Savings","Savings","Savings",null,"Savings"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","%","MBH","%","MBH","EER","EER","kW","kW","COP","COP","kW","kW","kW","kW","kW",null,"%","MBH","%","MBH","EER","EER","kW","kW","COP","COP","kW","kW","kW","kW","kW",null,"kW"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A74","v":100},{"$f":"'Project Info'!B74","v":105},{"$f":"'Project Info'!C74","v":102},{"$f":"'Project Info'!D74","v":76},{"$f":"'Project Info'!E74","v":40},{"$f":"'Project Info'!F74","v":0},{"$f":"'Project Info'!G74","v":0},{"$f":"'Project Info'!H74","v":0},{"$f":"'Project Info'!I74","v":0},{"$f":"'Project Info'!J74","v":0},{"$f":"'Project Info'!K74","v":0},{"$f":"'Project Info'!L74","v":0},{"$f":"MAX(0,MIN(1,TREND($Y$102:$Z$102,$W$102:$X$102,$I72)))*($I72>=$X$102)","v":0.53166666666666662},{"$f":"$R$34*S72","v":186.08333333333331},{"$f":"MAX(0,MIN(1,TREND($AH$102:$AI$102,$AF$102:$AG$102,$I72)))*($I72<=$AF$102)","v":0},{"$f":"$S$34*U72","v":0},{"$f":"OFFSET($G$122,MATCH($I72,$G$123:$G$133,-1),MATCH(S72,$H$122:$L$122,-1))*(S72>0)","v":13.36810631229236},{"$f":"OFFSET($G$135,MATCH($I72,$G$136:$G$146,-1),MATCH(S72,$H$135:$L$135,-1))*(S72>0)","v":14.495847176079735},{"$f":"IF(T72>0,T72/W72,0)","v":13.919947147803898},{"$f":"IF(T72>0,T72/X72,0)","v":12.837009874138159},{"$f":"MIN($AB$119,TREND($AB$119:$AC$119,$AB$118:$AC$118,$I72))*(U72>0)","v":0},{"$f":"MIN($AB$120,TREND($AB$120:$AC$120,$AB$118:$AC$118,$I72))*(U72>0)","v":0},{"$f":"IF(V72>0,V72/AA72/3.412,0)","v":0},{"$f":"IF(V72>0,V72/AB72/3.412,0)","v":0},{"$f":"Y72-Z72","v":1.0829372736657383},{"$f":"AC72-AD72","v":0},{"$f":"AE72+AF72","v":1.0829372736657383},null,{"$f":"$X$106","v":0.55000000000000004},{"$f":"$R$35*AI72","v":71.5},{"$f":"$Y$106","v":0},{"$f":"$S$35*AK72","v":0},{"$f":"OFFSET($Q$122,MATCH($I72,$Q$123:$Q$133,-1),MATCH(AI72,$R$122:$V$122,-1))*(AI72>0)","v":16.220930232558139},{"$f":"OFFSET($Q$135,MATCH($I72,$Q$136:$Q$146,-1),MATCH(AI72,$R$135:$V$135,-1))*(AI72>0)","v":17.122093023255815},{"$f":"IF(AJ72>0,AJ72/AM72,0)","v":4.4078853046594979},{"$f":"IF(AJ72>0,AJ72/AN72,0)","v":4.1758913412563663},{"$f":"MIN($AB$119,TREND($AB$119:$AC$119,$AB$118:$AC$118,$I72))*(AK72>0)","v":0},{"$f":"MIN($AB$120,TREND($AB$120:$AC$120,$AB$118:$AC$118,$I72))*(AK72>0)","v":0},{"$f":"IF(AL72>0,AL72/AQ72/3.412,0)","v":0},{"$f":"IF(AL72>0,AL72/AR72/3.412,0)","v":0},{"$f":"AO72-AP72","v":0.23199396340313161},{"$f":"AS72-AT72","v":0},{"$f":"AU72+AV72","v":0.23199396340313161},null,{"$f":"AG72+AW72","v":1.3149312370688699}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A75","v":95},{"$f":"'Project Info'!B75","v":100},{"$f":"'Project Info'!C75","v":95.219272727272724},{"$f":"'Project Info'!D75","v":74.534025272781079},{"$f":"'Project Info'!E75","v":37.923296058061368},{"$f":"'Project Info'!F75","v":0},{"$f":"'Project Info'!G75","v":0},{"$f":"'Project Info'!H75","v":0},{"$f":"'Project Info'!I75","v":0},{"$f":"'Project Info'!J75","v":0},{"$f":"'Project Info'!K75","v":0},{"$f":"'Project Info'!L75","v":0},{"$f":"MAX(0,MIN(1,TREND($Y$102:$Z$102,$W$102:$X$102,$I73)))*($I73>=$X$102)","v":0.45255818181818175},158.39536363636361,{"$f":"MAX(0,MIN(1,TREND($AH$102:$AI$102,$AF$102:$AG$102,$I73)))*($I73<=$AF$102)","v":0},0,13.843044091710757,15.010850970017636,{"$f":"IF(T73>0,T73/W73,0)","v":11.442235001708264},{"$f":"IF(T73>0,T73/X73,0)","v":10.552057571735224},0,0,{"$f":"IF(V73>0,V73/AA73/3.412,0)","v":0},{"$f":"IF(V73>0,V73/AB73/3.412,0)","v":0},{"$f":"Y73-Z73","v":0.89017742997303984},{"$f":"AC73-AD73","v":0},{"$f":"AE73+AF73","v":0.89017742997303984},null,{"$f":"$X$106","v":0.55000000000000004},71.5,{"$f":"$Y$106","v":0},0,16.220930232558139,17.122093023255815,{"$f":"IF(AJ73>0,AJ73/AM73,0)","v":4.4078853046594979},{"$f":"IF(AJ73>0,AJ73/AN73,0)","v":4.1758913412563663},0,0,{"$f":"IF(AL73>0,AL73/AQ73/3.412,0)","v":0},{"$f":"IF(AL73>0,AL73/AR73/3.412,0)","v":0},{"$f":"AO73-AP73","v":0.23199396340313161},{"$f":"AS73-AT73","v":0},{"$f":"AU73+AV73","v":0.23199396340313161},null,{"$f":"AG73+AW73","v":1.1221713933761714}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A76","v":90},{"$f":"'Project Info'!B76","v":95},{"$f":"'Project Info'!C76","v":92.016049160256074},{"$f":"'Project Info'!D76","v":72.911561930607689},{"$f":"'Project Info'!E76","v":36.467095439351091},{"$f":"'Project Info'!F76","v":0},{"$f":"'Project Info'!G76","v":0},{"$f":"'Project Info'!H76","v":0},{"$f":"'Project Info'!I76","v":0},{"$f":"'Project Info'!J76","v":0},{"$f":"'Project Info'!K76","v":0},{"$f":"'Project Info'!L76","v":0},0.41518724020298758,145.31553407104565,0,0,13.843044091710757,15.010850970017636,10.49736843344022,9.6806992728990444,0,0,0,0,0.816669160541176,0,0.816669160541176,null,0.55000000000000004,71.5,0,0,16.220930232558139,17.122093023255815,4.4078853046594979,4.1758913412563663,0,0,0,0,0.23199396340313161,0,0.23199396340313161,null,1.0486631239443076]
[null,null,null,null,null,null,{"$f":"'Project Info'!A77","v":85},{"$f":"'Project Info'!B77","v":90},{"$f":"'Project Info'!C77","v":87.457811360655285},{"$f":"'Project Info'!D77","v":70.80538329449476},{"$f":"'Project Info'!E77","v":34.679413213566804},{"$f":"'Project Info'!F77","v":0},{"$f":"'Project Info'!G77","v":0},{"$f":"'Project Info'!H77","v":0},{"$f":"'Project Info'!I77","v":0},{"$f":"'Project Info'!J77","v":0},{"$f":"'Project Info'!K77","v":0},{"$f":"'Project Info'!L77","v":0},0.36200779920764503,126.70272972267576,0,0,14.157658730158728,15.35200667388167,8.9494126209422511,8.2531705733449687,0,0,0,0,0.69624204759728237,0,0.69624204759728237,null,0.55000000000000004,71.5,0,0,16.607142857142858,17.529761904761905,4.3053763440860218,4.0787775891341251,0,0,0,0,0.22659875495189663,0,0.22659875495189663,null,0.922840802549179]
[null,null,null,null,null,null,{"$f":"'Project Info'!A78","v":80},{"$f":"'Project Info'!B78","v":85},{"$f":"'Project Info'!C78","v":82.136788830239965},{"$f":"'Project Info'!D78","v":67.872393622439333},{"$f":"'Project Info'!E78","v":32.296248223809314},{"$f":"'Project Info'!F78","v":0},{"$f":"'Project Info'!G78","v":0},{"$f":"'Project Info'!H78","v":0},{"$f":"'Project Info'!I78","v":0},{"$f":"'Project Info'!J78","v":0},{"$f":"'Project Info'!K78","v":0},{"$f":"'Project Info'!L78","v":0},0.29992920301946624,104.97522105681318,0,0,14.486906607604281,15.709030084902176,7.2462136949037097,6.6824762884440609,0,0,0,0,0.56373740645964876,0,0.56373740645964876,null,0.55000000000000004,71.5,0,0,17.012195121951223,17.957317073170735,4.2028673835125439,3.981663837011884,0,0,0,0,0.22120354650065988,0,0.22120354650065988,null,0.78494095296030864]
[null,null,null,null,null,null,{"$f":"'Project Info'!A79","v":75},{"$f":"'Project Info'!B79","v":80},{"$f":"'Project Info'!C79","v":76.988400157585886},{"$f":"'Project Info'!D79","v":65.129261896908645},{"$f":"'Project Info'!E79","v":30.190476812806729},{"$f":"'Project Info'!F79","v":0},{"$f":"'Project Info'!G79","v":0},{"$f":"'Project Info'!H79","v":0},{"$f":"'Project Info'!I79","v":0},{"$f":"'Project Info'!J79","v":0},{"$f":"'Project Info'!K79","v":0},{"$f":"'Project Info'!L79","v":0},0.23986466850516863,83.952633976809025,0,0,15.099012550756735,16.372773624953858,5.5601406843390881,5.1275755653798472,0,0,0,0,0.43256511895924099,0,0.43256511895924099,null,0.55000000000000004,71.5,0,0,17.4375,18.40625,4.1003584229390677,3.8845500848896433,0,0,0,0,0.21580833804942445,0,0.21580833804942445,null,0.64837345700866544]
[null,null,null,null,null,null,{"$f":"'Project Info'!A80","v":70},{"$f":"'Project Info'!B80","v":75},{"$f":"'Project Info'!C80","v":72.457982050814195},{"$f":"'Project Info'!D80","v":63.604425012889301},{"$f":"'Project Info'!E80","v":29.088683095945193},{"$f":"'Project Info'!F80","v":0},{"$f":"'Project Info'!G80","v":0},{"$f":"'Project Info'!H80","v":0},{"$f":"'Project Info'!I80","v":0},{"$f":"'Project Info'!J80","v":0},{"$f":"'Project Info'!K80","v":0},{"$f":"'Project Info'!L80","v":0},0.18700979059283229,65.453426707491303,0,0,15.458512849584276,16.762601568405142,4.2341347673202296,3.9047296113546408,0,0,0,0,0.32940515596558884,0,0.32940515596558884,null,0.55000000000000004,71.5,0,0,17.884615384615383,18.878205128205128,3.9978494623655916,3.7874363327674025,0,0,0,0,0.21041312959818903,0,0.21041312959818903,null,0.53981828556377787]
[null,null,null,null,null,null,{"$f":"'Project Info'!A81","v":65},{"$f":"'Project Info'!B81","v":70},{"$f":"'Project Info'!C81","v":67.815831070966169},{"$f":"'Project Info'!D81","v":61.631331368130574},{"$f":"'Project Info'!E81","v":27.661514889731574},{"$f":"'Project Info'!F81","v":0},{"$f":"'Project Info'!G81","v":0},{"$f":"'Project Info'!H81","v":0},{"$f":"'Project Info'!I81","v":0},{"$f":"'Project Info'!J81","v":0},{"$f":"'Project Info'!K81","v":0},{"$f":"'Project Info'!L81","v":0},0.13285136249460539,46.497976873111888,0,0,15.835549748354625,17.17144550909795,2.9363032930349138,2.7078661984790888,0,0,0,0,0.22843709455582495,0,0.22843709455582495,null,0.55000000000000004,71.5,0,0,18.355263157894736,19.375,3.895340501792115,3.6903225806451614,0,0,0,0,0.20501792114695361,0,0.20501792114695361,null,0.43345501570277856]
[null,null,null,null,null,null,{"$f":"'Project Info'!A82","v":60},{"$f":"'Project Info'!B82","v":65},{"$f":"'Project Info'!C82","v":62.535961472271332},{"$f":"'Project Info'!D82","v":57.135476922863582},{"$f":"'Project Info'!E82","v":24.623037157728302},{"$f":"'Project Info'!F82","v":0},{"$f":"'Project Info'!G82","v":0},{"$f":"'Project Info'!H82","v":0},{"$f":"'Project Info'!I82","v":0},{"$f":"'Project Info'!J82","v":0},{"$f":"'Project Info'!K82","v":0},{"$f":"'Project Info'!L82","v":0},0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A83","v":55},{"$f":"'Project Info'!B83","v":60},{"$f":"'Project Info'!C83","v":57.125792270740902},{"$f":"'Project Info'!D83","v":52.596971157053673},{"$f":"'Project Info'!E83","v":21.818001539159841},{"$f":"'Project Info'!F83","v":0},{"$f":"'Project Info'!G83","v":0},{"$f":"'Project Info'!H83","v":0},{"$f":"'Project Info'!I83","v":0},{"$f":"'Project Info'!J83","v":0},{"$f":"'Project Info'!K83","v":0},{"$f":"'Project Info'!L83","v":0},0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A84","v":50},{"$f":"'Project Info'!B84","v":55},{"$f":"'Project Info'!C84","v":52.235698854337961},{"$f":"'Project Info'!D84","v":48.022768090099298},{"$f":"'Project Info'!E84","v":19.246640192796217},{"$f":"'Project Info'!F84","v":0},{"$f":"'Project Info'!G84","v":0},{"$f":"'Project Info'!H84","v":0},{"$f":"'Project Info'!I84","v":0},{"$f":"'Project Info'!J84","v":0},{"$f":"'Project Info'!K84","v":0},{"$f":"'Project Info'!L84","v":0},0,0,2.7643011456620292E-2,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A85","v":45},{"$f":"'Project Info'!B85","v":50},{"$f":"'Project Info'!C85","v":47.459170258371508},{"$f":"'Project Info'!D85","v":43.465397050422162},{"$f":"'Project Info'!E85","v":16.894183241713304},{"$f":"'Project Info'!F85","v":0},{"$f":"'Project Info'!G85","v":0},{"$f":"'Project Info'!H85","v":0},{"$f":"'Project Info'!I85","v":0},{"$f":"'Project Info'!J85","v":0},{"$f":"'Project Info'!K85","v":0},{"$f":"'Project Info'!L85","v":0},0,0,7.5408297416284853E-2,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A86","v":40},{"$f":"'Project Info'!B86","v":45},{"$f":"'Project Info'!C86","v":42.677030404888129},{"$f":"'Project Info'!D86","v":38.812544504634097},{"$f":"'Project Info'!E86","v":14.690265649465921},{"$f":"'Project Info'!F86","v":0},{"$f":"'Project Info'!G86","v":0},{"$f":"'Project Info'!H86","v":0},{"$f":"'Project Info'!I86","v":0},{"$f":"'Project Info'!J86","v":0},{"$f":"'Project Info'!K86","v":0},{"$f":"'Project Info'!L86","v":0},0,0,0.12322969595111866,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A87","v":35},{"$f":"'Project Info'!B87","v":40},{"$f":"'Project Info'!C87","v":37.333046773755832},{"$f":"'Project Info'!D87","v":33.904706919479686},{"$f":"'Project Info'!E87","v":12.53841602318813},{"$f":"'Project Info'!F87","v":0},{"$f":"'Project Info'!G87","v":0},{"$f":"'Project Info'!H87","v":0},{"$f":"'Project Info'!I87","v":0},{"$f":"'Project Info'!J87","v":0},{"$f":"'Project Info'!K87","v":0},{"$f":"'Project Info'!L87","v":0},0,0,0.17666953226244164,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A88","v":30},{"$f":"'Project Info'!B88","v":35},{"$f":"'Project Info'!C88","v":32.638179845662044},{"$f":"'Project Info'!D88","v":29.547170928664851},{"$f":"'Project Info'!E88","v":10.728972818165861},{"$f":"'Project Info'!F88","v":0},{"$f":"'Project Info'!G88","v":0},{"$f":"'Project Info'!H88","v":0},{"$f":"'Project Info'!I88","v":0},{"$f":"'Project Info'!J88","v":0},{"$f":"'Project Info'!K88","v":0},{"$f":"'Project Info'!L88","v":0},0,0,0.22361820154337952,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A89","v":25},{"$f":"'Project Info'!B89","v":30},{"$f":"'Project Info'!C89","v":27.529264646850947},{"$f":"'Project Info'!D89","v":24.652717392657845},{"$f":"'Project Info'!E89","v":8.8041305482613303},{"$f":"'Project Info'!F89","v":0},{"$f":"'Project Info'!G89","v":0},{"$f":"'Project Info'!H89","v":0},{"$f":"'Project Info'!I89","v":0},{"$f":"'Project Info'!J89","v":0},{"$f":"'Project Info'!K89","v":0},{"$f":"'Project Info'!L89","v":0},0,0,0.27470735353149051,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A90","v":20},{"$f":"'Project Info'!B90","v":25},{"$f":"'Project Info'!C90","v":22.998111483544687},{"$f":"'Project Info'!D90","v":20.383306659827422},{"$f":"'Project Info'!E90","v":7.246164547543378},{"$f":"'Project Info'!F90","v":0},{"$f":"'Project Info'!G90","v":0},{"$f":"'Project Info'!H90","v":0},{"$f":"'Project Info'!I90","v":0},{"$f":"'Project Info'!J90","v":0},{"$f":"'Project Info'!K90","v":0},{"$f":"'Project Info'!L90","v":0},0,0,0.32001888516455312,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A91","v":15},{"$f":"'Project Info'!B91","v":20},{"$f":"'Project Info'!C91","v":17.808510327474309},{"$f":"'Project Info'!D91","v":15.420865796304254},{"$f":"'Project Info'!E91","v":5.5490484131518292},{"$f":"'Project Info'!F91","v":0},{"$f":"'Project Info'!G91","v":0},{"$f":"'Project Info'!H91","v":0},{"$f":"'Project Info'!I91","v":0},{"$f":"'Project Info'!J91","v":0},{"$f":"'Project Info'!K91","v":0},{"$f":"'Project Info'!L91","v":0},0,0,0.3719148967252569,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A92","v":10},{"$f":"'Project Info'!B92","v":15},{"$f":"'Project Info'!C92","v":12.269931130346862},{"$f":"'Project Info'!D92","v":10.318264913023604},{"$f":"'Project Info'!E92","v":3.9082824916941998},{"$f":"'Project Info'!F92","v":0},{"$f":"'Project Info'!G92","v":0},{"$f":"'Project Info'!H92","v":0},{"$f":"'Project Info'!I92","v":0},{"$f":"'Project Info'!J92","v":0},{"$f":"'Project Info'!K92","v":0},{"$f":"'Project Info'!L92","v":0},0,0,0.42730068869653137,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A93","v":5},{"$f":"'Project Info'!B93","v":10},{"$f":"'Project Info'!C93","v":7.3137581369917548},{"$f":"'Project Info'!D93","v":5.7052382449247707},{"$f":"'Project Info'!E93","v":2.5019418419888937},{"$f":"'Project Info'!F93","v":0},{"$f":"'Project Info'!G93","v":0},{"$f":"'Project Info'!H93","v":0},{"$f":"'Project Info'!I93","v":0},{"$f":"'Project Info'!J93","v":0},{"$f":"'Project Info'!K93","v":0},{"$f":"'Project Info'!L93","v":0},0,0,0.4768624186300825,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A94","v":0},{"$f":"'Project Info'!B94","v":5},{"$f":"'Project Info'!C94","v":2.6119461836144886},{"$f":"'Project Info'!D94","v":1.2699770062067783},{"$f":"'Project Info'!E94","v":1.2046477897733283},{"$f":"'Project Info'!F94","v":8760},{"$f":"'Project Info'!G94","v":2672},{"$f":"'Project Info'!H94","v":3160},{"$f":"'Project Info'!I94","v":1344},{"$f":"'Project Info'!J94","v":1584},{"$f":"'Project Info'!K94","v":88},{"$f":"'Project Info'!L94","v":264},0,0,0.52388053816385516,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A95","v":-5},{"$f":"'Project Info'!B95","v":0},{"$f":"'Project Info'!C95","v":-1.6731398516793925},{"$f":"'Project Info'!D95","v":-2.7083318773557807},{"$f":"'Project Info'!E95","v":7.9391832815876459E-2},{"$f":"'Project Info'!F95","v":0},{"$f":"'Project Info'!G95","v":0},{"$f":"'Project Info'!H95","v":0},{"$f":"'Project Info'!I95","v":0},{"$f":"'Project Info'!J95","v":0},{"$f":"'Project Info'!K95","v":0},{"$f":"'Project Info'!L95","v":0},0,0,0.56673139851679399,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A96","v":-10},{"$f":"'Project Info'!B96","v":-5},{"$f":"'Project Info'!C96","v":-6.5729865085377277},{"$f":"'Project Info'!D96","v":-7.2465935998252222},{"$f":"'Project Info'!E96","v":-1.168423365310433},{"$f":"'Project Info'!F96","v":0},{"$f":"'Project Info'!G96","v":0},{"$f":"'Project Info'!H96","v":0},{"$f":"'Project Info'!I96","v":0},{"$f":"'Project Info'!J96","v":0},{"$f":"'Project Info'!K96","v":0},{"$f":"'Project Info'!L96","v":0},0,0,0.6157298650853773,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[null,null,null,null,null,null,{"$f":"'Project Info'!A97","v":-15},{"$f":"'Project Info'!B97","v":-10},{"$f":"'Project Info'!C97","v":-15.32570353422995},{"$f":"'Project Info'!D97","v":-15.707838211108999},{"$f":"'Project Info'!E97","v":-3.4051318156661381},{"$f":"'Project Info'!F97","v":0},{"$f":"'Project Info'!G97","v":0},{"$f":"'Project Info'!H97","v":0},{"$f":"'Project Info'!I97","v":0},{"$f":"'Project Info'!J97","v":0},{"$f":"'Project Info'!K97","v":0},{"$f":"'Project Info'!L97","v":0},0,0,0.70325703534229955,0,0,0,0,0,0,0,0,0,0,0,0,null,0.55000000000000004,71.5,0,0,18.851351351351351,19.898648648648649,3.792831541218638,3.5932088285229202,0,0,0,0,0.19962271269571774,0,0.19962271269571774,null,0.19962271269571774]
[]
[null,null,null,null,null,null,"System Types",null,"Condenser Type",null,null,null,null,null,"VRF Heat Recovery?"]
[null,null,null,null,null,null,"Air Conditioner",null,"Air Cooled","Water Cooled","Evap Cooled",null,null,null,"No",null,null,null,"VRF System Cooling Load Profile",null,null,null,null,null,null,null,null,"VRF System Heating Load Profile"]
[null,null,null,null,null,null,"Heat Pump",null,"Air Cooled","Water Loop (HP)","Ground Water (HP)","Ground Loop (HP)",null,null,"Yes",null,null,null,"Occupied Profile",null,null,null,"Unocc Profile",null,null,null,null,"Occupied Profile",null,null,null,"Unocc Profile"]
[null,null,null,null,null,null,"VRF AC Only",null,"Air Cooled",null,null,null,null,null,null,null,null,null,"Max OAT","Min OAT","% Load @","%Load @","Max OAT","Min OAT","% Load @","%Load @",null,"Max OAT","Min OAT","% Load @","%Load @","Max OAT","Min OAT","% Load @","%Load @"]
[null,null,null,null,null,null,"VRF Heat Pump",null,"Air Cooled","Water Cooled","Ground Water (HP)","Ground Loop (HP)",null,null,"Load Profiles",null,null,null,"°F","°F","Max OAT","Min OAT","°F","°F","Max OAT","Min OAT",null,"°F","°F","Max OAT","Min OAT","°F","°F","Max OAT","Min OAT"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Comfort/HVAC",null,null,null,95,50,0.95,0.15,95,65,0.45,0.1,null,60,5,0.05,0.8,55,5,0,0.5]
[null,null,null,null,null,null,"Heating System Type",null,"Perf. Unit",null,null,null,null,null,"Constant/IT-Elec Rooms",null,null,null,95,55,{"$f":"U102*$R$34","v":332.5},{"$f":"V102*$R$34","v":52.5},95,65,{"$f":"Y102*$R$34","v":157.5},{"$f":"Z102*$R$34","v":35},null,55,5,{"$f":"AD102*$S$34","v":0},{"$f":"AE102*$S$34","v":0},55,5,{"$f":"AH102*$S$34","v":0},{"$f":"AI102*$S$34","v":0}]
[null,null,null,null,null,null,"1-Fossil Fuel Furnace",null,"Efficiency (%)",null,null,null,null,null,null,null,null,null,"Bin Model EFLH Cooling",null,null,{"$f":"SUMPRODUCT(S42:S65,L42:L65)+SUMPRODUCT(S72:S95,L72:L95)","v":0}]
[null,null,null,null,null,null,"2-Heat Pump (Elec)",null,"COP",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Cooling","Heating"]
[null,null,null,null,null,null,"3-Electric Resistance",null,"COP",null,null,null,null,null,null,null,null,null,"Constant/IT-Elec Rooms Average 24/7 % Load",null,null,null,null,0.55000000000000004,0]
[null,null,null,null,null,null,"4-None",null,"None"]
[]
[]
[null,null,null,null,null,null,"OAT Perf. Impact",null,5.0000000000000001E-3,"% improvement per °F OAT reduction"]
[]
[null,null,null,null,null,null,null,null,0.75,0.5,0.25]
[null,null,null,null,null,null,"PL EER Factors",null,0.96875,1.0498263888888888,1.0941840277777777]
[]
[null,null,null,null,null,null,null,"HVAC Systems - Part Load Cooling Performance",null,null,null,null,null,null,null,null,null,"HVAC Load Profile -Part Load Cooling Performance",null,null,null,null,null,null,null,null,"HVAC Load Profile"]
[null,null,null,null,null,null,null,0.02,0.61699999999999999,0.23799999999999999,0.125,null,null,"IEER",null,null,null,0.02,0.61699999999999999,0.23799999999999999,0.125,null,null,"IEER",null,null,"Heating Performance - COP vs. OAT°F"]
[null,null,null,null,null,null,null,1,0.75,0.5,0.25,-0.01,"IEER","Calculated",null,null,null,1,0.75,0.5,0.25,-0.01,"IEER","Calculated",null,null,null,"OAT (°F)"]
[null,null,null,null,null,null,"Base",{"$f":"$Y$34","v":13.64},{"$f":"IF(H118=0,0,($M118/$H118)*I$113*$H118)","v":14.370714285714287},15.573424603174601,16.231438492063489,{"$f":"K118*0.75","v":12.173578869047617},{"$f":"$Z$34","v":14.834285714285715},{"$f":"SUMPRODUCT(H118:K118,$H$116:$K$116)","v":14.874935581349206},{"$f":"1-N118/M118","v":-2.7402645362522016E-3},null,"Base",{"$f":"$Y$35","v":18},{"$f":"IF(R118=0,0,($W118/$R118)*I$113*$R118)","v":17.4375},18.896874999999998,19.6953125,{"$f":"U118*0.75","v":14.771484375},{"$f":"$Z$35","v":18},{"$f":"SUMPRODUCT(R118:U118,$H$116:$K$116)","v":18.0783078125},{"$f":"1-X118/W118","v":-4.3504340277777942E-3},null,null,47,17]
[null,null,null,null,null,null,"Proposed",{"$f":"$T$34","v":12.2},15.583035714285714,16.887207341269839,17.600731646825398,{"$f":"K119*0.75","v":13.20054873511905},{"$f":"$U$34","v":16.085714285714285},{"$f":"SUMPRODUCT(H119:K119,$H$116:$K$116)","v":16.077979838789684},{"$f":"1-N119/M119","v":4.8082707346541742E-4},null,"Proposed",{"$f":"$T$35","v":19},18.40625,19.946701388888886,20.789496527777775,{"$f":"U119*0.75","v":15.592122395833332},{"$f":"$U$35","v":19},{"$f":"SUMPRODUCT(R119:U119,$H$116:$K$116)","v":19.082658246527778},{"$f":"1-X119/W119","v":-4.3504340277777942E-3},null,"Base",{"$f":"AA34","v":0},{"$f":"AB34","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Proposed",{"$f":"V34","v":0},{"$f":"W34","v":0}]
[null,null,null,null,null,null,"HVAC Systems - Baseline Cooling Performance Table",null,null,null,null,null,null,null,null,null,"Constant/IT-Elec Room Systems - Baseline Cooling Performance Table"]
[null,null,null,null,null,null,"OAT",1,0.75,0.5,0.25,-0.01,null,null,null,null,"OAT",1,0.75,0.5,0.25,-0.01]
[null,null,null,null,null,null,105,{"$f":"H124","v":13.64},{"$f":"I124","v":13.36810631229236},{"$f":"J124","v":13.843044091710757},{"$f":"K124","v":14.114294340924774},{"$f":"L124","v":14.114294340924774},null,null,null,null,105,{"$f":"R124","v":18},{"$f":"S124","v":16.220930232558139},{"$f":"T124","v":16.797222222222221},{"$f":"U124","v":17.126358695652176},{"$f":"V124","v":17.126358695652176}]
[null,null,null,null,null,null,95,{"$f":"H118","v":13.64},{"$f":"$I$127/(1-($G$127-$G124)*$I$110)","v":13.36810631229236},{"$f":"$J$129/(1-($G$129-$G124)*$I$110)","v":13.843044091710757},{"$f":"$K$130/(1-($G$130-$G124)*$I$110)","v":14.114294340924774},{"$f":"K124","v":14.114294340924774},null,null,null,null,95,{"$f":"R118","v":18},{"$f":"$S$127/(1-($Q$127-$Q124)*$I$110)","v":16.220930232558139},{"$f":"$T$129/(1-($Q$129-$Q124)*$I$110)","v":16.797222222222221},{"$f":"$U$130/(1-($Q$130-$Q124)*$I$110)","v":17.126358695652176},{"$f":"U124","v":17.126358695652176}]
[null,null,null,null,null,null,90,{"$f":"$H$124/(1-($G$124-$G125)*$I$110)","v":13.98974358974359},{"$f":"$I$127/(1-($G$127-$G125)*$I$110)","v":13.68639455782313},{"$f":"$J$129/(1-($G$129-$G125)*$I$110)","v":14.157658730158728},14.427945326278657,14.427945326278657,null,null,null,null,90,{"$f":"$R$124/(1-($Q$124-$Q125)*$I$110)","v":18.461538461538463},{"$f":"$S$127/(1-($Q$127-$Q125)*$I$110)","v":16.607142857142858},{"$f":"$T$129/(1-($Q$129-$Q125)*$I$110)","v":17.17897727272727},17.506944444444443,17.506944444444443]
[null,null,null,null,null,null,85,14.357894736842107,{"$f":"$I$127/(1-($G$127-$G126)*$I$110)","v":14.020209059233451},{"$f":"$J$129/(1-($G$129-$G126)*$I$110)","v":14.486906607604281},14.755853174603171,14.755853174603171,null,null,null,null,85,18.947368421052634,{"$f":"$S$127/(1-($Q$127-$Q126)*$I$110)","v":17.012195121951223},{"$f":"$T$129/(1-($Q$129-$Q126)*$I$110)","v":17.578488372093023},17.904829545454543,17.904829545454543]
[null,null,null,null,null,null,80,14.745945945945946,{"$f":"I118","v":14.370714285714287},{"$f":"$J$129/(1-($G$129-$G127)*$I$110)","v":14.831832955404382},15.099012550756735,15.099012550756735,null,null,null,null,80,19.45945945945946,{"$f":"S118","v":17.4375},{"$f":"$T$129/(1-($Q$129-$Q127)*$I$110)","v":17.997023809523807},18.32122093023256,18.32122093023256]
[null,null,null,null,null,null,75,15.155555555555555,{"$f":"$I$127/(1-($G$127-$G128)*$I$110)","v":14.739194139194142},{"$f":"$J$129/(1-($G$129-$G128)*$I$110)","v":15.193584978706928},15.458512849584276,15.458512849584276,null,null,null,null,75,20,{"$f":"$S$127/(1-($Q$127-$Q128)*$I$110)","v":17.884615384615383},{"$f":"$T$129/(1-($Q$129-$Q128)*$I$110)","v":18.435975609756095},18.757440476190474,18.757440476190474]
[null,null,null,null,null,null,70,15.588571428571429,{"$f":"$I$127/(1-($G$127-$G129)*$I$110)","v":15.127067669172934},{"$f":"J118","v":15.573424603174601},15.835549748354625,15.835549748354625,null,null,null,null,70,20.571428571428573,{"$f":"$S$127/(1-($Q$127-$Q129)*$I$110)","v":18.355263157894736},{"$f":"T118","v":18.896874999999998},19.214939024390244,19.214939024390244]
[null,null,null,null,null,null,65,16.047058823529412,{"$f":"$I$127/(1-($G$127-$G130)*$I$110)","v":15.535907335907337},{"$f":"$J$129/(1-($G$129-$G130)*$I$110)","v":15.972743182743182},{"$f":"K118","v":16.231438492063489},16.231438492063489,"< Min Cond Temp",null,null,null,65,21.176470588235293,{"$f":"$S$127/(1-($Q$127-$Q130)*$I$110)","v":18.851351351351351},{"$f":"$T$129/(1-($Q$129-$Q130)*$I$110)","v":19.381410256410255},{"$f":"U118","v":19.6953125},19.6953125,"< Min Cond Temp"]
[null,null,null,null,null,null,60,{"$f":"H130","v":16.047058823529412},{"$f":"I130","v":15.535907335907337},15.972743182743182,16.231438492063489,16.231438492063489,null,null,null,null,60,{"$f":"R130","v":21.176470588235293},{"$f":"S130","v":18.851351351351351},19.381410256410255,19.6953125,19.6953125]
[null,null,null,null,null,null,55,{"$f":"H131","v":16.047058823529412},15.535907335907337,15.972743182743182,16.231438492063489,16.231438492063489,null,null,null,null,55,{"$f":"R131","v":21.176470588235293},18.851351351351351,19.381410256410255,19.6953125,19.6953125]
[null,null,null,null,null,null,-20,{"$f":"H132","v":16.047058823529412},{"$f":"I132","v":15.535907335907337},{"$f":"J132","v":15.972743182743182},{"$f":"K132","v":16.231438492063489},{"$f":"L132","v":16.231438492063489},null,null,null,null,-20,{"$f":"R132","v":21.176470588235293},{"$f":"S132","v":18.851351351351351},{"$f":"T132","v":19.381410256410255},{"$f":"U132","v":19.6953125},{"$f":"V132","v":19.6953125}]
[null,null,null,null,null,null,"HVAC Systems - Proposed Cooling Performance Table",null,null,null,null,null,null,null,null,null,"Constant/IT-Elec Room Systems - Proposed Cooling Performance Table"]
[null,null,null,null,null,null,"OAT",1,0.75,0.5,0.25,-0.01,null,null,null,null,"OAT",1,0.75,0.5,0.25,-0.01]
[null,null,null,null,null,null,105,{"$f":"H137","v":12.2},{"$f":"I137","v":14.495847176079735},{"$f":"J137","v":15.010850970017636},{"$f":"K137","v":15.30498404071774},{"$f":"L137","v":15.30498404071774},null,null,null,null,105,{"$f":"R137","v":19},{"$f":"S137","v":17.122093023255815},{"$f":"T137","v":17.7304012345679},{"$f":"U137","v":18.077823067632849},{"$f":"V137","v":18.077823067632849}]
[null,null,null,null,null,null,95,{"$f":"H119","v":12.2},{"$f":"$I$140/(1-($G$140-$G137)*$I$110)","v":14.495847176079735},{"$f":"$J$142/(1-($G$142-$G137)*$I$110)","v":15.010850970017636},{"$f":"$K$143/(1-($G$143-$G137)*$I$110)","v":15.30498404071774},{"$f":"K137","v":15.30498404071774},null,null,null,null,95,{"$f":"R119","v":19},{"$f":"$S$140/(1-($Q$140-$Q137)*$I$110)","v":17.122093023255815},{"$f":"$T$142/(1-($Q$142-$Q137)*$I$110)","v":17.7304012345679},{"$f":"$U$143/(1-($Q$143-$Q137)*$I$110)","v":18.077823067632849},{"$f":"U137","v":18.077823067632849}]
[null,null,null,null,null,null,90,{"$f":"$H$137/(1-($G$137-$G138)*$I$110)","v":12.512820512820513},{"$f":"$I$140/(1-($G$140-$G138)*$I$110)","v":14.840986394557822},{"$f":"$J$142/(1-($G$142-$G138)*$I$110)","v":15.35200667388167},15.645094797178132,{"$f":"K138","v":15.645094797178132},null,null,null,null,90,{"$f":"$R$137/(1-($Q$137-$Q138)*$I$110)","v":19.487179487179489},{"$f":"$S$140/(1-($Q$140-$Q138)*$I$110)","v":17.529761904761905},{"$f":"$T$142/(1-($Q$142-$Q138)*$I$110)","v":18.133364898989896},18.4795524691358,{"$f":"U138","v":18.4795524691358}]
[null,null,null,null,null,null,85,12.842105263157894,{"$f":"$I$140/(1-($G$140-$G139)*$I$110)","v":15.202961672473869},{"$f":"$J$142/(1-($G$142-$G139)*$I$110)","v":15.709030084902176},16.000665133477632,16.000665133477632,null,null,null,null,85,20,{"$f":"$S$140/(1-($Q$140-$Q139)*$I$110)","v":17.957317073170735},{"$f":"$T$142/(1-($Q$142-$Q139)*$I$110)","v":18.555071059431523},18.899542297979792,18.899542297979792]
[null,null,null,null,null,null,80,13.189189189189188,{"$f":"I119","v":15.583035714285714},{"$f":"$J$142/(1-($G$142-$G140)*$I$110)","v":16.083054610733178},16.372773624953858,16.372773624953858,null,null,null,null,80,20.54054054054054,{"$f":"S119","v":18.40625},{"$f":"$T$142/(1-($Q$142-$Q140)*$I$110)","v":18.996858465608462},19.339066537467698,19.339066537467698]
[null,null,null,null,null,null,75,13.555555555555554,{"$f":"$I$140/(1-($G$140-$G141)*$I$110)","v":15.982600732600732},{"$f":"$J$142/(1-($G$142-$G141)*$I$110)","v":16.475324235385209},16.762601568405142,16.762601568405142,null,null,null,null,75,21.111111111111111,{"$f":"$S$140/(1-($Q$140-$Q141)*$I$110)","v":18.878205128205128},{"$f":"$T$142/(1-($Q$142-$Q141)*$I$110)","v":19.460196476964768},19.7995205026455,19.7995205026455]
[null,null,null,null,null,null,70,13.942857142857141,{"$f":"$I$140/(1-($G$140-$G142)*$I$110)","v":16.403195488721806},{"$f":"J119","v":16.887207341269839},17.17144550909795,17.17144550909795,null,null,null,null,70,21.714285714285715,{"$f":"$S$140/(1-($Q$140-$Q142)*$I$110)","v":19.375},{"$f":"T119","v":19.946701388888886},20.282435636856366,20.282435636856366]
[null,null,null,null,null,null,65,14.352941176470587,{"$f":"$I$140/(1-($G$140-$G143)*$I$110)","v":16.846525096525095},{"$f":"$J$142/(1-($G$142-$G143)*$I$110)","v":17.320212657712656},{"$f":"K119","v":17.600731646825398},17.600731646825398,"< Min Cond Temp",null,null,null,65,22.352941176470591,{"$f":"$S$140/(1-($Q$140-$Q143)*$I$110)","v":19.898648648648649},{"$f":"$T$142/(1-($Q$142-$Q143)*$I$110)","v":20.458155270655269},{"$f":"U119","v":20.789496527777775},20.789496527777775,"< Min Cond Temp"]
[null,null,null,null,null,null,60,{"$f":"H143","v":14.352941176470587},{"$f":"I143","v":16.846525096525095},17.320212657712656,17.600731646825398,17.600731646825398,null,null,null,null,60,{"$f":"R143","v":22.352941176470591},{"$f":"S143","v":19.898648648648649},20.458155270655269,{"$f":"U143","v":20.789496527777775},20.789496527777775]
[null,null,null,null,null,null,55,{"$f":"H144","v":14.352941176470587},16.846525096525095,17.320212657712656,17.600731646825398,17.600731646825398,null,null,null,null,55,{"$f":"R144","v":22.352941176470591},19.898648648648649,20.458155270655269,20.789496527777775,20.789496527777775]
[null,null,null,null,null,null,-20,{"$f":"H145","v":14.352941176470587},16.846525096525095,17.320212657712656,17.600731646825398,17.600731646825398,null,null,null,null,-20,{"$f":"R145","v":22.352941176470591},19.898648648648649,20.458155270655269,20.789496527777775,20.789496527777775]
[]
[null,null,null,"** Using AC values fo electric heat or no heat)"]
[null,null,null,null,null,2015,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2018]
[null,null,null,null,null,null,null,"Baseline EER",null,null,null,null,null,null,null,null,"Baseline IEER",null,null,null,null,null,null,null,null,"Baseline COP 47",null,null,null,null,null,null,null,null,"Baseline COP 17"]
[null,null,null,null,null,null,null,null,"MBH ≥",0,17,65,135,240,760,null,null,"MBH ≥",0,17,65,135,240,760,null,null,"MBH ≥",0,17,65,135,240,760,null,null,"MBH ≥",0,17,65,135,240,760]
[null,null,null,null,null,null,null,null,"MBH <",17,65,135,240,760,10000,null,null,"MBH <",17,65,135,240,760,10000,null,null,"MBH <",17,65,135,240,760,10000,null,null,"MBH <",17,65,135,240,760,10000]
[null,null,null,null,null,{"$f":"G98","v":"Air Conditioner"},null,"AC - Cooling Only",null,null,null,null,null,null,null,null,"AC - Cooling Only",null,null,null,null,null,null,null,null,"AC - Cooling Only",null,null,null,null,null,null,null,null,"AC - Cooling Only"]
[null,null,null,null,null,null,null,"Air Cooled",null,{"$f":"K154","v":11.3},11.3,11.2,11,10,null,null,"Air Cooled",null,{"$f":"T154","v":13},13,12.8,12.4,11.6,11.2,null,"Air Cooled",null,0,0,0,0,0,0,null,"Air Cooled",null,0,0,0,0,0,0]
[null,null,null,null,null,null,null,"Water Cooled",null,{"$f":"K155","v":12.1},12.1,12.1,12.5,12.4,12.2,null,"Water Cooled",null,{"$f":"T155","v":12.3},12.3,13.9,13.9,13.6,13.5,null,"Water Cooled",null,0,0,0,0,0,0,null,"Water Cooled",null,0,0,0,0,0,0]
[null,null,null,null,null,null,null,"Evap Cooled",null,{"$f":"K156","v":12.1},12.1,12.1,12,11.9,11.7,null,"Evap Cooled",null,{"$f":"T156","v":12.3},12.3,12.3,12.2,12.1,11.9,null,"Evap Cooled",null,0,0,0,0,0,0,null,"Evap Cooled",null,0,0,0,0,0,0]
[null,null,null,null,null,null,null,"Water Loop (HP)",null,0,0,0,0,0,0,null,"Water Loop (HP)",null,0,0,0,0,0,0,null,"Water Loop (HP)",null,0,0,0,0,0,0,null,"Water Loop (HP)",null,0,0,0,0,0,0]
[null,null,null,null,null,null,null,"Ground Water (HP)",null,0,0,0,0,0,0,null,"Ground Water (HP)",null,0,0,0,0,0,0,null,"Ground Water (HP)",null,0,0,0,0,0,0,null,"Ground Water (HP)",null,0,0,0,0,0,0]
[null,null,null,null,null,null,null,"Ground Loop (HP)",null,0,0,0,0,0,0,null,"Ground Loop (HP)",null,0,0,0,0,0,0,null,"Ground Loop (HP)",null,0,0,0,0,0,0,null,"Ground Loop (HP)",null,0,0,0,0,0,0]
[null,null,null,null,null,{"$f":"G99","v":"Heat Pump"},null,"AC - Cooling Only",null,null,null,null,null,null,null,null,"AC - Cooling Only",null,null,null,null,null,null,null,null,"AC - Cooling Only",null,null,null,null,null,null,null,null,"AC - Cooling Only"]
[null,null,null,null,null,null,null,"Air Cooled",null,{"$f":"K161","v":11.8},11.8,11,10.6,9.5,9.5,null,"Air Cooled",null,{"$f":"T161","v":14},14,12,11.6,10.6,10.6,null,"Air Cooled",null,{"$f":"8.2/3.412","v":2.4032825322391558},{"$f":"8.2/3.412","v":2.4032825322391558},3.3,3.2,3.2,3.2,null,"Air Cooled",null,{"$f":"8.2/3.412","v":2.4032825322391558},{"$f":"8.2/3.412","v":2.4032825322391558},2.25,2.0499999999999998,2.0499999999999998,2.0499999999999998]
[null,null,null,null,null,null,null,"Water Cooled",null,0,0,0,0,0,0,null,"Water Cooled",null,0,0,0,0,0,0,null,"Water Cooled",null,0,0,0,0,0,0,null,"Water Cooled",null,0,0,0,0,0,0]
[null,null,null,null,null,null,null,"Evap Cooled",null,0,0,0,0,0,0,null,"Evap Cooled",null,0,0,0,0,0,0,null,"Evap Cooled",null,0,0,0,0,0,0,null,"Evap Cooled",null,0,0,0,0,0,0]
[null,null,null,null,null,null,null,"Water Loop (HP)",null,12.2,13,13,0,0,0,null,"Water Loop (HP)",null,12.2,13,13,0,0,0,null,"Water Loop (HP)",null,4.3,4.3,4.3,0,0,0,null,"Water Loop (HP)",null,4.3,4.3,4.3,0,0,0]
[null,null,null,null,null,null,null,"Ground Water (HP)",null,18,18,18,0,0,0,null,"Ground Water (HP)",null,18,18,18,0,0,0,null,"Ground Water (HP)",null,3.7,3.7,3.7,0,0,0,null,"Ground Water (HP)",null,3.7,3.7,3.7,0,0,0]
[null,null,null,null,null,null,null,"Ground Loop (HP)",null,14.1,14.1,14.1,0,0,0,null,"Ground Loop (HP)",null,14.1,14.1,14.1,0,0,0,null,"Ground Loop (HP)",null,3.2,3.2,3.2,0,0,0,null,"Ground Loop (HP)",null,3.2,3.2,3.2,0,0,0]
[null,null,null,null,null,{"$f":"G101","v":"VRF Heat Pump"},null,"AC - Cooling Only",null,{"$f":"K167","v":11.3},11.3,11.2,11,10,10,null,"AC - Cooling Only",null,{"$f":"T167","v":13},13,13.1,12.9,11.6,11.6,null,"AC - Cooling Only",null,{"$f":"AC167","v":0},0,0,0,0,0,null,"AC - Cooling Only",null,{"$f":"AL167","v":0},0,0,0,0,0]
[null,null,null,null,null,null,null,"Air Cooled",null,{"$f":"K168","v":11.1},11.1,11,10.6,9.5,9.5,null,"Air Cooled",null,{"$f":"T168","v":13},13,12.3,11.8,10.6,10.6,null,"Air Cooled",null,{"$f":"AC168","v":2.2567409144196953},{"$f":"7.7/3.412","v":2.2567409144196953},3.3,3.2,3.2,3.2,null,"Air Cooled",null,{"$f":"AL168","v":2.2567409144196953},{"$f":"7.7/3.412","v":2.2567409144196953},2.25,2.0499999999999998,2.0499999999999998,2.0499999999999998]
[null,null,null,null,null,null,null,"Water Cooled",null,12,12,12,10,10,10,null,"Water Cooled",null,12,{"$f":"K169","v":12},{"$f":"L169","v":12},{"$f":"M169","v":10},{"$f":"N169","v":10},{"$f":"O169","v":10},null,"Water Cooled",null,4.2,4.2,4.2,3.9,3.9,3.9,null,"Water Cooled",null,4.2,4.2,4.2,3.9,3.9,3.9]
[null,null,null,null,null,null,null,"Evap Cooled",null,0,0,0,0,0,0,null,"Evap Cooled",null,0,0,0,0,0,0,null,"Evap Cooled",null,0,0,0,0,0,0,null,"Evap Cooled",null,0,0,0,0,0,0]
[null,null,null,null,null,null,null,"Water Loop (HP)",null,0,0,0,0,0,0,null,"Water Loop (HP)",null,0,0,0,0,0,0,null,"Water Loop (HP)",null,0,0,0,0,0,0,null,"Water Loop (HP)",null,0,0,0,0,0,0]
[null,null,null,null,null,null,null,"Ground Water (HP)",null,16.2,16.2,16.2,13.8,13.8,13.8,null,"Ground Water (HP)",null,16.2,{"$f":"K172","v":16.2},16.2,13.8,13.8,13.8,null,"Ground Water (HP)",null,3.6,3.6,3.6,3.3,3.3,3.3,null,"Ground Water (HP)",null,3.6,3.6,3.6,3.3,3.3,3.3]
[null,null,null,null,null,null,null,"Ground Loop (HP)",null,13.4,13.4,13.4,11,11,11,null,"Ground Loop (HP)",null,13.4,13.4,13.4,11,11,11,null,"Ground Loop (HP)",null,3.1,3.1,3.1,2.8,2.8,2.8,null,"Ground Loop (HP)",null,3.1,3.1,3.1,2.8,2.8,2.8]
[null,null,null,null,null,{"$f":"G100","v":"VRF AC Only"},null,"AC - Cooling Only",null,{"$f":"K174","v":11.3},11.3,11.2,11,10,10,null,"AC - Cooling Only",null,{"$f":"T174","v":13},13,13.1,12.9,11.6,11.6,null,"AC - Cooling Only",null,0,0,0,0,0,0,null,"AC - Cooling Only",null,0,0,0,0,0,0]
[null,null,null,null,null,null,null,"Air Cooled",null,{"$f":"K175","v":11.3},11.3,11.2,11,10,10,null,"Air Cooled",null,{"$f":"T175","v":13},13,13.1,12.9,11.6,11.6,null,"Air Cooled",null,0,0,0,0,0,0,null,"Air Cooled",null,0,0,0,0,0,0]

{"sheet":"User Defined 1","index":25,"n_rows":87,"n_cols":18,"rows_kept":87,"cut":false,"hidden":true,"merged":[[3,10,8,19],[11,10,17,19],[20,10,26,19],[17,7,17,8],[18,7,18,8],[16,7,16,8]]}
["Savings Summary",null,null,null,null,"Measure Summary",null,null,null,null,"Measure Title"]
["Annual kWh Savings",null,null,null,null,null,null,"Value","Unit"]
["% On Peak",null,null,null,null,"Annual Electric Savings",null,{"$f":"D2","v":0},"kWh",null,"Measure Description"]
["Max kW",null,null,null,null,"Annual Fuel Savings",null,{"$f":"D7*C28","v":{"$error":"#N/A"}},{"$f":"D20","v":{"$error":"#N/A"}}]
["Summer kW",null,null,null,null,"Incremental Cost",null,{"$f":"D8","v":0},"$"]
["Winter kW",null,null,null,null,"Estimated Custom Incentive",null,{"$f":"IF(AND($C$24>=0,$C$25>=0),MAX(0,H3)*C24+MAX(0,H4)*C25,\"TBD\")","v":{"$error":"#N/A"}},"$"]
["Annual Fuel Savings (MMBtu)",null,null,null,null,"Override Incentive (Optional)",null,null,"$"]
["Incremental Cost",null,null,null,null,"Custom Payback",null,{"$f":"H5/(H3*$C$19+H4*$C$20)","v":{"$error":"#N/A"}},"years"]
[null,null,null,null,null,"Project Information Summary"]
["kWh Savings by Peak Period",null,null,null,null,null,"STATE (MA or RI)",{"$f":"'Project Info'!C15","v":"NH"}]
["Winter","Winter","Summer","Summer",null,null,"Program Year",{"$f":"'Project Info'!C19","v":0},null,null,"Base Case Description"]
["On-Peak","Off-Peak","On-Peak","Off-Peak",null,null,"Code IECC Version",{"$f":"MID('Project Info'!C20,1,4)","v":"2018"}]
["kWh","kWh","kWh","kWh",null,null,"Electric PA",{"$f":"'Project Info'!F3","v":0}]
[null,null,null,null,null,null,"Gas PA",{"$f":"'Project Info'!I3","v":0}]
[{"$f":"ROUND(IF(A14<=0,0,A14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(B14<=0,0,B14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(C14<=0,0,C14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"IF(SUM(A14:D14)=0,0,1-SUM(A15:C15))","v":0}]
[null,null,null,null,null,"Information For BCR Inputs"]
["Utility Rates",null,null,null,null,"Program Type"]
[null,null,"Rate","Unit",null,"Fuel Savings Type"]
["Electric",null,{"$f":"'ECM Summary'!$E$31","v":0.1593},"kWh",null,"Measure Type"]
[{"$f":"'ECM Summary'!$C$32","v":0},null,{"$f":"'ECM Summary'!$E$32","v":{"$error":"#N/A"}},{"$f":"'ECM Summary'!$F$32","v":{"$error":"#N/A"}},null,"Measure Life",null,{"$f":"LOOKUP($H$19,'PA Impacts'!$G$84:$G$118,'PA Impacts'!$H$84:$H$118)","v":{"$error":"#N/A"}},null,null,"Proposed Case Description"]
[]
["Custom Incentive Rates"]
[null,null,"Rate","Unit"]
["Electric",null,{"$f":"'ECM Summary'!$J$31","v":0.28000000000000003},"kWh"]
[{"$f":"'ECM Summary'!$H$32","v":0},null,{"$f":"'ECM Summary'!$J$32","v":0},{"$f":"'ECM Summary'!$K$32","v":{"$error":"#N/A"}}]
[]
["Fossil Fuel",null,{"$f":"'Project Info'!C21","v":0}]
["Fuel Conversion",null,{"$f":"LOOKUP(C27,'Project Info'!X102:X104,'Project Info'!Z102:Z104)","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,"BIN Model Hours Based on Project/Facility Parameters (Project Info Tab)"]
[null,null,null,null,null,null,"Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A44","v":100},{"$f":"'Project Info'!B44","v":105},{"$f":"'Project Info'!C44","v":102},{"$f":"'Project Info'!D44","v":76},{"$f":"'Project Info'!E44","v":40},{"$f":"'Project Info'!F44","v":0},{"$f":"'Project Info'!G44","v":0},{"$f":"'Project Info'!H44","v":0},{"$f":"'Project Info'!I44","v":0},{"$f":"'Project Info'!J44","v":0},{"$f":"'Project Info'!K44","v":0},{"$f":"'Project Info'!L44","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A45","v":95},{"$f":"'Project Info'!B45","v":100},{"$f":"'Project Info'!C45","v":95.219272727272724},{"$f":"'Project Info'!D45","v":74.534025272781079},{"$f":"'Project Info'!E45","v":37.923296058061368},{"$f":"'Project Info'!F45","v":0},{"$f":"'Project Info'!G45","v":0},{"$f":"'Project Info'!H45","v":0},{"$f":"'Project Info'!I45","v":0},{"$f":"'Project Info'!J45","v":0},{"$f":"'Project Info'!K45","v":0},{"$f":"'Project Info'!L45","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A46","v":90},{"$f":"'Project Info'!B46","v":95},{"$f":"'Project Info'!C46","v":92.016049160256074},{"$f":"'Project Info'!D46","v":72.911561930607689},{"$f":"'Project Info'!E46","v":36.467095439351091},{"$f":"'Project Info'!F46","v":0},{"$f":"'Project Info'!G46","v":0},{"$f":"'Project Info'!H46","v":0},{"$f":"'Project Info'!I46","v":0},{"$f":"'Project Info'!J46","v":0},{"$f":"'Project Info'!K46","v":0},{"$f":"'Project Info'!L46","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A47","v":85},{"$f":"'Project Info'!B47","v":90},{"$f":"'Project Info'!C47","v":87.457811360655285},{"$f":"'Project Info'!D47","v":70.80538329449476},{"$f":"'Project Info'!E47","v":34.679413213566804},{"$f":"'Project Info'!F47","v":0},{"$f":"'Project Info'!G47","v":0},{"$f":"'Project Info'!H47","v":0},{"$f":"'Project Info'!I47","v":0},{"$f":"'Project Info'!J47","v":0},{"$f":"'Project Info'!K47","v":0},{"$f":"'Project Info'!L47","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A48","v":80},{"$f":"'Project Info'!B48","v":85},{"$f":"'Project Info'!C48","v":82.136788830239965},{"$f":"'Project Info'!D48","v":67.872393622439333},{"$f":"'Project Info'!E48","v":32.296248223809314},{"$f":"'Project Info'!F48","v":0},{"$f":"'Project Info'!G48","v":0},{"$f":"'Project Info'!H48","v":0},{"$f":"'Project Info'!I48","v":0},{"$f":"'Project Info'!J48","v":0},{"$f":"'Project Info'!K48","v":0},{"$f":"'Project Info'!L48","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A49","v":75},{"$f":"'Project Info'!B49","v":80},{"$f":"'Project Info'!C49","v":76.988400157585886},{"$f":"'Project Info'!D49","v":65.129261896908645},{"$f":"'Project Info'!E49","v":30.190476812806729},{"$f":"'Project Info'!F49","v":0},{"$f":"'Project Info'!G49","v":0},{"$f":"'Project Info'!H49","v":0},{"$f":"'Project Info'!I49","v":0},{"$f":"'Project Info'!J49","v":0},{"$f":"'Project Info'!K49","v":0},{"$f":"'Project Info'!L49","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A50","v":70},{"$f":"'Project Info'!B50","v":75},{"$f":"'Project Info'!C50","v":72.457982050814195},{"$f":"'Project Info'!D50","v":63.604425012889301},{"$f":"'Project Info'!E50","v":29.088683095945193},{"$f":"'Project Info'!F50","v":0},{"$f":"'Project Info'!G50","v":0},{"$f":"'Project Info'!H50","v":0},{"$f":"'Project Info'!I50","v":0},{"$f":"'Project Info'!J50","v":0},{"$f":"'Project Info'!K50","v":0},{"$f":"'Project Info'!L50","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A51","v":65},{"$f":"'Project Info'!B51","v":70},{"$f":"'Project Info'!C51","v":67.815831070966169},{"$f":"'Project Info'!D51","v":61.631331368130574},{"$f":"'Project Info'!E51","v":27.661514889731574},{"$f":"'Project Info'!F51","v":0},{"$f":"'Project Info'!G51","v":0},{"$f":"'Project Info'!H51","v":0},{"$f":"'Project Info'!I51","v":0},{"$f":"'Project Info'!J51","v":0},{"$f":"'Project Info'!K51","v":0},{"$f":"'Project Info'!L51","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A52","v":60},{"$f":"'Project Info'!B52","v":65},{"$f":"'Project Info'!C52","v":62.535961472271332},{"$f":"'Project Info'!D52","v":57.135476922863582},{"$f":"'Project Info'!E52","v":24.623037157728302},{"$f":"'Project Info'!F52","v":0},{"$f":"'Project Info'!G52","v":0},{"$f":"'Project Info'!H52","v":0},{"$f":"'Project Info'!I52","v":0},{"$f":"'Project Info'!J52","v":0},{"$f":"'Project Info'!K52","v":0},{"$f":"'Project Info'!L52","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A53","v":55},{"$f":"'Project Info'!B53","v":60},{"$f":"'Project Info'!C53","v":57.125792270740902},{"$f":"'Project Info'!D53","v":52.596971157053673},{"$f":"'Project Info'!E53","v":21.818001539159841},{"$f":"'Project Info'!F53","v":0},{"$f":"'Project Info'!G53","v":0},{"$f":"'Project Info'!H53","v":0},{"$f":"'Project Info'!I53","v":0},{"$f":"'Project Info'!J53","v":0},{"$f":"'Project Info'!K53","v":0},{"$f":"'Project Info'!L53","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A54","v":50},{"$f":"'Project Info'!B54","v":55},{"$f":"'Project Info'!C54","v":52.235698854337961},{"$f":"'Project Info'!D54","v":48.022768090099298},{"$f":"'Project Info'!E54","v":19.246640192796217},{"$f":"'Project Info'!F54","v":0},{"$f":"'Project Info'!G54","v":0},{"$f":"'Project Info'!H54","v":0},{"$f":"'Project Info'!I54","v":0},{"$f":"'Project Info'!J54","v":0},{"$f":"'Project Info'!K54","v":0},{"$f":"'Project Info'!L54","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A55","v":45},{"$f":"'Project Info'!B55","v":50},{"$f":"'Project Info'!C55","v":47.459170258371508},{"$f":"'Project Info'!D55","v":43.465397050422162},{"$f":"'Project Info'!E55","v":16.894183241713304},{"$f":"'Project Info'!F55","v":0},{"$f":"'Project Info'!G55","v":0},{"$f":"'Project Info'!H55","v":0},{"$f":"'Project Info'!I55","v":0},{"$f":"'Project Info'!J55","v":0},{"$f":"'Project Info'!K55","v":0},{"$f":"'Project Info'!L55","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A56","v":40},{"$f":"'Project Info'!B56","v":45},{"$f":"'Project Info'!C56","v":42.677030404888129},{"$f":"'Project Info'!D56","v":38.812544504634097},{"$f":"'Project Info'!E56","v":14.690265649465921},{"$f":"'Project Info'!F56","v":0},{"$f":"'Project Info'!G56","v":0},{"$f":"'Project Info'!H56","v":0},{"$f":"'Project Info'!I56","v":0},{"$f":"'Project Info'!J56","v":0},{"$f":"'Project Info'!K56","v":0},{"$f":"'Project Info'!L56","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A57","v":35},{"$f":"'Project Info'!B57","v":40},{"$f":"'Project Info'!C57","v":37.333046773755832},{"$f":"'Project Info'!D57","v":33.904706919479686},{"$f":"'Project Info'!E57","v":12.53841602318813},{"$f":"'Project Info'!F57","v":0},{"$f":"'Project Info'!G57","v":0},{"$f":"'Project Info'!H57","v":0},{"$f":"'Project Info'!I57","v":0},{"$f":"'Project Info'!J57","v":0},{"$f":"'Project Info'!K57","v":0},{"$f":"'Project Info'!L57","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A58","v":30},{"$f":"'Project Info'!B58","v":35},{"$f":"'Project Info'!C58","v":32.638179845662044},{"$f":"'Project Info'!D58","v":29.547170928664851},{"$f":"'Project Info'!E58","v":10.728972818165861},{"$f":"'Project Info'!F58","v":0},{"$f":"'Project Info'!G58","v":0},{"$f":"'Project Info'!H58","v":0},{"$f":"'Project Info'!I58","v":0},{"$f":"'Project Info'!J58","v":0},{"$f":"'Project Info'!K58","v":0},{"$f":"'Project Info'!L58","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A59","v":25},{"$f":"'Project Info'!B59","v":30},{"$f":"'Project Info'!C59","v":27.529264646850947},{"$f":"'Project Info'!D59","v":24.652717392657845},{"$f":"'Project Info'!E59","v":8.8041305482613303},{"$f":"'Project Info'!F59","v":0},{"$f":"'Project Info'!G59","v":0},{"$f":"'Project Info'!H59","v":0},{"$f":"'Project Info'!I59","v":0},{"$f":"'Project Info'!J59","v":0},{"$f":"'Project Info'!K59","v":0},{"$f":"'Project Info'!L59","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A60","v":20},{"$f":"'Project Info'!B60","v":25},{"$f":"'Project Info'!C60","v":22.998111483544687},{"$f":"'Project Info'!D60","v":20.383306659827422},{"$f":"'Project Info'!E60","v":7.246164547543378},{"$f":"'Project Info'!F60","v":0},{"$f":"'Project Info'!G60","v":0},{"$f":"'Project Info'!H60","v":0},{"$f":"'Project Info'!I60","v":0},{"$f":"'Project Info'!J60","v":0},{"$f":"'Project Info'!K60","v":0},{"$f":"'Project Info'!L60","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A61","v":15},{"$f":"'Project Info'!B61","v":20},{"$f":"'Project Info'!C61","v":17.808510327474309},{"$f":"'Project Info'!D61","v":15.420865796304254},{"$f":"'Project Info'!E61","v":5.5490484131518292},{"$f":"'Project Info'!F61","v":0},{"$f":"'Project Info'!G61","v":0},{"$f":"'Project Info'!H61","v":0},{"$f":"'Project Info'!I61","v":0},{"$f":"'Project Info'!J61","v":0},{"$f":"'Project Info'!K61","v":0},{"$f":"'Project Info'!L61","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A62","v":10},{"$f":"'Project Info'!B62","v":15},{"$f":"'Project Info'!C62","v":12.269931130346862},{"$f":"'Project Info'!D62","v":10.318264913023604},{"$f":"'Project Info'!E62","v":3.9082824916941998},{"$f":"'Project Info'!F62","v":0},{"$f":"'Project Info'!G62","v":0},{"$f":"'Project Info'!H62","v":0},{"$f":"'Project Info'!I62","v":0},{"$f":"'Project Info'!J62","v":0},{"$f":"'Project Info'!K62","v":0},{"$f":"'Project Info'!L62","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A63","v":5},{"$f":"'Project Info'!B63","v":10},{"$f":"'Project Info'!C63","v":7.3137581369917548},{"$f":"'Project Info'!D63","v":5.7052382449247707},{"$f":"'Project Info'!E63","v":2.5019418419888937},{"$f":"'Project Info'!F63","v":0},{"$f":"'Project Info'!G63","v":0},{"$f":"'Project Info'!H63","v":0},{"$f":"'Project Info'!I63","v":0},{"$f":"'Project Info'!J63","v":0},{"$f":"'Project Info'!K63","v":0},{"$f":"'Project Info'!L63","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A64","v":0},{"$f":"'Project Info'!B64","v":5},{"$f":"'Project Info'!C64","v":2.6119461836144886},{"$f":"'Project Info'!D64","v":1.2699770062067783},{"$f":"'Project Info'!E64","v":1.2046477897733283},{"$f":"'Project Info'!F64","v":0},{"$f":"'Project Info'!G64","v":0},{"$f":"'Project Info'!H64","v":0},{"$f":"'Project Info'!I64","v":0},{"$f":"'Project Info'!J64","v":0},{"$f":"'Project Info'!K64","v":0},{"$f":"'Project Info'!L64","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A65","v":-5},{"$f":"'Project Info'!B65","v":0},{"$f":"'Project Info'!C65","v":-1.6731398516793925},{"$f":"'Project Info'!D65","v":-2.7083318773557807},{"$f":"'Project Info'!E65","v":7.9391832815876459E-2},{"$f":"'Project Info'!F65","v":0},{"$f":"'Project Info'!G65","v":0},{"$f":"'Project Info'!H65","v":0},{"$f":"'Project Info'!I65","v":0},{"$f":"'Project Info'!J65","v":0},{"$f":"'Project Info'!K65","v":0},{"$f":"'Project Info'!L65","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A66","v":-10},{"$f":"'Project Info'!B66","v":-5},{"$f":"'Project Info'!C66","v":-6.5729865085377277},{"$f":"'Project Info'!D66","v":-7.2465935998252222},{"$f":"'Project Info'!E66","v":-1.168423365310433},{"$f":"'Project Info'!F66","v":0},{"$f":"'Project Info'!G66","v":0},{"$f":"'Project Info'!H66","v":0},{"$f":"'Project Info'!I66","v":0},{"$f":"'Project Info'!J66","v":0},{"$f":"'Project Info'!K66","v":0},{"$f":"'Project Info'!L66","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A67","v":-15},{"$f":"'Project Info'!B67","v":-10},{"$f":"'Project Info'!C67","v":-15.32570353422995},{"$f":"'Project Info'!D67","v":-15.707838211108999},{"$f":"'Project Info'!E67","v":-3.4051318156661381},{"$f":"'Project Info'!F67","v":0},{"$f":"'Project Info'!G67","v":0},{"$f":"'Project Info'!H67","v":0},{"$f":"'Project Info'!I67","v":0},{"$f":"'Project Info'!J67","v":0},{"$f":"'Project Info'!K67","v":0},{"$f":"'Project Info'!L67","v":0}]
[]
[]
[null,null,null,null,null,null,"Unoccupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A74","v":100},{"$f":"'Project Info'!B74","v":105},{"$f":"'Project Info'!C74","v":102},{"$f":"'Project Info'!D74","v":76},{"$f":"'Project Info'!E74","v":40},{"$f":"'Project Info'!F74","v":0},{"$f":"'Project Info'!G74","v":0},{"$f":"'Project Info'!H74","v":0},{"$f":"'Project Info'!I74","v":0},{"$f":"'Project Info'!J74","v":0},{"$f":"'Project Info'!K74","v":0},{"$f":"'Project Info'!L74","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A75","v":95},{"$f":"'Project Info'!B75","v":100},{"$f":"'Project Info'!C75","v":95.219272727272724},{"$f":"'Project Info'!D75","v":74.534025272781079},{"$f":"'Project Info'!E75","v":37.923296058061368},{"$f":"'Project Info'!F75","v":0},{"$f":"'Project Info'!G75","v":0},{"$f":"'Project Info'!H75","v":0},{"$f":"'Project Info'!I75","v":0},{"$f":"'Project Info'!J75","v":0},{"$f":"'Project Info'!K75","v":0},{"$f":"'Project Info'!L75","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A76","v":90},{"$f":"'Project Info'!B76","v":95},{"$f":"'Project Info'!C76","v":92.016049160256074},{"$f":"'Project Info'!D76","v":72.911561930607689},{"$f":"'Project Info'!E76","v":36.467095439351091},{"$f":"'Project Info'!F76","v":0},{"$f":"'Project Info'!G76","v":0},{"$f":"'Project Info'!H76","v":0},{"$f":"'Project Info'!I76","v":0},{"$f":"'Project Info'!J76","v":0},{"$f":"'Project Info'!K76","v":0},{"$f":"'Project Info'!L76","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A77","v":85},{"$f":"'Project Info'!B77","v":90},{"$f":"'Project Info'!C77","v":87.457811360655285},{"$f":"'Project Info'!D77","v":70.80538329449476},{"$f":"'Project Info'!E77","v":34.679413213566804},{"$f":"'Project Info'!F77","v":0},{"$f":"'Project Info'!G77","v":0},{"$f":"'Project Info'!H77","v":0},{"$f":"'Project Info'!I77","v":0},{"$f":"'Project Info'!J77","v":0},{"$f":"'Project Info'!K77","v":0},{"$f":"'Project Info'!L77","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A78","v":80},{"$f":"'Project Info'!B78","v":85},{"$f":"'Project Info'!C78","v":82.136788830239965},{"$f":"'Project Info'!D78","v":67.872393622439333},{"$f":"'Project Info'!E78","v":32.296248223809314},{"$f":"'Project Info'!F78","v":0},{"$f":"'Project Info'!G78","v":0},{"$f":"'Project Info'!H78","v":0},{"$f":"'Project Info'!I78","v":0},{"$f":"'Project Info'!J78","v":0},{"$f":"'Project Info'!K78","v":0},{"$f":"'Project Info'!L78","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A79","v":75},{"$f":"'Project Info'!B79","v":80},{"$f":"'Project Info'!C79","v":76.988400157585886},{"$f":"'Project Info'!D79","v":65.129261896908645},{"$f":"'Project Info'!E79","v":30.190476812806729},{"$f":"'Project Info'!F79","v":0},{"$f":"'Project Info'!G79","v":0},{"$f":"'Project Info'!H79","v":0},{"$f":"'Project Info'!I79","v":0},{"$f":"'Project Info'!J79","v":0},{"$f":"'Project Info'!K79","v":0},{"$f":"'Project Info'!L79","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A80","v":70},{"$f":"'Project Info'!B80","v":75},{"$f":"'Project Info'!C80","v":72.457982050814195},{"$f":"'Project Info'!D80","v":63.604425012889301},{"$f":"'Project Info'!E80","v":29.088683095945193},{"$f":"'Project Info'!F80","v":0},{"$f":"'Project Info'!G80","v":0},{"$f":"'Project Info'!H80","v":0},{"$f":"'Project Info'!I80","v":0},{"$f":"'Project Info'!J80","v":0},{"$f":"'Project Info'!K80","v":0},{"$f":"'Project Info'!L80","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A81","v":65},{"$f":"'Project Info'!B81","v":70},{"$f":"'Project Info'!C81","v":67.815831070966169},{"$f":"'Project Info'!D81","v":61.631331368130574},{"$f":"'Project Info'!E81","v":27.661514889731574},{"$f":"'Project Info'!F81","v":0},{"$f":"'Project Info'!G81","v":0},{"$f":"'Project Info'!H81","v":0},{"$f":"'Project Info'!I81","v":0},{"$f":"'Project Info'!J81","v":0},{"$f":"'Project Info'!K81","v":0},{"$f":"'Project Info'!L81","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A82","v":60},{"$f":"'Project Info'!B82","v":65},{"$f":"'Project Info'!C82","v":62.535961472271332},{"$f":"'Project Info'!D82","v":57.135476922863582},{"$f":"'Project Info'!E82","v":24.623037157728302},{"$f":"'Project Info'!F82","v":0},{"$f":"'Project Info'!G82","v":0},{"$f":"'Project Info'!H82","v":0},{"$f":"'Project Info'!I82","v":0},{"$f":"'Project Info'!J82","v":0},{"$f":"'Project Info'!K82","v":0},{"$f":"'Project Info'!L82","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A83","v":55},{"$f":"'Project Info'!B83","v":60},{"$f":"'Project Info'!C83","v":57.125792270740902},{"$f":"'Project Info'!D83","v":52.596971157053673},{"$f":"'Project Info'!E83","v":21.818001539159841},{"$f":"'Project Info'!F83","v":0},{"$f":"'Project Info'!G83","v":0},{"$f":"'Project Info'!H83","v":0},{"$f":"'Project Info'!I83","v":0},{"$f":"'Project Info'!J83","v":0},{"$f":"'Project Info'!K83","v":0},{"$f":"'Project Info'!L83","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A84","v":50},{"$f":"'Project Info'!B84","v":55},{"$f":"'Project Info'!C84","v":52.235698854337961},{"$f":"'Project Info'!D84","v":48.022768090099298},{"$f":"'Project Info'!E84","v":19.246640192796217},{"$f":"'Project Info'!F84","v":0},{"$f":"'Project Info'!G84","v":0},{"$f":"'Project Info'!H84","v":0},{"$f":"'Project Info'!I84","v":0},{"$f":"'Project Info'!J84","v":0},{"$f":"'Project Info'!K84","v":0},{"$f":"'Project Info'!L84","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A85","v":45},{"$f":"'Project Info'!B85","v":50},{"$f":"'Project Info'!C85","v":47.459170258371508},{"$f":"'Project Info'!D85","v":43.465397050422162},{"$f":"'Project Info'!E85","v":16.894183241713304},{"$f":"'Project Info'!F85","v":0},{"$f":"'Project Info'!G85","v":0},{"$f":"'Project Info'!H85","v":0},{"$f":"'Project Info'!I85","v":0},{"$f":"'Project Info'!J85","v":0},{"$f":"'Project Info'!K85","v":0},{"$f":"'Project Info'!L85","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A86","v":40},{"$f":"'Project Info'!B86","v":45},{"$f":"'Project Info'!C86","v":42.677030404888129},{"$f":"'Project Info'!D86","v":38.812544504634097},{"$f":"'Project Info'!E86","v":14.690265649465921},{"$f":"'Project Info'!F86","v":0},{"$f":"'Project Info'!G86","v":0},{"$f":"'Project Info'!H86","v":0},{"$f":"'Project Info'!I86","v":0},{"$f":"'Project Info'!J86","v":0},{"$f":"'Project Info'!K86","v":0},{"$f":"'Project Info'!L86","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A87","v":35},{"$f":"'Project Info'!B87","v":40},{"$f":"'Project Info'!C87","v":37.333046773755832},{"$f":"'Project Info'!D87","v":33.904706919479686},{"$f":"'Project Info'!E87","v":12.53841602318813},{"$f":"'Project Info'!F87","v":0},{"$f":"'Project Info'!G87","v":0},{"$f":"'Project Info'!H87","v":0},{"$f":"'Project Info'!I87","v":0},{"$f":"'Project Info'!J87","v":0},{"$f":"'Project Info'!K87","v":0},{"$f":"'Project Info'!L87","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A88","v":30},{"$f":"'Project Info'!B88","v":35},{"$f":"'Project Info'!C88","v":32.638179845662044},{"$f":"'Project Info'!D88","v":29.547170928664851},{"$f":"'Project Info'!E88","v":10.728972818165861},{"$f":"'Project Info'!F88","v":0},{"$f":"'Project Info'!G88","v":0},{"$f":"'Project Info'!H88","v":0},{"$f":"'Project Info'!I88","v":0},{"$f":"'Project Info'!J88","v":0},{"$f":"'Project Info'!K88","v":0},{"$f":"'Project Info'!L88","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A89","v":25},{"$f":"'Project Info'!B89","v":30},{"$f":"'Project Info'!C89","v":27.529264646850947},{"$f":"'Project Info'!D89","v":24.652717392657845},{"$f":"'Project Info'!E89","v":8.8041305482613303},{"$f":"'Project Info'!F89","v":0},{"$f":"'Project Info'!G89","v":0},{"$f":"'Project Info'!H89","v":0},{"$f":"'Project Info'!I89","v":0},{"$f":"'Project Info'!J89","v":0},{"$f":"'Project Info'!K89","v":0},{"$f":"'Project Info'!L89","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A90","v":20},{"$f":"'Project Info'!B90","v":25},{"$f":"'Project Info'!C90","v":22.998111483544687},{"$f":"'Project Info'!D90","v":20.383306659827422},{"$f":"'Project Info'!E90","v":7.246164547543378},{"$f":"'Project Info'!F90","v":0},{"$f":"'Project Info'!G90","v":0},{"$f":"'Project Info'!H90","v":0},{"$f":"'Project Info'!I90","v":0},{"$f":"'Project Info'!J90","v":0},{"$f":"'Project Info'!K90","v":0},{"$f":"'Project Info'!L90","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A91","v":15},{"$f":"'Project Info'!B91","v":20},{"$f":"'Project Info'!C91","v":17.808510327474309},{"$f":"'Project Info'!D91","v":15.420865796304254},{"$f":"'Project Info'!E91","v":5.5490484131518292},{"$f":"'Project Info'!F91","v":0},{"$f":"'Project Info'!G91","v":0},{"$f":"'Project Info'!H91","v":0},{"$f":"'Project Info'!I91","v":0},{"$f":"'Project Info'!J91","v":0},{"$f":"'Project Info'!K91","v":0},{"$f":"'Project Info'!L91","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A92","v":10},{"$f":"'Project Info'!B92","v":15},{"$f":"'Project Info'!C92","v":12.269931130346862},{"$f":"'Project Info'!D92","v":10.318264913023604},{"$f":"'Project Info'!E92","v":3.9082824916941998},{"$f":"'Project Info'!F92","v":0},{"$f":"'Project Info'!G92","v":0},{"$f":"'Project Info'!H92","v":0},{"$f":"'Project Info'!I92","v":0},{"$f":"'Project Info'!J92","v":0},{"$f":"'Project Info'!K92","v":0},{"$f":"'Project Info'!L92","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A93","v":5},{"$f":"'Project Info'!B93","v":10},{"$f":"'Project Info'!C93","v":7.3137581369917548},{"$f":"'Project Info'!D93","v":5.7052382449247707},{"$f":"'Project Info'!E93","v":2.5019418419888937},{"$f":"'Project Info'!F93","v":0},{"$f":"'Project Info'!G93","v":0},{"$f":"'Project Info'!H93","v":0},{"$f":"'Project Info'!I93","v":0},{"$f":"'Project Info'!J93","v":0},{"$f":"'Project Info'!K93","v":0},{"$f":"'Project Info'!L93","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A94","v":0},{"$f":"'Project Info'!B94","v":5},{"$f":"'Project Info'!C94","v":2.6119461836144886},{"$f":"'Project Info'!D94","v":1.2699770062067783},{"$f":"'Project Info'!E94","v":1.2046477897733283},{"$f":"'Project Info'!F94","v":8760},{"$f":"'Project Info'!G94","v":2672},{"$f":"'Project Info'!H94","v":3160},{"$f":"'Project Info'!I94","v":1344},{"$f":"'Project Info'!J94","v":1584},{"$f":"'Project Info'!K94","v":88},{"$f":"'Project Info'!L94","v":264}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A95","v":-5},{"$f":"'Project Info'!B95","v":0},{"$f":"'Project Info'!C95","v":-1.6731398516793925},{"$f":"'Project Info'!D95","v":-2.7083318773557807},{"$f":"'Project Info'!E95","v":7.9391832815876459E-2},{"$f":"'Project Info'!F95","v":0},{"$f":"'Project Info'!G95","v":0},{"$f":"'Project Info'!H95","v":0},{"$f":"'Project Info'!I95","v":0},{"$f":"'Project Info'!J95","v":0},{"$f":"'Project Info'!K95","v":0},{"$f":"'Project Info'!L95","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A96","v":-10},{"$f":"'Project Info'!B96","v":-5},{"$f":"'Project Info'!C96","v":-6.5729865085377277},{"$f":"'Project Info'!D96","v":-7.2465935998252222},{"$f":"'Project Info'!E96","v":-1.168423365310433},{"$f":"'Project Info'!F96","v":0},{"$f":"'Project Info'!G96","v":0},{"$f":"'Project Info'!H96","v":0},{"$f":"'Project Info'!I96","v":0},{"$f":"'Project Info'!J96","v":0},{"$f":"'Project Info'!K96","v":0},{"$f":"'Project Info'!L96","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A97","v":-15},{"$f":"'Project Info'!B97","v":-10},{"$f":"'Project Info'!C97","v":-15.32570353422995},{"$f":"'Project Info'!D97","v":-15.707838211108999},{"$f":"'Project Info'!E97","v":-3.4051318156661381},{"$f":"'Project Info'!F97","v":0},{"$f":"'Project Info'!G97","v":0},{"$f":"'Project Info'!H97","v":0},{"$f":"'Project Info'!I97","v":0},{"$f":"'Project Info'!J97","v":0},{"$f":"'Project Info'!K97","v":0},{"$f":"'Project Info'!L97","v":0}]

{"sheet":"User Defined 2","index":26,"n_rows":87,"n_cols":18,"rows_kept":87,"cut":false,"hidden":true,"merged":[[3,10,8,19],[11,10,17,19],[20,10,26,19],[17,7,17,8],[18,7,18,8],[16,7,16,8]]}
["Savings Summary",null,null,null,null,"Measure Summary",null,null,null,null,"Measure Title"]
["Annual kWh Savings",null,null,null,null,null,null,"Value","Unit"]
["% On Peak",null,null,null,null,"Annual Electric Savings",null,{"$f":"D2","v":0},"kWh",null,"Measure Description"]
["Max kW",null,null,null,null,"Annual Fuel Savings",null,{"$f":"D7*C28","v":{"$error":"#N/A"}},{"$f":"D20","v":{"$error":"#N/A"}}]
["Summer kW",null,null,null,null,"Incremental Cost",null,{"$f":"D8","v":0},"$"]
["Winter kW",null,null,null,null,"Estimated Custom Incentive",null,{"$f":"IF(AND($C$24>=0,$C$25>=0),MAX(0,H3)*C24+MAX(0,H4)*C25,\"TBD\")","v":{"$error":"#N/A"}},"$"]
["Annual Fuel Savings (MMBtu)",null,null,null,null,"Override Incentive (Optional)",null,null,"$"]
["Incremental Cost",null,null,null,null,"Custom Payback",null,{"$f":"H5/(H3*$C$19+H4*$C$20)","v":{"$error":"#N/A"}},"years"]
[null,null,null,null,null,"Project Information Summary"]
["kWh Savings by Peak Period",null,null,null,null,null,"STATE (MA or RI)",{"$f":"'Project Info'!C15","v":"NH"}]
["Winter","Winter","Summer","Summer",null,null,"Program Year",{"$f":"'Project Info'!C19","v":0},null,null,"Base Case Description"]
["On-Peak","Off-Peak","On-Peak","Off-Peak",null,null,"Code IECC Version",{"$f":"MID('Project Info'!C20,1,4)","v":"2018"}]
["kWh","kWh","kWh","kWh",null,null,"Electric PA",{"$f":"'Project Info'!F3","v":0}]
[null,null,null,null,null,null,"Gas PA",{"$f":"'Project Info'!I3","v":0}]
[{"$f":"ROUND(IF(A14<=0,0,A14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(B14<=0,0,B14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(C14<=0,0,C14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"IF(SUM(A14:D14)=0,0,1-SUM(A15:C15))","v":0}]
[null,null,null,null,null,"Information For BCR Inputs"]
["Utility Rates",null,null,null,null,"Program Type"]
[null,null,"Rate","Unit",null,"Fuel Savings Type"]
["Electric",null,{"$f":"'ECM Summary'!$E$31","v":0.1593},"kWh",null,"Measure Type"]
[{"$f":"'ECM Summary'!$C$32","v":0},null,{"$f":"'ECM Summary'!$E$32","v":{"$error":"#N/A"}},{"$f":"'ECM Summary'!$F$32","v":{"$error":"#N/A"}},null,"Measure Life",null,{"$f":"LOOKUP($H$19,'PA Impacts'!$G$84:$G$118,'PA Impacts'!$H$84:$H$118)","v":{"$error":"#N/A"}},null,null,"Proposed Case Description"]
[]
["Custom Incentive Rates"]
[null,null,"Rate","Unit"]
["Electric",null,{"$f":"'ECM Summary'!$J$31","v":0.28000000000000003},"kWh"]
[{"$f":"'ECM Summary'!$H$32","v":0},null,{"$f":"'ECM Summary'!$J$32","v":0},{"$f":"'ECM Summary'!$K$32","v":{"$error":"#N/A"}}]
[]
["Fossil Fuel",null,{"$f":"'Project Info'!C21","v":0}]
["Fuel Conversion",null,{"$f":"LOOKUP(C27,'Project Info'!X102:X104,'Project Info'!Z102:Z104)","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,"BIN Model Hours Based on Project/Facility Parameters (Project Info Tab)"]
[null,null,null,null,null,null,"Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A44","v":100},{"$f":"'Project Info'!B44","v":105},{"$f":"'Project Info'!C44","v":102},{"$f":"'Project Info'!D44","v":76},{"$f":"'Project Info'!E44","v":40},{"$f":"'Project Info'!F44","v":0},{"$f":"'Project Info'!G44","v":0},{"$f":"'Project Info'!H44","v":0},{"$f":"'Project Info'!I44","v":0},{"$f":"'Project Info'!J44","v":0},{"$f":"'Project Info'!K44","v":0},{"$f":"'Project Info'!L44","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A45","v":95},{"$f":"'Project Info'!B45","v":100},{"$f":"'Project Info'!C45","v":95.219272727272724},{"$f":"'Project Info'!D45","v":74.534025272781079},{"$f":"'Project Info'!E45","v":37.923296058061368},{"$f":"'Project Info'!F45","v":0},{"$f":"'Project Info'!G45","v":0},{"$f":"'Project Info'!H45","v":0},{"$f":"'Project Info'!I45","v":0},{"$f":"'Project Info'!J45","v":0},{"$f":"'Project Info'!K45","v":0},{"$f":"'Project Info'!L45","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A46","v":90},{"$f":"'Project Info'!B46","v":95},{"$f":"'Project Info'!C46","v":92.016049160256074},{"$f":"'Project Info'!D46","v":72.911561930607689},{"$f":"'Project Info'!E46","v":36.467095439351091},{"$f":"'Project Info'!F46","v":0},{"$f":"'Project Info'!G46","v":0},{"$f":"'Project Info'!H46","v":0},{"$f":"'Project Info'!I46","v":0},{"$f":"'Project Info'!J46","v":0},{"$f":"'Project Info'!K46","v":0},{"$f":"'Project Info'!L46","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A47","v":85},{"$f":"'Project Info'!B47","v":90},{"$f":"'Project Info'!C47","v":87.457811360655285},{"$f":"'Project Info'!D47","v":70.80538329449476},{"$f":"'Project Info'!E47","v":34.679413213566804},{"$f":"'Project Info'!F47","v":0},{"$f":"'Project Info'!G47","v":0},{"$f":"'Project Info'!H47","v":0},{"$f":"'Project Info'!I47","v":0},{"$f":"'Project Info'!J47","v":0},{"$f":"'Project Info'!K47","v":0},{"$f":"'Project Info'!L47","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A48","v":80},{"$f":"'Project Info'!B48","v":85},{"$f":"'Project Info'!C48","v":82.136788830239965},{"$f":"'Project Info'!D48","v":67.872393622439333},{"$f":"'Project Info'!E48","v":32.296248223809314},{"$f":"'Project Info'!F48","v":0},{"$f":"'Project Info'!G48","v":0},{"$f":"'Project Info'!H48","v":0},{"$f":"'Project Info'!I48","v":0},{"$f":"'Project Info'!J48","v":0},{"$f":"'Project Info'!K48","v":0},{"$f":"'Project Info'!L48","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A49","v":75},{"$f":"'Project Info'!B49","v":80},{"$f":"'Project Info'!C49","v":76.988400157585886},{"$f":"'Project Info'!D49","v":65.129261896908645},{"$f":"'Project Info'!E49","v":30.190476812806729},{"$f":"'Project Info'!F49","v":0},{"$f":"'Project Info'!G49","v":0},{"$f":"'Project Info'!H49","v":0},{"$f":"'Project Info'!I49","v":0},{"$f":"'Project Info'!J49","v":0},{"$f":"'Project Info'!K49","v":0},{"$f":"'Project Info'!L49","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A50","v":70},{"$f":"'Project Info'!B50","v":75},{"$f":"'Project Info'!C50","v":72.457982050814195},{"$f":"'Project Info'!D50","v":63.604425012889301},{"$f":"'Project Info'!E50","v":29.088683095945193},{"$f":"'Project Info'!F50","v":0},{"$f":"'Project Info'!G50","v":0},{"$f":"'Project Info'!H50","v":0},{"$f":"'Project Info'!I50","v":0},{"$f":"'Project Info'!J50","v":0},{"$f":"'Project Info'!K50","v":0},{"$f":"'Project Info'!L50","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A51","v":65},{"$f":"'Project Info'!B51","v":70},{"$f":"'Project Info'!C51","v":67.815831070966169},{"$f":"'Project Info'!D51","v":61.631331368130574},{"$f":"'Project Info'!E51","v":27.661514889731574},{"$f":"'Project Info'!F51","v":0},{"$f":"'Project Info'!G51","v":0},{"$f":"'Project Info'!H51","v":0},{"$f":"'Project Info'!I51","v":0},{"$f":"'Project Info'!J51","v":0},{"$f":"'Project Info'!K51","v":0},{"$f":"'Project Info'!L51","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A52","v":60},{"$f":"'Project Info'!B52","v":65},{"$f":"'Project Info'!C52","v":62.535961472271332},{"$f":"'Project Info'!D52","v":57.135476922863582},{"$f":"'Project Info'!E52","v":24.623037157728302},{"$f":"'Project Info'!F52","v":0},{"$f":"'Project Info'!G52","v":0},{"$f":"'Project Info'!H52","v":0},{"$f":"'Project Info'!I52","v":0},{"$f":"'Project Info'!J52","v":0},{"$f":"'Project Info'!K52","v":0},{"$f":"'Project Info'!L52","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A53","v":55},{"$f":"'Project Info'!B53","v":60},{"$f":"'Project Info'!C53","v":57.125792270740902},{"$f":"'Project Info'!D53","v":52.596971157053673},{"$f":"'Project Info'!E53","v":21.818001539159841},{"$f":"'Project Info'!F53","v":0},{"$f":"'Project Info'!G53","v":0},{"$f":"'Project Info'!H53","v":0},{"$f":"'Project Info'!I53","v":0},{"$f":"'Project Info'!J53","v":0},{"$f":"'Project Info'!K53","v":0},{"$f":"'Project Info'!L53","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A54","v":50},{"$f":"'Project Info'!B54","v":55},{"$f":"'Project Info'!C54","v":52.235698854337961},{"$f":"'Project Info'!D54","v":48.022768090099298},{"$f":"'Project Info'!E54","v":19.246640192796217},{"$f":"'Project Info'!F54","v":0},{"$f":"'Project Info'!G54","v":0},{"$f":"'Project Info'!H54","v":0},{"$f":"'Project Info'!I54","v":0},{"$f":"'Project Info'!J54","v":0},{"$f":"'Project Info'!K54","v":0},{"$f":"'Project Info'!L54","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A55","v":45},{"$f":"'Project Info'!B55","v":50},{"$f":"'Project Info'!C55","v":47.459170258371508},{"$f":"'Project Info'!D55","v":43.465397050422162},{"$f":"'Project Info'!E55","v":16.894183241713304},{"$f":"'Project Info'!F55","v":0},{"$f":"'Project Info'!G55","v":0},{"$f":"'Project Info'!H55","v":0},{"$f":"'Project Info'!I55","v":0},{"$f":"'Project Info'!J55","v":0},{"$f":"'Project Info'!K55","v":0},{"$f":"'Project Info'!L55","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A56","v":40},{"$f":"'Project Info'!B56","v":45},{"$f":"'Project Info'!C56","v":42.677030404888129},{"$f":"'Project Info'!D56","v":38.812544504634097},{"$f":"'Project Info'!E56","v":14.690265649465921},{"$f":"'Project Info'!F56","v":0},{"$f":"'Project Info'!G56","v":0},{"$f":"'Project Info'!H56","v":0},{"$f":"'Project Info'!I56","v":0},{"$f":"'Project Info'!J56","v":0},{"$f":"'Project Info'!K56","v":0},{"$f":"'Project Info'!L56","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A57","v":35},{"$f":"'Project Info'!B57","v":40},{"$f":"'Project Info'!C57","v":37.333046773755832},{"$f":"'Project Info'!D57","v":33.904706919479686},{"$f":"'Project Info'!E57","v":12.53841602318813},{"$f":"'Project Info'!F57","v":0},{"$f":"'Project Info'!G57","v":0},{"$f":"'Project Info'!H57","v":0},{"$f":"'Project Info'!I57","v":0},{"$f":"'Project Info'!J57","v":0},{"$f":"'Project Info'!K57","v":0},{"$f":"'Project Info'!L57","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A58","v":30},{"$f":"'Project Info'!B58","v":35},{"$f":"'Project Info'!C58","v":32.638179845662044},{"$f":"'Project Info'!D58","v":29.547170928664851},{"$f":"'Project Info'!E58","v":10.728972818165861},{"$f":"'Project Info'!F58","v":0},{"$f":"'Project Info'!G58","v":0},{"$f":"'Project Info'!H58","v":0},{"$f":"'Project Info'!I58","v":0},{"$f":"'Project Info'!J58","v":0},{"$f":"'Project Info'!K58","v":0},{"$f":"'Project Info'!L58","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A59","v":25},{"$f":"'Project Info'!B59","v":30},{"$f":"'Project Info'!C59","v":27.529264646850947},{"$f":"'Project Info'!D59","v":24.652717392657845},{"$f":"'Project Info'!E59","v":8.8041305482613303},{"$f":"'Project Info'!F59","v":0},{"$f":"'Project Info'!G59","v":0},{"$f":"'Project Info'!H59","v":0},{"$f":"'Project Info'!I59","v":0},{"$f":"'Project Info'!J59","v":0},{"$f":"'Project Info'!K59","v":0},{"$f":"'Project Info'!L59","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A60","v":20},{"$f":"'Project Info'!B60","v":25},{"$f":"'Project Info'!C60","v":22.998111483544687},{"$f":"'Project Info'!D60","v":20.383306659827422},{"$f":"'Project Info'!E60","v":7.246164547543378},{"$f":"'Project Info'!F60","v":0},{"$f":"'Project Info'!G60","v":0},{"$f":"'Project Info'!H60","v":0},{"$f":"'Project Info'!I60","v":0},{"$f":"'Project Info'!J60","v":0},{"$f":"'Project Info'!K60","v":0},{"$f":"'Project Info'!L60","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A61","v":15},{"$f":"'Project Info'!B61","v":20},{"$f":"'Project Info'!C61","v":17.808510327474309},{"$f":"'Project Info'!D61","v":15.420865796304254},{"$f":"'Project Info'!E61","v":5.5490484131518292},{"$f":"'Project Info'!F61","v":0},{"$f":"'Project Info'!G61","v":0},{"$f":"'Project Info'!H61","v":0},{"$f":"'Project Info'!I61","v":0},{"$f":"'Project Info'!J61","v":0},{"$f":"'Project Info'!K61","v":0},{"$f":"'Project Info'!L61","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A62","v":10},{"$f":"'Project Info'!B62","v":15},{"$f":"'Project Info'!C62","v":12.269931130346862},{"$f":"'Project Info'!D62","v":10.318264913023604},{"$f":"'Project Info'!E62","v":3.9082824916941998},{"$f":"'Project Info'!F62","v":0},{"$f":"'Project Info'!G62","v":0},{"$f":"'Project Info'!H62","v":0},{"$f":"'Project Info'!I62","v":0},{"$f":"'Project Info'!J62","v":0},{"$f":"'Project Info'!K62","v":0},{"$f":"'Project Info'!L62","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A63","v":5},{"$f":"'Project Info'!B63","v":10},{"$f":"'Project Info'!C63","v":7.3137581369917548},{"$f":"'Project Info'!D63","v":5.7052382449247707},{"$f":"'Project Info'!E63","v":2.5019418419888937},{"$f":"'Project Info'!F63","v":0},{"$f":"'Project Info'!G63","v":0},{"$f":"'Project Info'!H63","v":0},{"$f":"'Project Info'!I63","v":0},{"$f":"'Project Info'!J63","v":0},{"$f":"'Project Info'!K63","v":0},{"$f":"'Project Info'!L63","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A64","v":0},{"$f":"'Project Info'!B64","v":5},{"$f":"'Project Info'!C64","v":2.6119461836144886},{"$f":"'Project Info'!D64","v":1.2699770062067783},{"$f":"'Project Info'!E64","v":1.2046477897733283},{"$f":"'Project Info'!F64","v":0},{"$f":"'Project Info'!G64","v":0},{"$f":"'Project Info'!H64","v":0},{"$f":"'Project Info'!I64","v":0},{"$f":"'Project Info'!J64","v":0},{"$f":"'Project Info'!K64","v":0},{"$f":"'Project Info'!L64","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A65","v":-5},{"$f":"'Project Info'!B65","v":0},{"$f":"'Project Info'!C65","v":-1.6731398516793925},{"$f":"'Project Info'!D65","v":-2.7083318773557807},{"$f":"'Project Info'!E65","v":7.9391832815876459E-2},{"$f":"'Project Info'!F65","v":0},{"$f":"'Project Info'!G65","v":0},{"$f":"'Project Info'!H65","v":0},{"$f":"'Project Info'!I65","v":0},{"$f":"'Project Info'!J65","v":0},{"$f":"'Project Info'!K65","v":0},{"$f":"'Project Info'!L65","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A66","v":-10},{"$f":"'Project Info'!B66","v":-5},{"$f":"'Project Info'!C66","v":-6.5729865085377277},{"$f":"'Project Info'!D66","v":-7.2465935998252222},{"$f":"'Project Info'!E66","v":-1.168423365310433},{"$f":"'Project Info'!F66","v":0},{"$f":"'Project Info'!G66","v":0},{"$f":"'Project Info'!H66","v":0},{"$f":"'Project Info'!I66","v":0},{"$f":"'Project Info'!J66","v":0},{"$f":"'Project Info'!K66","v":0},{"$f":"'Project Info'!L66","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A67","v":-15},{"$f":"'Project Info'!B67","v":-10},{"$f":"'Project Info'!C67","v":-15.32570353422995},{"$f":"'Project Info'!D67","v":-15.707838211108999},{"$f":"'Project Info'!E67","v":-3.4051318156661381},{"$f":"'Project Info'!F67","v":0},{"$f":"'Project Info'!G67","v":0},{"$f":"'Project Info'!H67","v":0},{"$f":"'Project Info'!I67","v":0},{"$f":"'Project Info'!J67","v":0},{"$f":"'Project Info'!K67","v":0},{"$f":"'Project Info'!L67","v":0}]
[]
[]
[null,null,null,null,null,null,"Unoccupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A74","v":100},{"$f":"'Project Info'!B74","v":105},{"$f":"'Project Info'!C74","v":102},{"$f":"'Project Info'!D74","v":76},{"$f":"'Project Info'!E74","v":40},{"$f":"'Project Info'!F74","v":0},{"$f":"'Project Info'!G74","v":0},{"$f":"'Project Info'!H74","v":0},{"$f":"'Project Info'!I74","v":0},{"$f":"'Project Info'!J74","v":0},{"$f":"'Project Info'!K74","v":0},{"$f":"'Project Info'!L74","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A75","v":95},{"$f":"'Project Info'!B75","v":100},{"$f":"'Project Info'!C75","v":95.219272727272724},{"$f":"'Project Info'!D75","v":74.534025272781079},{"$f":"'Project Info'!E75","v":37.923296058061368},{"$f":"'Project Info'!F75","v":0},{"$f":"'Project Info'!G75","v":0},{"$f":"'Project Info'!H75","v":0},{"$f":"'Project Info'!I75","v":0},{"$f":"'Project Info'!J75","v":0},{"$f":"'Project Info'!K75","v":0},{"$f":"'Project Info'!L75","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A76","v":90},{"$f":"'Project Info'!B76","v":95},{"$f":"'Project Info'!C76","v":92.016049160256074},{"$f":"'Project Info'!D76","v":72.911561930607689},{"$f":"'Project Info'!E76","v":36.467095439351091},{"$f":"'Project Info'!F76","v":0},{"$f":"'Project Info'!G76","v":0},{"$f":"'Project Info'!H76","v":0},{"$f":"'Project Info'!I76","v":0},{"$f":"'Project Info'!J76","v":0},{"$f":"'Project Info'!K76","v":0},{"$f":"'Project Info'!L76","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A77","v":85},{"$f":"'Project Info'!B77","v":90},{"$f":"'Project Info'!C77","v":87.457811360655285},{"$f":"'Project Info'!D77","v":70.80538329449476},{"$f":"'Project Info'!E77","v":34.679413213566804},{"$f":"'Project Info'!F77","v":0},{"$f":"'Project Info'!G77","v":0},{"$f":"'Project Info'!H77","v":0},{"$f":"'Project Info'!I77","v":0},{"$f":"'Project Info'!J77","v":0},{"$f":"'Project Info'!K77","v":0},{"$f":"'Project Info'!L77","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A78","v":80},{"$f":"'Project Info'!B78","v":85},{"$f":"'Project Info'!C78","v":82.136788830239965},{"$f":"'Project Info'!D78","v":67.872393622439333},{"$f":"'Project Info'!E78","v":32.296248223809314},{"$f":"'Project Info'!F78","v":0},{"$f":"'Project Info'!G78","v":0},{"$f":"'Project Info'!H78","v":0},{"$f":"'Project Info'!I78","v":0},{"$f":"'Project Info'!J78","v":0},{"$f":"'Project Info'!K78","v":0},{"$f":"'Project Info'!L78","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A79","v":75},{"$f":"'Project Info'!B79","v":80},{"$f":"'Project Info'!C79","v":76.988400157585886},{"$f":"'Project Info'!D79","v":65.129261896908645},{"$f":"'Project Info'!E79","v":30.190476812806729},{"$f":"'Project Info'!F79","v":0},{"$f":"'Project Info'!G79","v":0},{"$f":"'Project Info'!H79","v":0},{"$f":"'Project Info'!I79","v":0},{"$f":"'Project Info'!J79","v":0},{"$f":"'Project Info'!K79","v":0},{"$f":"'Project Info'!L79","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A80","v":70},{"$f":"'Project Info'!B80","v":75},{"$f":"'Project Info'!C80","v":72.457982050814195},{"$f":"'Project Info'!D80","v":63.604425012889301},{"$f":"'Project Info'!E80","v":29.088683095945193},{"$f":"'Project Info'!F80","v":0},{"$f":"'Project Info'!G80","v":0},{"$f":"'Project Info'!H80","v":0},{"$f":"'Project Info'!I80","v":0},{"$f":"'Project Info'!J80","v":0},{"$f":"'Project Info'!K80","v":0},{"$f":"'Project Info'!L80","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A81","v":65},{"$f":"'Project Info'!B81","v":70},{"$f":"'Project Info'!C81","v":67.815831070966169},{"$f":"'Project Info'!D81","v":61.631331368130574},{"$f":"'Project Info'!E81","v":27.661514889731574},{"$f":"'Project Info'!F81","v":0},{"$f":"'Project Info'!G81","v":0},{"$f":"'Project Info'!H81","v":0},{"$f":"'Project Info'!I81","v":0},{"$f":"'Project Info'!J81","v":0},{"$f":"'Project Info'!K81","v":0},{"$f":"'Project Info'!L81","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A82","v":60},{"$f":"'Project Info'!B82","v":65},{"$f":"'Project Info'!C82","v":62.535961472271332},{"$f":"'Project Info'!D82","v":57.135476922863582},{"$f":"'Project Info'!E82","v":24.623037157728302},{"$f":"'Project Info'!F82","v":0},{"$f":"'Project Info'!G82","v":0},{"$f":"'Project Info'!H82","v":0},{"$f":"'Project Info'!I82","v":0},{"$f":"'Project Info'!J82","v":0},{"$f":"'Project Info'!K82","v":0},{"$f":"'Project Info'!L82","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A83","v":55},{"$f":"'Project Info'!B83","v":60},{"$f":"'Project Info'!C83","v":57.125792270740902},{"$f":"'Project Info'!D83","v":52.596971157053673},{"$f":"'Project Info'!E83","v":21.818001539159841},{"$f":"'Project Info'!F83","v":0},{"$f":"'Project Info'!G83","v":0},{"$f":"'Project Info'!H83","v":0},{"$f":"'Project Info'!I83","v":0},{"$f":"'Project Info'!J83","v":0},{"$f":"'Project Info'!K83","v":0},{"$f":"'Project Info'!L83","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A84","v":50},{"$f":"'Project Info'!B84","v":55},{"$f":"'Project Info'!C84","v":52.235698854337961},{"$f":"'Project Info'!D84","v":48.022768090099298},{"$f":"'Project Info'!E84","v":19.246640192796217},{"$f":"'Project Info'!F84","v":0},{"$f":"'Project Info'!G84","v":0},{"$f":"'Project Info'!H84","v":0},{"$f":"'Project Info'!I84","v":0},{"$f":"'Project Info'!J84","v":0},{"$f":"'Project Info'!K84","v":0},{"$f":"'Project Info'!L84","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A85","v":45},{"$f":"'Project Info'!B85","v":50},{"$f":"'Project Info'!C85","v":47.459170258371508},{"$f":"'Project Info'!D85","v":43.465397050422162},{"$f":"'Project Info'!E85","v":16.894183241713304},{"$f":"'Project Info'!F85","v":0},{"$f":"'Project Info'!G85","v":0},{"$f":"'Project Info'!H85","v":0},{"$f":"'Project Info'!I85","v":0},{"$f":"'Project Info'!J85","v":0},{"$f":"'Project Info'!K85","v":0},{"$f":"'Project Info'!L85","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A86","v":40},{"$f":"'Project Info'!B86","v":45},{"$f":"'Project Info'!C86","v":42.677030404888129},{"$f":"'Project Info'!D86","v":38.812544504634097},{"$f":"'Project Info'!E86","v":14.690265649465921},{"$f":"'Project Info'!F86","v":0},{"$f":"'Project Info'!G86","v":0},{"$f":"'Project Info'!H86","v":0},{"$f":"'Project Info'!I86","v":0},{"$f":"'Project Info'!J86","v":0},{"$f":"'Project Info'!K86","v":0},{"$f":"'Project Info'!L86","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A87","v":35},{"$f":"'Project Info'!B87","v":40},{"$f":"'Project Info'!C87","v":37.333046773755832},{"$f":"'Project Info'!D87","v":33.904706919479686},{"$f":"'Project Info'!E87","v":12.53841602318813},{"$f":"'Project Info'!F87","v":0},{"$f":"'Project Info'!G87","v":0},{"$f":"'Project Info'!H87","v":0},{"$f":"'Project Info'!I87","v":0},{"$f":"'Project Info'!J87","v":0},{"$f":"'Project Info'!K87","v":0},{"$f":"'Project Info'!L87","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A88","v":30},{"$f":"'Project Info'!B88","v":35},{"$f":"'Project Info'!C88","v":32.638179845662044},{"$f":"'Project Info'!D88","v":29.547170928664851},{"$f":"'Project Info'!E88","v":10.728972818165861},{"$f":"'Project Info'!F88","v":0},{"$f":"'Project Info'!G88","v":0},{"$f":"'Project Info'!H88","v":0},{"$f":"'Project Info'!I88","v":0},{"$f":"'Project Info'!J88","v":0},{"$f":"'Project Info'!K88","v":0},{"$f":"'Project Info'!L88","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A89","v":25},{"$f":"'Project Info'!B89","v":30},{"$f":"'Project Info'!C89","v":27.529264646850947},{"$f":"'Project Info'!D89","v":24.652717392657845},{"$f":"'Project Info'!E89","v":8.8041305482613303},{"$f":"'Project Info'!F89","v":0},{"$f":"'Project Info'!G89","v":0},{"$f":"'Project Info'!H89","v":0},{"$f":"'Project Info'!I89","v":0},{"$f":"'Project Info'!J89","v":0},{"$f":"'Project Info'!K89","v":0},{"$f":"'Project Info'!L89","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A90","v":20},{"$f":"'Project Info'!B90","v":25},{"$f":"'Project Info'!C90","v":22.998111483544687},{"$f":"'Project Info'!D90","v":20.383306659827422},{"$f":"'Project Info'!E90","v":7.246164547543378},{"$f":"'Project Info'!F90","v":0},{"$f":"'Project Info'!G90","v":0},{"$f":"'Project Info'!H90","v":0},{"$f":"'Project Info'!I90","v":0},{"$f":"'Project Info'!J90","v":0},{"$f":"'Project Info'!K90","v":0},{"$f":"'Project Info'!L90","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A91","v":15},{"$f":"'Project Info'!B91","v":20},{"$f":"'Project Info'!C91","v":17.808510327474309},{"$f":"'Project Info'!D91","v":15.420865796304254},{"$f":"'Project Info'!E91","v":5.5490484131518292},{"$f":"'Project Info'!F91","v":0},{"$f":"'Project Info'!G91","v":0},{"$f":"'Project Info'!H91","v":0},{"$f":"'Project Info'!I91","v":0},{"$f":"'Project Info'!J91","v":0},{"$f":"'Project Info'!K91","v":0},{"$f":"'Project Info'!L91","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A92","v":10},{"$f":"'Project Info'!B92","v":15},{"$f":"'Project Info'!C92","v":12.269931130346862},{"$f":"'Project Info'!D92","v":10.318264913023604},{"$f":"'Project Info'!E92","v":3.9082824916941998},{"$f":"'Project Info'!F92","v":0},{"$f":"'Project Info'!G92","v":0},{"$f":"'Project Info'!H92","v":0},{"$f":"'Project Info'!I92","v":0},{"$f":"'Project Info'!J92","v":0},{"$f":"'Project Info'!K92","v":0},{"$f":"'Project Info'!L92","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A93","v":5},{"$f":"'Project Info'!B93","v":10},{"$f":"'Project Info'!C93","v":7.3137581369917548},{"$f":"'Project Info'!D93","v":5.7052382449247707},{"$f":"'Project Info'!E93","v":2.5019418419888937},{"$f":"'Project Info'!F93","v":0},{"$f":"'Project Info'!G93","v":0},{"$f":"'Project Info'!H93","v":0},{"$f":"'Project Info'!I93","v":0},{"$f":"'Project Info'!J93","v":0},{"$f":"'Project Info'!K93","v":0},{"$f":"'Project Info'!L93","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A94","v":0},{"$f":"'Project Info'!B94","v":5},{"$f":"'Project Info'!C94","v":2.6119461836144886},{"$f":"'Project Info'!D94","v":1.2699770062067783},{"$f":"'Project Info'!E94","v":1.2046477897733283},{"$f":"'Project Info'!F94","v":8760},{"$f":"'Project Info'!G94","v":2672},{"$f":"'Project Info'!H94","v":3160},{"$f":"'Project Info'!I94","v":1344},{"$f":"'Project Info'!J94","v":1584},{"$f":"'Project Info'!K94","v":88},{"$f":"'Project Info'!L94","v":264}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A95","v":-5},{"$f":"'Project Info'!B95","v":0},{"$f":"'Project Info'!C95","v":-1.6731398516793925},{"$f":"'Project Info'!D95","v":-2.7083318773557807},{"$f":"'Project Info'!E95","v":7.9391832815876459E-2},{"$f":"'Project Info'!F95","v":0},{"$f":"'Project Info'!G95","v":0},{"$f":"'Project Info'!H95","v":0},{"$f":"'Project Info'!I95","v":0},{"$f":"'Project Info'!J95","v":0},{"$f":"'Project Info'!K95","v":0},{"$f":"'Project Info'!L95","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A96","v":-10},{"$f":"'Project Info'!B96","v":-5},{"$f":"'Project Info'!C96","v":-6.5729865085377277},{"$f":"'Project Info'!D96","v":-7.2465935998252222},{"$f":"'Project Info'!E96","v":-1.168423365310433},{"$f":"'Project Info'!F96","v":0},{"$f":"'Project Info'!G96","v":0},{"$f":"'Project Info'!H96","v":0},{"$f":"'Project Info'!I96","v":0},{"$f":"'Project Info'!J96","v":0},{"$f":"'Project Info'!K96","v":0},{"$f":"'Project Info'!L96","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A97","v":-15},{"$f":"'Project Info'!B97","v":-10},{"$f":"'Project Info'!C97","v":-15.32570353422995},{"$f":"'Project Info'!D97","v":-15.707838211108999},{"$f":"'Project Info'!E97","v":-3.4051318156661381},{"$f":"'Project Info'!F97","v":0},{"$f":"'Project Info'!G97","v":0},{"$f":"'Project Info'!H97","v":0},{"$f":"'Project Info'!I97","v":0},{"$f":"'Project Info'!J97","v":0},{"$f":"'Project Info'!K97","v":0},{"$f":"'Project Info'!L97","v":0}]

{"sheet":"User Defined 3","index":27,"n_rows":87,"n_cols":18,"rows_kept":87,"cut":false,"hidden":true,"merged":[[3,10,8,19],[11,10,17,19],[20,10,26,19],[17,7,17,8],[18,7,18,8],[16,7,16,8]]}
["Savings Summary",null,null,null,null,"Measure Summary",null,null,null,null,"Measure Title"]
["Annual kWh Savings",null,null,null,null,null,null,"Value","Unit"]
["% On Peak",null,null,null,null,"Annual Electric Savings",null,{"$f":"D2","v":0},"kWh",null,"Measure Description"]
["Max kW",null,null,null,null,"Annual Fuel Savings",null,{"$f":"D7*C28","v":{"$error":"#N/A"}},{"$f":"D20","v":{"$error":"#N/A"}}]
["Summer kW",null,null,null,null,"Incremental Cost",null,{"$f":"D8","v":0},"$"]
["Winter kW",null,null,null,null,"Estimated Custom Incentive",null,{"$f":"IF(AND($C$24>=0,$C$25>=0),MAX(0,H3)*C24+MAX(0,H4)*C25,\"TBD\")","v":{"$error":"#N/A"}},"$"]
["Annual Fuel Savings (MMBtu)",null,null,null,null,"Override Incentive (Optional)",null,null,"$"]
["Incremental Cost",null,null,null,null,"Custom Payback",null,{"$f":"H5/(H3*$C$19+H4*$C$20)","v":{"$error":"#N/A"}},"years"]
[null,null,null,null,null,"Project Information Summary"]
["kWh Savings by Peak Period",null,null,null,null,null,"STATE (MA or RI)",{"$f":"'Project Info'!C15","v":"NH"}]
["Winter","Winter","Summer","Summer",null,null,"Program Year",{"$f":"'Project Info'!C19","v":0},null,null,"Base Case Description"]
["On-Peak","Off-Peak","On-Peak","Off-Peak",null,null,"Code IECC Version",{"$f":"MID('Project Info'!C20,1,4)","v":"2018"}]
["kWh","kWh","kWh","kWh",null,null,"Electric PA",{"$f":"'Project Info'!F3","v":0}]
[null,null,null,null,null,null,"Gas PA",{"$f":"'Project Info'!I3","v":0}]
[{"$f":"ROUND(IF(A14<=0,0,A14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(B14<=0,0,B14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(C14<=0,0,C14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"IF(SUM(A14:D14)=0,0,1-SUM(A15:C15))","v":0}]
[null,null,null,null,null,"Information For BCR Inputs"]
["Utility Rates",null,null,null,null,"Program Type"]
[null,null,"Rate","Unit",null,"Fuel Savings Type"]
["Electric",null,{"$f":"'ECM Summary'!$E$31","v":0.1593},"kWh",null,"Measure Type"]
[{"$f":"'ECM Summary'!$C$32","v":0},null,{"$f":"'ECM Summary'!$E$32","v":{"$error":"#N/A"}},{"$f":"'ECM Summary'!$F$32","v":{"$error":"#N/A"}},null,"Measure Life",null,{"$f":"LOOKUP($H$19,'PA Impacts'!$G$84:$G$118,'PA Impacts'!$H$84:$H$118)","v":{"$error":"#N/A"}},null,null,"Proposed Case Description"]
[]
["Custom Incentive Rates"]
[null,null,"Rate","Unit"]
["Electric",null,{"$f":"'ECM Summary'!$J$31","v":0.28000000000000003},"kWh"]
[{"$f":"'ECM Summary'!$H$32","v":0},null,{"$f":"'ECM Summary'!$J$32","v":0},{"$f":"'ECM Summary'!$K$32","v":{"$error":"#N/A"}}]
[]
["Fossil Fuel",null,{"$f":"'Project Info'!C21","v":0}]
["Fuel Conversion",null,{"$f":"LOOKUP(C27,'Project Info'!X102:X104,'Project Info'!Z102:Z104)","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,"BIN Model Hours Based on Project/Facility Parameters (Project Info Tab)"]
[null,null,null,null,null,null,"Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A44","v":100},{"$f":"'Project Info'!B44","v":105},{"$f":"'Project Info'!C44","v":102},{"$f":"'Project Info'!D44","v":76},{"$f":"'Project Info'!E44","v":40},{"$f":"'Project Info'!F44","v":0},{"$f":"'Project Info'!G44","v":0},{"$f":"'Project Info'!H44","v":0},{"$f":"'Project Info'!I44","v":0},{"$f":"'Project Info'!J44","v":0},{"$f":"'Project Info'!K44","v":0},{"$f":"'Project Info'!L44","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A45","v":95},{"$f":"'Project Info'!B45","v":100},{"$f":"'Project Info'!C45","v":95.219272727272724},{"$f":"'Project Info'!D45","v":74.534025272781079},{"$f":"'Project Info'!E45","v":37.923296058061368},{"$f":"'Project Info'!F45","v":0},{"$f":"'Project Info'!G45","v":0},{"$f":"'Project Info'!H45","v":0},{"$f":"'Project Info'!I45","v":0},{"$f":"'Project Info'!J45","v":0},{"$f":"'Project Info'!K45","v":0},{"$f":"'Project Info'!L45","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A46","v":90},{"$f":"'Project Info'!B46","v":95},{"$f":"'Project Info'!C46","v":92.016049160256074},{"$f":"'Project Info'!D46","v":72.911561930607689},{"$f":"'Project Info'!E46","v":36.467095439351091},{"$f":"'Project Info'!F46","v":0},{"$f":"'Project Info'!G46","v":0},{"$f":"'Project Info'!H46","v":0},{"$f":"'Project Info'!I46","v":0},{"$f":"'Project Info'!J46","v":0},{"$f":"'Project Info'!K46","v":0},{"$f":"'Project Info'!L46","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A47","v":85},{"$f":"'Project Info'!B47","v":90},{"$f":"'Project Info'!C47","v":87.457811360655285},{"$f":"'Project Info'!D47","v":70.80538329449476},{"$f":"'Project Info'!E47","v":34.679413213566804},{"$f":"'Project Info'!F47","v":0},{"$f":"'Project Info'!G47","v":0},{"$f":"'Project Info'!H47","v":0},{"$f":"'Project Info'!I47","v":0},{"$f":"'Project Info'!J47","v":0},{"$f":"'Project Info'!K47","v":0},{"$f":"'Project Info'!L47","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A48","v":80},{"$f":"'Project Info'!B48","v":85},{"$f":"'Project Info'!C48","v":82.136788830239965},{"$f":"'Project Info'!D48","v":67.872393622439333},{"$f":"'Project Info'!E48","v":32.296248223809314},{"$f":"'Project Info'!F48","v":0},{"$f":"'Project Info'!G48","v":0},{"$f":"'Project Info'!H48","v":0},{"$f":"'Project Info'!I48","v":0},{"$f":"'Project Info'!J48","v":0},{"$f":"'Project Info'!K48","v":0},{"$f":"'Project Info'!L48","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A49","v":75},{"$f":"'Project Info'!B49","v":80},{"$f":"'Project Info'!C49","v":76.988400157585886},{"$f":"'Project Info'!D49","v":65.129261896908645},{"$f":"'Project Info'!E49","v":30.190476812806729},{"$f":"'Project Info'!F49","v":0},{"$f":"'Project Info'!G49","v":0},{"$f":"'Project Info'!H49","v":0},{"$f":"'Project Info'!I49","v":0},{"$f":"'Project Info'!J49","v":0},{"$f":"'Project Info'!K49","v":0},{"$f":"'Project Info'!L49","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A50","v":70},{"$f":"'Project Info'!B50","v":75},{"$f":"'Project Info'!C50","v":72.457982050814195},{"$f":"'Project Info'!D50","v":63.604425012889301},{"$f":"'Project Info'!E50","v":29.088683095945193},{"$f":"'Project Info'!F50","v":0},{"$f":"'Project Info'!G50","v":0},{"$f":"'Project Info'!H50","v":0},{"$f":"'Project Info'!I50","v":0},{"$f":"'Project Info'!J50","v":0},{"$f":"'Project Info'!K50","v":0},{"$f":"'Project Info'!L50","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A51","v":65},{"$f":"'Project Info'!B51","v":70},{"$f":"'Project Info'!C51","v":67.815831070966169},{"$f":"'Project Info'!D51","v":61.631331368130574},{"$f":"'Project Info'!E51","v":27.661514889731574},{"$f":"'Project Info'!F51","v":0},{"$f":"'Project Info'!G51","v":0},{"$f":"'Project Info'!H51","v":0},{"$f":"'Project Info'!I51","v":0},{"$f":"'Project Info'!J51","v":0},{"$f":"'Project Info'!K51","v":0},{"$f":"'Project Info'!L51","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A52","v":60},{"$f":"'Project Info'!B52","v":65},{"$f":"'Project Info'!C52","v":62.535961472271332},{"$f":"'Project Info'!D52","v":57.135476922863582},{"$f":"'Project Info'!E52","v":24.623037157728302},{"$f":"'Project Info'!F52","v":0},{"$f":"'Project Info'!G52","v":0},{"$f":"'Project Info'!H52","v":0},{"$f":"'Project Info'!I52","v":0},{"$f":"'Project Info'!J52","v":0},{"$f":"'Project Info'!K52","v":0},{"$f":"'Project Info'!L52","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A53","v":55},{"$f":"'Project Info'!B53","v":60},{"$f":"'Project Info'!C53","v":57.125792270740902},{"$f":"'Project Info'!D53","v":52.596971157053673},{"$f":"'Project Info'!E53","v":21.818001539159841},{"$f":"'Project Info'!F53","v":0},{"$f":"'Project Info'!G53","v":0},{"$f":"'Project Info'!H53","v":0},{"$f":"'Project Info'!I53","v":0},{"$f":"'Project Info'!J53","v":0},{"$f":"'Project Info'!K53","v":0},{"$f":"'Project Info'!L53","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A54","v":50},{"$f":"'Project Info'!B54","v":55},{"$f":"'Project Info'!C54","v":52.235698854337961},{"$f":"'Project Info'!D54","v":48.022768090099298},{"$f":"'Project Info'!E54","v":19.246640192796217},{"$f":"'Project Info'!F54","v":0},{"$f":"'Project Info'!G54","v":0},{"$f":"'Project Info'!H54","v":0},{"$f":"'Project Info'!I54","v":0},{"$f":"'Project Info'!J54","v":0},{"$f":"'Project Info'!K54","v":0},{"$f":"'Project Info'!L54","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A55","v":45},{"$f":"'Project Info'!B55","v":50},{"$f":"'Project Info'!C55","v":47.459170258371508},{"$f":"'Project Info'!D55","v":43.465397050422162},{"$f":"'Project Info'!E55","v":16.894183241713304},{"$f":"'Project Info'!F55","v":0},{"$f":"'Project Info'!G55","v":0},{"$f":"'Project Info'!H55","v":0},{"$f":"'Project Info'!I55","v":0},{"$f":"'Project Info'!J55","v":0},{"$f":"'Project Info'!K55","v":0},{"$f":"'Project Info'!L55","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A56","v":40},{"$f":"'Project Info'!B56","v":45},{"$f":"'Project Info'!C56","v":42.677030404888129},{"$f":"'Project Info'!D56","v":38.812544504634097},{"$f":"'Project Info'!E56","v":14.690265649465921},{"$f":"'Project Info'!F56","v":0},{"$f":"'Project Info'!G56","v":0},{"$f":"'Project Info'!H56","v":0},{"$f":"'Project Info'!I56","v":0},{"$f":"'Project Info'!J56","v":0},{"$f":"'Project Info'!K56","v":0},{"$f":"'Project Info'!L56","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A57","v":35},{"$f":"'Project Info'!B57","v":40},{"$f":"'Project Info'!C57","v":37.333046773755832},{"$f":"'Project Info'!D57","v":33.904706919479686},{"$f":"'Project Info'!E57","v":12.53841602318813},{"$f":"'Project Info'!F57","v":0},{"$f":"'Project Info'!G57","v":0},{"$f":"'Project Info'!H57","v":0},{"$f":"'Project Info'!I57","v":0},{"$f":"'Project Info'!J57","v":0},{"$f":"'Project Info'!K57","v":0},{"$f":"'Project Info'!L57","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A58","v":30},{"$f":"'Project Info'!B58","v":35},{"$f":"'Project Info'!C58","v":32.638179845662044},{"$f":"'Project Info'!D58","v":29.547170928664851},{"$f":"'Project Info'!E58","v":10.728972818165861},{"$f":"'Project Info'!F58","v":0},{"$f":"'Project Info'!G58","v":0},{"$f":"'Project Info'!H58","v":0},{"$f":"'Project Info'!I58","v":0},{"$f":"'Project Info'!J58","v":0},{"$f":"'Project Info'!K58","v":0},{"$f":"'Project Info'!L58","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A59","v":25},{"$f":"'Project Info'!B59","v":30},{"$f":"'Project Info'!C59","v":27.529264646850947},{"$f":"'Project Info'!D59","v":24.652717392657845},{"$f":"'Project Info'!E59","v":8.8041305482613303},{"$f":"'Project Info'!F59","v":0},{"$f":"'Project Info'!G59","v":0},{"$f":"'Project Info'!H59","v":0},{"$f":"'Project Info'!I59","v":0},{"$f":"'Project Info'!J59","v":0},{"$f":"'Project Info'!K59","v":0},{"$f":"'Project Info'!L59","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A60","v":20},{"$f":"'Project Info'!B60","v":25},{"$f":"'Project Info'!C60","v":22.998111483544687},{"$f":"'Project Info'!D60","v":20.383306659827422},{"$f":"'Project Info'!E60","v":7.246164547543378},{"$f":"'Project Info'!F60","v":0},{"$f":"'Project Info'!G60","v":0},{"$f":"'Project Info'!H60","v":0},{"$f":"'Project Info'!I60","v":0},{"$f":"'Project Info'!J60","v":0},{"$f":"'Project Info'!K60","v":0},{"$f":"'Project Info'!L60","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A61","v":15},{"$f":"'Project Info'!B61","v":20},{"$f":"'Project Info'!C61","v":17.808510327474309},{"$f":"'Project Info'!D61","v":15.420865796304254},{"$f":"'Project Info'!E61","v":5.5490484131518292},{"$f":"'Project Info'!F61","v":0},{"$f":"'Project Info'!G61","v":0},{"$f":"'Project Info'!H61","v":0},{"$f":"'Project Info'!I61","v":0},{"$f":"'Project Info'!J61","v":0},{"$f":"'Project Info'!K61","v":0},{"$f":"'Project Info'!L61","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A62","v":10},{"$f":"'Project Info'!B62","v":15},{"$f":"'Project Info'!C62","v":12.269931130346862},{"$f":"'Project Info'!D62","v":10.318264913023604},{"$f":"'Project Info'!E62","v":3.9082824916941998},{"$f":"'Project Info'!F62","v":0},{"$f":"'Project Info'!G62","v":0},{"$f":"'Project Info'!H62","v":0},{"$f":"'Project Info'!I62","v":0},{"$f":"'Project Info'!J62","v":0},{"$f":"'Project Info'!K62","v":0},{"$f":"'Project Info'!L62","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A63","v":5},{"$f":"'Project Info'!B63","v":10},{"$f":"'Project Info'!C63","v":7.3137581369917548},{"$f":"'Project Info'!D63","v":5.7052382449247707},{"$f":"'Project Info'!E63","v":2.5019418419888937},{"$f":"'Project Info'!F63","v":0},{"$f":"'Project Info'!G63","v":0},{"$f":"'Project Info'!H63","v":0},{"$f":"'Project Info'!I63","v":0},{"$f":"'Project Info'!J63","v":0},{"$f":"'Project Info'!K63","v":0},{"$f":"'Project Info'!L63","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A64","v":0},{"$f":"'Project Info'!B64","v":5},{"$f":"'Project Info'!C64","v":2.6119461836144886},{"$f":"'Project Info'!D64","v":1.2699770062067783},{"$f":"'Project Info'!E64","v":1.2046477897733283},{"$f":"'Project Info'!F64","v":0},{"$f":"'Project Info'!G64","v":0},{"$f":"'Project Info'!H64","v":0},{"$f":"'Project Info'!I64","v":0},{"$f":"'Project Info'!J64","v":0},{"$f":"'Project Info'!K64","v":0},{"$f":"'Project Info'!L64","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A65","v":-5},{"$f":"'Project Info'!B65","v":0},{"$f":"'Project Info'!C65","v":-1.6731398516793925},{"$f":"'Project Info'!D65","v":-2.7083318773557807},{"$f":"'Project Info'!E65","v":7.9391832815876459E-2},{"$f":"'Project Info'!F65","v":0},{"$f":"'Project Info'!G65","v":0},{"$f":"'Project Info'!H65","v":0},{"$f":"'Project Info'!I65","v":0},{"$f":"'Project Info'!J65","v":0},{"$f":"'Project Info'!K65","v":0},{"$f":"'Project Info'!L65","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A66","v":-10},{"$f":"'Project Info'!B66","v":-5},{"$f":"'Project Info'!C66","v":-6.5729865085377277},{"$f":"'Project Info'!D66","v":-7.2465935998252222},{"$f":"'Project Info'!E66","v":-1.168423365310433},{"$f":"'Project Info'!F66","v":0},{"$f":"'Project Info'!G66","v":0},{"$f":"'Project Info'!H66","v":0},{"$f":"'Project Info'!I66","v":0},{"$f":"'Project Info'!J66","v":0},{"$f":"'Project Info'!K66","v":0},{"$f":"'Project Info'!L66","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A67","v":-15},{"$f":"'Project Info'!B67","v":-10},{"$f":"'Project Info'!C67","v":-15.32570353422995},{"$f":"'Project Info'!D67","v":-15.707838211108999},{"$f":"'Project Info'!E67","v":-3.4051318156661381},{"$f":"'Project Info'!F67","v":0},{"$f":"'Project Info'!G67","v":0},{"$f":"'Project Info'!H67","v":0},{"$f":"'Project Info'!I67","v":0},{"$f":"'Project Info'!J67","v":0},{"$f":"'Project Info'!K67","v":0},{"$f":"'Project Info'!L67","v":0}]
[]
[]
[null,null,null,null,null,null,"Unoccupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A74","v":100},{"$f":"'Project Info'!B74","v":105},{"$f":"'Project Info'!C74","v":102},{"$f":"'Project Info'!D74","v":76},{"$f":"'Project Info'!E74","v":40},{"$f":"'Project Info'!F74","v":0},{"$f":"'Project Info'!G74","v":0},{"$f":"'Project Info'!H74","v":0},{"$f":"'Project Info'!I74","v":0},{"$f":"'Project Info'!J74","v":0},{"$f":"'Project Info'!K74","v":0},{"$f":"'Project Info'!L74","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A75","v":95},{"$f":"'Project Info'!B75","v":100},{"$f":"'Project Info'!C75","v":95.219272727272724},{"$f":"'Project Info'!D75","v":74.534025272781079},{"$f":"'Project Info'!E75","v":37.923296058061368},{"$f":"'Project Info'!F75","v":0},{"$f":"'Project Info'!G75","v":0},{"$f":"'Project Info'!H75","v":0},{"$f":"'Project Info'!I75","v":0},{"$f":"'Project Info'!J75","v":0},{"$f":"'Project Info'!K75","v":0},{"$f":"'Project Info'!L75","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A76","v":90},{"$f":"'Project Info'!B76","v":95},{"$f":"'Project Info'!C76","v":92.016049160256074},{"$f":"'Project Info'!D76","v":72.911561930607689},{"$f":"'Project Info'!E76","v":36.467095439351091},{"$f":"'Project Info'!F76","v":0},{"$f":"'Project Info'!G76","v":0},{"$f":"'Project Info'!H76","v":0},{"$f":"'Project Info'!I76","v":0},{"$f":"'Project Info'!J76","v":0},{"$f":"'Project Info'!K76","v":0},{"$f":"'Project Info'!L76","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A77","v":85},{"$f":"'Project Info'!B77","v":90},{"$f":"'Project Info'!C77","v":87.457811360655285},{"$f":"'Project Info'!D77","v":70.80538329449476},{"$f":"'Project Info'!E77","v":34.679413213566804},{"$f":"'Project Info'!F77","v":0},{"$f":"'Project Info'!G77","v":0},{"$f":"'Project Info'!H77","v":0},{"$f":"'Project Info'!I77","v":0},{"$f":"'Project Info'!J77","v":0},{"$f":"'Project Info'!K77","v":0},{"$f":"'Project Info'!L77","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A78","v":80},{"$f":"'Project Info'!B78","v":85},{"$f":"'Project Info'!C78","v":82.136788830239965},{"$f":"'Project Info'!D78","v":67.872393622439333},{"$f":"'Project Info'!E78","v":32.296248223809314},{"$f":"'Project Info'!F78","v":0},{"$f":"'Project Info'!G78","v":0},{"$f":"'Project Info'!H78","v":0},{"$f":"'Project Info'!I78","v":0},{"$f":"'Project Info'!J78","v":0},{"$f":"'Project Info'!K78","v":0},{"$f":"'Project Info'!L78","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A79","v":75},{"$f":"'Project Info'!B79","v":80},{"$f":"'Project Info'!C79","v":76.988400157585886},{"$f":"'Project Info'!D79","v":65.129261896908645},{"$f":"'Project Info'!E79","v":30.190476812806729},{"$f":"'Project Info'!F79","v":0},{"$f":"'Project Info'!G79","v":0},{"$f":"'Project Info'!H79","v":0},{"$f":"'Project Info'!I79","v":0},{"$f":"'Project Info'!J79","v":0},{"$f":"'Project Info'!K79","v":0},{"$f":"'Project Info'!L79","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A80","v":70},{"$f":"'Project Info'!B80","v":75},{"$f":"'Project Info'!C80","v":72.457982050814195},{"$f":"'Project Info'!D80","v":63.604425012889301},{"$f":"'Project Info'!E80","v":29.088683095945193},{"$f":"'Project Info'!F80","v":0},{"$f":"'Project Info'!G80","v":0},{"$f":"'Project Info'!H80","v":0},{"$f":"'Project Info'!I80","v":0},{"$f":"'Project Info'!J80","v":0},{"$f":"'Project Info'!K80","v":0},{"$f":"'Project Info'!L80","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A81","v":65},{"$f":"'Project Info'!B81","v":70},{"$f":"'Project Info'!C81","v":67.815831070966169},{"$f":"'Project Info'!D81","v":61.631331368130574},{"$f":"'Project Info'!E81","v":27.661514889731574},{"$f":"'Project Info'!F81","v":0},{"$f":"'Project Info'!G81","v":0},{"$f":"'Project Info'!H81","v":0},{"$f":"'Project Info'!I81","v":0},{"$f":"'Project Info'!J81","v":0},{"$f":"'Project Info'!K81","v":0},{"$f":"'Project Info'!L81","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A82","v":60},{"$f":"'Project Info'!B82","v":65},{"$f":"'Project Info'!C82","v":62.535961472271332},{"$f":"'Project Info'!D82","v":57.135476922863582},{"$f":"'Project Info'!E82","v":24.623037157728302},{"$f":"'Project Info'!F82","v":0},{"$f":"'Project Info'!G82","v":0},{"$f":"'Project Info'!H82","v":0},{"$f":"'Project Info'!I82","v":0},{"$f":"'Project Info'!J82","v":0},{"$f":"'Project Info'!K82","v":0},{"$f":"'Project Info'!L82","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A83","v":55},{"$f":"'Project Info'!B83","v":60},{"$f":"'Project Info'!C83","v":57.125792270740902},{"$f":"'Project Info'!D83","v":52.596971157053673},{"$f":"'Project Info'!E83","v":21.818001539159841},{"$f":"'Project Info'!F83","v":0},{"$f":"'Project Info'!G83","v":0},{"$f":"'Project Info'!H83","v":0},{"$f":"'Project Info'!I83","v":0},{"$f":"'Project Info'!J83","v":0},{"$f":"'Project Info'!K83","v":0},{"$f":"'Project Info'!L83","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A84","v":50},{"$f":"'Project Info'!B84","v":55},{"$f":"'Project Info'!C84","v":52.235698854337961},{"$f":"'Project Info'!D84","v":48.022768090099298},{"$f":"'Project Info'!E84","v":19.246640192796217},{"$f":"'Project Info'!F84","v":0},{"$f":"'Project Info'!G84","v":0},{"$f":"'Project Info'!H84","v":0},{"$f":"'Project Info'!I84","v":0},{"$f":"'Project Info'!J84","v":0},{"$f":"'Project Info'!K84","v":0},{"$f":"'Project Info'!L84","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A85","v":45},{"$f":"'Project Info'!B85","v":50},{"$f":"'Project Info'!C85","v":47.459170258371508},{"$f":"'Project Info'!D85","v":43.465397050422162},{"$f":"'Project Info'!E85","v":16.894183241713304},{"$f":"'Project Info'!F85","v":0},{"$f":"'Project Info'!G85","v":0},{"$f":"'Project Info'!H85","v":0},{"$f":"'Project Info'!I85","v":0},{"$f":"'Project Info'!J85","v":0},{"$f":"'Project Info'!K85","v":0},{"$f":"'Project Info'!L85","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A86","v":40},{"$f":"'Project Info'!B86","v":45},{"$f":"'Project Info'!C86","v":42.677030404888129},{"$f":"'Project Info'!D86","v":38.812544504634097},{"$f":"'Project Info'!E86","v":14.690265649465921},{"$f":"'Project Info'!F86","v":0},{"$f":"'Project Info'!G86","v":0},{"$f":"'Project Info'!H86","v":0},{"$f":"'Project Info'!I86","v":0},{"$f":"'Project Info'!J86","v":0},{"$f":"'Project Info'!K86","v":0},{"$f":"'Project Info'!L86","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A87","v":35},{"$f":"'Project Info'!B87","v":40},{"$f":"'Project Info'!C87","v":37.333046773755832},{"$f":"'Project Info'!D87","v":33.904706919479686},{"$f":"'Project Info'!E87","v":12.53841602318813},{"$f":"'Project Info'!F87","v":0},{"$f":"'Project Info'!G87","v":0},{"$f":"'Project Info'!H87","v":0},{"$f":"'Project Info'!I87","v":0},{"$f":"'Project Info'!J87","v":0},{"$f":"'Project Info'!K87","v":0},{"$f":"'Project Info'!L87","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A88","v":30},{"$f":"'Project Info'!B88","v":35},{"$f":"'Project Info'!C88","v":32.638179845662044},{"$f":"'Project Info'!D88","v":29.547170928664851},{"$f":"'Project Info'!E88","v":10.728972818165861},{"$f":"'Project Info'!F88","v":0},{"$f":"'Project Info'!G88","v":0},{"$f":"'Project Info'!H88","v":0},{"$f":"'Project Info'!I88","v":0},{"$f":"'Project Info'!J88","v":0},{"$f":"'Project Info'!K88","v":0},{"$f":"'Project Info'!L88","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A89","v":25},{"$f":"'Project Info'!B89","v":30},{"$f":"'Project Info'!C89","v":27.529264646850947},{"$f":"'Project Info'!D89","v":24.652717392657845},{"$f":"'Project Info'!E89","v":8.8041305482613303},{"$f":"'Project Info'!F89","v":0},{"$f":"'Project Info'!G89","v":0},{"$f":"'Project Info'!H89","v":0},{"$f":"'Project Info'!I89","v":0},{"$f":"'Project Info'!J89","v":0},{"$f":"'Project Info'!K89","v":0},{"$f":"'Project Info'!L89","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A90","v":20},{"$f":"'Project Info'!B90","v":25},{"$f":"'Project Info'!C90","v":22.998111483544687},{"$f":"'Project Info'!D90","v":20.383306659827422},{"$f":"'Project Info'!E90","v":7.246164547543378},{"$f":"'Project Info'!F90","v":0},{"$f":"'Project Info'!G90","v":0},{"$f":"'Project Info'!H90","v":0},{"$f":"'Project Info'!I90","v":0},{"$f":"'Project Info'!J90","v":0},{"$f":"'Project Info'!K90","v":0},{"$f":"'Project Info'!L90","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A91","v":15},{"$f":"'Project Info'!B91","v":20},{"$f":"'Project Info'!C91","v":17.808510327474309},{"$f":"'Project Info'!D91","v":15.420865796304254},{"$f":"'Project Info'!E91","v":5.5490484131518292},{"$f":"'Project Info'!F91","v":0},{"$f":"'Project Info'!G91","v":0},{"$f":"'Project Info'!H91","v":0},{"$f":"'Project Info'!I91","v":0},{"$f":"'Project Info'!J91","v":0},{"$f":"'Project Info'!K91","v":0},{"$f":"'Project Info'!L91","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A92","v":10},{"$f":"'Project Info'!B92","v":15},{"$f":"'Project Info'!C92","v":12.269931130346862},{"$f":"'Project Info'!D92","v":10.318264913023604},{"$f":"'Project Info'!E92","v":3.9082824916941998},{"$f":"'Project Info'!F92","v":0},{"$f":"'Project Info'!G92","v":0},{"$f":"'Project Info'!H92","v":0},{"$f":"'Project Info'!I92","v":0},{"$f":"'Project Info'!J92","v":0},{"$f":"'Project Info'!K92","v":0},{"$f":"'Project Info'!L92","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A93","v":5},{"$f":"'Project Info'!B93","v":10},{"$f":"'Project Info'!C93","v":7.3137581369917548},{"$f":"'Project Info'!D93","v":5.7052382449247707},{"$f":"'Project Info'!E93","v":2.5019418419888937},{"$f":"'Project Info'!F93","v":0},{"$f":"'Project Info'!G93","v":0},{"$f":"'Project Info'!H93","v":0},{"$f":"'Project Info'!I93","v":0},{"$f":"'Project Info'!J93","v":0},{"$f":"'Project Info'!K93","v":0},{"$f":"'Project Info'!L93","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A94","v":0},{"$f":"'Project Info'!B94","v":5},{"$f":"'Project Info'!C94","v":2.6119461836144886},{"$f":"'Project Info'!D94","v":1.2699770062067783},{"$f":"'Project Info'!E94","v":1.2046477897733283},{"$f":"'Project Info'!F94","v":8760},{"$f":"'Project Info'!G94","v":2672},{"$f":"'Project Info'!H94","v":3160},{"$f":"'Project Info'!I94","v":1344},{"$f":"'Project Info'!J94","v":1584},{"$f":"'Project Info'!K94","v":88},{"$f":"'Project Info'!L94","v":264}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A95","v":-5},{"$f":"'Project Info'!B95","v":0},{"$f":"'Project Info'!C95","v":-1.6731398516793925},{"$f":"'Project Info'!D95","v":-2.7083318773557807},{"$f":"'Project Info'!E95","v":7.9391832815876459E-2},{"$f":"'Project Info'!F95","v":0},{"$f":"'Project Info'!G95","v":0},{"$f":"'Project Info'!H95","v":0},{"$f":"'Project Info'!I95","v":0},{"$f":"'Project Info'!J95","v":0},{"$f":"'Project Info'!K95","v":0},{"$f":"'Project Info'!L95","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A96","v":-10},{"$f":"'Project Info'!B96","v":-5},{"$f":"'Project Info'!C96","v":-6.5729865085377277},{"$f":"'Project Info'!D96","v":-7.2465935998252222},{"$f":"'Project Info'!E96","v":-1.168423365310433},{"$f":"'Project Info'!F96","v":0},{"$f":"'Project Info'!G96","v":0},{"$f":"'Project Info'!H96","v":0},{"$f":"'Project Info'!I96","v":0},{"$f":"'Project Info'!J96","v":0},{"$f":"'Project Info'!K96","v":0},{"$f":"'Project Info'!L96","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A97","v":-15},{"$f":"'Project Info'!B97","v":-10},{"$f":"'Project Info'!C97","v":-15.32570353422995},{"$f":"'Project Info'!D97","v":-15.707838211108999},{"$f":"'Project Info'!E97","v":-3.4051318156661381},{"$f":"'Project Info'!F97","v":0},{"$f":"'Project Info'!G97","v":0},{"$f":"'Project Info'!H97","v":0},{"$f":"'Project Info'!I97","v":0},{"$f":"'Project Info'!J97","v":0},{"$f":"'Project Info'!K97","v":0},{"$f":"'Project Info'!L97","v":0}]

{"sheet":"User Defined 4","index":28,"n_rows":87,"n_cols":18,"rows_kept":87,"cut":false,"hidden":true,"merged":[[3,10,8,19],[11,10,17,19],[20,10,26,19],[16,7,16,8],[17,7,17,8],[18,7,18,8]]}
["Savings Summary",null,null,null,null,"Measure Summary",null,null,null,null,"Measure Title"]
["Annual kWh Savings",null,null,null,null,null,null,"Value","Unit"]
["% On Peak",null,null,null,null,"Annual Electric Savings",null,{"$f":"D2","v":0},"kWh",null,"Measure Description"]
["Max kW",null,null,null,null,"Annual Fuel Savings",null,{"$f":"D7*C28","v":{"$error":"#N/A"}},{"$f":"D20","v":{"$error":"#N/A"}}]
["Summer kW",null,null,null,null,"Incremental Cost",null,{"$f":"D8","v":0},"$"]
["Winter kW",null,null,null,null,"Estimated Custom Incentive",null,{"$f":"IF(AND($C$24>=0,$C$25>=0),MAX(0,H3)*C24+MAX(0,H4)*C25,\"TBD\")","v":{"$error":"#N/A"}},"$"]
["Annual Fuel Savings (MMBtu)",null,null,null,null,"Override Incentive (Optional)",null,null,"$"]
["Incremental Cost",null,null,null,null,"Custom Payback",null,{"$f":"H5/(H3*$C$19+H4*$C$20)","v":{"$error":"#N/A"}},"years"]
[null,null,null,null,null,"Project Information Summary"]
["kWh Savings by Peak Period",null,null,null,null,null,"STATE (MA or RI)",{"$f":"'Project Info'!C15","v":"NH"}]
["Winter","Winter","Summer","Summer",null,null,"Program Year",{"$f":"'Project Info'!C19","v":0},null,null,"Base Case Description"]
["On-Peak","Off-Peak","On-Peak","Off-Peak",null,null,"Code IECC Version",{"$f":"MID('Project Info'!C20,1,4)","v":"2018"}]
["kWh","kWh","kWh","kWh",null,null,"Electric PA",{"$f":"'Project Info'!F3","v":0}]
[null,null,null,null,null,null,"Gas PA",{"$f":"'Project Info'!I3","v":0}]
[{"$f":"ROUND(IF(A14<=0,0,A14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(B14<=0,0,B14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"ROUND(IF(C14<=0,0,C14/SUMIF($A$14:$D$14,\">0\")),2)","v":0},{"$f":"IF(SUM(A14:D14)=0,0,1-SUM(A15:C15))","v":0}]
[null,null,null,null,null,"Information For BCR Inputs"]
["Utility Rates",null,null,null,null,"Program Type"]
[null,null,"Rate","Unit",null,"Fuel Savings Type"]
["Electric",null,{"$f":"'ECM Summary'!$E$31","v":0.1593},"kWh",null,"Measure Type"]
[{"$f":"'ECM Summary'!$C$32","v":0},null,{"$f":"'ECM Summary'!$E$32","v":{"$error":"#N/A"}},{"$f":"'ECM Summary'!$F$32","v":{"$error":"#N/A"}},null,"Measure Life",null,{"$f":"LOOKUP($H$19,'PA Impacts'!$G$84:$G$118,'PA Impacts'!$H$84:$H$118)","v":{"$error":"#N/A"}},null,null,"Proposed Case Description"]
[]
["Custom Incentive Rates"]
[null,null,"Rate","Unit"]
["Electric",null,{"$f":"'ECM Summary'!$J$31","v":0.28000000000000003},"kWh"]
[{"$f":"'ECM Summary'!$H$32","v":0},null,{"$f":"'ECM Summary'!$J$32","v":0},{"$f":"'ECM Summary'!$K$32","v":{"$error":"#N/A"}}]
[]
["Fossil Fuel",null,{"$f":"'Project Info'!C21","v":0}]
["Fuel Conversion",null,{"$f":"LOOKUP(C27,'Project Info'!X102:X104,'Project Info'!Z102:Z104)","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,"BIN Model Hours Based on Project/Facility Parameters (Project Info Tab)"]
[null,null,null,null,null,null,"Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A44","v":100},{"$f":"'Project Info'!B44","v":105},{"$f":"'Project Info'!C44","v":102},{"$f":"'Project Info'!D44","v":76},{"$f":"'Project Info'!E44","v":40},{"$f":"'Project Info'!F44","v":0},{"$f":"'Project Info'!G44","v":0},{"$f":"'Project Info'!H44","v":0},{"$f":"'Project Info'!I44","v":0},{"$f":"'Project Info'!J44","v":0},{"$f":"'Project Info'!K44","v":0},{"$f":"'Project Info'!L44","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A45","v":95},{"$f":"'Project Info'!B45","v":100},{"$f":"'Project Info'!C45","v":95.219272727272724},{"$f":"'Project Info'!D45","v":74.534025272781079},{"$f":"'Project Info'!E45","v":37.923296058061368},{"$f":"'Project Info'!F45","v":0},{"$f":"'Project Info'!G45","v":0},{"$f":"'Project Info'!H45","v":0},{"$f":"'Project Info'!I45","v":0},{"$f":"'Project Info'!J45","v":0},{"$f":"'Project Info'!K45","v":0},{"$f":"'Project Info'!L45","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A46","v":90},{"$f":"'Project Info'!B46","v":95},{"$f":"'Project Info'!C46","v":92.016049160256074},{"$f":"'Project Info'!D46","v":72.911561930607689},{"$f":"'Project Info'!E46","v":36.467095439351091},{"$f":"'Project Info'!F46","v":0},{"$f":"'Project Info'!G46","v":0},{"$f":"'Project Info'!H46","v":0},{"$f":"'Project Info'!I46","v":0},{"$f":"'Project Info'!J46","v":0},{"$f":"'Project Info'!K46","v":0},{"$f":"'Project Info'!L46","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A47","v":85},{"$f":"'Project Info'!B47","v":90},{"$f":"'Project Info'!C47","v":87.457811360655285},{"$f":"'Project Info'!D47","v":70.80538329449476},{"$f":"'Project Info'!E47","v":34.679413213566804},{"$f":"'Project Info'!F47","v":0},{"$f":"'Project Info'!G47","v":0},{"$f":"'Project Info'!H47","v":0},{"$f":"'Project Info'!I47","v":0},{"$f":"'Project Info'!J47","v":0},{"$f":"'Project Info'!K47","v":0},{"$f":"'Project Info'!L47","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A48","v":80},{"$f":"'Project Info'!B48","v":85},{"$f":"'Project Info'!C48","v":82.136788830239965},{"$f":"'Project Info'!D48","v":67.872393622439333},{"$f":"'Project Info'!E48","v":32.296248223809314},{"$f":"'Project Info'!F48","v":0},{"$f":"'Project Info'!G48","v":0},{"$f":"'Project Info'!H48","v":0},{"$f":"'Project Info'!I48","v":0},{"$f":"'Project Info'!J48","v":0},{"$f":"'Project Info'!K48","v":0},{"$f":"'Project Info'!L48","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A49","v":75},{"$f":"'Project Info'!B49","v":80},{"$f":"'Project Info'!C49","v":76.988400157585886},{"$f":"'Project Info'!D49","v":65.129261896908645},{"$f":"'Project Info'!E49","v":30.190476812806729},{"$f":"'Project Info'!F49","v":0},{"$f":"'Project Info'!G49","v":0},{"$f":"'Project Info'!H49","v":0},{"$f":"'Project Info'!I49","v":0},{"$f":"'Project Info'!J49","v":0},{"$f":"'Project Info'!K49","v":0},{"$f":"'Project Info'!L49","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A50","v":70},{"$f":"'Project Info'!B50","v":75},{"$f":"'Project Info'!C50","v":72.457982050814195},{"$f":"'Project Info'!D50","v":63.604425012889301},{"$f":"'Project Info'!E50","v":29.088683095945193},{"$f":"'Project Info'!F50","v":0},{"$f":"'Project Info'!G50","v":0},{"$f":"'Project Info'!H50","v":0},{"$f":"'Project Info'!I50","v":0},{"$f":"'Project Info'!J50","v":0},{"$f":"'Project Info'!K50","v":0},{"$f":"'Project Info'!L50","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A51","v":65},{"$f":"'Project Info'!B51","v":70},{"$f":"'Project Info'!C51","v":67.815831070966169},{"$f":"'Project Info'!D51","v":61.631331368130574},{"$f":"'Project Info'!E51","v":27.661514889731574},{"$f":"'Project Info'!F51","v":0},{"$f":"'Project Info'!G51","v":0},{"$f":"'Project Info'!H51","v":0},{"$f":"'Project Info'!I51","v":0},{"$f":"'Project Info'!J51","v":0},{"$f":"'Project Info'!K51","v":0},{"$f":"'Project Info'!L51","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A52","v":60},{"$f":"'Project Info'!B52","v":65},{"$f":"'Project Info'!C52","v":62.535961472271332},{"$f":"'Project Info'!D52","v":57.135476922863582},{"$f":"'Project Info'!E52","v":24.623037157728302},{"$f":"'Project Info'!F52","v":0},{"$f":"'Project Info'!G52","v":0},{"$f":"'Project Info'!H52","v":0},{"$f":"'Project Info'!I52","v":0},{"$f":"'Project Info'!J52","v":0},{"$f":"'Project Info'!K52","v":0},{"$f":"'Project Info'!L52","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A53","v":55},{"$f":"'Project Info'!B53","v":60},{"$f":"'Project Info'!C53","v":57.125792270740902},{"$f":"'Project Info'!D53","v":52.596971157053673},{"$f":"'Project Info'!E53","v":21.818001539159841},{"$f":"'Project Info'!F53","v":0},{"$f":"'Project Info'!G53","v":0},{"$f":"'Project Info'!H53","v":0},{"$f":"'Project Info'!I53","v":0},{"$f":"'Project Info'!J53","v":0},{"$f":"'Project Info'!K53","v":0},{"$f":"'Project Info'!L53","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A54","v":50},{"$f":"'Project Info'!B54","v":55},{"$f":"'Project Info'!C54","v":52.235698854337961},{"$f":"'Project Info'!D54","v":48.022768090099298},{"$f":"'Project Info'!E54","v":19.246640192796217},{"$f":"'Project Info'!F54","v":0},{"$f":"'Project Info'!G54","v":0},{"$f":"'Project Info'!H54","v":0},{"$f":"'Project Info'!I54","v":0},{"$f":"'Project Info'!J54","v":0},{"$f":"'Project Info'!K54","v":0},{"$f":"'Project Info'!L54","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A55","v":45},{"$f":"'Project Info'!B55","v":50},{"$f":"'Project Info'!C55","v":47.459170258371508},{"$f":"'Project Info'!D55","v":43.465397050422162},{"$f":"'Project Info'!E55","v":16.894183241713304},{"$f":"'Project Info'!F55","v":0},{"$f":"'Project Info'!G55","v":0},{"$f":"'Project Info'!H55","v":0},{"$f":"'Project Info'!I55","v":0},{"$f":"'Project Info'!J55","v":0},{"$f":"'Project Info'!K55","v":0},{"$f":"'Project Info'!L55","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A56","v":40},{"$f":"'Project Info'!B56","v":45},{"$f":"'Project Info'!C56","v":42.677030404888129},{"$f":"'Project Info'!D56","v":38.812544504634097},{"$f":"'Project Info'!E56","v":14.690265649465921},{"$f":"'Project Info'!F56","v":0},{"$f":"'Project Info'!G56","v":0},{"$f":"'Project Info'!H56","v":0},{"$f":"'Project Info'!I56","v":0},{"$f":"'Project Info'!J56","v":0},{"$f":"'Project Info'!K56","v":0},{"$f":"'Project Info'!L56","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A57","v":35},{"$f":"'Project Info'!B57","v":40},{"$f":"'Project Info'!C57","v":37.333046773755832},{"$f":"'Project Info'!D57","v":33.904706919479686},{"$f":"'Project Info'!E57","v":12.53841602318813},{"$f":"'Project Info'!F57","v":0},{"$f":"'Project Info'!G57","v":0},{"$f":"'Project Info'!H57","v":0},{"$f":"'Project Info'!I57","v":0},{"$f":"'Project Info'!J57","v":0},{"$f":"'Project Info'!K57","v":0},{"$f":"'Project Info'!L57","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A58","v":30},{"$f":"'Project Info'!B58","v":35},{"$f":"'Project Info'!C58","v":32.638179845662044},{"$f":"'Project Info'!D58","v":29.547170928664851},{"$f":"'Project Info'!E58","v":10.728972818165861},{"$f":"'Project Info'!F58","v":0},{"$f":"'Project Info'!G58","v":0},{"$f":"'Project Info'!H58","v":0},{"$f":"'Project Info'!I58","v":0},{"$f":"'Project Info'!J58","v":0},{"$f":"'Project Info'!K58","v":0},{"$f":"'Project Info'!L58","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A59","v":25},{"$f":"'Project Info'!B59","v":30},{"$f":"'Project Info'!C59","v":27.529264646850947},{"$f":"'Project Info'!D59","v":24.652717392657845},{"$f":"'Project Info'!E59","v":8.8041305482613303},{"$f":"'Project Info'!F59","v":0},{"$f":"'Project Info'!G59","v":0},{"$f":"'Project Info'!H59","v":0},{"$f":"'Project Info'!I59","v":0},{"$f":"'Project Info'!J59","v":0},{"$f":"'Project Info'!K59","v":0},{"$f":"'Project Info'!L59","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A60","v":20},{"$f":"'Project Info'!B60","v":25},{"$f":"'Project Info'!C60","v":22.998111483544687},{"$f":"'Project Info'!D60","v":20.383306659827422},{"$f":"'Project Info'!E60","v":7.246164547543378},{"$f":"'Project Info'!F60","v":0},{"$f":"'Project Info'!G60","v":0},{"$f":"'Project Info'!H60","v":0},{"$f":"'Project Info'!I60","v":0},{"$f":"'Project Info'!J60","v":0},{"$f":"'Project Info'!K60","v":0},{"$f":"'Project Info'!L60","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A61","v":15},{"$f":"'Project Info'!B61","v":20},{"$f":"'Project Info'!C61","v":17.808510327474309},{"$f":"'Project Info'!D61","v":15.420865796304254},{"$f":"'Project Info'!E61","v":5.5490484131518292},{"$f":"'Project Info'!F61","v":0},{"$f":"'Project Info'!G61","v":0},{"$f":"'Project Info'!H61","v":0},{"$f":"'Project Info'!I61","v":0},{"$f":"'Project Info'!J61","v":0},{"$f":"'Project Info'!K61","v":0},{"$f":"'Project Info'!L61","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A62","v":10},{"$f":"'Project Info'!B62","v":15},{"$f":"'Project Info'!C62","v":12.269931130346862},{"$f":"'Project Info'!D62","v":10.318264913023604},{"$f":"'Project Info'!E62","v":3.9082824916941998},{"$f":"'Project Info'!F62","v":0},{"$f":"'Project Info'!G62","v":0},{"$f":"'Project Info'!H62","v":0},{"$f":"'Project Info'!I62","v":0},{"$f":"'Project Info'!J62","v":0},{"$f":"'Project Info'!K62","v":0},{"$f":"'Project Info'!L62","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A63","v":5},{"$f":"'Project Info'!B63","v":10},{"$f":"'Project Info'!C63","v":7.3137581369917548},{"$f":"'Project Info'!D63","v":5.7052382449247707},{"$f":"'Project Info'!E63","v":2.5019418419888937},{"$f":"'Project Info'!F63","v":0},{"$f":"'Project Info'!G63","v":0},{"$f":"'Project Info'!H63","v":0},{"$f":"'Project Info'!I63","v":0},{"$f":"'Project Info'!J63","v":0},{"$f":"'Project Info'!K63","v":0},{"$f":"'Project Info'!L63","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A64","v":0},{"$f":"'Project Info'!B64","v":5},{"$f":"'Project Info'!C64","v":2.6119461836144886},{"$f":"'Project Info'!D64","v":1.2699770062067783},{"$f":"'Project Info'!E64","v":1.2046477897733283},{"$f":"'Project Info'!F64","v":0},{"$f":"'Project Info'!G64","v":0},{"$f":"'Project Info'!H64","v":0},{"$f":"'Project Info'!I64","v":0},{"$f":"'Project Info'!J64","v":0},{"$f":"'Project Info'!K64","v":0},{"$f":"'Project Info'!L64","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A65","v":-5},{"$f":"'Project Info'!B65","v":0},{"$f":"'Project Info'!C65","v":-1.6731398516793925},{"$f":"'Project Info'!D65","v":-2.7083318773557807},{"$f":"'Project Info'!E65","v":7.9391832815876459E-2},{"$f":"'Project Info'!F65","v":0},{"$f":"'Project Info'!G65","v":0},{"$f":"'Project Info'!H65","v":0},{"$f":"'Project Info'!I65","v":0},{"$f":"'Project Info'!J65","v":0},{"$f":"'Project Info'!K65","v":0},{"$f":"'Project Info'!L65","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A66","v":-10},{"$f":"'Project Info'!B66","v":-5},{"$f":"'Project Info'!C66","v":-6.5729865085377277},{"$f":"'Project Info'!D66","v":-7.2465935998252222},{"$f":"'Project Info'!E66","v":-1.168423365310433},{"$f":"'Project Info'!F66","v":0},{"$f":"'Project Info'!G66","v":0},{"$f":"'Project Info'!H66","v":0},{"$f":"'Project Info'!I66","v":0},{"$f":"'Project Info'!J66","v":0},{"$f":"'Project Info'!K66","v":0},{"$f":"'Project Info'!L66","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A67","v":-15},{"$f":"'Project Info'!B67","v":-10},{"$f":"'Project Info'!C67","v":-15.32570353422995},{"$f":"'Project Info'!D67","v":-15.707838211108999},{"$f":"'Project Info'!E67","v":-3.4051318156661381},{"$f":"'Project Info'!F67","v":0},{"$f":"'Project Info'!G67","v":0},{"$f":"'Project Info'!H67","v":0},{"$f":"'Project Info'!I67","v":0},{"$f":"'Project Info'!J67","v":0},{"$f":"'Project Info'!K67","v":0},{"$f":"'Project Info'!L67","v":0}]
[]
[]
[null,null,null,null,null,null,"Unoccupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown"]
[null,null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer"]
[null,null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand"]
[null,null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours"]
[null,null,null,null,null,null,{"$f":"'Project Info'!A74","v":100},{"$f":"'Project Info'!B74","v":105},{"$f":"'Project Info'!C74","v":102},{"$f":"'Project Info'!D74","v":76},{"$f":"'Project Info'!E74","v":40},{"$f":"'Project Info'!F74","v":0},{"$f":"'Project Info'!G74","v":0},{"$f":"'Project Info'!H74","v":0},{"$f":"'Project Info'!I74","v":0},{"$f":"'Project Info'!J74","v":0},{"$f":"'Project Info'!K74","v":0},{"$f":"'Project Info'!L74","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A75","v":95},{"$f":"'Project Info'!B75","v":100},{"$f":"'Project Info'!C75","v":95.219272727272724},{"$f":"'Project Info'!D75","v":74.534025272781079},{"$f":"'Project Info'!E75","v":37.923296058061368},{"$f":"'Project Info'!F75","v":0},{"$f":"'Project Info'!G75","v":0},{"$f":"'Project Info'!H75","v":0},{"$f":"'Project Info'!I75","v":0},{"$f":"'Project Info'!J75","v":0},{"$f":"'Project Info'!K75","v":0},{"$f":"'Project Info'!L75","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A76","v":90},{"$f":"'Project Info'!B76","v":95},{"$f":"'Project Info'!C76","v":92.016049160256074},{"$f":"'Project Info'!D76","v":72.911561930607689},{"$f":"'Project Info'!E76","v":36.467095439351091},{"$f":"'Project Info'!F76","v":0},{"$f":"'Project Info'!G76","v":0},{"$f":"'Project Info'!H76","v":0},{"$f":"'Project Info'!I76","v":0},{"$f":"'Project Info'!J76","v":0},{"$f":"'Project Info'!K76","v":0},{"$f":"'Project Info'!L76","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A77","v":85},{"$f":"'Project Info'!B77","v":90},{"$f":"'Project Info'!C77","v":87.457811360655285},{"$f":"'Project Info'!D77","v":70.80538329449476},{"$f":"'Project Info'!E77","v":34.679413213566804},{"$f":"'Project Info'!F77","v":0},{"$f":"'Project Info'!G77","v":0},{"$f":"'Project Info'!H77","v":0},{"$f":"'Project Info'!I77","v":0},{"$f":"'Project Info'!J77","v":0},{"$f":"'Project Info'!K77","v":0},{"$f":"'Project Info'!L77","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A78","v":80},{"$f":"'Project Info'!B78","v":85},{"$f":"'Project Info'!C78","v":82.136788830239965},{"$f":"'Project Info'!D78","v":67.872393622439333},{"$f":"'Project Info'!E78","v":32.296248223809314},{"$f":"'Project Info'!F78","v":0},{"$f":"'Project Info'!G78","v":0},{"$f":"'Project Info'!H78","v":0},{"$f":"'Project Info'!I78","v":0},{"$f":"'Project Info'!J78","v":0},{"$f":"'Project Info'!K78","v":0},{"$f":"'Project Info'!L78","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A79","v":75},{"$f":"'Project Info'!B79","v":80},{"$f":"'Project Info'!C79","v":76.988400157585886},{"$f":"'Project Info'!D79","v":65.129261896908645},{"$f":"'Project Info'!E79","v":30.190476812806729},{"$f":"'Project Info'!F79","v":0},{"$f":"'Project Info'!G79","v":0},{"$f":"'Project Info'!H79","v":0},{"$f":"'Project Info'!I79","v":0},{"$f":"'Project Info'!J79","v":0},{"$f":"'Project Info'!K79","v":0},{"$f":"'Project Info'!L79","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A80","v":70},{"$f":"'Project Info'!B80","v":75},{"$f":"'Project Info'!C80","v":72.457982050814195},{"$f":"'Project Info'!D80","v":63.604425012889301},{"$f":"'Project Info'!E80","v":29.088683095945193},{"$f":"'Project Info'!F80","v":0},{"$f":"'Project Info'!G80","v":0},{"$f":"'Project Info'!H80","v":0},{"$f":"'Project Info'!I80","v":0},{"$f":"'Project Info'!J80","v":0},{"$f":"'Project Info'!K80","v":0},{"$f":"'Project Info'!L80","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A81","v":65},{"$f":"'Project Info'!B81","v":70},{"$f":"'Project Info'!C81","v":67.815831070966169},{"$f":"'Project Info'!D81","v":61.631331368130574},{"$f":"'Project Info'!E81","v":27.661514889731574},{"$f":"'Project Info'!F81","v":0},{"$f":"'Project Info'!G81","v":0},{"$f":"'Project Info'!H81","v":0},{"$f":"'Project Info'!I81","v":0},{"$f":"'Project Info'!J81","v":0},{"$f":"'Project Info'!K81","v":0},{"$f":"'Project Info'!L81","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A82","v":60},{"$f":"'Project Info'!B82","v":65},{"$f":"'Project Info'!C82","v":62.535961472271332},{"$f":"'Project Info'!D82","v":57.135476922863582},{"$f":"'Project Info'!E82","v":24.623037157728302},{"$f":"'Project Info'!F82","v":0},{"$f":"'Project Info'!G82","v":0},{"$f":"'Project Info'!H82","v":0},{"$f":"'Project Info'!I82","v":0},{"$f":"'Project Info'!J82","v":0},{"$f":"'Project Info'!K82","v":0},{"$f":"'Project Info'!L82","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A83","v":55},{"$f":"'Project Info'!B83","v":60},{"$f":"'Project Info'!C83","v":57.125792270740902},{"$f":"'Project Info'!D83","v":52.596971157053673},{"$f":"'Project Info'!E83","v":21.818001539159841},{"$f":"'Project Info'!F83","v":0},{"$f":"'Project Info'!G83","v":0},{"$f":"'Project Info'!H83","v":0},{"$f":"'Project Info'!I83","v":0},{"$f":"'Project Info'!J83","v":0},{"$f":"'Project Info'!K83","v":0},{"$f":"'Project Info'!L83","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A84","v":50},{"$f":"'Project Info'!B84","v":55},{"$f":"'Project Info'!C84","v":52.235698854337961},{"$f":"'Project Info'!D84","v":48.022768090099298},{"$f":"'Project Info'!E84","v":19.246640192796217},{"$f":"'Project Info'!F84","v":0},{"$f":"'Project Info'!G84","v":0},{"$f":"'Project Info'!H84","v":0},{"$f":"'Project Info'!I84","v":0},{"$f":"'Project Info'!J84","v":0},{"$f":"'Project Info'!K84","v":0},{"$f":"'Project Info'!L84","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A85","v":45},{"$f":"'Project Info'!B85","v":50},{"$f":"'Project Info'!C85","v":47.459170258371508},{"$f":"'Project Info'!D85","v":43.465397050422162},{"$f":"'Project Info'!E85","v":16.894183241713304},{"$f":"'Project Info'!F85","v":0},{"$f":"'Project Info'!G85","v":0},{"$f":"'Project Info'!H85","v":0},{"$f":"'Project Info'!I85","v":0},{"$f":"'Project Info'!J85","v":0},{"$f":"'Project Info'!K85","v":0},{"$f":"'Project Info'!L85","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A86","v":40},{"$f":"'Project Info'!B86","v":45},{"$f":"'Project Info'!C86","v":42.677030404888129},{"$f":"'Project Info'!D86","v":38.812544504634097},{"$f":"'Project Info'!E86","v":14.690265649465921},{"$f":"'Project Info'!F86","v":0},{"$f":"'Project Info'!G86","v":0},{"$f":"'Project Info'!H86","v":0},{"$f":"'Project Info'!I86","v":0},{"$f":"'Project Info'!J86","v":0},{"$f":"'Project Info'!K86","v":0},{"$f":"'Project Info'!L86","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A87","v":35},{"$f":"'Project Info'!B87","v":40},{"$f":"'Project Info'!C87","v":37.333046773755832},{"$f":"'Project Info'!D87","v":33.904706919479686},{"$f":"'Project Info'!E87","v":12.53841602318813},{"$f":"'Project Info'!F87","v":0},{"$f":"'Project Info'!G87","v":0},{"$f":"'Project Info'!H87","v":0},{"$f":"'Project Info'!I87","v":0},{"$f":"'Project Info'!J87","v":0},{"$f":"'Project Info'!K87","v":0},{"$f":"'Project Info'!L87","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A88","v":30},{"$f":"'Project Info'!B88","v":35},{"$f":"'Project Info'!C88","v":32.638179845662044},{"$f":"'Project Info'!D88","v":29.547170928664851},{"$f":"'Project Info'!E88","v":10.728972818165861},{"$f":"'Project Info'!F88","v":0},{"$f":"'Project Info'!G88","v":0},{"$f":"'Project Info'!H88","v":0},{"$f":"'Project Info'!I88","v":0},{"$f":"'Project Info'!J88","v":0},{"$f":"'Project Info'!K88","v":0},{"$f":"'Project Info'!L88","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A89","v":25},{"$f":"'Project Info'!B89","v":30},{"$f":"'Project Info'!C89","v":27.529264646850947},{"$f":"'Project Info'!D89","v":24.652717392657845},{"$f":"'Project Info'!E89","v":8.8041305482613303},{"$f":"'Project Info'!F89","v":0},{"$f":"'Project Info'!G89","v":0},{"$f":"'Project Info'!H89","v":0},{"$f":"'Project Info'!I89","v":0},{"$f":"'Project Info'!J89","v":0},{"$f":"'Project Info'!K89","v":0},{"$f":"'Project Info'!L89","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A90","v":20},{"$f":"'Project Info'!B90","v":25},{"$f":"'Project Info'!C90","v":22.998111483544687},{"$f":"'Project Info'!D90","v":20.383306659827422},{"$f":"'Project Info'!E90","v":7.246164547543378},{"$f":"'Project Info'!F90","v":0},{"$f":"'Project Info'!G90","v":0},{"$f":"'Project Info'!H90","v":0},{"$f":"'Project Info'!I90","v":0},{"$f":"'Project Info'!J90","v":0},{"$f":"'Project Info'!K90","v":0},{"$f":"'Project Info'!L90","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A91","v":15},{"$f":"'Project Info'!B91","v":20},{"$f":"'Project Info'!C91","v":17.808510327474309},{"$f":"'Project Info'!D91","v":15.420865796304254},{"$f":"'Project Info'!E91","v":5.5490484131518292},{"$f":"'Project Info'!F91","v":0},{"$f":"'Project Info'!G91","v":0},{"$f":"'Project Info'!H91","v":0},{"$f":"'Project Info'!I91","v":0},{"$f":"'Project Info'!J91","v":0},{"$f":"'Project Info'!K91","v":0},{"$f":"'Project Info'!L91","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A92","v":10},{"$f":"'Project Info'!B92","v":15},{"$f":"'Project Info'!C92","v":12.269931130346862},{"$f":"'Project Info'!D92","v":10.318264913023604},{"$f":"'Project Info'!E92","v":3.9082824916941998},{"$f":"'Project Info'!F92","v":0},{"$f":"'Project Info'!G92","v":0},{"$f":"'Project Info'!H92","v":0},{"$f":"'Project Info'!I92","v":0},{"$f":"'Project Info'!J92","v":0},{"$f":"'Project Info'!K92","v":0},{"$f":"'Project Info'!L92","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A93","v":5},{"$f":"'Project Info'!B93","v":10},{"$f":"'Project Info'!C93","v":7.3137581369917548},{"$f":"'Project Info'!D93","v":5.7052382449247707},{"$f":"'Project Info'!E93","v":2.5019418419888937},{"$f":"'Project Info'!F93","v":0},{"$f":"'Project Info'!G93","v":0},{"$f":"'Project Info'!H93","v":0},{"$f":"'Project Info'!I93","v":0},{"$f":"'Project Info'!J93","v":0},{"$f":"'Project Info'!K93","v":0},{"$f":"'Project Info'!L93","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A94","v":0},{"$f":"'Project Info'!B94","v":5},{"$f":"'Project Info'!C94","v":2.6119461836144886},{"$f":"'Project Info'!D94","v":1.2699770062067783},{"$f":"'Project Info'!E94","v":1.2046477897733283},{"$f":"'Project Info'!F94","v":8760},{"$f":"'Project Info'!G94","v":2672},{"$f":"'Project Info'!H94","v":3160},{"$f":"'Project Info'!I94","v":1344},{"$f":"'Project Info'!J94","v":1584},{"$f":"'Project Info'!K94","v":88},{"$f":"'Project Info'!L94","v":264}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A95","v":-5},{"$f":"'Project Info'!B95","v":0},{"$f":"'Project Info'!C95","v":-1.6731398516793925},{"$f":"'Project Info'!D95","v":-2.7083318773557807},{"$f":"'Project Info'!E95","v":7.9391832815876459E-2},{"$f":"'Project Info'!F95","v":0},{"$f":"'Project Info'!G95","v":0},{"$f":"'Project Info'!H95","v":0},{"$f":"'Project Info'!I95","v":0},{"$f":"'Project Info'!J95","v":0},{"$f":"'Project Info'!K95","v":0},{"$f":"'Project Info'!L95","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A96","v":-10},{"$f":"'Project Info'!B96","v":-5},{"$f":"'Project Info'!C96","v":-6.5729865085377277},{"$f":"'Project Info'!D96","v":-7.2465935998252222},{"$f":"'Project Info'!E96","v":-1.168423365310433},{"$f":"'Project Info'!F96","v":0},{"$f":"'Project Info'!G96","v":0},{"$f":"'Project Info'!H96","v":0},{"$f":"'Project Info'!I96","v":0},{"$f":"'Project Info'!J96","v":0},{"$f":"'Project Info'!K96","v":0},{"$f":"'Project Info'!L96","v":0}]
[null,null,null,null,null,null,{"$f":"'Project Info'!A97","v":-15},{"$f":"'Project Info'!B97","v":-10},{"$f":"'Project Info'!C97","v":-15.32570353422995},{"$f":"'Project Info'!D97","v":-15.707838211108999},{"$f":"'Project Info'!E97","v":-3.4051318156661381},{"$f":"'Project Info'!F97","v":0},{"$f":"'Project Info'!G97","v":0},{"$f":"'Project Info'!H97","v":0},{"$f":"'Project Info'!I97","v":0},{"$f":"'Project Info'!J97","v":0},{"$f":"'Project Info'!K97","v":0},{"$f":"'Project Info'!L97","v":0}]

{"sheet":"Report","index":29,"n_rows":1433,"n_cols":9,"rows_kept":1433,"cut":false,"hidden":true,"merged":[[242,3,242,5],[238,1,238,2],[238,3,238,5],[273,0,292,8],[565,0,565,5],[565,6,566,6],[565,7,566,7],[565,8,566,8],[566,0,566,5],[567,0,567,5],[568,0,568,5],[508,0,508,4],[517,0,529,8],[561,0,561,5],[561,6,562,6],[561,7,562,7],[561,8,562,8],[562,0,562,5],[563,0,563,5],[563,6,564,6],[563,7,564,7],[563,8,564,8],[564,0,564,5],[136,0,140,8],[579,0,606,8],[1062,0,1062,4],[231,1,231,2],[231,3,231,5],[239,3,239,5],[240,3,240,5],[627,1,627,3],[627,6,627,7],[628,1,628,3],[628,6,628,7],[701,8,706,8],[922,0,924,0],[922,1,924,2],[692,0,692,4],[687,0,687,4],[698,0,698,4],[699,0,699,2],[699,3,699,4],[699,5,699,6],[699,7,699,8],[761,0,769,8],[625,6,625,7],[754,0,754,2],[98,1,98,2],[98,3,98,7],[101,1,101,7],[70,2,70,8],[71,2,71,8],[72,2,72,8],[30,1,30,7],[31,1,31,7],[46,1,46,7],[48,1,54,8],[57,1,57,7],[76,2,76,8],[77,2,77,8],[93,1,93,7],[95,1,95,2],[95,3,95,7],[96,1,96,2],[96,3,96,7],[97,1,97,2],[97,3,97,7],[58,1,58,2],[59,1,59,7],[60,1,60,7],[6,1,6,7],[7,1,7,7],[8,1,8,7],[16,1,16,7],[17,1,17,7],[18,1,18,7],[73,2,73,8],[74,2,74,8],[75,2,75,8],[64,2,64,8],[65,2,65,8],[66,2,66,8],[67,2,67,8],[68,2,68,8],[69,2,69,8],[61,1,61,7],[62,2,62,8],[63,2,63,8],[22,1,22,7],[23,1,23,7],[40,1,43,7],[103,1,103,2],[103,3,103,7],[104,1,104,2],[104,3,104,7],[105,1,105,2],[105,3,105,7],[106,1,106,2],[106,3,106,7],[109,1,109,7],[111,1,111,2],[111,3,111,7],[112,1,112,2],[112,3,112,7],[113,1,113,2],[113,3,113,7],[114,1,114,2],[114,3,114,7],[239,1,239,2],[232,1,232,2],[233,1,233,2],[234,1,234,2],[235,1,235,2],[236,1,236,2],[237,1,237,2],[232,3,232,5],[233,3,233,5],[234,3,234,5],[235,3,235,5],[236,3,236,5],[164,0,164,3],[155,1,155,3],[156,1,156,3],[157,1,157,3],[629,6,629,7],[632,6,632,7],[633,1,633,3],[670,0,686,8],[1072,0,1072,1],[1072,6,1072,7],[921,0,921,4],[770,0,770,1],[770,3,770,4],[771,3,771,4],[928,1,928,2],[929,1,929,2],[930,1,930,2],[931,1,931,2],[932,1,932,2],[1056,0,1060,8],[965,0,990,8],[933,1,933,2],[934,1,934,2],[937,0,937,4],[806,0,833,8],[922,7,922,8],[925,1,925,2],[926,1,926,2],[732,0,732,4],[739,2,740,2],[700,3,700,4],[700,5,700,6],[1070,6,1070,7],[165,0,165,3],[396,0,396,4],[237,3,237,5],[241,3,241,5],[636,1,636,3],[636,6,636,7],[632,1,632,3],[487,0,500,8],[623,0,623,4],[624,0,626,0],[624,1,626,3],[624,6,624,7],[626,6,626,7],[630,1,630,3],[630,6,630,7],[609,0,609,4],[631,1,631,3],[631,6,631,7],[629,1,629,3],[1075,0,1075,1],[1076,0,1076,1],[1221,0,1221,8],[1222,0,1222,4],[755,0,755,2],[738,0,738,4],[739,0,740,0],[739,1,740,1],[739,3,740,3],[927,1,927,2],[801,0,801,3],[885,0,909,8],[776,0,780,8],[1223,0,1229,8],[1230,0,1230,4],[633,6,633,7],[634,1,634,3],[634,6,634,7],[635,1,635,3],[635,6,635,7],[1150,8,1152,8],[1151,0,1152,2],[1128,0,1143,8],[1220,0,1220,4],[1068,0,1069,1],[1068,2,1069,2],[1068,3,1069,3],[1068,4,1069,4],[1068,5,1069,5],[1068,6,1069,7],[1082,0,1082,1],[1083,0,1083,1],[700,7,700,8],[701,4,706,4],[701,6,705,6],[715,0,730,8],[1068,8,1069,8],[1231,0,1237,8],[1238,0,1238,4],[1077,0,1077,1],[1078,0,1078,1],[1079,0,1079,1],[1080,0,1080,1],[1081,0,1081,1],[1070,0,1070,1],[1239,0,1244,8],[1085,0,1092,8],[1111,6,1112,6],[1111,5,1112,5],[1098,0,1103,8],[1074,0,1074,1],[1074,6,1074,7],[1075,6,1075,7],[1076,6,1076,7],[1077,6,1077,7],[1078,6,1078,7],[1079,6,1079,7],[1073,0,1073,1],[1073,6,1073,7],[1071,0,1071,1],[1071,6,1071,7],[1247,0,1247,4],[1266,0,1266,4],[1267,0,1267,8],[1268,0,1268,4],[1269,0,1275,8],[1276,0,1276,4],[1277,0,1283,8],[1284,0,1284,4],[1285,0,1290,8],[1293,0,1293,4],[1312,0,1312,4],[1313,0,1313,8],[1314,0,1314,4],[1315,0,1321,8],[1322,0,1322,4],[1323,0,1329,8],[1330,0,1330,4],[1331,0,1336,8],[1339,0,1339,4],[1358,0,1358,4],[1359,0,1359,8],[1360,0,1360,4],[1361,0,1367,8],[1368,0,1368,4],[1369,0,1375,8],[1376,0,1376,4],[1377,0,1382,8],[1385,0,1385,4],[1404,0,1404,1],[1405,0,1410,1],[1405,2,1405,3],[1406,2,1406,3],[1407,2,1407,3],[1408,2,1408,3],[1409,2,1409,3],[1410,2,1410,3],[1424,2,1424,3],[1425,2,1425,3],[1426,2,1426,3],[1427,2,1427,3],[1428,2,1428,3],[1411,0,1412,1],[1411,2,1411,3],[1412,2,1412,3],[1413,0,1413,1],[1413,2,1413,3],[1414,0,1414,1],[1414,2,1414,3],[1415,2,1415,3],[1416,2,1416,3],[1432,0,1549,8],[158,1,158,3],[159,1,159,3],[160,1,160,3],[161,1,161,3],[146,1,146,3],[147,1,147,3],[148,1,148,3],[149,1,149,3],[150,1,150,3],[151,1,151,3],[152,1,152,3],[153,1,153,3],[154,1,154,3],[1417,2,1417,3],[1418,0,1419,1],[1418,2,1418,3],[1419,2,1419,3],[1420,0,1422,1],[1420,2,1420,3],[1421,2,1421,3],[1422,2,1422,3],[1423,0,1428,1],[1423,2,1423,3]]}
[]
[]
[]
[]
[]
[]
[null,{"$f":"'Project Info'!C12","v":0}]
[null,{"$f":"CONCATENATE('Project Info'!C13, \", \",'Project Info'!C14,\", \",'Project Info'!C15)","v":", , NH"}]
[null,"Energy Savings Analysis"]
[]
[]
[]
[]
[]
[]
[]
[null,"PREPARED FOR"]
[null,{"$f":"'Project Info'!F3","v":0}]
[null,{"$f":"'Project Info'!I3","v":0}]
[]
[]
[]
[null,"Draft Report"]
[null,{"$f":"TODAY()","v":"2026-02-24"}]
[]
[]
[null,null,null,null,{"$f":"\"Tool Version: \"& Instructions!$T$9","v":"Tool Version: v2026.02.19"}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"New Construction/Major Renovation\nStreamlined Savings Tool"]
[]
[]
[]
[]
[]
[null,"Disclaimer"]
[]
[null,"Neither the proposed building performance nor the baseline building performance are predictions of actual energy consumption or costs for the proposed design after construction. Actual experience will differ from these calculations due to variations such as occupancy, building operation and maintenance, weather, energy use not covered by this procedure, changes in energy rates between design of the building and occupancy, and the precision of the calculation tool."]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"Table of contents"]
[]
[null,"Savings Summary"]
[null,"Facility Description"]
[null,"Energy Conservation Measures"]
[null,null,{"$f":"IFERROR(VLOOKUP(1,'ECM Summary'!$D$10:$H$25,2,FALSE),\"\")","v":""}]
[null,null,{"$f":"IFERROR(VLOOKUP(2,'ECM Summary'!$D$10:$H$25,2,FALSE),\"\")","v":""}]
[null,null,{"$f":"IFERROR(VLOOKUP(3,'ECM Summary'!$D$10:$H$25,2,FALSE),\"\")","v":""}]
[null,null,{"$f":"IFERROR(VLOOKUP(4,'ECM Summary'!$D$10:$H$25,2,FALSE),\"\")","v":""}]
[null,null,{"$f":"IFERROR(VLOOKUP(5,'ECM Summary'!$D$10:$H$25,2,FALSE),\"\")","v":""}]
[null,null,{"$f":"IFERROR(VLOOKUP(6,'ECM Summary'!$D$10:$H$25,2,FALSE),\"\")","v":""}]
[null,null,{"$f":"IFERROR(VLOOKUP(7,'ECM Summary'!$D$10:$H$25,2,FALSE),\"\")","v":""}]
[null,null,{"$f":"IFERROR(VLOOKUP(8,'ECM Summary'!$D$10:$H$25,2,FALSE),\"\")","v":""}]
[null,null,{"$f":"IFERROR(VLOOKUP(9,'ECM Summary'!$D$10:$H$25,2,FALSE),\"\")","v":""}]
[null,null,{"$f":"IFERROR(VLOOKUP(10,'ECM Summary'!$D$10:$H$25,2,FALSE),\"\")","v":""}]
[null,null,{"$f":"IFERROR(VLOOKUP(11,'ECM Summary'!$D$10:$H$25,2,FALSE),\"\")","v":""}]
[null,null,{"$f":"IFERROR(VLOOKUP(12,'ECM Summary'!$D$10:$H$25,2,FALSE),\"\")","v":""}]
[null,null,{"$f":"IFERROR(VLOOKUP(13,'ECM Summary'!$D$10:$H$25,2,FALSE),\"\")","v":""}]
[null,null,{"$f":"IFERROR(VLOOKUP(14,'ECM Summary'!$D$10:$H$25,2,FALSE),\"\")","v":""}]
[null,null,{"$f":"IFERROR(VLOOKUP(15,'ECM Summary'!$D$10:$H$25,2,FALSE),\"\")","v":""}]
[null,null,{"$f":"IFERROR(VLOOKUP(16,'ECM Summary'!$D$10:$H$25,2,FALSE),\"\")","v":""}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"PROJECT CONTACT INFORMATION"]
[]
[null,{"$f":"'Project Info'!C2","v":"Customer"}]
[]
[null,"Company",null,{"$f":"IF('Project Info'!C3=\"\",\"\",'Project Info'!C3)","v":""}]
[null,"Contact Name",null,{"$f":"IF('Project Info'!C4=\"\",\"\",'Project Info'!C4)","v":""}]
[null,"Contact Email",null,{"$f":"IF('Project Info'!C5=\"\",\"\",'Project Info'!C5)","v":""}]
[null,"Contact Phone",null,{"$f":"IF('Project Info'!C6=\"\",\"\",'Project Info'!C6)","v":""}]
[]
[]
[null,{"$f":"'Project Info'!F2","v":"Electric PA"}]
[]
[null,"Company",null,{"$f":"IF('Project Info'!F3=\"\",\"\",'Project Info'!F3)","v":""}]
[null,"Contact Name",null,{"$f":"IF('Project Info'!F4=\"\",\"\",'Project Info'!F4)","v":""}]
[null,"Contact Email",null,{"$f":"IF('Project Info'!F5=\"\",\"\",'Project Info'!F5)","v":""}]
[null,"Contact Phone",null,{"$f":"IF('Project Info'!F6=\"\",\"\",'Project Info'!F6)","v":""}]
[]
[]
[null,{"$f":"'Project Info'!I2","v":"Gas PA"}]
[]
[null,"Company",null,{"$f":"IF('Project Info'!I3=\"\",\"\",'Project Info'!I3)","v":""}]
[null,"Contact Name",null,{"$f":"IF('Project Info'!I4=\"\",\"\",'Project Info'!I4)","v":""}]
[null,"Contact Email",null,{"$f":"IF('Project Info'!I5=\"\",\"\",'Project Info'!I5)","v":""}]
[null,"Contact Phone",null,{"$f":"IF('Project Info'!I6=\"\",\"\",'Project Info'!I6)","v":""}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Executive  Summary"]
["This project is participating in the New Construction/Major Renovation incentive program under the Performance Buildings or Systems Pathway, which is generally offered to new construction or major renovation projects with building floor area at least 5,000 ft².  Energy savings are evaluated by comparing the design features to the applicable state's Baseline Document, which mostly follows the current Energy Code.\nA summary of the projected energy savings and costs for the project is presented in the tables below."]
[]
[]
[]
[]
["Baseline Code:",null,{"$f":"'Project Info'!C20","v":"2018 IECC / ASHRAE 90.1-2016"}]
["Summary of Annual Energy Savings\n"]
["ECM",null,null,null,"Annual Savings",null,null,"Increm-","Estimated"]
[null,"Description",null,null,{"$f":"'ECM Summary'!J8","v":"Electric"},{"$f":"'ECM Summary'!K8","v":0},"Energy","ental","Incentive"]
[null,null,null,null,{"$f":"'ECM Summary'!J9","v":"kWh"},{"$f":"'ECM Summary'!K9","v":{"$error":"#N/A"}},"Cost","Cost","$"]
[{"$f":"'ECM Summary'!D10","v":""},{"$f":"'ECM Summary'!E10","v":"Bldg Envelope"},null,null,{"$f":"'ECM Summary'!J10","v":""},{"$f":"'ECM Summary'!K10","v":""},{"$f":"'ECM Summary'!L10","v":""},{"$f":"'ECM Summary'!U10","v":""},{"$f":"'ECM Summary'!X10","v":""}]
[{"$f":"'ECM Summary'!D11","v":""},{"$f":"'ECM Summary'!E11","v":"Interior Lighting"},null,null,{"$f":"'ECM Summary'!J11","v":""},{"$f":"'ECM Summary'!K11","v":""},{"$f":"'ECM Summary'!L11","v":""},{"$f":"'ECM Summary'!U11","v":""},{"$f":"'ECM Summary'!X11","v":""}]
[{"$f":"'ECM Summary'!D12","v":""},{"$f":"'ECM Summary'!E12","v":"Exterior Lighting"},null,null,{"$f":"'ECM Summary'!J12","v":""},{"$f":"'ECM Summary'!K12","v":""},{"$f":"'ECM Summary'!L12","v":""},{"$f":"'ECM Summary'!U12","v":""},{"$f":"'ECM Summary'!X12","v":""}]
[{"$f":"'ECM Summary'!D13","v":""},{"$f":"'ECM Summary'!E13","v":"Unitary HVAC (RTU, AC, HP, VRF)"},null,null,{"$f":"'ECM Summary'!J13","v":""},{"$f":"'ECM Summary'!K13","v":""},{"$f":"'ECM Summary'!L13","v":""},{"$f":"'ECM Summary'!U13","v":""},{"$f":"'ECM Summary'!X13","v":""}]
[{"$f":"'ECM Summary'!D14","v":""},{"$f":"'ECM Summary'!E14","v":"High Efficiency Chillers"},null,null,{"$f":"'ECM Summary'!J14","v":""},{"$f":"'ECM Summary'!K14","v":""},{"$f":"'ECM Summary'!L14","v":""},{"$f":"'ECM Summary'!U14","v":""},{"$f":"'ECM Summary'!X14","v":""}]
[{"$f":"'ECM Summary'!D15","v":""},{"$f":"'ECM Summary'!E15","v":"Variable Frequency Drives"},null,null,{"$f":"'ECM Summary'!J15","v":""},{"$f":"'ECM Summary'!K15","v":""},{"$f":"'ECM Summary'!L15","v":""},{"$f":"'ECM Summary'!U15","v":""},{"$f":"'ECM Summary'!X15","v":""}]
[{"$f":"'ECM Summary'!D16","v":""},{"$f":"'ECM Summary'!E16","v":"Energy Recovery"},null,null,{"$f":"'ECM Summary'!J16","v":""},{"$f":"'ECM Summary'!K16","v":""},{"$f":"'ECM Summary'!L16","v":""},{"$f":"'ECM Summary'!U16","v":""},{"$f":"'ECM Summary'!X16","v":""}]
[{"$f":"'ECM Summary'!D17","v":""},{"$f":"'ECM Summary'!E17","v":"Demand Control Ventilation"},null,null,{"$f":"'ECM Summary'!J17","v":""},{"$f":"'ECM Summary'!K17","v":""},{"$f":"'ECM Summary'!L17","v":""},{"$f":"'ECM Summary'!U17","v":""},{"$f":"'ECM Summary'!X17","v":""}]
[{"$f":"'ECM Summary'!D18","v":""},{"$f":"'ECM Summary'!E18","v":"Variable Flow Kitchen Hood"},null,null,{"$f":"'ECM Summary'!J18","v":""},{"$f":"'ECM Summary'!K18","v":""},{"$f":"'ECM Summary'!L18","v":""},{"$f":"'ECM Summary'!U18","v":""},{"$f":"'ECM Summary'!X18","v":""}]
[{"$f":"'ECM Summary'!D19","v":""},{"$f":"'ECM Summary'!E19","v":"Condensing Boilers"},null,null,{"$f":"'ECM Summary'!J19","v":""},{"$f":"'ECM Summary'!K19","v":""},{"$f":"'ECM Summary'!L19","v":""},{"$f":"'ECM Summary'!U19","v":""},{"$f":"'ECM Summary'!X19","v":""}]
[{"$f":"'ECM Summary'!D20","v":""},{"$f":"'ECM Summary'!E20","v":"DHW Heaters"},null,null,{"$f":"'ECM Summary'!J20","v":""},{"$f":"'ECM Summary'!K20","v":""},{"$f":"'ECM Summary'!L20","v":""},{"$f":"'ECM Summary'!U20","v":""},{"$f":"'ECM Summary'!X20","v":""}]
[{"$f":"'ECM Summary'!D21","v":""},{"$f":"'ECM Summary'!E21","v":"Low Flow DHW Fixtures"},null,null,{"$f":"'ECM Summary'!J21","v":""},{"$f":"'ECM Summary'!K21","v":""},{"$f":"'ECM Summary'!L21","v":""},{"$f":"'ECM Summary'!U21","v":""},{"$f":"'ECM Summary'!X21","v":""}]
[{"$f":"'ECM Summary'!D22","v":""},{"$f":"'ECM Summary'!E22","v":0},null,null,{"$f":"'ECM Summary'!J22","v":""},{"$f":"'ECM Summary'!K22","v":""},{"$f":"'ECM Summary'!L22","v":""},{"$f":"'ECM Summary'!U22","v":""},{"$f":"'ECM Summary'!X22","v":""}]
[{"$f":"'ECM Summary'!D23","v":""},{"$f":"'ECM Summary'!E23","v":0},null,null,{"$f":"'ECM Summary'!J23","v":""},{"$f":"'ECM Summary'!K23","v":""},{"$f":"'ECM Summary'!L23","v":""},{"$f":"'ECM Summary'!U23","v":""},{"$f":"'ECM Summary'!X23","v":""}]
[{"$f":"'ECM Summary'!D24","v":""},{"$f":"'ECM Summary'!E24","v":0},null,null,{"$f":"'ECM Summary'!J24","v":""},{"$f":"'ECM Summary'!K24","v":""},{"$f":"'ECM Summary'!L24","v":""},{"$f":"'ECM Summary'!U24","v":""},{"$f":"'ECM Summary'!X24","v":""}]
[{"$f":"'ECM Summary'!D25","v":""},{"$f":"'ECM Summary'!E25","v":0},null,null,{"$f":"'ECM Summary'!J25","v":""},{"$f":"'ECM Summary'!K25","v":""},{"$f":"'ECM Summary'!L25","v":""},{"$f":"'ECM Summary'!U25","v":""},{"$f":"'ECM Summary'!X25","v":""}]
["Total Project Savings",null,null,null,{"$f":"'ECM Summary'!J26","v":0},{"$f":"'ECM Summary'!K26","v":0},{"$f":"'ECM Summary'!L26","v":0},{"$f":"'ECM Summary'!U26","v":0},{"$f":"'ECM Summary'!X26","v":0}]
[]
["Total Electric Savings in MMBtu",null,null,null,{"$f":"(E163*3412)/1000000","v":0}]
["Total Gas Savings in MMBtu",null,null,null,{"$f":"IF(F146=\"therms\",F163/10,F163/1)","v":{"$error":"#N/A"}}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"Facility Description"]
[]
[null,"The project details are as below:"]
[null,{"$f":"'Project Info'!A12","v":"Project Name"},null,{"$f":"'Project Info'!C12","v":0}]
[null,{"$f":"'Project Info'!A13","v":"Street Address"},null,{"$f":"'Project Info'!C13","v":0}]
[null,{"$f":"'Project Info'!A14","v":"City"},null,{"$f":"'Project Info'!C14","v":0}]
[null,{"$f":"'Project Info'!A15","v":"State"},null,{"$f":"'Project Info'!C15","v":"NH"}]
[null,{"$f":"'Project Info'!A16","v":"Weather Data Location (TMYx)"},null,{"$f":"'Project Info'!C16","v":0}]
[null,{"$f":"'Project Info'!A17","v":"Building Area, ft² (excluding parking garage)"},null,{"$f":"'Project Info'!C17","v":0}]
[null,{"$f":"'Project Info'!A18","v":"Building Type"},null,{"$f":"'Project Info'!C18","v":0}]
[null,"Number of Floors",null,{"$f":"'Project Info'!C22","v":0}]
[null,{"$f":"'Project Info'!A19","v":"Program Year"},null,{"$f":"'Project Info'!C19","v":0}]
[null,{"$f":"'Project Info'!A20","v":"Permitting Code"},null,{"$f":"'Project Info'!C20","v":"2018 IECC / ASHRAE 90.1-2016"}]
[null,{"$f":"'Project Info'!A21","v":"Fossil Fuel Type"},null,{"$f":"'Project Info'!C21","v":0}]
[null,{"$f":"'Project Info'!A23","v":"Program Path "},null,{"$f":"'Project Info'!C23","v":0}]
[]
[null,"The building hours of operation are as below:"]
[null,null,null,"Start","End"]
[null,{"$f":"'Project Info'!G15","v":"Weekdays"},null,{"$f":"'Project Info'!I15","v":0},{"$f":"'Project Info'!J15","v":0}]
[null,{"$f":"'Project Info'!G16","v":"Saturday"},null,{"$f":"'Project Info'!I16","v":0},{"$f":"'Project Info'!J16","v":0}]
[null,{"$f":"'Project Info'!G17","v":"Sunday"},null,{"$f":"'Project Info'!I17","v":0},{"$f":"'Project Info'!J17","v":0}]
[null,{"$f":"'Project Info'!G18","v":"Holiday Closures?"},null,{"$f":"'Project Info'!I18","v":"1-Standard US Holidays"}]
[null,{"$f":"'Project Info'!G19","v":"Seasonal Bldg Hours?"},null,{"$f":"'Project Info'!I19","v":"Constant Year-Round"}]
[]
[null,"The monthly/seasonal building use diversity are as below:"]
[null,"Month","Usage Div."]
[null,"Jan",{"$f":"IF($D$251=\"Constant Year-Round\",\"N/A\",'Project Info'!M15)","v":"N/A"}]
[null,"Feb",{"$f":"IF($D$251=\"Constant Year-Round\",\"N/A\",'Project Info'!M16)","v":"N/A"}]
[null,"Mar",{"$f":"IF($D$251=\"Constant Year-Round\",\"N/A\",'Project Info'!M17)","v":"N/A"}]
[null,"Apr",{"$f":"IF($D$251=\"Constant Year-Round\",\"N/A\",'Project Info'!M18)","v":"N/A"}]
[null,"May",{"$f":"IF($D$251=\"Constant Year-Round\",\"N/A\",'Project Info'!M19)","v":"N/A"}]
[null,"Jun",{"$f":"IF($D$251=\"Constant Year-Round\",\"N/A\",'Project Info'!M20)","v":"N/A"}]
[null,"Jul",{"$f":"IF($D$251=\"Constant Year-Round\",\"N/A\",'Project Info'!M21)","v":"N/A"}]
[null,"Aug",{"$f":"IF($D$251=\"Constant Year-Round\",\"N/A\",'Project Info'!M22)","v":"N/A"}]
[null,"Sep",{"$f":"IF($D$251=\"Constant Year-Round\",\"N/A\",'Project Info'!M23)","v":"N/A"}]
[null,"Oct",{"$f":"IF($D$251=\"Constant Year-Round\",\"N/A\",'Project Info'!M24)","v":"N/A"}]
[null,"Nov",{"$f":"IF($D$251=\"Constant Year-Round\",\"N/A\",'Project Info'!M25)","v":"N/A"}]
[null,"Dec",{"$f":"IF($D$251=\"Constant Year-Round\",\"N/A\",'Project Info'!M26)","v":"N/A"}]
[]
[]
[]
[]
[]
[]
["Interior Lighting"]
["\nMeasure Description\nThis measure considers savings from a high performance interior lighting system design with reduced lighting power density below the baseline maximum allowable value.   \n\nCalculation Methodology\nThe baseline reflects the maximum allowable LPD for the building type under the applicable energy code standard and/or state-specific program guidelines.\nThe baseline allowable lighting power density is set automatically based on the building type, state, and energy code or Industry Standard Practice (ISP) minimum performance.  The baseline LPD is multiplied by building area (excluding parking garages) to calculated baseline total interior lighting watts.\nThe proposed/design total interior watts (excluding parking garages) is calculated based on individual lighting fixture wattages and quantities as entered in the lighting fixture table in the tool. There is also an override input option to enter the total design watts directly.\nThe total proposed reduction in design interior lighting power from the baseline is multiplied by the equivalent full load lighting operating hours to determined annual energy savings.  The lighting hours are automatically set by the tool based on building type and data provided from either statewide evaluation reports or the Technical Reference Manual.\n"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Total Savings & Incentive"]
[{"$f":"'Interior Lighting'!F3","v":"Annual Electric Savings"},null,null,{"$f":"'Interior Lighting'!H3","v":0},{"$f":"'Interior Lighting'!I3","v":"kWh"}]
[{"$f":"'Interior Lighting'!F4","v":"Annual Fuel Savings"},null,null,{"$f":"'Interior Lighting'!H4","v":{"$error":"#N/A"}},{"$f":"'Interior Lighting'!I4","v":{"$error":"#N/A"}}]
[{"$f":"'Interior Lighting'!F5","v":"Incremental"},null,null,{"$f":"IF('Interior Lighting'!H6=\"\",'Interior Lighting'!H5,'Interior Lighting'!H6)","v":"NA"},{"$f":"'Interior Lighting'!I5","v":"$"}]
[{"$f":"'Interior Lighting'!F7","v":"Estimated Incentive"},null,null,{"$f":"'Interior Lighting'!H7","v":0},{"$f":"'Interior Lighting'!I7","v":"$"}]
["Interior Lighting Baseline & Savings"]
["Total Baseline Watts",null,null,null,{"$f":"'Interior Lighting'!V5","v":0}]
["Total Proposed Watts",null,null,null,{"$f":"'Interior Lighting'!V10","v":0}]
["Total Watts Saved",null,null,null,{"$f":"'Interior Lighting'!V11","v":0}]
["Base Lighting Hours (EFLH)",null,null,null,{"$f":"IF('Interior Lighting'!W7=\"\",'Interior Lighting'!V7,'Interior Lighting'!W7)","v":{"$error":"#N/A"}}]
["Interior Lighting Incentive"]
["% DLC/ES Certified Fixtures",null,null,null,{"$f":"'Interior Lighting'!V14","v":0}]
["Total Incentive $",null,null,null,{"$f":"'Interior Lighting'!V16","v":0}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Interior Lighting Fixtures",null,null,null,null,null,null,"Total Design Watts:",{"$f":"'Interior Lighting'!T25","v":0}]
["Fixture",null,null,null,null,"Tier 1","Total","Fixture","Total"]
["ID","Model Number",null,null,null,"DLC/ES","Fixture","Wattage","Design"]
[null,null,null,null,null,"Certified?","Qty","W/Fixture","Watts"]
[{"$f":"'Interior Lighting'!G30","v":0},{"$f":"'Interior Lighting'!I30","v":0},null,null,null,{"$f":"'Interior Lighting'!Q30","v":0},{"$f":"'Interior Lighting'!R30","v":0},{"$f":"'Interior Lighting'!S30","v":0},{"$f":"'Interior Lighting'!T30","v":0}]
[{"$f":"'Interior Lighting'!G31","v":0},{"$f":"'Interior Lighting'!I31","v":0},null,null,null,{"$f":"'Interior Lighting'!Q31","v":0},{"$f":"'Interior Lighting'!R31","v":0},{"$f":"'Interior Lighting'!S31","v":0},{"$f":"'Interior Lighting'!T31","v":0}]
[{"$f":"'Interior Lighting'!G32","v":0},{"$f":"'Interior Lighting'!I32","v":0},null,null,null,{"$f":"'Interior Lighting'!Q32","v":0},{"$f":"'Interior Lighting'!R32","v":0},{"$f":"'Interior Lighting'!S32","v":0},{"$f":"'Interior Lighting'!T32","v":0}]
[{"$f":"'Interior Lighting'!G33","v":0},{"$f":"'Interior Lighting'!I33","v":0},null,null,null,{"$f":"'Interior Lighting'!Q33","v":0},{"$f":"'Interior Lighting'!R33","v":0},{"$f":"'Interior Lighting'!S33","v":0},{"$f":"'Interior Lighting'!T33","v":0}]
[{"$f":"'Interior Lighting'!G34","v":0},{"$f":"'Interior Lighting'!I34","v":0},null,null,null,{"$f":"'Interior Lighting'!Q34","v":0},{"$f":"'Interior Lighting'!R34","v":0},{"$f":"'Interior Lighting'!S34","v":0},{"$f":"'Interior Lighting'!T34","v":0}]
[{"$f":"'Interior Lighting'!G35","v":0},{"$f":"'Interior Lighting'!I35","v":0},null,null,null,{"$f":"'Interior Lighting'!Q35","v":0},{"$f":"'Interior Lighting'!R35","v":0},{"$f":"'Interior Lighting'!S35","v":0},{"$f":"'Interior Lighting'!T35","v":0}]
[{"$f":"'Interior Lighting'!G36","v":0},{"$f":"'Interior Lighting'!I36","v":0},null,null,null,{"$f":"'Interior Lighting'!Q36","v":0},{"$f":"'Interior Lighting'!R36","v":0},{"$f":"'Interior Lighting'!S36","v":0},{"$f":"'Interior Lighting'!T36","v":0}]
[{"$f":"'Interior Lighting'!G37","v":0},{"$f":"'Interior Lighting'!I37","v":0},null,null,null,{"$f":"'Interior Lighting'!Q37","v":0},{"$f":"'Interior Lighting'!R37","v":0},{"$f":"'Interior Lighting'!S37","v":0},{"$f":"'Interior Lighting'!T37","v":0}]
[{"$f":"'Interior Lighting'!G38","v":0},{"$f":"'Interior Lighting'!I38","v":0},null,null,null,{"$f":"'Interior Lighting'!Q38","v":0},{"$f":"'Interior Lighting'!R38","v":0},{"$f":"'Interior Lighting'!S38","v":0},{"$f":"'Interior Lighting'!T38","v":0}]
[{"$f":"'Interior Lighting'!G39","v":0},{"$f":"'Interior Lighting'!I39","v":0},null,null,null,{"$f":"'Interior Lighting'!Q39","v":0},{"$f":"'Interior Lighting'!R39","v":0},{"$f":"'Interior Lighting'!S39","v":0},{"$f":"'Interior Lighting'!T39","v":0}]
[{"$f":"'Interior Lighting'!G40","v":0},{"$f":"'Interior Lighting'!I40","v":0},null,null,null,{"$f":"'Interior Lighting'!Q40","v":0},{"$f":"'Interior Lighting'!R40","v":0},{"$f":"'Interior Lighting'!S40","v":0},{"$f":"'Interior Lighting'!T40","v":0}]
[{"$f":"'Interior Lighting'!G41","v":0},{"$f":"'Interior Lighting'!I41","v":0},null,null,null,{"$f":"'Interior Lighting'!Q41","v":0},{"$f":"'Interior Lighting'!R41","v":0},{"$f":"'Interior Lighting'!S41","v":0},{"$f":"'Interior Lighting'!T41","v":0}]
[{"$f":"'Interior Lighting'!G42","v":0},{"$f":"'Interior Lighting'!I42","v":0},null,null,null,{"$f":"'Interior Lighting'!Q42","v":0},{"$f":"'Interior Lighting'!R42","v":0},{"$f":"'Interior Lighting'!S42","v":0},{"$f":"'Interior Lighting'!T42","v":0}]
[{"$f":"'Interior Lighting'!G43","v":0},{"$f":"'Interior Lighting'!I43","v":0},null,null,null,{"$f":"'Interior Lighting'!Q43","v":0},{"$f":"'Interior Lighting'!R43","v":0},{"$f":"'Interior Lighting'!S43","v":0},{"$f":"'Interior Lighting'!T43","v":0}]
[{"$f":"'Interior Lighting'!G44","v":0},{"$f":"'Interior Lighting'!I44","v":0},null,null,null,{"$f":"'Interior Lighting'!Q44","v":0},{"$f":"'Interior Lighting'!R44","v":0},{"$f":"'Interior Lighting'!S44","v":0},{"$f":"'Interior Lighting'!T44","v":0}]
[{"$f":"'Interior Lighting'!G45","v":0},{"$f":"'Interior Lighting'!I45","v":0},null,null,null,{"$f":"'Interior Lighting'!Q45","v":0},{"$f":"'Interior Lighting'!R45","v":0},{"$f":"'Interior Lighting'!S45","v":0},{"$f":"'Interior Lighting'!T45","v":0}]
[{"$f":"'Interior Lighting'!G46","v":0},{"$f":"'Interior Lighting'!I46","v":0},null,null,null,{"$f":"'Interior Lighting'!Q46","v":0},{"$f":"'Interior Lighting'!R46","v":0},{"$f":"'Interior Lighting'!S46","v":0},{"$f":"'Interior Lighting'!T46","v":0}]
[{"$f":"'Interior Lighting'!G47","v":0},{"$f":"'Interior Lighting'!I47","v":0},null,null,null,{"$f":"'Interior Lighting'!Q47","v":0},{"$f":"'Interior Lighting'!R47","v":0},{"$f":"'Interior Lighting'!S47","v":0},{"$f":"'Interior Lighting'!T47","v":0}]
[{"$f":"'Interior Lighting'!G48","v":0},{"$f":"'Interior Lighting'!I48","v":0},null,null,null,{"$f":"'Interior Lighting'!Q48","v":0},{"$f":"'Interior Lighting'!R48","v":0},{"$f":"'Interior Lighting'!S48","v":0},{"$f":"'Interior Lighting'!T48","v":0}]
[{"$f":"'Interior Lighting'!G49","v":0},{"$f":"'Interior Lighting'!I49","v":0},null,null,null,{"$f":"'Interior Lighting'!Q49","v":0},{"$f":"'Interior Lighting'!R49","v":0},{"$f":"'Interior Lighting'!S49","v":0},{"$f":"'Interior Lighting'!T49","v":0}]
[{"$f":"'Interior Lighting'!G50","v":0},{"$f":"'Interior Lighting'!I50","v":0},null,null,null,{"$f":"'Interior Lighting'!Q50","v":0},{"$f":"'Interior Lighting'!R50","v":0},{"$f":"'Interior Lighting'!S50","v":0},{"$f":"'Interior Lighting'!T50","v":0}]
[{"$f":"'Interior Lighting'!G51","v":0},{"$f":"'Interior Lighting'!I51","v":0},null,null,null,{"$f":"'Interior Lighting'!Q51","v":0},{"$f":"'Interior Lighting'!R51","v":0},{"$f":"'Interior Lighting'!S51","v":0},{"$f":"'Interior Lighting'!T51","v":0}]
[{"$f":"'Interior Lighting'!G52","v":0},{"$f":"'Interior Lighting'!I52","v":0},null,null,null,{"$f":"'Interior Lighting'!Q52","v":0},{"$f":"'Interior Lighting'!R52","v":0},{"$f":"'Interior Lighting'!S52","v":0},{"$f":"'Interior Lighting'!T52","v":0}]
[{"$f":"'Interior Lighting'!G53","v":0},{"$f":"'Interior Lighting'!I53","v":0},null,null,null,{"$f":"'Interior Lighting'!Q53","v":0},{"$f":"'Interior Lighting'!R53","v":0},{"$f":"'Interior Lighting'!S53","v":0},{"$f":"'Interior Lighting'!T53","v":0}]
[{"$f":"'Interior Lighting'!G54","v":0},{"$f":"'Interior Lighting'!I54","v":0},null,null,null,{"$f":"'Interior Lighting'!Q54","v":0},{"$f":"'Interior Lighting'!R54","v":0},{"$f":"'Interior Lighting'!S54","v":0},{"$f":"'Interior Lighting'!T54","v":0}]
[{"$f":"'Interior Lighting'!G55","v":0},{"$f":"'Interior Lighting'!I55","v":0},null,null,null,{"$f":"'Interior Lighting'!Q55","v":0},{"$f":"'Interior Lighting'!R55","v":0},{"$f":"'Interior Lighting'!S55","v":0},{"$f":"'Interior Lighting'!T55","v":0}]
[{"$f":"'Interior Lighting'!G56","v":0},{"$f":"'Interior Lighting'!I56","v":0},null,null,null,{"$f":"'Interior Lighting'!Q56","v":0},{"$f":"'Interior Lighting'!R56","v":0},{"$f":"'Interior Lighting'!S56","v":0},{"$f":"'Interior Lighting'!T56","v":0}]
[{"$f":"'Interior Lighting'!G57","v":0},{"$f":"'Interior Lighting'!I57","v":0},null,null,null,{"$f":"'Interior Lighting'!Q57","v":0},{"$f":"'Interior Lighting'!R57","v":0},{"$f":"'Interior Lighting'!S57","v":0},{"$f":"'Interior Lighting'!T57","v":0}]
[{"$f":"'Interior Lighting'!G58","v":0},{"$f":"'Interior Lighting'!I58","v":0},null,null,null,{"$f":"'Interior Lighting'!Q58","v":0},{"$f":"'Interior Lighting'!R58","v":0},{"$f":"'Interior Lighting'!S58","v":0},{"$f":"'Interior Lighting'!T58","v":0}]
[{"$f":"'Interior Lighting'!G59","v":0},{"$f":"'Interior Lighting'!I59","v":0},null,null,null,{"$f":"'Interior Lighting'!Q59","v":0},{"$f":"'Interior Lighting'!R59","v":0},{"$f":"'Interior Lighting'!S59","v":0},{"$f":"'Interior Lighting'!T59","v":0}]
[{"$f":"'Interior Lighting'!G60","v":0},{"$f":"'Interior Lighting'!I60","v":0},null,null,null,{"$f":"'Interior Lighting'!Q60","v":0},{"$f":"'Interior Lighting'!R60","v":0},{"$f":"'Interior Lighting'!S60","v":0},{"$f":"'Interior Lighting'!T60","v":0}]
[{"$f":"'Interior Lighting'!G61","v":0},{"$f":"'Interior Lighting'!I61","v":0},null,null,null,{"$f":"'Interior Lighting'!Q61","v":0},{"$f":"'Interior Lighting'!R61","v":0},{"$f":"'Interior Lighting'!S61","v":0},{"$f":"'Interior Lighting'!T61","v":0}]
[{"$f":"'Interior Lighting'!G62","v":0},{"$f":"'Interior Lighting'!I62","v":0},null,null,null,{"$f":"'Interior Lighting'!Q62","v":0},{"$f":"'Interior Lighting'!R62","v":0},{"$f":"'Interior Lighting'!S62","v":0},{"$f":"'Interior Lighting'!T62","v":0}]
[{"$f":"'Interior Lighting'!G63","v":0},{"$f":"'Interior Lighting'!I63","v":0},null,null,null,{"$f":"'Interior Lighting'!Q63","v":0},{"$f":"'Interior Lighting'!R63","v":0},{"$f":"'Interior Lighting'!S63","v":0},{"$f":"'Interior Lighting'!T63","v":0}]
[{"$f":"'Interior Lighting'!G64","v":0},{"$f":"'Interior Lighting'!I64","v":0},null,null,null,{"$f":"'Interior Lighting'!Q64","v":0},{"$f":"'Interior Lighting'!R64","v":0},{"$f":"'Interior Lighting'!S64","v":0},{"$f":"'Interior Lighting'!T64","v":0}]
[{"$f":"'Interior Lighting'!G65","v":0},{"$f":"'Interior Lighting'!I65","v":0},null,null,null,{"$f":"'Interior Lighting'!Q65","v":0},{"$f":"'Interior Lighting'!R65","v":0},{"$f":"'Interior Lighting'!S65","v":0},{"$f":"'Interior Lighting'!T65","v":0}]
[{"$f":"'Interior Lighting'!G66","v":0},{"$f":"'Interior Lighting'!I66","v":0},null,null,null,{"$f":"'Interior Lighting'!Q66","v":0},{"$f":"'Interior Lighting'!R66","v":0},{"$f":"'Interior Lighting'!S66","v":0},{"$f":"'Interior Lighting'!T66","v":0}]
[{"$f":"'Interior Lighting'!G67","v":0},{"$f":"'Interior Lighting'!I67","v":0},null,null,null,{"$f":"'Interior Lighting'!Q67","v":0},{"$f":"'Interior Lighting'!R67","v":0},{"$f":"'Interior Lighting'!S67","v":0},{"$f":"'Interior Lighting'!T67","v":0}]
[{"$f":"'Interior Lighting'!G68","v":0},{"$f":"'Interior Lighting'!I68","v":0},null,null,null,{"$f":"'Interior Lighting'!Q68","v":0},{"$f":"'Interior Lighting'!R68","v":0},{"$f":"'Interior Lighting'!S68","v":0},{"$f":"'Interior Lighting'!T68","v":0}]
[{"$f":"'Interior Lighting'!G69","v":0},{"$f":"'Interior Lighting'!I69","v":0},null,null,null,{"$f":"'Interior Lighting'!Q69","v":0},{"$f":"'Interior Lighting'!R69","v":0},{"$f":"'Interior Lighting'!S69","v":0},{"$f":"'Interior Lighting'!T69","v":0}]
[{"$f":"'Interior Lighting'!G70","v":0},{"$f":"'Interior Lighting'!I70","v":0},null,null,null,{"$f":"'Interior Lighting'!Q70","v":0},{"$f":"'Interior Lighting'!R70","v":0},{"$f":"'Interior Lighting'!S70","v":0},{"$f":"'Interior Lighting'!T70","v":0}]
[{"$f":"'Interior Lighting'!G71","v":0},{"$f":"'Interior Lighting'!I71","v":0},null,null,null,{"$f":"'Interior Lighting'!Q71","v":0},{"$f":"'Interior Lighting'!R71","v":0},{"$f":"'Interior Lighting'!S71","v":0},{"$f":"'Interior Lighting'!T71","v":0}]
[{"$f":"'Interior Lighting'!G73","v":0},{"$f":"'Interior Lighting'!I73","v":0},null,null,null,{"$f":"'Interior Lighting'!Q73","v":0},{"$f":"'Interior Lighting'!R73","v":0},{"$f":"'Interior Lighting'!S73","v":0},{"$f":"'Interior Lighting'!T73","v":0}]
[{"$f":"'Interior Lighting'!G74","v":0},{"$f":"'Interior Lighting'!I74","v":0},null,null,null,{"$f":"'Interior Lighting'!Q74","v":0},{"$f":"'Interior Lighting'!R74","v":0},{"$f":"'Interior Lighting'!S74","v":0},{"$f":"'Interior Lighting'!T74","v":0}]
[{"$f":"'Interior Lighting'!G75","v":0},{"$f":"'Interior Lighting'!I75","v":0},null,null,null,{"$f":"'Interior Lighting'!Q75","v":0},{"$f":"'Interior Lighting'!R75","v":0},{"$f":"'Interior Lighting'!S75","v":0},{"$f":"'Interior Lighting'!T75","v":0}]
[{"$f":"'Interior Lighting'!G76","v":0},{"$f":"'Interior Lighting'!I76","v":0},null,null,null,{"$f":"'Interior Lighting'!Q76","v":0},{"$f":"'Interior Lighting'!R76","v":0},{"$f":"'Interior Lighting'!S76","v":0},{"$f":"'Interior Lighting'!T76","v":0}]
[{"$f":"'Interior Lighting'!G77","v":0},{"$f":"'Interior Lighting'!I77","v":0},null,null,null,{"$f":"'Interior Lighting'!Q77","v":0},{"$f":"'Interior Lighting'!R77","v":0},{"$f":"'Interior Lighting'!S77","v":0},{"$f":"'Interior Lighting'!T77","v":0}]
[{"$f":"'Interior Lighting'!G78","v":0},{"$f":"'Interior Lighting'!I78","v":0},null,null,null,{"$f":"'Interior Lighting'!Q78","v":0},{"$f":"'Interior Lighting'!R78","v":0},{"$f":"'Interior Lighting'!S78","v":0},{"$f":"'Interior Lighting'!T78","v":0}]
[{"$f":"'Interior Lighting'!G79","v":0},{"$f":"'Interior Lighting'!I79","v":0},null,null,null,{"$f":"'Interior Lighting'!Q79","v":0},{"$f":"'Interior Lighting'!R79","v":0},{"$f":"'Interior Lighting'!S79","v":0},{"$f":"'Interior Lighting'!T79","v":0}]
[{"$f":"'Interior Lighting'!G80","v":0},{"$f":"'Interior Lighting'!I80","v":0},null,null,null,{"$f":"'Interior Lighting'!Q80","v":0},{"$f":"'Interior Lighting'!R80","v":0},{"$f":"'Interior Lighting'!S80","v":0},{"$f":"'Interior Lighting'!T80","v":0}]
[{"$f":"'Interior Lighting'!G81","v":0},{"$f":"'Interior Lighting'!I81","v":0},null,null,null,{"$f":"'Interior Lighting'!Q81","v":0},{"$f":"'Interior Lighting'!R81","v":0},{"$f":"'Interior Lighting'!S81","v":0},{"$f":"'Interior Lighting'!T81","v":0}]
[{"$f":"'Interior Lighting'!G82","v":0},{"$f":"'Interior Lighting'!I82","v":0},null,null,null,{"$f":"'Interior Lighting'!Q82","v":0},{"$f":"'Interior Lighting'!R82","v":0},{"$f":"'Interior Lighting'!S82","v":0},{"$f":"'Interior Lighting'!T82","v":0}]
[{"$f":"'Interior Lighting'!G83","v":0},{"$f":"'Interior Lighting'!I83","v":0},null,null,null,{"$f":"'Interior Lighting'!Q83","v":0},{"$f":"'Interior Lighting'!R83","v":0},{"$f":"'Interior Lighting'!S83","v":0},{"$f":"'Interior Lighting'!T83","v":0}]
[{"$f":"'Interior Lighting'!G84","v":0},{"$f":"'Interior Lighting'!I84","v":0},null,null,null,{"$f":"'Interior Lighting'!Q84","v":0},{"$f":"'Interior Lighting'!R84","v":0},{"$f":"'Interior Lighting'!S84","v":0},{"$f":"'Interior Lighting'!T84","v":0}]
[{"$f":"'Interior Lighting'!G85","v":0},{"$f":"'Interior Lighting'!I85","v":0},null,null,null,{"$f":"'Interior Lighting'!Q85","v":0},{"$f":"'Interior Lighting'!R85","v":0},{"$f":"'Interior Lighting'!S85","v":0},{"$f":"'Interior Lighting'!T85","v":0}]
[{"$f":"'Interior Lighting'!G86","v":0},{"$f":"'Interior Lighting'!I86","v":0},null,null,null,{"$f":"'Interior Lighting'!Q86","v":0},{"$f":"'Interior Lighting'!R86","v":0},{"$f":"'Interior Lighting'!S86","v":0},{"$f":"'Interior Lighting'!T86","v":0}]
[{"$f":"'Interior Lighting'!G87","v":0},{"$f":"'Interior Lighting'!I87","v":0},null,null,null,{"$f":"'Interior Lighting'!Q87","v":0},{"$f":"'Interior Lighting'!R87","v":0},{"$f":"'Interior Lighting'!S87","v":0},{"$f":"'Interior Lighting'!T87","v":0}]
[{"$f":"'Interior Lighting'!G88","v":0},{"$f":"'Interior Lighting'!I88","v":0},null,null,null,{"$f":"'Interior Lighting'!Q88","v":0},{"$f":"'Interior Lighting'!R88","v":0},{"$f":"'Interior Lighting'!S88","v":0},{"$f":"'Interior Lighting'!T88","v":0}]
[{"$f":"'Interior Lighting'!G89","v":0},{"$f":"'Interior Lighting'!I89","v":0},null,null,null,{"$f":"'Interior Lighting'!Q89","v":0},{"$f":"'Interior Lighting'!R89","v":0},{"$f":"'Interior Lighting'!S89","v":0},{"$f":"'Interior Lighting'!T89","v":0}]
[{"$f":"'Interior Lighting'!G90","v":0},{"$f":"'Interior Lighting'!I90","v":0},null,null,null,{"$f":"'Interior Lighting'!Q90","v":0},{"$f":"'Interior Lighting'!R90","v":0},{"$f":"'Interior Lighting'!S90","v":0},{"$f":"'Interior Lighting'!T90","v":0}]
[{"$f":"'Interior Lighting'!G91","v":0},{"$f":"'Interior Lighting'!I91","v":0},null,null,null,{"$f":"'Interior Lighting'!Q91","v":0},{"$f":"'Interior Lighting'!R91","v":0},{"$f":"'Interior Lighting'!S91","v":0},{"$f":"'Interior Lighting'!T91","v":0}]
[{"$f":"'Interior Lighting'!G92","v":0},{"$f":"'Interior Lighting'!I92","v":0},null,null,null,{"$f":"'Interior Lighting'!Q92","v":0},{"$f":"'Interior Lighting'!R92","v":0},{"$f":"'Interior Lighting'!S92","v":0},{"$f":"'Interior Lighting'!T92","v":0}]
[{"$f":"'Interior Lighting'!G93","v":0},{"$f":"'Interior Lighting'!I93","v":0},null,null,null,{"$f":"'Interior Lighting'!Q93","v":0},{"$f":"'Interior Lighting'!R93","v":0},{"$f":"'Interior Lighting'!S93","v":0},{"$f":"'Interior Lighting'!T93","v":0}]
[{"$f":"'Interior Lighting'!G94","v":0},{"$f":"'Interior Lighting'!I94","v":0},null,null,null,{"$f":"'Interior Lighting'!Q94","v":0},{"$f":"'Interior Lighting'!R94","v":0},{"$f":"'Interior Lighting'!S94","v":0},{"$f":"'Interior Lighting'!T94","v":0}]
[{"$f":"'Interior Lighting'!G95","v":0},{"$f":"'Interior Lighting'!I95","v":0},null,null,null,{"$f":"'Interior Lighting'!Q95","v":0},{"$f":"'Interior Lighting'!R95","v":0},{"$f":"'Interior Lighting'!S95","v":0},{"$f":"'Interior Lighting'!T95","v":0}]
[{"$f":"'Interior Lighting'!G96","v":0},{"$f":"'Interior Lighting'!I96","v":0},null,null,null,{"$f":"'Interior Lighting'!Q96","v":0},{"$f":"'Interior Lighting'!R96","v":0},{"$f":"'Interior Lighting'!S96","v":0},{"$f":"'Interior Lighting'!T96","v":0}]
[{"$f":"'Interior Lighting'!G97","v":0},{"$f":"'Interior Lighting'!I97","v":0},null,null,null,{"$f":"'Interior Lighting'!Q97","v":0},{"$f":"'Interior Lighting'!R97","v":0},{"$f":"'Interior Lighting'!S97","v":0},{"$f":"'Interior Lighting'!T97","v":0}]
[{"$f":"'Interior Lighting'!G98","v":0},{"$f":"'Interior Lighting'!I98","v":0},null,null,null,{"$f":"'Interior Lighting'!Q98","v":0},{"$f":"'Interior Lighting'!R98","v":0},{"$f":"'Interior Lighting'!S98","v":0},{"$f":"'Interior Lighting'!T98","v":0}]
[{"$f":"'Interior Lighting'!G99","v":0},{"$f":"'Interior Lighting'!I99","v":0},null,null,null,{"$f":"'Interior Lighting'!Q99","v":0},{"$f":"'Interior Lighting'!R99","v":0},{"$f":"'Interior Lighting'!S99","v":0},{"$f":"'Interior Lighting'!T99","v":0}]
[]
[]
[]
["Enclosed Parking Garage Lighting"]
[]
["Enclosed Parking Garage Lighting Baseline"]
["Total Baseline Watts",null,null,null,{"$f":"'Interior Lighting'!AB5","v":0}]
["Base Lighting Hours (EFLH)",null,null,null,{"$f":"IF('Interior Lighting'!AC7=\"\",'Interior Lighting'!AB7,'Interior Lighting'!AC7)","v":6552}]
["Enclosed Parking Garage Lighting Proposed"]
["Total Proposed Watts",null,null,null,{"$f":"'Interior Lighting'!AB10","v":0}]
["Total Watts Saved",null,null,null,{"$f":"'Interior Lighting'!AB11","v":0}]
["Enclosed Parking Garage Lighting Incentive"]
["% Tier 1 Eligible",null,null,null,{"$f":"'Interior Lighting'!AB14","v":0}]
["Total Incentive $",null,null,null,{"$f":"'Interior Lighting'!AB16","v":0}]
[]
[]
[]
[]
[]
[]
[]
["Enclosed Parking Garage Lighting Fixtures",null,null,null,null,null,"Total Design Watts",null,{"$f":"'Interior Lighting'!AM25","v":0}]
["Fixture",null,null,null,null,"Tier 1","Total","Fixture","Total"]
["ID","Model Number",null,null,null,"DLC/ES","Fixture","Wattage","Design"]
[null,null,null,null,null,"Certified?","Qty","W/Fixture","Watts"]
[{"$f":"'Interior Lighting'!Z30","v":0},{"$f":"'Interior Lighting'!AA30","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ30","v":0},{"$f":"'Interior Lighting'!AK30","v":0},{"$f":"'Interior Lighting'!AL30","v":0},{"$f":"'Interior Lighting'!AM30","v":0}]
[{"$f":"'Interior Lighting'!Z31","v":0},{"$f":"'Interior Lighting'!AA31","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ31","v":0},{"$f":"'Interior Lighting'!AK31","v":0},{"$f":"'Interior Lighting'!AL31","v":0},{"$f":"'Interior Lighting'!AM31","v":0}]
[{"$f":"'Interior Lighting'!Z32","v":0},{"$f":"'Interior Lighting'!AA32","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ32","v":0},{"$f":"'Interior Lighting'!AK32","v":0},{"$f":"'Interior Lighting'!AL32","v":0},{"$f":"'Interior Lighting'!AM32","v":0}]
[{"$f":"'Interior Lighting'!Z33","v":0},{"$f":"'Interior Lighting'!AA33","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ33","v":0},{"$f":"'Interior Lighting'!AK33","v":0},{"$f":"'Interior Lighting'!AL33","v":0},{"$f":"'Interior Lighting'!AM33","v":0}]
[{"$f":"'Interior Lighting'!Z34","v":0},{"$f":"'Interior Lighting'!AA34","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ34","v":0},{"$f":"'Interior Lighting'!AK34","v":0},{"$f":"'Interior Lighting'!AL34","v":0},{"$f":"'Interior Lighting'!AM34","v":0}]
[{"$f":"'Interior Lighting'!Z35","v":0},{"$f":"'Interior Lighting'!AA35","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ35","v":0},{"$f":"'Interior Lighting'!AK35","v":0},{"$f":"'Interior Lighting'!AL35","v":0},{"$f":"'Interior Lighting'!AM35","v":0}]
[{"$f":"'Interior Lighting'!Z36","v":0},{"$f":"'Interior Lighting'!AA36","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ36","v":0},{"$f":"'Interior Lighting'!AK36","v":0},{"$f":"'Interior Lighting'!AL36","v":0},{"$f":"'Interior Lighting'!AM36","v":0}]
[{"$f":"'Interior Lighting'!Z37","v":0},{"$f":"'Interior Lighting'!AA37","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ37","v":0},{"$f":"'Interior Lighting'!AK37","v":0},{"$f":"'Interior Lighting'!AL37","v":0},{"$f":"'Interior Lighting'!AM37","v":0}]
[{"$f":"'Interior Lighting'!Z38","v":0},{"$f":"'Interior Lighting'!AA38","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ38","v":0},{"$f":"'Interior Lighting'!AK38","v":0},{"$f":"'Interior Lighting'!AL38","v":0},{"$f":"'Interior Lighting'!AM38","v":0}]
[{"$f":"'Interior Lighting'!Z39","v":0},{"$f":"'Interior Lighting'!AA39","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ39","v":0},{"$f":"'Interior Lighting'!AK39","v":0},{"$f":"'Interior Lighting'!AL39","v":0},{"$f":"'Interior Lighting'!AM39","v":0}]
[{"$f":"'Interior Lighting'!Z40","v":0},{"$f":"'Interior Lighting'!AA40","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ40","v":0},{"$f":"'Interior Lighting'!AK40","v":0},{"$f":"'Interior Lighting'!AL40","v":0},{"$f":"'Interior Lighting'!AM40","v":0}]
[{"$f":"'Interior Lighting'!Z41","v":0},{"$f":"'Interior Lighting'!AA41","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ41","v":0},{"$f":"'Interior Lighting'!AK41","v":0},{"$f":"'Interior Lighting'!AL41","v":0},{"$f":"'Interior Lighting'!AM41","v":0}]
[{"$f":"'Interior Lighting'!Z42","v":0},{"$f":"'Interior Lighting'!AA42","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ42","v":0},{"$f":"'Interior Lighting'!AK42","v":0},{"$f":"'Interior Lighting'!AL42","v":0},{"$f":"'Interior Lighting'!AM42","v":0}]
[{"$f":"'Interior Lighting'!Z43","v":0},{"$f":"'Interior Lighting'!AA43","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ43","v":0},{"$f":"'Interior Lighting'!AK43","v":0},{"$f":"'Interior Lighting'!AL43","v":0},{"$f":"'Interior Lighting'!AM43","v":0}]
[{"$f":"'Interior Lighting'!Z44","v":0},{"$f":"'Interior Lighting'!AA44","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ44","v":0},{"$f":"'Interior Lighting'!AK44","v":0},{"$f":"'Interior Lighting'!AL44","v":0},{"$f":"'Interior Lighting'!AM44","v":0}]
[{"$f":"'Interior Lighting'!Z45","v":0},{"$f":"'Interior Lighting'!AA45","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ45","v":0},{"$f":"'Interior Lighting'!AK45","v":0},{"$f":"'Interior Lighting'!AL45","v":0},{"$f":"'Interior Lighting'!AM45","v":0}]
[{"$f":"'Interior Lighting'!Z46","v":0},{"$f":"'Interior Lighting'!AA46","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ46","v":0},{"$f":"'Interior Lighting'!AK46","v":0},{"$f":"'Interior Lighting'!AL46","v":0},{"$f":"'Interior Lighting'!AM46","v":0}]
[{"$f":"'Interior Lighting'!Z47","v":0},{"$f":"'Interior Lighting'!AA47","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ47","v":0},{"$f":"'Interior Lighting'!AK47","v":0},{"$f":"'Interior Lighting'!AL47","v":0},{"$f":"'Interior Lighting'!AM47","v":0}]
[{"$f":"'Interior Lighting'!Z48","v":0},{"$f":"'Interior Lighting'!AA48","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ48","v":0},{"$f":"'Interior Lighting'!AK48","v":0},{"$f":"'Interior Lighting'!AL48","v":0},{"$f":"'Interior Lighting'!AM48","v":0}]
[{"$f":"'Interior Lighting'!Z49","v":0},{"$f":"'Interior Lighting'!AA49","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ49","v":0},{"$f":"'Interior Lighting'!AK49","v":0},{"$f":"'Interior Lighting'!AL49","v":0},{"$f":"'Interior Lighting'!AM49","v":0}]
[{"$f":"'Interior Lighting'!Z50","v":0},{"$f":"'Interior Lighting'!AA50","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ50","v":0},{"$f":"'Interior Lighting'!AK50","v":0},{"$f":"'Interior Lighting'!AL50","v":0},{"$f":"'Interior Lighting'!AM50","v":0}]
[{"$f":"'Interior Lighting'!Z51","v":0},{"$f":"'Interior Lighting'!AA51","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ51","v":0},{"$f":"'Interior Lighting'!AK51","v":0},{"$f":"'Interior Lighting'!AL51","v":0},{"$f":"'Interior Lighting'!AM51","v":0}]
[{"$f":"'Interior Lighting'!Z52","v":0},{"$f":"'Interior Lighting'!AA52","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ52","v":0},{"$f":"'Interior Lighting'!AK52","v":0},{"$f":"'Interior Lighting'!AL52","v":0},{"$f":"'Interior Lighting'!AM52","v":0}]
[{"$f":"'Interior Lighting'!Z53","v":0},{"$f":"'Interior Lighting'!AA53","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ53","v":0},{"$f":"'Interior Lighting'!AK53","v":0},{"$f":"'Interior Lighting'!AL53","v":0},{"$f":"'Interior Lighting'!AM53","v":0}]
[{"$f":"'Interior Lighting'!Z54","v":0},{"$f":"'Interior Lighting'!AA54","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ54","v":0},{"$f":"'Interior Lighting'!AK54","v":0},{"$f":"'Interior Lighting'!AL54","v":0},{"$f":"'Interior Lighting'!AM54","v":0}]
[{"$f":"'Interior Lighting'!Z55","v":0},{"$f":"'Interior Lighting'!AA55","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ55","v":0},{"$f":"'Interior Lighting'!AK55","v":0},{"$f":"'Interior Lighting'!AL55","v":0},{"$f":"'Interior Lighting'!AM55","v":0}]
[{"$f":"'Interior Lighting'!Z56","v":0},{"$f":"'Interior Lighting'!AA56","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ56","v":0},{"$f":"'Interior Lighting'!AK56","v":0},{"$f":"'Interior Lighting'!AL56","v":0},{"$f":"'Interior Lighting'!AM56","v":0}]
[{"$f":"'Interior Lighting'!Z57","v":0},{"$f":"'Interior Lighting'!AA57","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ57","v":0},{"$f":"'Interior Lighting'!AK57","v":0},{"$f":"'Interior Lighting'!AL57","v":0},{"$f":"'Interior Lighting'!AM57","v":0}]
[{"$f":"'Interior Lighting'!Z58","v":0},{"$f":"'Interior Lighting'!AA58","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ58","v":0},{"$f":"'Interior Lighting'!AK58","v":0},{"$f":"'Interior Lighting'!AL58","v":0},{"$f":"'Interior Lighting'!AM58","v":0}]
[{"$f":"'Interior Lighting'!Z59","v":0},{"$f":"'Interior Lighting'!AA59","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ59","v":0},{"$f":"'Interior Lighting'!AK59","v":0},{"$f":"'Interior Lighting'!AL59","v":0},{"$f":"'Interior Lighting'!AM59","v":0}]
[{"$f":"'Interior Lighting'!Z60","v":0},{"$f":"'Interior Lighting'!AA60","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ60","v":0},{"$f":"'Interior Lighting'!AK60","v":0},{"$f":"'Interior Lighting'!AL60","v":0},{"$f":"'Interior Lighting'!AM60","v":0}]
[{"$f":"'Interior Lighting'!Z61","v":0},{"$f":"'Interior Lighting'!AA61","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ61","v":0},{"$f":"'Interior Lighting'!AK61","v":0},{"$f":"'Interior Lighting'!AL61","v":0},{"$f":"'Interior Lighting'!AM61","v":0}]
[{"$f":"'Interior Lighting'!Z62","v":0},{"$f":"'Interior Lighting'!AA62","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ62","v":0},{"$f":"'Interior Lighting'!AK62","v":0},{"$f":"'Interior Lighting'!AL62","v":0},{"$f":"'Interior Lighting'!AM62","v":0}]
[{"$f":"'Interior Lighting'!Z63","v":0},{"$f":"'Interior Lighting'!AA63","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ63","v":0},{"$f":"'Interior Lighting'!AK63","v":0},{"$f":"'Interior Lighting'!AL63","v":0},{"$f":"'Interior Lighting'!AM63","v":0}]
[{"$f":"'Interior Lighting'!Z64","v":0},{"$f":"'Interior Lighting'!AA64","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ64","v":0},{"$f":"'Interior Lighting'!AK64","v":0},{"$f":"'Interior Lighting'!AL64","v":0},{"$f":"'Interior Lighting'!AM64","v":0}]
[{"$f":"'Interior Lighting'!Z65","v":0},{"$f":"'Interior Lighting'!AA65","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ65","v":0},{"$f":"'Interior Lighting'!AK65","v":0},{"$f":"'Interior Lighting'!AL65","v":0},{"$f":"'Interior Lighting'!AM65","v":0}]
[{"$f":"'Interior Lighting'!Z66","v":0},{"$f":"'Interior Lighting'!AA66","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ66","v":0},{"$f":"'Interior Lighting'!AK66","v":0},{"$f":"'Interior Lighting'!AL66","v":0},{"$f":"'Interior Lighting'!AM66","v":0}]
[{"$f":"'Interior Lighting'!Z67","v":0},{"$f":"'Interior Lighting'!AA67","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ67","v":0},{"$f":"'Interior Lighting'!AK67","v":0},{"$f":"'Interior Lighting'!AL67","v":0},{"$f":"'Interior Lighting'!AM67","v":0}]
[{"$f":"'Interior Lighting'!Z68","v":0},{"$f":"'Interior Lighting'!AA68","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ68","v":0},{"$f":"'Interior Lighting'!AK68","v":0},{"$f":"'Interior Lighting'!AL68","v":0},{"$f":"'Interior Lighting'!AM68","v":0}]
[{"$f":"'Interior Lighting'!Z69","v":0},{"$f":"'Interior Lighting'!AA69","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ69","v":0},{"$f":"'Interior Lighting'!AK69","v":0},{"$f":"'Interior Lighting'!AL69","v":0},{"$f":"'Interior Lighting'!AM69","v":0}]
[{"$f":"'Interior Lighting'!Z70","v":0},{"$f":"'Interior Lighting'!AA70","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ70","v":0},{"$f":"'Interior Lighting'!AK70","v":0},{"$f":"'Interior Lighting'!AL70","v":0},{"$f":"'Interior Lighting'!AM70","v":0}]
[{"$f":"'Interior Lighting'!Z71","v":0},{"$f":"'Interior Lighting'!AA71","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ71","v":0},{"$f":"'Interior Lighting'!AK71","v":0},{"$f":"'Interior Lighting'!AL71","v":0},{"$f":"'Interior Lighting'!AM71","v":0}]
[{"$f":"'Interior Lighting'!Z72","v":0},{"$f":"'Interior Lighting'!AA72","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ72","v":0},{"$f":"'Interior Lighting'!AK72","v":0},{"$f":"'Interior Lighting'!AL72","v":0},{"$f":"'Interior Lighting'!AM72","v":0}]
[{"$f":"'Interior Lighting'!Z73","v":0},{"$f":"'Interior Lighting'!AA73","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ73","v":0},{"$f":"'Interior Lighting'!AK73","v":0},{"$f":"'Interior Lighting'!AL73","v":0},{"$f":"'Interior Lighting'!AM73","v":0}]
[{"$f":"'Interior Lighting'!Z74","v":0},{"$f":"'Interior Lighting'!AA74","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ74","v":0},{"$f":"'Interior Lighting'!AK74","v":0},{"$f":"'Interior Lighting'!AL74","v":0},{"$f":"'Interior Lighting'!AM74","v":0}]
[{"$f":"'Interior Lighting'!Z75","v":0},{"$f":"'Interior Lighting'!AA75","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ75","v":0},{"$f":"'Interior Lighting'!AK75","v":0},{"$f":"'Interior Lighting'!AL75","v":0},{"$f":"'Interior Lighting'!AM75","v":0}]
[{"$f":"'Interior Lighting'!Z76","v":0},{"$f":"'Interior Lighting'!AA76","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ76","v":0},{"$f":"'Interior Lighting'!AK76","v":0},{"$f":"'Interior Lighting'!AL76","v":0},{"$f":"'Interior Lighting'!AM76","v":0}]
[{"$f":"'Interior Lighting'!Z77","v":0},{"$f":"'Interior Lighting'!AA77","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ77","v":0},{"$f":"'Interior Lighting'!AK77","v":0},{"$f":"'Interior Lighting'!AL77","v":0},{"$f":"'Interior Lighting'!AM77","v":0}]
[{"$f":"'Interior Lighting'!Z78","v":0},{"$f":"'Interior Lighting'!AA78","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ78","v":0},{"$f":"'Interior Lighting'!AK78","v":0},{"$f":"'Interior Lighting'!AL78","v":0},{"$f":"'Interior Lighting'!AM78","v":0}]
[{"$f":"'Interior Lighting'!Z79","v":0},{"$f":"'Interior Lighting'!AA79","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ79","v":0},{"$f":"'Interior Lighting'!AK79","v":0},{"$f":"'Interior Lighting'!AL79","v":0},{"$f":"'Interior Lighting'!AM79","v":0}]
[{"$f":"'Interior Lighting'!Z80","v":0},{"$f":"'Interior Lighting'!AA80","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ80","v":0},{"$f":"'Interior Lighting'!AK80","v":0},{"$f":"'Interior Lighting'!AL80","v":0},{"$f":"'Interior Lighting'!AM80","v":0}]
[{"$f":"'Interior Lighting'!Z81","v":0},{"$f":"'Interior Lighting'!AA81","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ81","v":0},{"$f":"'Interior Lighting'!AK81","v":0},{"$f":"'Interior Lighting'!AL81","v":0},{"$f":"'Interior Lighting'!AM81","v":0}]
[{"$f":"'Interior Lighting'!Z82","v":0},{"$f":"'Interior Lighting'!AA82","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ82","v":0},{"$f":"'Interior Lighting'!AK82","v":0},{"$f":"'Interior Lighting'!AL82","v":0},{"$f":"'Interior Lighting'!AM82","v":0}]
[{"$f":"'Interior Lighting'!Z83","v":0},{"$f":"'Interior Lighting'!AA83","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ83","v":0},{"$f":"'Interior Lighting'!AK83","v":0},{"$f":"'Interior Lighting'!AL83","v":0},{"$f":"'Interior Lighting'!AM83","v":0}]
[{"$f":"'Interior Lighting'!Z84","v":0},{"$f":"'Interior Lighting'!AA84","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ84","v":0},{"$f":"'Interior Lighting'!AK84","v":0},{"$f":"'Interior Lighting'!AL84","v":0},{"$f":"'Interior Lighting'!AM84","v":0}]
[{"$f":"'Interior Lighting'!Z85","v":0},{"$f":"'Interior Lighting'!AA85","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ85","v":0},{"$f":"'Interior Lighting'!AK85","v":0},{"$f":"'Interior Lighting'!AL85","v":0},{"$f":"'Interior Lighting'!AM85","v":0}]
[{"$f":"'Interior Lighting'!Z86","v":0},{"$f":"'Interior Lighting'!AA86","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ86","v":0},{"$f":"'Interior Lighting'!AK86","v":0},{"$f":"'Interior Lighting'!AL86","v":0},{"$f":"'Interior Lighting'!AM86","v":0}]
[{"$f":"'Interior Lighting'!Z87","v":0},{"$f":"'Interior Lighting'!AA87","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ87","v":0},{"$f":"'Interior Lighting'!AK87","v":0},{"$f":"'Interior Lighting'!AL87","v":0},{"$f":"'Interior Lighting'!AM87","v":0}]
[{"$f":"'Interior Lighting'!Z88","v":0},{"$f":"'Interior Lighting'!AA88","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ88","v":0},{"$f":"'Interior Lighting'!AK88","v":0},{"$f":"'Interior Lighting'!AL88","v":0},{"$f":"'Interior Lighting'!AM88","v":0}]
[{"$f":"'Interior Lighting'!Z89","v":0},{"$f":"'Interior Lighting'!AA89","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ89","v":0},{"$f":"'Interior Lighting'!AK89","v":0},{"$f":"'Interior Lighting'!AL89","v":0},{"$f":"'Interior Lighting'!AM89","v":0}]
[{"$f":"'Interior Lighting'!Z90","v":0},{"$f":"'Interior Lighting'!AA90","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ90","v":0},{"$f":"'Interior Lighting'!AK90","v":0},{"$f":"'Interior Lighting'!AL90","v":0},{"$f":"'Interior Lighting'!AM90","v":0}]
[{"$f":"'Interior Lighting'!Z91","v":0},{"$f":"'Interior Lighting'!AA91","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ91","v":0},{"$f":"'Interior Lighting'!AK91","v":0},{"$f":"'Interior Lighting'!AL91","v":0},{"$f":"'Interior Lighting'!AM91","v":0}]
[{"$f":"'Interior Lighting'!Z92","v":0},{"$f":"'Interior Lighting'!AA92","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ92","v":0},{"$f":"'Interior Lighting'!AK92","v":0},{"$f":"'Interior Lighting'!AL92","v":0},{"$f":"'Interior Lighting'!AM92","v":0}]
[{"$f":"'Interior Lighting'!Z93","v":0},{"$f":"'Interior Lighting'!AA93","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ93","v":0},{"$f":"'Interior Lighting'!AK93","v":0},{"$f":"'Interior Lighting'!AL93","v":0},{"$f":"'Interior Lighting'!AM93","v":0}]
[{"$f":"'Interior Lighting'!Z94","v":0},{"$f":"'Interior Lighting'!AA94","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ94","v":0},{"$f":"'Interior Lighting'!AK94","v":0},{"$f":"'Interior Lighting'!AL94","v":0},{"$f":"'Interior Lighting'!AM94","v":0}]
[{"$f":"'Interior Lighting'!Z95","v":0},{"$f":"'Interior Lighting'!AA95","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ95","v":0},{"$f":"'Interior Lighting'!AK95","v":0},{"$f":"'Interior Lighting'!AL95","v":0},{"$f":"'Interior Lighting'!AM95","v":0}]
[{"$f":"'Interior Lighting'!Z96","v":0},{"$f":"'Interior Lighting'!AA96","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ96","v":0},{"$f":"'Interior Lighting'!AK96","v":0},{"$f":"'Interior Lighting'!AL96","v":0},{"$f":"'Interior Lighting'!AM96","v":0}]
[{"$f":"'Interior Lighting'!Z97","v":0},{"$f":"'Interior Lighting'!AA97","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ97","v":0},{"$f":"'Interior Lighting'!AK97","v":0},{"$f":"'Interior Lighting'!AL97","v":0},{"$f":"'Interior Lighting'!AM97","v":0}]
[{"$f":"'Interior Lighting'!Z98","v":0},{"$f":"'Interior Lighting'!AA98","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ98","v":0},{"$f":"'Interior Lighting'!AK98","v":0},{"$f":"'Interior Lighting'!AL98","v":0},{"$f":"'Interior Lighting'!AM98","v":0}]
[{"$f":"'Interior Lighting'!Z99","v":0},{"$f":"'Interior Lighting'!AA99","v":0},null,null,null,{"$f":"'Interior Lighting'!AJ99","v":0},{"$f":"'Interior Lighting'!AK99","v":0},{"$f":"'Interior Lighting'!AL99","v":0},{"$f":"'Interior Lighting'!AM99","v":0}]
["Exterior Lighting"]
["\nMeasure Description\nThis measure considers savings from a high performance EXTERIOR lighting system design with reduced lighting power below the baseline maximum allowable value.  This measure is analyzed through the custom incentive program.\nThe baseline assumes the maximum allowable total exterior ligthing watts based on the respective areas and maximum allowable baseline lighting intensities for each illuminated exterior space type.\n\nCalculation Methodology\nSavings are estimated by comparing baseline and proposed/design total exterior lighting watts.  Annual energy savings assume that all exterior fixtures operate for 3,672 hours per year (this accounts for code required controls for exterior fixtures).\n"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Savings & Incentive"]
[{"$f":"'Exterior Lighting'!F3","v":"Annual Electric Savings"},null,null,null,{"$f":"'Exterior Lighting'!H3","v":0},{"$f":"'Exterior Lighting'!I3","v":"kWh"}]
[{"$f":"'Exterior Lighting'!F4","v":"Annual Fuel Savings"},null,null,null,{"$f":"'Exterior Lighting'!H4","v":{"$error":"#N/A"}},{"$f":"'Exterior Lighting'!I4","v":{"$error":"#N/A"}}]
[{"$f":"'Exterior Lighting'!F5","v":"Incremental"},null,null,null,{"$f":"IF('Exterior Lighting'!H6=\"\",'Exterior Lighting'!H5,'Exterior Lighting'!H6)","v":0},{"$f":"'Exterior Lighting'!I5","v":"$"}]
[{"$f":"'Exterior Lighting'!F7","v":"Estimated Incentive"},null,null,null,{"$f":"'Exterior Lighting'!H7","v":{"$error":"#N/A"}},{"$f":"'Exterior Lighting'!I7","v":"$"}]
[]
["Base vs. Proposed Comparison"]
[null,null,null,null,"Baseline","Design","Savings"]
[null,null,null,null,"Watts","Watts","Watts"]
["Tradable Exterior Lighting Watts",null,null,null,{"$f":"'Exterior Lighting'!R18","v":600}]
["Non-Tradable Exterior Lighting Watts",null,null,null,{"$f":"'Exterior Lighting'!S18","v":0}]
["Total Exterior Lighting Watts",null,null,null,{"$f":"'Exterior Lighting'!R21","v":600},{"$f":"'Exterior Lighting'!R22","v":0},{"$f":"E514-F514","v":600}]
["Annual Exterior Lighting Hours (EFLH)",null,null,null,{"$f":"'Exterior Lighting'!R24","v":4345}]
[]
["Notes"]
[{"$f":"'Exterior Lighting'!K8","v":0}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,{"$f":"'Exterior Lighting'!J23","v":"Project Lighting Zone"},{"$f":"'Exterior Lighting'!K23","v":0}]
[{"$f":"'Exterior Lighting'!F22","v":"Table 2: Baseline Lighting Allowance Inputs"}]
[null,null,null,null,null,null,{"$f":"'Exterior Lighting'!J24","v":"Unit"},{"$f":"'Exterior Lighting'!K24","v":"Qty"},{"$f":"'Exterior Lighting'!N23","v":"Baseline"}]
[null,null,null,null,null,null,null,null,{"$f":"'Exterior Lighting'!N24","v":"Watts"}]
[{"$f":"'Exterior Lighting'!F25","v":"Base Allowance"},null,null,null,null,null,null,{"$f":"'Exterior Lighting'!K25","v":1},{"$f":"'Exterior Lighting'!N25","v":600}]
[{"$f":"'Exterior Lighting'!F26","v":"Uncovered Parking Areas"}]
[{"$f":"'Exterior Lighting'!F27","v":"Parking Areas and Drives"},null,null,null,null,null,{"$f":"'Exterior Lighting'!J27","v":"ft²"},{"$f":"'Exterior Lighting'!K27","v":0},{"$f":"'Exterior Lighting'!N27","v":0}]
[{"$f":"'Exterior Lighting'!F28","v":"Building Grounds"}]
[{"$f":"'Exterior Lighting'!F29","v":"Walkways and ramps less than 10 ft wide"},null,null,null,null,null,{"$f":"'Exterior Lighting'!J29","v":"linear ft"},{"$f":"'Exterior Lighting'!K29","v":0},{"$f":"'Exterior Lighting'!N29","v":0}]
[{"$f":"'Exterior Lighting'!F30","v":"Walkways and ramps 10 ft wide or greater, "},null,null,null,null,null,{"$f":"'Exterior Lighting'!J30","v":"ft²"},{"$f":"'Exterior Lighting'!K30","v":0},{"$f":"'Exterior Lighting'!N30","v":0}]
[{"$f":"'Exterior Lighting'!F31","v":"           plaza areas, special feature areas"}]
[{"$f":"'Exterior Lighting'!F32","v":"Dining Areas"},null,null,null,null,null,{"$f":"'Exterior Lighting'!J32","v":"ft²"},{"$f":"'Exterior Lighting'!K32","v":0},{"$f":"'Exterior Lighting'!N32","v":0}]
[{"$f":"'Exterior Lighting'!F33","v":"Stairways"},null,null,null,null,null,{"$f":"'Exterior Lighting'!J33","v":"ft²"},{"$f":"'Exterior Lighting'!K33","v":0},{"$f":"'Exterior Lighting'!N33","v":0}]
[{"$f":"'Exterior Lighting'!F34","v":"Pedestrian Tunnels"},null,null,null,null,null,{"$f":"'Exterior Lighting'!J34","v":"ft²"},{"$f":"'Exterior Lighting'!K34","v":0},{"$f":"'Exterior Lighting'!N34","v":0}]
[{"$f":"'Exterior Lighting'!F35","v":"Landscaping"},null,null,null,null,null,{"$f":"'Exterior Lighting'!J35","v":"ft²"},{"$f":"'Exterior Lighting'!K35","v":0},{"$f":"'Exterior Lighting'!N35","v":0}]
[{"$f":"'Exterior Lighting'!F36","v":"Building Entrances and Exits"}]
[{"$f":"'Exterior Lighting'!F37","v":"Main Entries"},null,null,null,null,null,{"$f":"'Exterior Lighting'!J37","v":"linear ft"},{"$f":"'Exterior Lighting'!K37","v":0},{"$f":"'Exterior Lighting'!N37","v":0}]
[{"$f":"'Exterior Lighting'!F38","v":"Entry canopies"},null,null,null,null,null,{"$f":"'Exterior Lighting'!J38","v":"ft²"},{"$f":"'Exterior Lighting'!K38","v":0},{"$f":"'Exterior Lighting'!N38","v":0}]
[{"$f":"'Exterior Lighting'!F39","v":"Other Doors"},null,null,null,null,null,{"$f":"'Exterior Lighting'!J39","v":"linear ft"},{"$f":"'Exterior Lighting'!K39","v":0},{"$f":"'Exterior Lighting'!N39","v":0}]
[{"$f":"'Exterior Lighting'!F40","v":"Sales Canopies"}]
[{"$f":"'Exterior Lighting'!F41","v":"Free-standing and attached"},null,null,null,null,null,{"$f":"'Exterior Lighting'!J41","v":"ft²"},{"$f":"'Exterior Lighting'!K41","v":0},{"$f":"'Exterior Lighting'!N41","v":0}]
[{"$f":"'Exterior Lighting'!F42","v":"Outdoor Sales"}]
[{"$f":"'Exterior Lighting'!F43","v":"Open areas (including vehicle sales lots)"},null,null,null,null,null,{"$f":"'Exterior Lighting'!J43","v":"ft²"},{"$f":"'Exterior Lighting'!K43","v":0},{"$f":"'Exterior Lighting'!N43","v":0}]
[{"$f":"'Exterior Lighting'!F44","v":"Street frontage for vehicle sales lots"},null,null,null,null,null,{"$f":"'Exterior Lighting'!J44","v":"linear ft"},{"$f":"'Exterior Lighting'!K44","v":0},{"$f":"'Exterior Lighting'!N44","v":0}]
[{"$f":"'Exterior Lighting'!F45","v":"          in addition to \"open area\" allowance"}]
[{"$f":"'Exterior Lighting'!F46","v":"Building Exteriors (Non-Tradable)"}]
[{"$f":"'Exterior Lighting'!F47","v":"Building facades"},null,null,null,null,null,{"$f":"'Exterior Lighting'!J47","v":"ft²"},{"$f":"'Exterior Lighting'!K47","v":0},{"$f":"'Exterior Lighting'!N47","v":0}]
[{"$f":"'Exterior Lighting'!F48","v":"Automated teller machines (ATM)"},null,null,null,null,null,{"$f":"'Exterior Lighting'!J48","v":"Watts"},{"$f":"'Exterior Lighting'!K48","v":0},{"$f":"'Exterior Lighting'!N48","v":0}]
[{"$f":"'Exterior Lighting'!F49","v":"          and night depositories"}]
[{"$f":"'Exterior Lighting'!F50","v":"Uncovered entrances and gatehouse inpection"},null,null,null,null,null,{"$f":"'Exterior Lighting'!J50","v":"ft²"},{"$f":"'Exterior Lighting'!K50","v":0},{"$f":"'Exterior Lighting'!N50","v":0}]
[{"$f":"'Exterior Lighting'!F51","v":"          stations at guarded facilities"}]
[{"$f":"'Exterior Lighting'!F52","v":"Uncovered loading areas for law enforcement, fire,"},null,null,null,null,null,{"$f":"'Exterior Lighting'!J52","v":"ft²"},{"$f":"'Exterior Lighting'!K52","v":0},{"$f":"'Exterior Lighting'!N52","v":0}]
[{"$f":"'Exterior Lighting'!F53","v":"          ambulance and other emergency service vehicles"}]
[{"$f":"'Exterior Lighting'!F54","v":"Drive-up windows and doors"},null,null,null,null,null,{"$f":"'Exterior Lighting'!J54","v":"Drive-thru Qty"},{"$f":"'Exterior Lighting'!K54","v":0},{"$f":"'Exterior Lighting'!N54","v":0}]
[{"$f":"'Exterior Lighting'!F55","v":"Parking near 24-hour retail entrances"},null,null,null,null,null,{"$f":"'Exterior Lighting'!J55","v":"Main Entry Qty"},{"$f":"'Exterior Lighting'!K55","v":0},{"$f":"'Exterior Lighting'!N55","v":0}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Energy Recovery"]
["Measure Description\nThis measure considers savings from high performance airside energy recovery systems that exceed the minimum energy code requirements for recovery performance.\nThe baseline reflects the minimum requirements for the specified equipment under the applicable energy code standard and/or state-specific program guidelines.\n\nCalculation Methodology\nSavings are estimated with an ambient temperature bin model using TMYx weather data.  The bin model for this measure includes only scheduled building operating hours, as the ventilation air handlers are assumed to be off during scheduled unoccupied hours. Each air handler with energy recovery included in the inputs table is modeled individually for savings.\nAir handlers can be modeled as constant volume or variable air volume (VAV) systems, as selected by the user.  The OA rates are assumed to be constant in both system types.  For VAV systems that are not 100% OA, the total supply flow varies based on assumed space cooling and heating load profiles but OA flow is constant.  VAV turndown is limited to the larger of the OA CFM or 50% of design total supply CFM.  The system flow profile impacts %OA in each bin.\nIn each bin, supply OA temperature or enthalpy (temperature is used for heating loads, enthalpy is used for cooling loads) leaving the recovery section is calculated separately for the base and proposed case based on values for entering outside air, space return air, and the respective effectiveness.  The tool assumes that the recovery section has capacity control to maintain air handler discharge air setpoints.\nCooling and heating load reduction is calculated in each bin based on the OA CFM and difference between the base and proposed recovery section leaving air conditions.  Cooling or heating equipment performance is applied to the load reduction to calculate energy demand reduction.\nIn each bin, space return air conditions, entering OA conditions, OA CFM, and total supply CFM are identical in the base and proposed case.\nIf the base case does not have energy recovery, the effectiveness is set to zero and a fan penalty is applied to the proposed case to account for increased static pressure.\n"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Savings & Incentive"]
[{"$f":"'Energy Recovery'!F3","v":"Annual Electric Savings"},null,null,null,{"$f":"'Energy Recovery'!H3","v":0},{"$f":"'Energy Recovery'!I3","v":"kWh"}]
[{"$f":"'Energy Recovery'!F4","v":"Annual Fuel Savings"},null,null,null,{"$f":"'Energy Recovery'!H4","v":{"$error":"#N/A"}},{"$f":"'Energy Recovery'!I4","v":{"$error":"#N/A"}}]
[{"$f":"'Energy Recovery'!F5","v":"Incremental"},null,null,null,{"$f":"IF('Energy Recovery'!H6=\"\",'Energy Recovery'!H5,'Energy Recovery'!H6)","v":0},{"$f":"'Energy Recovery'!I5","v":"$"}]
[{"$f":"'Energy Recovery'!F7","v":"Estimated Incentive"},null,null,null,{"$f":"'Energy Recovery'!H7","v":{"$error":"#N/A"}},{"$f":"'Energy Recovery'!I7","v":"$"}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Air Handling Unit Parameters"]
["Unit\nTag/Name","Description",null,null,"Total","Total","Recovery"]
[null,null,null,null,"Supply","OA","Section",null,"Cooling"]
[null,null,null,null,"CFM","CFM","Type",null,"Included?"]
[{"$f":"'Energy Recovery'!H22","v":0},{"$f":"'Energy Recovery'!J22","v":0},null,null,{"$f":"'Energy Recovery'!L22","v":0},{"$f":"'Energy Recovery'!M22","v":0},{"$f":"'Energy Recovery'!N22","v":0},null,{"$f":"'Energy Recovery'!R22","v":0}]
[{"$f":"'Energy Recovery'!H23","v":0},{"$f":"'Energy Recovery'!J23","v":0},null,null,{"$f":"'Energy Recovery'!L23","v":0},{"$f":"'Energy Recovery'!M23","v":0},{"$f":"'Energy Recovery'!N23","v":0},null,{"$f":"'Energy Recovery'!R23","v":0}]
[{"$f":"'Energy Recovery'!H24","v":0},{"$f":"'Energy Recovery'!J24","v":0},null,null,{"$f":"'Energy Recovery'!L24","v":0},{"$f":"'Energy Recovery'!M24","v":0},{"$f":"'Energy Recovery'!N24","v":0},null,{"$f":"'Energy Recovery'!R24","v":0}]
[{"$f":"'Energy Recovery'!H25","v":0},{"$f":"'Energy Recovery'!J25","v":0},null,null,{"$f":"'Energy Recovery'!L25","v":0},{"$f":"'Energy Recovery'!M25","v":0},{"$f":"'Energy Recovery'!N25","v":0},null,{"$f":"'Energy Recovery'!R25","v":0}]
[{"$f":"'Energy Recovery'!H26","v":0},{"$f":"'Energy Recovery'!J26","v":0},null,null,{"$f":"'Energy Recovery'!L26","v":0},{"$f":"'Energy Recovery'!M26","v":0},{"$f":"'Energy Recovery'!N26","v":0},null,{"$f":"'Energy Recovery'!R26","v":0}]
[{"$f":"'Energy Recovery'!H27","v":0},{"$f":"'Energy Recovery'!J27","v":0},null,null,{"$f":"'Energy Recovery'!L27","v":0},{"$f":"'Energy Recovery'!M27","v":0},{"$f":"'Energy Recovery'!N27","v":0},null,{"$f":"'Energy Recovery'!R27","v":0}]
[{"$f":"'Energy Recovery'!H28","v":0},{"$f":"'Energy Recovery'!J28","v":0},null,null,{"$f":"'Energy Recovery'!L28","v":0},{"$f":"'Energy Recovery'!M28","v":0},{"$f":"'Energy Recovery'!N28","v":0},null,{"$f":"'Energy Recovery'!R28","v":0}]
[{"$f":"'Energy Recovery'!H29","v":0},{"$f":"'Energy Recovery'!J29","v":0},null,null,{"$f":"'Energy Recovery'!L29","v":0},{"$f":"'Energy Recovery'!M29","v":0},{"$f":"'Energy Recovery'!N29","v":0},null,{"$f":"'Energy Recovery'!R29","v":0}]
[{"$f":"'Energy Recovery'!H30","v":0},{"$f":"'Energy Recovery'!J30","v":0},null,null,{"$f":"'Energy Recovery'!L30","v":0},{"$f":"'Energy Recovery'!M30","v":0},{"$f":"'Energy Recovery'!N30","v":0},null,{"$f":"'Energy Recovery'!R30","v":0}]
[{"$f":"'Energy Recovery'!H31","v":0},{"$f":"'Energy Recovery'!J31","v":0},null,null,{"$f":"'Energy Recovery'!L31","v":0},{"$f":"'Energy Recovery'!M31","v":0},{"$f":"'Energy Recovery'!N31","v":0},null,{"$f":"'Energy Recovery'!R31","v":0}]
[]
[]
["Energy Recovery Parameters"]
[null,"Design Case",null,"Base Case",null,"Base ERV",null,"(Optional) Recovery SP"]
[null,"Sensible","Total","Sensible","Total","Code","Exemption","Override (in wc)"]
["Unit","Eff","Eff","Eff","Eff","Exemption?","Used",{"$f":"'Energy Recovery'!Z21","v":"Supply"},{"$f":"'Energy Recovery'!AA21","v":"Exhaust"}]
[{"$f":"'Energy Recovery'!H22","v":0},{"$f":"'Energy Recovery'!P22","v":0},{"$f":"'Energy Recovery'!Q22","v":0},{"$f":"'Energy Recovery'!AC22","v":0},{"$f":"'Energy Recovery'!AD22","v":0},{"$f":"'Energy Recovery'!X22","v":0},{"$f":"'Energy Recovery'!Y22","v":0},{"$f":"'Energy Recovery'!Z22","v":0},{"$f":"'Energy Recovery'!AA22","v":0}]
[{"$f":"'Energy Recovery'!H23","v":0},{"$f":"'Energy Recovery'!P23","v":0},{"$f":"'Energy Recovery'!Q23","v":0},{"$f":"'Energy Recovery'!AC23","v":0},{"$f":"'Energy Recovery'!AD23","v":0},{"$f":"'Energy Recovery'!X23","v":0},{"$f":"'Energy Recovery'!Y23","v":0},{"$f":"'Energy Recovery'!Z23","v":0},{"$f":"'Energy Recovery'!AA23","v":0}]
[{"$f":"'Energy Recovery'!H24","v":0},{"$f":"'Energy Recovery'!P24","v":0},{"$f":"'Energy Recovery'!Q24","v":0},{"$f":"'Energy Recovery'!AC24","v":0},{"$f":"'Energy Recovery'!AD24","v":0},{"$f":"'Energy Recovery'!X24","v":0},{"$f":"'Energy Recovery'!Y24","v":0},{"$f":"'Energy Recovery'!Z24","v":0},{"$f":"'Energy Recovery'!AA24","v":0}]
[{"$f":"'Energy Recovery'!H25","v":0},{"$f":"'Energy Recovery'!P25","v":0},{"$f":"'Energy Recovery'!Q25","v":0},{"$f":"'Energy Recovery'!AC25","v":0},{"$f":"'Energy Recovery'!AD25","v":0},{"$f":"'Energy Recovery'!X25","v":0},{"$f":"'Energy Recovery'!Y25","v":0},{"$f":"'Energy Recovery'!Z25","v":0},{"$f":"'Energy Recovery'!AA25","v":0}]
[{"$f":"'Energy Recovery'!H26","v":0},{"$f":"'Energy Recovery'!P26","v":0},{"$f":"'Energy Recovery'!Q26","v":0},{"$f":"'Energy Recovery'!AC26","v":0},{"$f":"'Energy Recovery'!AD26","v":0},{"$f":"'Energy Recovery'!X26","v":0},{"$f":"'Energy Recovery'!Y26","v":0},{"$f":"'Energy Recovery'!Z26","v":0},{"$f":"'Energy Recovery'!AA26","v":0}]
[{"$f":"'Energy Recovery'!H27","v":0},{"$f":"'Energy Recovery'!P27","v":0},{"$f":"'Energy Recovery'!Q27","v":0},{"$f":"'Energy Recovery'!AC27","v":0},{"$f":"'Energy Recovery'!AD27","v":0},{"$f":"'Energy Recovery'!X27","v":0},{"$f":"'Energy Recovery'!Y27","v":0},{"$f":"'Energy Recovery'!Z27","v":0},{"$f":"'Energy Recovery'!AA27","v":0}]
[{"$f":"'Energy Recovery'!H28","v":0},{"$f":"'Energy Recovery'!P28","v":0},{"$f":"'Energy Recovery'!Q28","v":0},{"$f":"'Energy Recovery'!AC28","v":0},{"$f":"'Energy Recovery'!AD28","v":0},{"$f":"'Energy Recovery'!X28","v":0},{"$f":"'Energy Recovery'!Y28","v":0},{"$f":"'Energy Recovery'!Z28","v":0},{"$f":"'Energy Recovery'!AA28","v":0}]
[{"$f":"'Energy Recovery'!H29","v":0},{"$f":"'Energy Recovery'!P29","v":0},{"$f":"'Energy Recovery'!Q29","v":0},{"$f":"'Energy Recovery'!AC29","v":0},{"$f":"'Energy Recovery'!AD29","v":0},{"$f":"'Energy Recovery'!X29","v":0},{"$f":"'Energy Recovery'!Y29","v":0},{"$f":"'Energy Recovery'!Z29","v":0},{"$f":"'Energy Recovery'!AA29","v":0}]
[{"$f":"'Energy Recovery'!H30","v":0},{"$f":"'Energy Recovery'!P30","v":0},{"$f":"'Energy Recovery'!Q30","v":0},{"$f":"'Energy Recovery'!AC30","v":0},{"$f":"'Energy Recovery'!AD30","v":0},{"$f":"'Energy Recovery'!X30","v":0},{"$f":"'Energy Recovery'!Y30","v":0},{"$f":"'Energy Recovery'!Z30","v":0},{"$f":"'Energy Recovery'!AA30","v":0}]
[{"$f":"'Energy Recovery'!H31","v":0},{"$f":"'Energy Recovery'!P31","v":0},{"$f":"'Energy Recovery'!Q31","v":0},{"$f":"'Energy Recovery'!AC31","v":0},{"$f":"'Energy Recovery'!AD31","v":0},{"$f":"'Energy Recovery'!X31","v":0},{"$f":"'Energy Recovery'!Y31","v":0},{"$f":"'Energy Recovery'!Z31","v":0},{"$f":"'Energy Recovery'!AA31","v":0}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Condensing Boilers"]
["Measure Description\nThis measure considers savings from installing high performance condensing boilers that exceed the baseline boiler efficiency requirements.\nNote: ONLY condensing boilers are considered in this measure (not non-condensing high efficiency boilers). Non-condensing boilers that exceed baseline efficiency must be analyzed as a separate user-defined measure.\nThe baseline reflects the minimum required heating performance for the specified equipment under the applicable energy code standard and/or state-specific program guidelines.\n\nCalculation Methodology\nSavings are estimated with an ambient temperature bin model using TMYx weather data. Boiler plant loads are estimated using a linear profile that is dependent on ambient dry-bulb temperature and space use.  The following general load profiles are assumed:\nComfort/HVAC loads:  Heating load varies from peak load at 0°F OAdb to minimum load at 60°F OAdb.\nThe peak load is dependent on user inputs for boiler capacity, max quantity of operating boilers, and peak load % of max operating capacity.\nDuring unoccupied hours, the assumed loads are reduced by ~50%.\nConstant/Process:  Heating load assumed to be constant 24/7. The peak load is dependent on user inputs for boiler capacity, max quantity of operating boilers, and peak load % of max operating capacity.\nLoad profiles are identical in the base and proposed case.  Base case equipment performance is automatically set by the tool based on boiler capacity.  Proposed case performance reflects typical condensing boiler efficiency curves relative to return HW temperature (efficiency ranging from ~86 – 96%).  The range of HW supply and return temperatures is defined by user inputs for HW reset schedule and will vary from project to project. \nIn each bin, base case efficiency is assumed to be constant at the baseline value.  Proposed case efficiency varies based on ambient temperature and the assumed HW temperature reset schedule.  Base and proposed case equipment demand is calculated as a function of the load and performance value in each bin. \n"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Savings & Incentive"]
[{"$f":"'Condensing Boilers'!F3","v":"Annual Electric Savings"},null,null,null,{"$f":"'Condensing Boilers'!H3","v":0},{"$f":"'Condensing Boilers'!I3","v":"kWh"}]
[{"$f":"'Condensing Boilers'!F4","v":"Annual Fuel Savings"},null,null,null,{"$f":"'Condensing Boilers'!H4","v":{"$error":"#N/A"}},{"$f":"'Condensing Boilers'!I4","v":{"$error":"#N/A"}}]
[{"$f":"'Condensing Boilers'!F5","v":"Incremental"},null,null,null,{"$f":"IF('Condensing Boilers'!H6=\"\",'Condensing Boilers'!H5,'Condensing Boilers'!H6)","v":0},{"$f":"'Condensing Boilers'!I5","v":"$"}]
[{"$f":"'Condensing Boilers'!F7","v":"Estimated Incentive"},null,null,null,{"$f":"'Condensing Boilers'!H7","v":0},{"$f":"'Condensing Boilers'!I7","v":"$"}]
["Boiler Effciency Parameters"]
[null,"Base Eff (%)",null,"Proposed Eff (%)"]
[null,"Min","Max","Min","Max"]
["System 1",{"$f":"'Condensing Boilers'!V17","v":0.99},{"$f":"'Condensing Boilers'!W17","v":0.99},{"$f":"'Condensing Boilers'!X17","v":0.99},{"$f":"'Condensing Boilers'!Y17","v":0.99}]
["System 2",{"$f":"IF('Condensing Boilers'!$Q$15=\"No\",\"\",'Condensing Boilers'!V18)","v":""},{"$f":"IF('Condensing Boilers'!$Q$15=\"No\",\"\",'Condensing Boilers'!W18)","v":""},{"$f":"IF('Condensing Boilers'!$Q$15=\"No\",\"\",'Condensing Boilers'!X18)","v":""},{"$f":"IF('Condensing Boilers'!$Q$15=\"No\",\"\",'Condensing Boilers'!Y18)","v":""}]
["System 3",{"$f":"IF('Condensing Boilers'!$S$15=\"No\",\"\",'Condensing Boilers'!V19)","v":""},{"$f":"IF('Condensing Boilers'!$S$15=\"No\",\"\",'Condensing Boilers'!W19)","v":""},{"$f":"IF('Condensing Boilers'!$S$15=\"No\",\"\",'Condensing Boilers'!X19)","v":""},{"$f":"IF('Condensing Boilers'!$S$15=\"No\",\"\",'Condensing Boilers'!Y19)","v":""}]
["Boiler/Loop Parameters"]
[null,null,null,"System #1",null,"System #2",null,"System #3"]
["System Load Profile",null,null,{"$f":"'Condensing Boilers'!N16","v":0},null,{"$f":"IF('Condensing Boilers'!$Q$15=\"No\",\"\",'Condensing Boilers'!P16)","v":""},null,{"$f":"IF('Condensing Boilers'!$S$15=\"No\",\"\",'Condensing Boilers'!R16)","v":""}]
["Boiler Quantity",null,null,{"$f":"'Condensing Boilers'!N17","v":0},null,{"$f":"IF('Condensing Boilers'!$Q$15=\"No\",\"\",'Condensing Boilers'!P17)","v":""},null,{"$f":"IF('Condensing Boilers'!$S$15=\"No\",\"\",'Condensing Boilers'!R17)","v":""}]
["Output Capacity MBH (per Boiler)",null,null,{"$f":"'Condensing Boilers'!N18","v":0},null,{"$f":"IF('Condensing Boilers'!$Q$15=\"No\",\"\",'Condensing Boilers'!P18)","v":""},null,{"$f":"IF('Condensing Boilers'!$S$15=\"No\",\"\",'Condensing Boilers'!R18)","v":""}]
["Max # of Operating Boilers",null,null,{"$f":"'Condensing Boilers'!N19","v":0},null,{"$f":"IF('Condensing Boilers'!$Q$15=\"No\",\"\",'Condensing Boilers'!P19)","v":""},null,{"$f":"IF('Condensing Boilers'!$S$15=\"No\",\"\",'Condensing Boilers'!R19)","v":""}]
["Peak Load % of Max Op. Cap",null,null,{"$f":"'Condensing Boilers'!N20","v":0},null,{"$f":"IF('Condensing Boilers'!$Q$15=\"No\",\"\",'Condensing Boilers'!P20)","v":""},null,{"$f":"IF('Condensing Boilers'!$S$15=\"No\",\"\",'Condensing Boilers'!R20)","v":""}]
["Design Supply HW Temp. (°F)",null,null,{"$f":"'Condensing Boilers'!N21","v":0},null,{"$f":"IF('Condensing Boilers'!$Q$15=\"No\",\"\",'Condensing Boilers'!P21)","v":""},null,{"$f":"IF('Condensing Boilers'!$S$15=\"No\",\"\",'Condensing Boilers'!R21)","v":""}]
["Design HW Loop dT (°F)",null,null,{"$f":"'Condensing Boilers'!N22","v":0},null,{"$f":"IF('Condensing Boilers'!$Q$15=\"No\",\"\",'Condensing Boilers'!P22)","v":""},null,{"$f":"IF('Condensing Boilers'!$S$15=\"No\",\"\",'Condensing Boilers'!R22)","v":""}]
[null,null,null,{"$f":"'Condensing Boilers'!N23","v":"Outside Air"},{"$f":"'Condensing Boilers'!O23","v":"HW Supply"},{"$f":"'Condensing Boilers'!P23","v":"Outside Air"},{"$f":"'Condensing Boilers'!Q23","v":"HW Supply"},{"$f":"'Condensing Boilers'!R23","v":"Outside Air"},{"$f":"'Condensing Boilers'!S23","v":"HW Supply"}]
[null,null,null,{"$f":"'Condensing Boilers'!N24","v":"Temp (°F)"},{"$f":"'Condensing Boilers'!O24","v":"Temp (°F)"},{"$f":"'Condensing Boilers'!P24","v":"Temp (°F)"},{"$f":"'Condensing Boilers'!Q24","v":"Temp (°F)"},{"$f":"'Condensing Boilers'!R24","v":"Temp (°F)"},{"$f":"'Condensing Boilers'!S24","v":"Temp (°F)"}]
["Design HW Loop dT (°F)",null,null,{"$f":"'Condensing Boilers'!N25","v":0},{"$f":"'Condensing Boilers'!O25","v":0},{"$f":"IF('Condensing Boilers'!$Q$15=\"No\",\"\",'Condensing Boilers'!P25)","v":""},{"$f":"IF('Condensing Boilers'!$Q$15=\"No\",\"\",'Condensing Boilers'!Q25)","v":""},{"$f":"IF('Condensing Boilers'!$S$15=\"No\",\"\",'Condensing Boilers'!R25)","v":""},{"$f":"IF('Condensing Boilers'!$S$15=\"No\",\"\",'Condensing Boilers'!S25)","v":""}]
["HW Outside Air Reset Range",null,null,{"$f":"'Condensing Boilers'!N26","v":0},{"$f":"'Condensing Boilers'!O26","v":0},{"$f":"IF('Condensing Boilers'!$Q$15=\"No\",\"\",'Condensing Boilers'!P26)","v":""},{"$f":"IF('Condensing Boilers'!$Q$15=\"No\",\"\",'Condensing Boilers'!Q26)","v":""},{"$f":"IF('Condensing Boilers'!$S$15=\"No\",\"\",'Condensing Boilers'!R26)","v":""},{"$f":"IF('Condensing Boilers'!$S$15=\"No\",\"\",'Condensing Boilers'!S26)","v":""}]
["Incentive",null,null,{"$f":"'Condensing Boilers'!O27","v":0},null,{"$f":"IF('Condensing Boilers'!$Q$15=\"No\",\"\",'Condensing Boilers'!Q27)","v":""},null,{"$f":"IF('Condensing Boilers'!$S$15=\"No\",\"\",'Condensing Boilers'!S27)","v":""}]
[{"$f":"'Condensing Boilers'!K28","v":"Manufacturer & Model (Optional)"},null,null,{"$f":"'Condensing Boilers'!N28","v":0},null,{"$f":"IF('Condensing Boilers'!$Q$15=\"No\",\"\",'Condensing Boilers'!P28)","v":""},null,{"$f":"IF('Condensing Boilers'!$S$15=\"No\",\"\",'Condensing Boilers'!S28)","v":""}]
[]
["High Efficiency Chillers"]
["Measure Description\nThis measure considers savings from installing high performance chillers that exceed the energy code minimum performance requirements.\nThe baseline reflects the minimum required cooling performance for the specified equipment under the applicable energy code standard and/or state-specific program guidelines.\n\nCalculation Methodology\nSavings are estimated with an ambient temperature bin model using TMYx weather data. Chiller plant loads are estimated using a linear profile that is dependent on ambient dry-bulb temperature and space use.  The following general load profiles are assumed:\nComfort/HVAC loads:  Cooling load varies from peak load at 95°F OAdb to minimum load at 50°F OAdb.\nThe peak cooling load is dependent on user inputs for chiller capacity, max quantity of operating chillers, and peak load % of max operating capacity.\nDuring unoccupied hours, the assumed loads are reduced by ~60%.\nConstant/IT-Elec Rm:  Cooling load assumed to be constant 24/7. The peak load is dependent on user inputs for chiller capacity, max quantity of operating chillers, and peak load % of max operating capacity.\nLoad profiles are identical in the base and proposed case.  Base case equipment performance is automatically set by the tool to reflect energy code performance for the given equipment and condenser type.  Proposed case performance should reflect the AHRI performance ratings of the design equipment.\n In each bin, base and proposed equipment performance is estimated based on the inputs for rated full and seasonal average performance, accounting for variation in performance from % load and ambient temperature (part load performance assumes typical condensing temperature reset).  Base and proposed case equipment demand is calculated as a function of the load and performance value in each bin. \n"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Savings & Incentive"]
[{"$f":"'High Efficiency Chillers'!F3","v":"Annual Electric Savings"},null,null,null,{"$f":"'High Efficiency Chillers'!H3","v":0},{"$f":"'High Efficiency Chillers'!I3","v":"kWh"}]
[{"$f":"'High Efficiency Chillers'!F4","v":"Annual Fuel Savings"},null,null,null,{"$f":"'High Efficiency Chillers'!H4","v":{"$error":"#N/A"}},{"$f":"'High Efficiency Chillers'!I4","v":{"$error":"#N/A"}}]
[{"$f":"'High Efficiency Chillers'!F5","v":"Incremental"},null,null,null,{"$f":"IF('High Efficiency Chillers'!H6=\"\",'High Efficiency Chillers'!H5,'High Efficiency Chillers'!H6)","v":0},{"$f":"'High Efficiency Chillers'!I5","v":"$"}]
[{"$f":"'High Efficiency Chillers'!F7","v":"Estimated Incentive"},null,null,null,{"$f":"'High Efficiency Chillers'!H7","v":{"$error":"#N/A"}},{"$f":"'High Efficiency Chillers'!I7","v":"$"}]
[]
["Chiller Effciency Parameters"]
[null,"Tons per Chiller","Chiller\nQty","Perf.\nUnit","Base Performance",null,"Proposed Performance"]
[null,null,"Qty",null,"FL","IEER/IPLV","FL","IEER/IPLV"]
[{"$f":"'High Efficiency Chillers'!S17","v":"System 1"},{"$f":"'High Efficiency Chillers'!T17","v":0},{"$f":"'High Efficiency Chillers'!N17","v":0},{"$f":"'High Efficiency Chillers'!U17","v":"kW/ton"},{"$f":"'High Efficiency Chillers'!V17","v":0.75},{"$f":"'High Efficiency Chillers'!W17","v":0.6},{"$f":"'High Efficiency Chillers'!X17","v":0},{"$f":"'High Efficiency Chillers'!Y17","v":0}]
[{"$f":"'High Efficiency Chillers'!S18","v":"System 2"},{"$f":"IF('High Efficiency Chillers'!$Q$15=\"No\",\"\",'High Efficiency Chillers'!T18)","v":0},{"$f":"IF('High Efficiency Chillers'!$Q$15=\"No\",\"\",'High Efficiency Chillers'!P17)","v":0},{"$f":"IF('High Efficiency Chillers'!$Q$15=\"No\",\"\",'High Efficiency Chillers'!U18)","v":"kW/ton"},{"$f":"IF('High Efficiency Chillers'!$Q$15=\"No\",\"\",'High Efficiency Chillers'!V18)","v":0.75},{"$f":"IF('High Efficiency Chillers'!$Q$15=\"No\",\"\",'High Efficiency Chillers'!W18)","v":0.6},{"$f":"IF('High Efficiency Chillers'!$Q$15=\"No\",\"\",'High Efficiency Chillers'!X18)","v":0},{"$f":"IF('High Efficiency Chillers'!$Q$15=\"No\",\"\",'High Efficiency Chillers'!Y18)","v":0}]
[]
[]
[null,null,null,null,{"$f":"'High Efficiency Chillers'!N15","v":"System 1"},null,{"$f":"'High Efficiency Chillers'!P14","v":"Optional: System 2"}]
[{"$f":"'High Efficiency Chillers'!K16","v":"System Load Profile"},null,null,null,{"$f":"'High Efficiency Chillers'!N16","v":0},null,{"$f":"IF('High Efficiency Chillers'!$Q$15=\"No\",\"\",'High Efficiency Chillers'!P16)","v":0}]
[{"$f":"'High Efficiency Chillers'!K17","v":"Chiller Quantity"},null,null,null,{"$f":"'High Efficiency Chillers'!N17","v":0},null,{"$f":"IF('High Efficiency Chillers'!$Q$15=\"No\",\"\",'High Efficiency Chillers'!P17)","v":0}]
[{"$f":"'High Efficiency Chillers'!K18","v":"Capacity, per Chiller (tons)"},null,null,null,{"$f":"'High Efficiency Chillers'!N18","v":0},null,{"$f":"IF('High Efficiency Chillers'!$Q$15=\"No\",\"\",'High Efficiency Chillers'!P18)","v":0}]
[{"$f":"'High Efficiency Chillers'!K19","v":"Chiller Type"},null,null,null,{"$f":"'High Efficiency Chillers'!N19","v":0},null,{"$f":"IF('High Efficiency Chillers'!$Q$15=\"No\",\"\",'High Efficiency Chillers'!P19)","v":0}]
[{"$f":"'High Efficiency Chillers'!K20","v":"AHRI Full Load Performance"},null,null,null,{"$f":"'High Efficiency Chillers'!N20","v":0},{"$f":"'High Efficiency Chillers'!O20","v":"kW/ton"},{"$f":"IF('High Efficiency Chillers'!$Q$15=\"No\",\"\",'High Efficiency Chillers'!P20)","v":0},{"$f":"IF('High Efficiency Chillers'!$Q$15=\"No\",\"\",'High Efficiency Chillers'!Q20)","v":"kW/ton"}]
[{"$f":"'High Efficiency Chillers'!K21","v":"AHRI Part Load Performance, IEER/IPLV"},null,null,null,{"$f":"'High Efficiency Chillers'!N21","v":0},{"$f":"'High Efficiency Chillers'!O21","v":"kW/ton (IPLV)"},{"$f":"IF('High Efficiency Chillers'!$Q$15=\"No\",\"\",'High Efficiency Chillers'!P21)","v":0},{"$f":"IF('High Efficiency Chillers'!$Q$15=\"No\",\"\",'High Efficiency Chillers'!Q21)","v":"kW/ton (IPLV)"}]
[{"$f":"'High Efficiency Chillers'!K22","v":"Max # of Operating Chillers"},null,null,null,{"$f":"'High Efficiency Chillers'!N22","v":0},null,{"$f":"IF('High Efficiency Chillers'!$Q$15=\"No\",\"\",'High Efficiency Chillers'!P22)","v":0}]
[{"$f":"'High Efficiency Chillers'!K23","v":"Peak Load % of Max Operating Capacity"},null,null,null,{"$f":"'High Efficiency Chillers'!N23","v":0},null,{"$f":"IF('High Efficiency Chillers'!$Q$15=\"No\",\"\",'High Efficiency Chillers'!P23)","v":0}]
[{"$f":"'High Efficiency Chillers'!K24","v":"Incentive (Custom)"},null,null,null,"`",null,{"$f":"IF('High Efficiency Chillers'!$Q$15=\"No\",\"\",'High Efficiency Chillers'!Q24)","v":0}]
[{"$f":"'High Efficiency Chillers'!K25","v":"Manufacturer & Model (Optional)"},null,null,null,{"$f":"IF('High Efficiency Chillers'!N25=\"\",\"\",'High Efficiency Chillers'!N25)","v":""},null,{"$f":"IF('High Efficiency Chillers'!P25=\"\",\"\",'High Efficiency Chillers'!P25)","v":""}]
[]
[]
[]
[]
["DHW Heaters"]
["Measure Description\nThis measure considers savings from installing high performance domestic hot water heaters that exceed the baseline efficiency requirements.  Two types of DHW heaters can be considered for savings: gas-fired heaters or electric heat pump heaters.\nThe baseline reflects the minimum required heating performance for the specified equipment under the applicable energy code standard and/or state-specific program guidelines.\nCalculation Methodology\nSavings calculations estimate daily domestic hot water usage based on building type and building area. Daily DHW gallons per ft² is set automatically by the tool to one of the following values, based on building type:\n"]
[]
[]
[]
[]
[]
[]
[]
[]
["DHW Load Category",null,"Daily gal/ft²","Example Bldg. Type"]
[1,"Minimal",0.01,"Office/School"]
[2,"Light",0.02,"Dining"]
[3,"Moderate",0.03,"Hotel"]
[4,"Heavy",0.04,"Dorm/Multifamily"]
[]
["Standby heat loss from storage water heaters is calculated based on rated storage gallons and heater input capacity using the following formula: Qstandby = Gallonsstorage/800 + 110*SqRT(MBHCap).\nDHW heater load is the same in the base and proposed case.  Heater load is applied to base and proposed efficiency to calculate the difference in heater demand.\n"]
[]
[]
[]
[]
[]
["Savings & Incentive"]
[{"$f":"'DHW Heaters'!F3","v":"Annual Electric Savings"},null,null,null,{"$f":"'DHW Heaters'!H3","v":0},{"$f":"'DHW Heaters'!I3","v":"kWh"}]
[{"$f":"'DHW Heaters'!F4","v":"Annual Fuel Savings"},null,null,null,{"$f":"'DHW Heaters'!H4","v":{"$error":"#N/A"}},{"$f":"'DHW Heaters'!I4","v":{"$error":"#N/A"}}]
[{"$f":"'DHW Heaters'!F5","v":"Incremental"},null,null,null,{"$f":"IF('DHW Heaters'!H6=\"\",'DHW Heaters'!H5,'DHW Heaters'!H6)","v":0},{"$f":"'DHW Heaters'!I5","v":"$"}]
[{"$f":"'DHW Heaters'!F7","v":"Estimated Incentive"},null,null,null,{"$f":"'DHW Heaters'!H7","v":{"$error":"#N/A"}},{"$f":"'DHW Heaters'!I7","v":"$"}]
[]
[{"$f":"'DHW Heaters'!K15","v":"Water Heater Type"},null,null,{"$f":"'DHW Heaters'!N15","v":0}]
[{"$f":"'DHW Heaters'!K16","v":"Storage Type"},null,null,{"$f":"'DHW Heaters'!N16","v":0}]
[{"$f":"'DHW Heaters'!K17","v":"Capacity, MBH (per heater)"},null,null,{"$f":"'DHW Heaters'!N17","v":0}]
[{"$f":"'DHW Heaters'!K18","v":"Storage, gallons (per heater)"},null,null,{"$f":"'DHW Heaters'!N18","v":0}]
[{"$f":"'DHW Heaters'!K19","v":"Heater Quantity"},null,null,{"$f":"'DHW Heaters'!N19","v":0}]
[null,null,null,{"$f":"'DHW Heaters'!N20","v":""}]
[{"$f":"'DHW Heaters'!K21","v":"Proposed Rated Performance"},null,null,{"$f":"'DHW Heaters'!N21","v":0.85}]
[{"$f":"'DHW Heaters'!K22","v":"Base Performance"},null,null,{"$f":"'DHW Heaters'!N22","v":""}]
[{"$f":"'DHW Heaters'!K23","v":"Manufacturer & Model (Optional)"},null,null,{"$f":"'DHW Heaters'!N23","v":0}]
[]
["Building Avg. Daily DHW Consumption"]
["Building Type",null,null,null,{"$f":"'DHW Heaters'!T15","v":0}]
["Estimated DHW gallons/day per ft²",null,null,null,{"$f":"IF('DHW Heaters'!T18=\"\",'DHW Heaters'!T16,'DHW Heaters'!T18)","v":{"$error":"#N/A"}}]
["DHW gallons per day - Calculated",null,null,null,{"$f":"'DHW Heaters'!T17","v":{"$error":"#N/A"}}]
[]
[]
[]
["Unitary HVAC (RTU, AC, HP, VRF)"]
["Measure Description\nThis measure considers savings from high performance electrically operated air-to-air and water-to-air unitary cooling/heating equipment with cooling and/or heating performance that exceeds the minimum requirements of energy code. Equipment analyzed can include the following:\n     o DX Air Handlers and Rooftop Units\n     o Unitary Air Conditioners\n     o Air-to-air Heat Pumps\n     o Variable Refrigerant Flow Systems (VRF)\n     o Small Water-to-Air Heat Pumps <= 135 MBH capacity\nThe baseline reflects the minimum required cooling and heating performance (heating savings are only considered for heat pump heating systems) for the specified equipment under the applicable energy code standard and/or state-specific program guidelines.\n\nCalculation Methodology\nSavings are estimated with an ambient temperature bin model using TMYx weather data. Space heating and cooling loads are estimated using a linear profile that is dependent on ambient dry-bulb temperature and space use.  The following general load profiles are assumed:\nComfort/HVAC loads:  Cooling load varies from peak load at 95°F OAdb to minimum load at 50°F OAdb.\nHeating load varies from peak load at 0°F OAdb to minimum load at 60°F OAdb.\nPeak cooling and heating load is assumed to be 90% of the equipment’s rated capacity.\nDuring unoccupied hours, the assumed loads are reduced by ~60%.\nConstant/IT-Elec Rm:  Cooling load assumed to be constant 24/7 at 40% of the equipment’s rated capacity.\nNo heating load.\nLoad profiles are identical in the base and proposed case.  Base case equipment performance is automatically set by the tool to reflect energy code performance for the given equipment and condenser type.  Proposed case performance should reflect the AHRI performance ratings of the design equipment.\n In each bin, base and proposed equipment performance is estimated based on the inputs for rated full and seasonal average performance, accounting for variation in performance from % load and ambient temperature.  Base and proposed case equipment demand is calculated as a function of the load and performance value in each bin.  All equipment serving Comfort/HVAC loads is modeled together in a single bin calculation based on the combined capacity and the weighted average performance value of all systems.  The same approach is used for the equipment serving Constant/IT-Elec Rm loads.\n"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Savings & Incentive"]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!F3","v":"Annual Electric Savings"},null,null,null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H3","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!I3","v":"kWh"}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!F4","v":"Annual Fuel Savings"},null,null,null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H4","v":{"$error":"#N/A"}},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!I4","v":{"$error":"#N/A"}}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!F5","v":"Incremental"},null,null,null,{"$f":"IF('Unitary HVAC (RTU, AC, HP, VRF)'!H6=\"\",'Unitary HVAC (RTU, AC, HP, VRF)'!H5,'Unitary HVAC (RTU, AC, HP, VRF)'!H6)","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!I5","v":"$"}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!F7","v":"Estimated Incentive"},null,null,null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H7","v":{"$error":"#N/A"}},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!I7","v":"$"}]
[]
[]
["Unitary Equipment Parameters"]
[null,null,null,null,"Primary",null,"Cooling","Heating","Qty of"]
["Unit","Unit Type",null,"Condenser","Load","Heating","Capacity","Capacity","Identical"]
["Tag/#",null,null,"Type","Profile","Source","MBH","MBH","Units"]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H24","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!I24","v":0},null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!K24","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!M24","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!O24","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!R24","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!S24","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!G24","v":0}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H25","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!I25","v":0},null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!K25","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!M25","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!O25","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!R25","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!S25","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!G25","v":0}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H26","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!I26","v":0},null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!K26","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!M26","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!O26","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!R26","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!S26","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!G26","v":0}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H27","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!I27","v":0},null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!K27","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!M27","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!O27","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!R27","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!S27","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!G27","v":0}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H28","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!I28","v":0},null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!K28","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!M28","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!O28","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!R28","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!S28","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!G28","v":0}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H29","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!I29","v":0},null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!K29","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!M29","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!O29","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!R29","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!S29","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!G29","v":0}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H30","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!I30","v":0},null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!K30","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!M30","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!O30","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!R30","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!S30","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!G30","v":0}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H31","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!I31","v":0},null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!K31","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!M31","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!O31","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!R31","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!S31","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!G31","v":0}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H32","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!I32","v":0},null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!K32","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!M32","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!O32","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!R32","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!S32","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!G32","v":0}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H33","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!I33","v":0},null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!K33","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!M33","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!O33","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!R33","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!S33","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!G33","v":0}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H34","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!I34","v":0},null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!K34","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!M34","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!O34","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!R34","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!S34","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!G34","v":0}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H35","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!I35","v":0},null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!K35","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!M35","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!O35","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!R35","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!S35","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!G35","v":0}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H36","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!I36","v":0},null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!K36","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!M36","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!O36","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!R36","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!S36","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!G36","v":0}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H37","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!I37","v":0},null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!K37","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!M37","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!O37","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!R37","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!S37","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!G37","v":0}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H38","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!I38","v":0},null,{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!K38","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!M38","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!O38","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!R38","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!S38","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!G38","v":0}]
[]
[null,"Proposed Performance",null,null,null,"Baseline Performance"]
[null,"Cooling",null,"Heating",null,"Cooling",null,"Heating"]
["Unit","Full Load",null,"COP","COP","Full Load",null,"COP","COP"]
["Tag/#","EER","IEER/SEER","47°F","17°F","EER","IEER","47°F","17°F"]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H24","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!Z24","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AA24","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AB24","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AC24","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AD24","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AE24","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AF24","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AG24","v":""}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H25","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!Z25","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AA25","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AB25","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AC25","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AD25","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AE25","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AF25","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AG25","v":""}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H26","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!Z26","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AA26","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AB26","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AC26","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AD26","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AE26","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AF26","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AG26","v":""}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H27","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!Z27","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AA27","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AB27","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AC27","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AD27","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AE27","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AF27","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AG27","v":""}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H28","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!Z28","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AA28","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AB28","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AC28","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AD28","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AE28","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AF28","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AG28","v":""}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H29","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!Z29","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AA29","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AB29","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AC29","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AD29","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AE29","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AF29","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AG29","v":""}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H30","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!Z30","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AA30","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AB30","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AC30","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AD30","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AE30","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AF30","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AG30","v":""}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H31","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!Z31","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AA31","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AB31","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AC31","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AD31","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AE31","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AF31","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AG31","v":""}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H32","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!Z32","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AA32","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AB32","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AC32","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AD32","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AE32","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AF32","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AG32","v":""}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H33","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!Z33","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AA33","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AB33","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AC33","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AD33","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AE33","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AF33","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AG33","v":""}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H34","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!Z34","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AA34","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AB34","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AC34","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AD34","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AE34","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AF34","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AG34","v":""}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H35","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!Z35","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AA35","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AB35","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AC35","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AD35","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AE35","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AF35","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AG35","v":""}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H36","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!Z36","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AA36","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AB36","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AC36","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AD36","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AE36","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AF36","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AG36","v":""}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H37","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!Z37","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AA37","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AB37","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AC37","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AD37","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AE37","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AF37","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AG37","v":""}]
[{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!H38","v":0},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!Z38","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AA38","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AB38","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AC38","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AD38","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AE38","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AF38","v":""},{"$f":"'Unitary HVAC (RTU, AC, HP, VRF)'!AG38","v":""}]
[]
[]
[]
["Demand Control Ventilation"]
["Measure Description\nThis measure considers savings from implementing demand controlled ventilation (DCV) in HVAC systems or zones where it is not required by the energy code.\nThe baseline reflects the minimum DCV requirements for the specified equipment under the applicable energy code standard and/or state-specific program guidelines.\n\nCalculation Methodology\nSavings are estimated with an ambient temperature bin model using TMYx weather data.  The bin model for this measure includes only scheduled building operating hours, as the ventilation air handlers are assumed to be off during scheduled unoccupied hours. Each air handler with DCV included in the inputs table is modeled individually for savings.\nAir handlers can be modeled as constant volume or variable air volume (VAV) systems, as selected by the user.  The average operating OA rates are assumed to be constant in both system types.  For VAV systems that are not 100% OA, the total supply flow varies based on assumed space cooling and heating load profiles.  VAV turndown is limited to the larger of the OA CFM or 50% of design total supply CFM. \nIn each bin, the required cooling or heating load to bring the supply OA to space temperature or enthalpy conditions is calculated, factoring in load impacts from energy recovery sections and supply fan heat (energy recovery effectiveness and design fan bhp are identical in the base and proposed case).  The DCV impact is modeled in the proposed case by assuming an average 25% reduction in OA CFM, only for the % of ventilation air that is impacted by the DCV control (this is controlled by a user input).\nCooling and heating load reduction is calculated in each bin based on the reduction in OA CFM.  Cooling or heating equipment performance is applied to the load reduction to calculate energy demand reduction.  The heating load reduction is allocated between air handler heating source and zone heating source based on the assumed air handler discharge air temperature setpoints.\nFor VAV systems with turndown limited by OA requirements, the model calculates the reduction in average air handler fan speed from the reduced OA rate and calculates the associated fan savings using a modified cube law with static pressure control.  The reduction in fan heat is also accounted for in the heating and cooling load impacts from DCV.\n"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Savings & Incentive"]
[{"$f":"'Demand Control Ventilation'!F3","v":"Annual Electric Savings"},null,null,null,{"$f":"'Demand Control Ventilation'!H3","v":0},{"$f":"'Demand Control Ventilation'!I3","v":"kWh"}]
[{"$f":"'Demand Control Ventilation'!F4","v":"Annual Fuel Savings"},null,null,null,{"$f":"'Demand Control Ventilation'!H4","v":{"$error":"#N/A"}},{"$f":"'Demand Control Ventilation'!I4","v":{"$error":"#N/A"}}]
[{"$f":"'Demand Control Ventilation'!F5","v":"Incremental"},null,null,null,{"$f":"IF('Demand Control Ventilation'!H6=\"\",'Demand Control Ventilation'!H5,'Demand Control Ventilation'!H6)","v":0},{"$f":"'Demand Control Ventilation'!I5","v":"$"}]
[{"$f":"'Demand Control Ventilation'!F7","v":"Estimated Incentive"},null,null,null,{"$f":"'Demand Control Ventilation'!H7","v":{"$error":"#N/A"}},{"$f":"'Demand Control Ventilation'!I7","v":"$"}]
[]
[]
[]
[]
["Air Handling Unit Parameters"]
["Unit","Description",null,"Total","Total","% of","Includes","Design ERV"]
[null,null,null,"Supply","OA","OA w/","Energy","Sensible","Total"]
[null,null,null,"CFM","CFM","Code DCV","Recovery?","Eff","Eff"]
[{"$f":"'Demand Control Ventilation'!H22","v":0},{"$f":"'Demand Control Ventilation'!J22","v":0},null,{"$f":"'Demand Control Ventilation'!L22","v":0},{"$f":"'Demand Control Ventilation'!M22","v":0},{"$f":"'Demand Control Ventilation'!N22","v":0},{"$f":"'Demand Control Ventilation'!O22","v":0},{"$f":"'Demand Control Ventilation'!P22","v":0},{"$f":"'Demand Control Ventilation'!Q22","v":0}]
[{"$f":"'Demand Control Ventilation'!H23","v":0},{"$f":"'Demand Control Ventilation'!J23","v":0},null,{"$f":"'Demand Control Ventilation'!L23","v":0},{"$f":"'Demand Control Ventilation'!M23","v":0},{"$f":"'Demand Control Ventilation'!N23","v":0},{"$f":"'Demand Control Ventilation'!O23","v":0},{"$f":"'Demand Control Ventilation'!P23","v":0},{"$f":"'Demand Control Ventilation'!Q23","v":0}]
[{"$f":"'Demand Control Ventilation'!H24","v":0},{"$f":"'Demand Control Ventilation'!J24","v":0},null,{"$f":"'Demand Control Ventilation'!L24","v":0},{"$f":"'Demand Control Ventilation'!M24","v":0},{"$f":"'Demand Control Ventilation'!N24","v":0},{"$f":"'Demand Control Ventilation'!O24","v":0},{"$f":"'Demand Control Ventilation'!P24","v":0},{"$f":"'Demand Control Ventilation'!Q24","v":0}]
[{"$f":"'Demand Control Ventilation'!H25","v":0},{"$f":"'Demand Control Ventilation'!J25","v":0},null,{"$f":"'Demand Control Ventilation'!L25","v":0},{"$f":"'Demand Control Ventilation'!M25","v":0},{"$f":"'Demand Control Ventilation'!N25","v":0},{"$f":"'Demand Control Ventilation'!O25","v":0},{"$f":"'Demand Control Ventilation'!P25","v":0},{"$f":"'Demand Control Ventilation'!Q25","v":0}]
[{"$f":"'Demand Control Ventilation'!H26","v":0},{"$f":"'Demand Control Ventilation'!J26","v":0},null,{"$f":"'Demand Control Ventilation'!L26","v":0},{"$f":"'Demand Control Ventilation'!M26","v":0},{"$f":"'Demand Control Ventilation'!N26","v":0},{"$f":"'Demand Control Ventilation'!O26","v":0},{"$f":"'Demand Control Ventilation'!P26","v":0},{"$f":"'Demand Control Ventilation'!Q26","v":0}]
[{"$f":"'Demand Control Ventilation'!H27","v":0},{"$f":"'Demand Control Ventilation'!J27","v":0},null,{"$f":"'Demand Control Ventilation'!L27","v":0},{"$f":"'Demand Control Ventilation'!M27","v":0},{"$f":"'Demand Control Ventilation'!N27","v":0},{"$f":"'Demand Control Ventilation'!O27","v":0},{"$f":"'Demand Control Ventilation'!P27","v":0},{"$f":"'Demand Control Ventilation'!Q27","v":0}]
[{"$f":"'Demand Control Ventilation'!H28","v":0},{"$f":"'Demand Control Ventilation'!J28","v":0},null,{"$f":"'Demand Control Ventilation'!L28","v":0},{"$f":"'Demand Control Ventilation'!M28","v":0},{"$f":"'Demand Control Ventilation'!N28","v":0},{"$f":"'Demand Control Ventilation'!O28","v":0},{"$f":"'Demand Control Ventilation'!P28","v":0},{"$f":"'Demand Control Ventilation'!Q28","v":0}]
[{"$f":"'Demand Control Ventilation'!H29","v":0},{"$f":"'Demand Control Ventilation'!J29","v":0},null,{"$f":"'Demand Control Ventilation'!L29","v":0},{"$f":"'Demand Control Ventilation'!M29","v":0},{"$f":"'Demand Control Ventilation'!N29","v":0},{"$f":"'Demand Control Ventilation'!O29","v":0},{"$f":"'Demand Control Ventilation'!P29","v":0},{"$f":"'Demand Control Ventilation'!Q29","v":0}]
[{"$f":"'Demand Control Ventilation'!H30","v":0},{"$f":"'Demand Control Ventilation'!J30","v":0},null,{"$f":"'Demand Control Ventilation'!L30","v":0},{"$f":"'Demand Control Ventilation'!M30","v":0},{"$f":"'Demand Control Ventilation'!N30","v":0},{"$f":"'Demand Control Ventilation'!O30","v":0},{"$f":"'Demand Control Ventilation'!P30","v":0},{"$f":"'Demand Control Ventilation'!Q30","v":0}]
[{"$f":"'Demand Control Ventilation'!H31","v":0},{"$f":"'Demand Control Ventilation'!J31","v":0},null,{"$f":"'Demand Control Ventilation'!L31","v":0},{"$f":"'Demand Control Ventilation'!M31","v":0},{"$f":"'Demand Control Ventilation'!N31","v":0},{"$f":"'Demand Control Ventilation'!O31","v":0},{"$f":"'Demand Control Ventilation'!P31","v":0},{"$f":"'Demand Control Ventilation'!Q31","v":0}]
[]
[]
["Cooling & Heating Parameters"]
["Cooling",null,null,"Air Handler Heating",null,null," Zone Heating"]
["Cooling","Peformance",null,"Heat","Fossil Fuel","Electric","Heat","Fossil Fuel","Electric"]
["Included?","EER","SEER/IEER","Fuel","Avg. Eff%","Avg COP","Fuel","Avg. Eff%","Avg COP"]
[{"$f":"'Demand Control Ventilation'!R22","v":0},{"$f":"'Demand Control Ventilation'!S22","v":0},{"$f":"'Demand Control Ventilation'!T22","v":0},{"$f":"'Demand Control Ventilation'!U22","v":0},{"$f":"'Demand Control Ventilation'!V22","v":0},{"$f":"'Demand Control Ventilation'!W22","v":0},{"$f":"'Demand Control Ventilation'!X22","v":0},{"$f":"'Demand Control Ventilation'!Y22","v":0},{"$f":"'Demand Control Ventilation'!Z22","v":0}]
[{"$f":"'Demand Control Ventilation'!R23","v":0},{"$f":"'Demand Control Ventilation'!S23","v":0},{"$f":"'Demand Control Ventilation'!T23","v":0},{"$f":"'Demand Control Ventilation'!U23","v":0},{"$f":"'Demand Control Ventilation'!V23","v":0},{"$f":"'Demand Control Ventilation'!W23","v":0},{"$f":"'Demand Control Ventilation'!X23","v":0},{"$f":"'Demand Control Ventilation'!Y23","v":0},{"$f":"'Demand Control Ventilation'!Z23","v":0}]
[{"$f":"'Demand Control Ventilation'!R24","v":0},{"$f":"'Demand Control Ventilation'!S24","v":0},{"$f":"'Demand Control Ventilation'!T24","v":0},{"$f":"'Demand Control Ventilation'!U24","v":0},{"$f":"'Demand Control Ventilation'!V24","v":0},{"$f":"'Demand Control Ventilation'!W24","v":0},{"$f":"'Demand Control Ventilation'!X24","v":0},{"$f":"'Demand Control Ventilation'!Y24","v":0},{"$f":"'Demand Control Ventilation'!Z24","v":0}]
[{"$f":"'Demand Control Ventilation'!R25","v":0},{"$f":"'Demand Control Ventilation'!S25","v":0},{"$f":"'Demand Control Ventilation'!T25","v":0},{"$f":"'Demand Control Ventilation'!U25","v":0},{"$f":"'Demand Control Ventilation'!V25","v":0},{"$f":"'Demand Control Ventilation'!W25","v":0},{"$f":"'Demand Control Ventilation'!X25","v":0},{"$f":"'Demand Control Ventilation'!Y25","v":0},{"$f":"'Demand Control Ventilation'!Z25","v":0}]
[{"$f":"'Demand Control Ventilation'!R26","v":0},{"$f":"'Demand Control Ventilation'!S26","v":0},{"$f":"'Demand Control Ventilation'!T26","v":0},{"$f":"'Demand Control Ventilation'!U26","v":0},{"$f":"'Demand Control Ventilation'!V26","v":0},{"$f":"'Demand Control Ventilation'!W26","v":0},{"$f":"'Demand Control Ventilation'!X26","v":0},{"$f":"'Demand Control Ventilation'!Y26","v":0},{"$f":"'Demand Control Ventilation'!Z26","v":0}]
[{"$f":"'Demand Control Ventilation'!R27","v":0},{"$f":"'Demand Control Ventilation'!S27","v":0},{"$f":"'Demand Control Ventilation'!T27","v":0},{"$f":"'Demand Control Ventilation'!U27","v":0},{"$f":"'Demand Control Ventilation'!V27","v":0},{"$f":"'Demand Control Ventilation'!W27","v":0},{"$f":"'Demand Control Ventilation'!X27","v":0},{"$f":"'Demand Control Ventilation'!Y27","v":0},{"$f":"'Demand Control Ventilation'!Z27","v":0}]
[{"$f":"'Demand Control Ventilation'!R28","v":0},{"$f":"'Demand Control Ventilation'!S28","v":0},{"$f":"'Demand Control Ventilation'!T28","v":0},{"$f":"'Demand Control Ventilation'!U28","v":0},{"$f":"'Demand Control Ventilation'!V28","v":0},{"$f":"'Demand Control Ventilation'!W28","v":0},{"$f":"'Demand Control Ventilation'!X28","v":0},{"$f":"'Demand Control Ventilation'!Y28","v":0},{"$f":"'Demand Control Ventilation'!Z28","v":0}]
[{"$f":"'Demand Control Ventilation'!R29","v":0},{"$f":"'Demand Control Ventilation'!S29","v":0},{"$f":"'Demand Control Ventilation'!T29","v":0},{"$f":"'Demand Control Ventilation'!U29","v":0},{"$f":"'Demand Control Ventilation'!V29","v":0},{"$f":"'Demand Control Ventilation'!W29","v":0},{"$f":"'Demand Control Ventilation'!X29","v":0},{"$f":"'Demand Control Ventilation'!Y29","v":0},{"$f":"'Demand Control Ventilation'!Z29","v":0}]
[{"$f":"'Demand Control Ventilation'!R30","v":0},{"$f":"'Demand Control Ventilation'!S30","v":0},{"$f":"'Demand Control Ventilation'!T30","v":0},{"$f":"'Demand Control Ventilation'!U30","v":0},{"$f":"'Demand Control Ventilation'!V30","v":0},{"$f":"'Demand Control Ventilation'!W30","v":0},{"$f":"'Demand Control Ventilation'!X30","v":0},{"$f":"'Demand Control Ventilation'!Y30","v":0},{"$f":"'Demand Control Ventilation'!Z30","v":0}]
[{"$f":"'Demand Control Ventilation'!R31","v":0},{"$f":"'Demand Control Ventilation'!S31","v":0},{"$f":"'Demand Control Ventilation'!T31","v":0},{"$f":"'Demand Control Ventilation'!U31","v":0},{"$f":"'Demand Control Ventilation'!V31","v":0},{"$f":"'Demand Control Ventilation'!W31","v":0},{"$f":"'Demand Control Ventilation'!X31","v":0},{"$f":"'Demand Control Ventilation'!Y31","v":0},{"$f":"'Demand Control Ventilation'!Z31","v":0}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Variable Flow Kitchen Hood"]
["Measure Description\nThis measure considers savings from installing a variable flow kitchen hood control system to modulate hood exhaust and make-up air in response to cooking activity.  This control is generally required by energy code for hood systems with 5,000 CFM or more, but it is not required when total hood exhaust flow is less than 5,000 CFM.\nFor eligible systems, the baseline assumes constant hood exhaust and make-up air flow at the design values during hours when the kitchen is in use.\n\nCalculation Methodology\nSavings are estimated with an ambient temperature bin model using TMYx weather data.  Total bin hours are adjusted to only include daily hours when the kitchen is expected to be used.   The base case is modeled with constant hood exhaust and make-up air flow, at the design CFM, during the hours when the kitchen is in use.  The proposed case assumes that the hoods and make-up air units operate at a reduced % of design flow, which varies based on the meal category. The user defines which meals have kitchen operation (set separately for weekdays, Saturdays, and Sundays). The hours per meal and average % hood flow per meal are automatically set by the tool as follows:\n      Breakfast: 4 hours of operation, avg. 65% of design flow with controls\n      Lunch: 5 hours of operation, avg. 70% of design flow with controls\n      Dinner: 6 hours of operation, avg. 75% of design flow with controls\n      Late Night: 3 hours of operation, avg. 60% of design flow with controls\nAverage hood and make-up air unit fan speed in the proposed case is modeled equal to the percent flow rate.  Fan power is calculated based on % speed using a modified cube law that accounts for static pressure control. Fan demand savings are calculated relative to the baseline fan power at full speed.\nMake-up air heating and cooling load reductions are calculated based on the difference in average make-up air flow and assuming a constant 68°F discharge air setpoint for heating mode and a 25 Btu/lb discharge air enthalpy setpoint for cooling mode.  Heating and cooling equipment performance assumptions are applied to the calculated load reductions to estimate the respective demand savings in each bin.\n"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Savings & Incentive"]
[{"$f":"'Variable Flow Kitchen Hood'!F3","v":"Annual Electric Savings"},null,null,null,{"$f":"'Variable Flow Kitchen Hood'!H3","v":{"$error":"#DIV/0!"}},{"$f":"'Variable Flow Kitchen Hood'!I3","v":"kWh"}]
[{"$f":"'Variable Flow Kitchen Hood'!F4","v":"Annual Fuel Savings"},null,null,null,{"$f":"'Variable Flow Kitchen Hood'!H4","v":{"$error":"#DIV/0!"}},{"$f":"'Variable Flow Kitchen Hood'!I4","v":{"$error":"#N/A"}}]
[{"$f":"'Variable Flow Kitchen Hood'!F5","v":"Incremental"},null,null,null,{"$f":"IF('Variable Flow Kitchen Hood'!H6=\"\",'Variable Flow Kitchen Hood'!H5,'Variable Flow Kitchen Hood'!H6)","v":0},{"$f":"'Variable Flow Kitchen Hood'!I5","v":"$"}]
[{"$f":"'Variable Flow Kitchen Hood'!F7","v":"Estimated Incentive"},null,null,null,{"$f":"'Variable Flow Kitchen Hood'!H7","v":{"$error":"#DIV/0!"}},{"$f":"'Variable Flow Kitchen Hood'!I7","v":"$"}]
[]
[null,null,null,"Fan Mtr Nameplate HP",null,"Fan Motor BHP",null,null,"Proposed"]
[null,null,"Airflow","Default","Or, User","Default","Or, User","Motor","VFD Burden"]
[null,"Unit","CFM","Calc","Input","Calc","Input","Efficiency","kW"]
[null,{"$f":"'Variable Flow Kitchen Hood'!G20","v":"EXHAUST HOOD FANS"}]
[null,{"$f":"'Variable Flow Kitchen Hood'!H21","v":1},{"$f":"'Variable Flow Kitchen Hood'!I21","v":0},{"$f":"IF('Variable Flow Kitchen Hood'!K21=\"\",'Variable Flow Kitchen Hood'!J21,\"\")","v":0},{"$f":"'Variable Flow Kitchen Hood'!K21","v":0},{"$f":"IF('Variable Flow Kitchen Hood'!M21=\"\",'Variable Flow Kitchen Hood'!L21,\"\")","v":0},{"$f":"'Variable Flow Kitchen Hood'!M21","v":0},{"$f":"'Variable Flow Kitchen Hood'!N21","v":0},{"$f":"'Variable Flow Kitchen Hood'!O21","v":0}]
[null,{"$f":"'Variable Flow Kitchen Hood'!H22","v":2},{"$f":"'Variable Flow Kitchen Hood'!I22","v":0},{"$f":"IF('Variable Flow Kitchen Hood'!K22=\"\",'Variable Flow Kitchen Hood'!J22,\"\")","v":0},{"$f":"'Variable Flow Kitchen Hood'!K22","v":0},{"$f":"IF('Variable Flow Kitchen Hood'!M22=\"\",'Variable Flow Kitchen Hood'!L22,\"\")","v":0},{"$f":"'Variable Flow Kitchen Hood'!M22","v":0},{"$f":"'Variable Flow Kitchen Hood'!N22","v":0},{"$f":"'Variable Flow Kitchen Hood'!O22","v":0}]
[null,{"$f":"'Variable Flow Kitchen Hood'!H23","v":3},{"$f":"'Variable Flow Kitchen Hood'!I23","v":0},{"$f":"IF('Variable Flow Kitchen Hood'!K23=\"\",'Variable Flow Kitchen Hood'!J23,\"\")","v":0},{"$f":"'Variable Flow Kitchen Hood'!K23","v":0},{"$f":"IF('Variable Flow Kitchen Hood'!M23=\"\",'Variable Flow Kitchen Hood'!L23,\"\")","v":0},{"$f":"'Variable Flow Kitchen Hood'!M23","v":0},{"$f":"'Variable Flow Kitchen Hood'!N23","v":0},{"$f":"'Variable Flow Kitchen Hood'!O23","v":0}]
[null,{"$f":"'Variable Flow Kitchen Hood'!G24","v":"MAKE-UP AIR FANS"}]
[null,{"$f":"'Variable Flow Kitchen Hood'!H25","v":1},{"$f":"'Variable Flow Kitchen Hood'!I25","v":0},{"$f":"IF('Variable Flow Kitchen Hood'!K25=\"\",'Variable Flow Kitchen Hood'!J25,\"\")","v":0},{"$f":"'Variable Flow Kitchen Hood'!K25","v":0},{"$f":"IF('Variable Flow Kitchen Hood'!M25=\"\",'Variable Flow Kitchen Hood'!L25,\"\")","v":0},{"$f":"'Variable Flow Kitchen Hood'!M25","v":0},{"$f":"'Variable Flow Kitchen Hood'!N25","v":0},{"$f":"'Variable Flow Kitchen Hood'!O25","v":0}]
[null,{"$f":"'Variable Flow Kitchen Hood'!H26","v":2},{"$f":"'Variable Flow Kitchen Hood'!I26","v":0},{"$f":"IF('Variable Flow Kitchen Hood'!K26=\"\",'Variable Flow Kitchen Hood'!J26,\"\")","v":0},{"$f":"'Variable Flow Kitchen Hood'!K26","v":0},{"$f":"IF('Variable Flow Kitchen Hood'!M26=\"\",'Variable Flow Kitchen Hood'!L26,\"\")","v":0},{"$f":"'Variable Flow Kitchen Hood'!M26","v":0},{"$f":"'Variable Flow Kitchen Hood'!N26","v":0},{"$f":"'Variable Flow Kitchen Hood'!O26","v":0}]
[null,{"$f":"'Variable Flow Kitchen Hood'!H27","v":3},{"$f":"'Variable Flow Kitchen Hood'!I27","v":0},{"$f":"IF('Variable Flow Kitchen Hood'!K27=\"\",'Variable Flow Kitchen Hood'!J27,\"\")","v":0},{"$f":"'Variable Flow Kitchen Hood'!K27","v":0},{"$f":"IF('Variable Flow Kitchen Hood'!M27=\"\",'Variable Flow Kitchen Hood'!L27,\"\")","v":0},{"$f":"'Variable Flow Kitchen Hood'!M27","v":0},{"$f":"'Variable Flow Kitchen Hood'!N27","v":0},{"$f":"'Variable Flow Kitchen Hood'!O27","v":0}]
[]
[]
[null,null,"Kitchen Hood Use Profile"]
[null,null,null,{"$f":"'Variable Flow Kitchen Hood'!L30","v":"Breakfast"},{"$f":"'Variable Flow Kitchen Hood'!M30","v":"Lunch"},{"$f":"'Variable Flow Kitchen Hood'!N30","v":"Dinner"},{"$f":"'Variable Flow Kitchen Hood'!O30","v":"Late Night"}]
[null,null,{"$f":"'Variable Flow Kitchen Hood'!K31","v":"Weekdays"},{"$f":"'Variable Flow Kitchen Hood'!L31","v":0},{"$f":"'Variable Flow Kitchen Hood'!M31","v":0},{"$f":"'Variable Flow Kitchen Hood'!N31","v":0},{"$f":"'Variable Flow Kitchen Hood'!O31","v":0}]
[null,null,{"$f":"'Variable Flow Kitchen Hood'!K32","v":"Saturday"},{"$f":"'Variable Flow Kitchen Hood'!L32","v":0},{"$f":"'Variable Flow Kitchen Hood'!M32","v":0},{"$f":"'Variable Flow Kitchen Hood'!N32","v":0},{"$f":"'Variable Flow Kitchen Hood'!O32","v":0}]
[null,null,{"$f":"'Variable Flow Kitchen Hood'!K33","v":"Sunday"},{"$f":"'Variable Flow Kitchen Hood'!L33","v":0},{"$f":"'Variable Flow Kitchen Hood'!M33","v":0},{"$f":"'Variable Flow Kitchen Hood'!N33","v":0},{"$f":"'Variable Flow Kitchen Hood'!O33","v":0}]
[]
[null,null,null,"Heating & Cooling Performance"]
[null,null,null,{"$f":"'Variable Flow Kitchen Hood'!G30","v":"Heating Fuel"},null,{"$f":"'Variable Flow Kitchen Hood'!I30","v":0}]
[null,null,null,{"$f":"'Variable Flow Kitchen Hood'!G31","v":"Fossil Fuel Baseline Eff (%)"},null,{"$f":"IF('Variable Flow Kitchen Hood'!I30=\"Fossil Fuel\",'Variable Flow Kitchen Hood'!I31,\"\")","v":""}]
[null,null,null,{"$f":"'Variable Flow Kitchen Hood'!G32","v":"Elec Heat Baseline COP"},null,{"$f":"IF('Variable Flow Kitchen Hood'!I30=\"Fossil Fuel\",\"\",'Variable Flow Kitchen Hood'!I32)","v":0}]
[null,null,null,{"$f":"'Variable Flow Kitchen Hood'!G33","v":"Cooling Included?"},null,{"$f":"'Variable Flow Kitchen Hood'!I33","v":0}]
[null,null,null,{"$f":"'Variable Flow Kitchen Hood'!G34","v":"Cooling Baseline IEER or IPLV"},null,{"$f":"IF('Variable Flow Kitchen Hood'!I33<>\"Yes\",\"\",'Variable Flow Kitchen Hood'!I34)","v":""}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Variable Frequency Drives"]
["Measure Description\nThis measure considers savings from installing variable frequency drives to control fans and/or pumps.  The tool analyzes this measure prescriptively, following the Prescriptive VFD guidelines for incentive eligibility based on motor category, size, and control strategy.  Savings are only considered for drives/motors that are eligible for prescriptive incentives.\n\nCalculation Methodology\nSavings for this prescriptive measure are the deemed savings, following the MA Technical Reference Manual guidelines.\n"]
[]
[]
[]
[]
[]
["Savings & Incentive"]
[{"$f":"'Variable Frequency Drives'!F3","v":"Annual Electric Savings"},null,null,null,{"$f":"'Variable Frequency Drives'!H3","v":0},{"$f":"'Variable Frequency Drives'!I3","v":"kWh"}]
[{"$f":"'Variable Frequency Drives'!F4","v":"Annual Fuel Savings"},null,null,null,{"$f":"'Variable Frequency Drives'!H4","v":{"$error":"#N/A"}},{"$f":"'Variable Frequency Drives'!I4","v":{"$error":"#N/A"}}]
[{"$f":"'Variable Frequency Drives'!F5","v":"Incremental"},null,null,null,{"$f":"IF('Variable Frequency Drives'!H6=\"\",'Variable Frequency Drives'!H5,'Variable Frequency Drives'!H6)","v":0},{"$f":"'Variable Frequency Drives'!I5","v":"$"}]
[{"$f":"'Variable Frequency Drives'!F7","v":"Estimated Incentive"},null,null,null,{"$f":"'Variable Frequency Drives'!H7","v":0},{"$f":"'Variable Frequency Drives'!I7","v":"$"}]
[]
["Installation Type",null,"Max Eligible Motor HP","Per Unit Motor HP","Motor Qty","Max Operating Qty","Control Type (Req.)",null,"Per Mtr Incentive"]
[]
[{"$f":"'Variable Frequency Drives'!L17","v":0},null,{"$f":"'Variable Frequency Drives'!O17","v":""},{"$f":"'Variable Frequency Drives'!P17","v":0},{"$f":"'Variable Frequency Drives'!Q17","v":0},{"$f":"'Variable Frequency Drives'!R17","v":0},{"$f":"'Variable Frequency Drives'!S17","v":0},null,{"$f":"'Variable Frequency Drives'!W17","v":0}]
[{"$f":"'Variable Frequency Drives'!L18","v":0},null,{"$f":"'Variable Frequency Drives'!O18","v":""},{"$f":"'Variable Frequency Drives'!P18","v":0},{"$f":"'Variable Frequency Drives'!Q18","v":0},{"$f":"'Variable Frequency Drives'!R18","v":0},{"$f":"'Variable Frequency Drives'!S18","v":0},null,{"$f":"'Variable Frequency Drives'!W18","v":0}]
[{"$f":"'Variable Frequency Drives'!L19","v":0},null,{"$f":"'Variable Frequency Drives'!O19","v":""},{"$f":"'Variable Frequency Drives'!P19","v":0},{"$f":"'Variable Frequency Drives'!Q19","v":0},{"$f":"'Variable Frequency Drives'!R19","v":0},{"$f":"'Variable Frequency Drives'!S19","v":0},null,{"$f":"'Variable Frequency Drives'!W19","v":0}]
[{"$f":"'Variable Frequency Drives'!L20","v":0},null,{"$f":"'Variable Frequency Drives'!O20","v":""},{"$f":"'Variable Frequency Drives'!P20","v":0},{"$f":"'Variable Frequency Drives'!Q20","v":0},{"$f":"'Variable Frequency Drives'!R20","v":0},{"$f":"'Variable Frequency Drives'!S20","v":0},null,{"$f":"'Variable Frequency Drives'!W20","v":0}]
[{"$f":"'Variable Frequency Drives'!L21","v":0},null,{"$f":"'Variable Frequency Drives'!O21","v":""},{"$f":"'Variable Frequency Drives'!P21","v":0},{"$f":"'Variable Frequency Drives'!Q21","v":0},{"$f":"'Variable Frequency Drives'!R21","v":0},{"$f":"'Variable Frequency Drives'!S21","v":0},null,{"$f":"'Variable Frequency Drives'!W21","v":0}]
[{"$f":"'Variable Frequency Drives'!L22","v":0},null,{"$f":"'Variable Frequency Drives'!O22","v":""},{"$f":"'Variable Frequency Drives'!P22","v":0},{"$f":"'Variable Frequency Drives'!Q22","v":0},{"$f":"'Variable Frequency Drives'!R22","v":0},{"$f":"'Variable Frequency Drives'!S22","v":0},null,{"$f":"'Variable Frequency Drives'!W22","v":0}]
[{"$f":"'Variable Frequency Drives'!L23","v":0},null,{"$f":"'Variable Frequency Drives'!O23","v":""},{"$f":"'Variable Frequency Drives'!P23","v":0},{"$f":"'Variable Frequency Drives'!Q23","v":0},{"$f":"'Variable Frequency Drives'!R23","v":0},{"$f":"'Variable Frequency Drives'!S23","v":0},null,{"$f":"'Variable Frequency Drives'!W23","v":0}]
[{"$f":"'Variable Frequency Drives'!L24","v":0},null,{"$f":"'Variable Frequency Drives'!O24","v":""},{"$f":"'Variable Frequency Drives'!P24","v":0},{"$f":"'Variable Frequency Drives'!Q24","v":0},{"$f":"'Variable Frequency Drives'!R24","v":0},{"$f":"'Variable Frequency Drives'!S24","v":0},null,{"$f":"'Variable Frequency Drives'!W24","v":0}]
[{"$f":"'Variable Frequency Drives'!L25","v":0},null,{"$f":"'Variable Frequency Drives'!O25","v":""},{"$f":"'Variable Frequency Drives'!P25","v":0},{"$f":"'Variable Frequency Drives'!Q25","v":0},{"$f":"'Variable Frequency Drives'!R25","v":0},{"$f":"'Variable Frequency Drives'!S25","v":0},null,{"$f":"'Variable Frequency Drives'!W25","v":0}]
[{"$f":"'Variable Frequency Drives'!L26","v":0},null,{"$f":"'Variable Frequency Drives'!O26","v":""},{"$f":"'Variable Frequency Drives'!P26","v":0},{"$f":"'Variable Frequency Drives'!Q26","v":0},{"$f":"'Variable Frequency Drives'!R26","v":0},{"$f":"'Variable Frequency Drives'!S26","v":0},null,{"$f":"'Variable Frequency Drives'!W26","v":0}]
[]
[]
[]
[]
["Low Flow DHW Fixtures"]
["Measure Description\nThis measure considers savings from installing low flow hot water fixtures to reduce DHW heating demand and water use.\nThe baseline reflects the LEED v4 baseline fixture flow ratings, which are assumed to be consistent with Federal standards.\nCalculation Methodology\nSavings are based on an estimated % reduction in average DHW demand.  The tool calculates baseline daily domestic hot water usage based on building type and building area. Daily DHW gallons per ft² is set to one of the following values based on building type:\n"]
[]
[]
[]
[]
[]
[]
[]
["DHW Load Category",null,"Daily gal/ft²","Example Bldg. Type"]
[1,"Minimal",0.01,"Office/School"]
[2,"Light",0.02,"Dining"]
[3,"Moderate",0.03,"Hotel"]
[4,"Heavy",0.04,"Dorm/Multifamily"]
["Four potential fixture types can be considered for savings.  Based on user inputs for design gpm and % of total DHW use allocated to the applicable fixture type, the tool calculates a weighted average gpm for baseline and proposed case for the portion of the DHW load that is impacted by the measure.  The overall % reduction in building DHW demand is calculated based on the difference in baseline and proposed gpm and the % of total load impacted by the applicable fixtures in the measure.  The DHW heating equipment performance is applied to the load reduction to determine energy savings."]
[]
[]
[]
[]
[]
["Savings & Incentive"]
[{"$f":"'Low Flow DHW Fixtures'!F3","v":"Annual Electric Savings"},null,null,null,{"$f":"'Low Flow DHW Fixtures'!H3","v":0},{"$f":"'Low Flow DHW Fixtures'!I3","v":"kWh"}]
[{"$f":"'Low Flow DHW Fixtures'!F4","v":"Annual Fuel Savings"},null,null,null,{"$f":"'Low Flow DHW Fixtures'!H4","v":{"$error":"#N/A"}},{"$f":"'Low Flow DHW Fixtures'!I4","v":{"$error":"#N/A"}}]
[{"$f":"'Low Flow DHW Fixtures'!F5","v":"Incremental"},null,null,null,{"$f":"IF('Low Flow DHW Fixtures'!H6=\"\",'Low Flow DHW Fixtures'!H5,'Low Flow DHW Fixtures'!H6)","v":0},{"$f":"'Low Flow DHW Fixtures'!I5","v":"$"}]
[{"$f":"'Low Flow DHW Fixtures'!F7","v":"Estimated Incentive"},null,null,null,{"$f":"'Low Flow DHW Fixtures'!H7","v":{"$error":"#N/A"}},{"$f":"'Low Flow DHW Fixtures'!I7","v":"$"}]
[]
["DHW Fixture Summary"]
["Fixture Type",null,null,"Base","Design","Fixture % of Total DHW Use","Fixture Qty (For Incr. Cost)"]
[null,null,null,"gpm","gpm"]
[{"$f":"'Low Flow DHW Fixtures'!K17","v":"Public Restroom Faucet"},null,null,{"$f":"'Low Flow DHW Fixtures'!M17","v":0.5},{"$f":"'Low Flow DHW Fixtures'!N17","v":0},{"$f":"'Low Flow DHW Fixtures'!O17","v":0},{"$f":"'Low Flow DHW Fixtures'!P17","v":0}]
[{"$f":"'Low Flow DHW Fixtures'!K18","v":"Private Restroom Faucet"},null,null,{"$f":"'Low Flow DHW Fixtures'!M18","v":2.2000000000000002},{"$f":"'Low Flow DHW Fixtures'!N18","v":0},{"$f":"'Low Flow DHW Fixtures'!O18","v":0},{"$f":"'Low Flow DHW Fixtures'!P18","v":0}]
[{"$f":"'Low Flow DHW Fixtures'!K19","v":"Kitchen Sink Faucet"},null,null,{"$f":"'Low Flow DHW Fixtures'!M19","v":2.2000000000000002},{"$f":"'Low Flow DHW Fixtures'!N19","v":0},{"$f":"'Low Flow DHW Fixtures'!O19","v":0},{"$f":"'Low Flow DHW Fixtures'!P19","v":0}]
[{"$f":"'Low Flow DHW Fixtures'!K20","v":"Showerhead"},null,null,{"$f":"'Low Flow DHW Fixtures'!M20","v":2.5},{"$f":"'Low Flow DHW Fixtures'!N20","v":0},{"$f":"'Low Flow DHW Fixtures'!O20","v":0},{"$f":"'Low Flow DHW Fixtures'!P20","v":0}]
[{"$f":"'Low Flow DHW Fixtures'!K21","v":"Other Fixtures/Equip. (Not Impacted by Low Flow Fixtures)"},null,null,null,null,{"$f":"'Low Flow DHW Fixtures'!O21","v":1}]
[null,null,null,{"$f":"'Low Flow DHW Fixtures'!M22","v":"Baseline"},{"$f":"'Low Flow DHW Fixtures'!N22","v":"Proposed"}]
[{"$f":"'Low Flow DHW Fixtures'!K23","v":"Avg. gpm from Impacted Load"},null,null,{"$f":"'Low Flow DHW Fixtures'!M23","v":0},{"$f":"'Low Flow DHW Fixtures'!N23","v":0}]
[{"$f":"'Low Flow DHW Fixtures'!K24","v":"Impacted Load % of Total Use"},null,null,{"$f":"'Low Flow DHW Fixtures'!M24","v":0}]
[{"$f":"'Low Flow DHW Fixtures'!K25","v":"% Reduction in Avg. DHW Flow"},null,null,{"$f":"'Low Flow DHW Fixtures'!M25","v":{"$error":"#DIV/0!"}}]
[]
[" Heater Performance",null,null,null,null,{"$f":"'Low Flow DHW Fixtures'!R19","v":"Building Avg. Daily DHW Consumption"}]
[{"$f":"'Low Flow DHW Fixtures'!R15","v":"Water Heater Type"},null,null,{"$f":"'Low Flow DHW Fixtures'!T15","v":0},null,{"$f":"'Low Flow DHW Fixtures'!R20","v":"Building Type"},null,null,{"$f":"'Low Flow DHW Fixtures'!U20","v":0}]
[{"$f":"'Low Flow DHW Fixtures'!R16","v":"Fossil Fuel Design Eff. (%)"},null,null,{"$f":"IF('Low Flow DHW Fixtures'!T15<>\"Fossil Fuel\",\"\",('Low Flow DHW Fixtures'!T16))","v":""},null,{"$f":"'Low Flow DHW Fixtures'!R21","v":"Estimated DHW gallons/day per ft²"},null,null,{"$f":"'Low Flow DHW Fixtures'!U21","v":{"$error":"#N/A"}}]
[{"$f":"'Low Flow DHW Fixtures'!R17","v":"Electric Design COP"},null,null,{"$f":"IF('Low Flow DHW Fixtures'!T15<>\"Fossil Fuel\", ('Low Flow DHW Fixtures'!T17),\"\")","v":0},null,{"$f":"'Low Flow DHW Fixtures'!R22","v":"DHW gallons per day - Calculated"},null,null,{"$f":"IF('Low Flow DHW Fixtures'!U23=\"\",'Low Flow DHW Fixtures'!U22,'Low Flow DHW Fixtures'!U23)","v":{"$error":"#N/A"}}]
["Bldg Envelope"]
["Measure Description\nThis measure considers savings from improved thermal performance of building envelope assemblies beyond the minimum requirements of the energy code.  Assemblies that could be considered in this measure include exterior walls, roofs, windows, and garage doors.\n\nCalculation Methodology\nSavings are estimated with an ambient temperature bin model using TMYx weather data.  The “UA” value of each envelope assembly entered into the tool (Note: not all assemblies need to be included, only those being considered for energy savings) is calculated in the base and design case based on the U-values and the total entered assembly area (which should reflect the actual building design).  For each bin, the envelope heat loss or heat gain is calculated based on the following formula:\n      Heat Loss/Gain, Q = ∑〖U_assembly*Area_assembly〗 * (Tambient – Tinterior)\nThe interior space temperature varies with heating/cooling mode and scheduled building occupancy based on the entered inputs for occupied and unoccupied heating and cooling setpoints.\nThe difference in heat loss or gain is combined with the heating or cooling performance to calculate the difference in heating or cooling demand that results from the improvement in envelope performance.\n"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Savings & Incentive"]
[{"$f":"'Bldg Envelope'!F3","v":"Annual Electric Savings"},null,null,null,{"$f":"'Bldg Envelope'!H3","v":{"$error":"#DIV/0!"}},{"$f":"'Bldg Envelope'!I3","v":"kWh"}]
[{"$f":"'Bldg Envelope'!F4","v":"Annual Fuel Savings"},null,null,null,{"$f":"'Bldg Envelope'!H4","v":{"$error":"#DIV/0!"}},{"$f":"'Bldg Envelope'!I4","v":{"$error":"#N/A"}}]
[{"$f":"'Bldg Envelope'!F5","v":"Incremental"},null,null,null,{"$f":"IF('Bldg Envelope'!H6=\"\",'Bldg Envelope'!H5,'Bldg Envelope'!H6)","v":0},{"$f":"'Bldg Envelope'!I5","v":"$"}]
[{"$f":"'Bldg Envelope'!F7","v":"Estimated Incentive"},null,null,null,{"$f":"'Bldg Envelope'!H7","v":{"$error":"#DIV/0!"}},{"$f":"'Bldg Envelope'!I7","v":"$"}]
[]
["Exterior Opaque Wall Insulation"]
["Assembly Type",null,null,"Area","Infill","c.i.","U-Value","Baseline"]
[null,null,null,"ft²","R-Value","R-Value","Btu/h·ft²·°F","U-Value"]
[{"$f":"'Bldg Envelope'!H21","v":0},null,null,{"$f":"'Bldg Envelope'!K21","v":0},{"$f":"'Bldg Envelope'!L21","v":0},{"$f":"'Bldg Envelope'!M21","v":0},{"$f":"IF('Bldg Envelope'!O21=\"\",'Bldg Envelope'!N21,'Bldg Envelope'!O21)","v":0},{"$f":"IF('Bldg Envelope'!$L$14<>\"Yes\",'Bldg Envelope'!P21,'Bldg Envelope'!U21)","v":0}]
[{"$f":"'Bldg Envelope'!H22","v":0},null,null,{"$f":"'Bldg Envelope'!K22","v":0},{"$f":"'Bldg Envelope'!L22","v":0},{"$f":"'Bldg Envelope'!M22","v":0},{"$f":"IF('Bldg Envelope'!O22=\"\",'Bldg Envelope'!N22,'Bldg Envelope'!O22)","v":0},{"$f":"IF('Bldg Envelope'!$L$14<>\"Yes\",'Bldg Envelope'!P22,'Bldg Envelope'!U22)","v":0}]
[{"$f":"'Bldg Envelope'!H23","v":0},null,null,{"$f":"'Bldg Envelope'!K23","v":0},{"$f":"'Bldg Envelope'!L23","v":0},{"$f":"'Bldg Envelope'!M23","v":0},{"$f":"IF('Bldg Envelope'!O23=\"\",'Bldg Envelope'!N23,'Bldg Envelope'!O23)","v":0},{"$f":"IF('Bldg Envelope'!$L$14<>\"Yes\",'Bldg Envelope'!P23,'Bldg Envelope'!U23)","v":0}]
[{"$f":"'Bldg Envelope'!H24","v":"Overall Performance"},null,null,{"$f":"'Bldg Envelope'!K24","v":0},null,null,{"$f":"'Bldg Envelope'!N24","v":0},{"$f":"IF('Bldg Envelope'!$L$14<>\"Yes\",'Bldg Envelope'!P24,'Bldg Envelope'!U24)","v":0}]
["Exterior Roof Insulation"]
["Assembly Type",null,null,"Area","Infill","c.i.","U-Value","Baseline"]
["Type",null,null,"ft²","R-Value","R-Value","Btu/h·ft²·°F","U-Value"]
[{"$f":"'Bldg Envelope'!H29","v":0},null,null,{"$f":"'Bldg Envelope'!K29","v":0},{"$f":"'Bldg Envelope'!L29","v":0},{"$f":"'Bldg Envelope'!M29","v":0},{"$f":"IF('Bldg Envelope'!O29=\"\",'Bldg Envelope'!N29,'Bldg Envelope'!O29)","v":0},{"$f":"IF('Bldg Envelope'!$L$14<>\"Yes\",'Bldg Envelope'!P29,'Bldg Envelope'!U29)","v":0}]
[{"$f":"'Bldg Envelope'!H30","v":0},null,null,{"$f":"'Bldg Envelope'!K30","v":0},{"$f":"'Bldg Envelope'!L30","v":0},{"$f":"'Bldg Envelope'!M30","v":0},{"$f":"IF('Bldg Envelope'!O30=\"\",'Bldg Envelope'!N30,'Bldg Envelope'!O30)","v":0},{"$f":"IF('Bldg Envelope'!$L$14<>\"Yes\",'Bldg Envelope'!P30,'Bldg Envelope'!U30)","v":0}]
[{"$f":"'Bldg Envelope'!H31","v":0},null,null,{"$f":"'Bldg Envelope'!K31","v":0},{"$f":"'Bldg Envelope'!L31","v":0},{"$f":"'Bldg Envelope'!M31","v":0},{"$f":"IF('Bldg Envelope'!O31=\"\",'Bldg Envelope'!N31,'Bldg Envelope'!O31)","v":0},{"$f":"IF('Bldg Envelope'!$L$14<>\"Yes\",'Bldg Envelope'!P31,'Bldg Envelope'!U31)","v":0}]
[{"$f":"'Bldg Envelope'!H32","v":"Overall Performance"},null,null,{"$f":"'Bldg Envelope'!K32","v":0},null,null,{"$f":"'Bldg Envelope'!N32","v":0},{"$f":"IF('Bldg Envelope'!$L$14<>\"Yes\",'Bldg Envelope'!P32,'Bldg Envelope'!U32)","v":0}]
[]
["Exterior Windows"]
["Assembly Type",null,"Area","% Area","% Area","Glass + Frame",null,"Baseline Glass + Frame"]
[null,null,"ft²","Operable","Fixed","U-Value","SHGC","U-Value","SHGC"]
[{"$f":"'Bldg Envelope'!H37","v":0},null,{"$f":"'Bldg Envelope'!K37","v":0},{"$f":"'Bldg Envelope'!L37","v":0},{"$f":"'Bldg Envelope'!M37","v":0.85},{"$f":"IF('Bldg Envelope'!R37=\"\",'Bldg Envelope'!P37,'Bldg Envelope'!R37)","v":0},{"$f":"IF('Bldg Envelope'!S37=\"\",'Bldg Envelope'!Q37,'Bldg Envelope'!R37)","v":0},{"$f":"IF('Bldg Envelope'!$L$14<>\"Yes\",'Bldg Envelope'!T37,'Bldg Envelope'!V37)","v":0},{"$f":"IF('Bldg Envelope'!$L$14<>\"Yes\",'Bldg Envelope'!U37,'Bldg Envelope'!W37)","v":0}]
[{"$f":"'Bldg Envelope'!H38","v":0},null,{"$f":"'Bldg Envelope'!K38","v":0},{"$f":"'Bldg Envelope'!L38","v":0},{"$f":"'Bldg Envelope'!M38","v":0.85},{"$f":"IF('Bldg Envelope'!R38=\"\",'Bldg Envelope'!P38,'Bldg Envelope'!R38)","v":0},{"$f":"IF('Bldg Envelope'!S38=\"\",'Bldg Envelope'!Q38,'Bldg Envelope'!R38)","v":0},{"$f":"IF('Bldg Envelope'!$L$14<>\"Yes\",'Bldg Envelope'!T38,'Bldg Envelope'!V38)","v":0},{"$f":"IF('Bldg Envelope'!$L$14<>\"Yes\",'Bldg Envelope'!U38,'Bldg Envelope'!W38)","v":0}]
[{"$f":"'Bldg Envelope'!H39","v":0},null,{"$f":"'Bldg Envelope'!K39","v":0},{"$f":"'Bldg Envelope'!L39","v":0},{"$f":"'Bldg Envelope'!M39","v":0.85},{"$f":"IF('Bldg Envelope'!R39=\"\",'Bldg Envelope'!P39,'Bldg Envelope'!R39)","v":0},{"$f":"IF('Bldg Envelope'!S39=\"\",'Bldg Envelope'!Q39,'Bldg Envelope'!R39)","v":0},{"$f":"IF('Bldg Envelope'!$L$14<>\"Yes\",'Bldg Envelope'!T39,'Bldg Envelope'!V39)","v":0},{"$f":"IF('Bldg Envelope'!$L$14<>\"Yes\",'Bldg Envelope'!U39,'Bldg Envelope'!W39)","v":0}]
[{"$f":"'Bldg Envelope'!H40","v":"Overall Performance"},null,{"$f":"'Bldg Envelope'!K40","v":0},{"$f":"'Bldg Envelope'!L40","v":0},{"$f":"'Bldg Envelope'!M40","v":0},{"$f":"'Bldg Envelope'!P40","v":0},{"$f":"'Bldg Envelope'!Q40","v":0},{"$f":"IF('Bldg Envelope'!$L$14<>\"Yes\",'Bldg Envelope'!T40,'Bldg Envelope'!V40)","v":0},{"$f":"IF('Bldg Envelope'!$L$14<>\"Yes\",'Bldg Envelope'!U40,'Bldg Envelope'!W40)","v":0}]
[]
["Garage Doors"]
["Door Area ft²",null,"Overall U-Value",null,"Baseline U-Value"]
[{"$f":"'Bldg Envelope'!G45","v":0},null,{"$f":"'Bldg Envelope'!H45","v":0},null,{"$f":"IF('Bldg Envelope'!$L$14<>\"Yes\",'Bldg Envelope'!I45,'Bldg Envelope'!J45)","v":0}]
[]
[]
["Space Temp Setpoints",null,null,null,"Heat & Cool Performance"]
[null,{"$f":"'Bldg Envelope'!T26","v":"Occ"},{"$f":"'Bldg Envelope'!U26","v":"Unocc"},null,{"$f":"'Bldg Envelope'!S19","v":"Heating Fuel"},null,{"$f":"'Bldg Envelope'!U19","v":0}]
[{"$f":"'Bldg Envelope'!S27","v":"Cooling"},{"$f":"'Bldg Envelope'!T27","v":0},{"$f":"'Bldg Envelope'!U27","v":0},null,{"$f":"'Bldg Envelope'!S20","v":"Fossil Fuel Baseline Eff (%)"},null,{"$f":"IF('Bldg Envelope'!U19=\"Fossil Fuel\", 'Bldg Envelope'!U20,\"\")","v":""}]
[{"$f":"'Bldg Envelope'!S28","v":"Heating"},{"$f":"'Bldg Envelope'!T28","v":0},{"$f":"'Bldg Envelope'!U28","v":0},null,{"$f":"'Bldg Envelope'!S21","v":"Elec Heat Baseline COP"},null,{"$f":"IF('Bldg Envelope'!U19<>\"Fossil Fuel\", 'Bldg Envelope'!U21,\"\")","v":0}]
[null,null,null,null,{"$f":"'Bldg Envelope'!S22","v":"Cooling Included?"},null,{"$f":"'Bldg Envelope'!U22","v":0}]
[null,null,null,null,{"$f":"'Bldg Envelope'!S23","v":"Cooling Baseline IEER or IPLV"},null,{"$f":"IF('Bldg Envelope'!U22=\"Yes\",'Bldg Envelope'!U23,\"\")","v":""}]
[]
[]
["Base vs Design Envelope Performance Summary"]
["Type",null,"Total Area ft² ","Base Average U-Value","Design Average U-Value"]
[null,null,null,"Average","Average"]
[{"$f":"'Bldg Envelope'!W22","v":"Opaque Walls"},null,{"$f":"'Bldg Envelope'!Y22","v":0},{"$f":"'Bldg Envelope'!Z22","v":0},{"$f":"'Bldg Envelope'!AA22","v":0}]
[{"$f":"'Bldg Envelope'!W23","v":"Roofs"},null,{"$f":"'Bldg Envelope'!Y23","v":0},{"$f":"'Bldg Envelope'!Z23","v":0},{"$f":"'Bldg Envelope'!AA23","v":0}]
[{"$f":"'Bldg Envelope'!W24","v":"Windows"},null,{"$f":"'Bldg Envelope'!Y24","v":0},{"$f":"'Bldg Envelope'!Z24","v":0},{"$f":"'Bldg Envelope'!AA24","v":0}]
[{"$f":"'Bldg Envelope'!W25","v":"Garage Doors"},null,{"$f":"'Bldg Envelope'!Y25","v":0},{"$f":"'Bldg Envelope'!Z25","v":0},{"$f":"'Bldg Envelope'!AA25","v":0}]
[{"$f":"'Bldg Envelope'!W26","v":"\"UA\" Value (BTU/h·°F)"},null,null,{"$f":"'Bldg Envelope'!Z26","v":0},{"$f":"'Bldg Envelope'!AA26","v":0}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["User Defined 1"]
[]
["Measure Title"]
[{"$f":"'User Defined 1'!M1","v":0}]
["Measure Description"]
[{"$f":"'User Defined 1'!K4","v":0}]
[]
[]
[]
[]
[]
[]
["Base Case Description"]
[{"$f":"'User Defined 1'!K12","v":0}]
[]
[]
[]
[]
[]
[]
["Proposed Case Description"]
[{"$f":"'User Defined 1'!K21","v":0}]
[]
[]
[]
[]
[]
[]
[]
["Savings & Incentive"]
[{"$f":"'User Defined 1'!F3","v":"Annual Electric Savings"},null,null,null,{"$f":"'User Defined 1'!H3","v":0},{"$f":"'User Defined 1'!I3","v":"kWh"}]
[{"$f":"'User Defined 1'!F4","v":"Annual Fuel Savings"},null,null,null,{"$f":"'User Defined 1'!H4","v":{"$error":"#N/A"}},{"$f":"'User Defined 1'!I4","v":{"$error":"#N/A"}}]
[{"$f":"'User Defined 1'!F5","v":"Incremental Cost"},null,null,null,{"$f":"'User Defined 1'!H5","v":0},{"$f":"'User Defined 1'!I5","v":"$"}]
[{"$f":"'User Defined 1'!F6","v":"Estimated Custom Incentive"},null,null,null,{"$f":"'User Defined 1'!H6","v":{"$error":"#N/A"}},{"$f":"'User Defined 1'!I6","v":"$"}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["User Defined 2"]
[]
["Measure Title"]
[{"$f":"'User Defined 2'!M1","v":0}]
["Measure Description"]
[{"$f":"'User Defined 2'!K4","v":0}]
[]
[]
[]
[]
[]
[]
["Base Case Description"]
[{"$f":"'User Defined 2'!K12","v":0}]
[]
[]
[]
[]
[]
[]
["Proposed Case Description"]
[{"$f":"'User Defined 2'!K21","v":0}]
[]
[]
[]
[]
[]
[]
[]
["Savings & Incentive"]
[{"$f":"'User Defined 2'!F3","v":"Annual Electric Savings"},null,null,null,{"$f":"'User Defined 2'!H3","v":0},{"$f":"'User Defined 2'!I3","v":"kWh"}]
[{"$f":"'User Defined 2'!F4","v":"Annual Fuel Savings"},null,null,null,{"$f":"'User Defined 2'!H4","v":{"$error":"#N/A"}},{"$f":"'User Defined 2'!I4","v":{"$error":"#N/A"}}]
[{"$f":"'User Defined 2'!F5","v":"Incremental Cost"},null,null,null,{"$f":"'User Defined 2'!H5","v":0},{"$f":"'User Defined 2'!I5","v":"$"}]
[{"$f":"'User Defined 2'!F6","v":"Estimated Custom Incentive"},null,null,null,{"$f":"'User Defined 2'!H6","v":{"$error":"#N/A"}},{"$f":"'User Defined 2'!I6","v":"$"}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["User Defined 3"]
[]
["Measure Title"]
[{"$f":"'User Defined 3'!M1","v":0}]
["Measure Description"]
[{"$f":"'User Defined 3'!K4","v":0}]
[]
[]
[]
[]
[]
[]
["Base Case Description"]
[{"$f":"'User Defined 3'!K12","v":0}]
[]
[]
[]
[]
[]
[]
["Proposed Case Description"]
[{"$f":"'User Defined 3'!K21","v":0}]
[]
[]
[]
[]
[]
[]
[]
["Savings & Incentive"]
[{"$f":"'User Defined 3'!F3","v":"Annual Electric Savings"},null,null,null,{"$f":"'User Defined 3'!H3","v":0},{"$f":"'User Defined 3'!I3","v":"kWh"}]
[{"$f":"'User Defined 3'!F4","v":"Annual Fuel Savings"},null,null,null,{"$f":"'User Defined 3'!H4","v":{"$error":"#N/A"}},{"$f":"'User Defined 3'!I4","v":{"$error":"#N/A"}}]
[{"$f":"'User Defined 3'!F5","v":"Incremental Cost"},null,null,null,{"$f":"'User Defined 3'!H5","v":0},{"$f":"'User Defined 3'!I5","v":"$"}]
[{"$f":"'User Defined 3'!F6","v":"Estimated Custom Incentive"},null,null,null,{"$f":"'User Defined 3'!IH6","v":0},{"$f":"'User Defined 3'!I6","v":"$"}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["User Defined 4"]
[]
["Measure Title"]
[{"$f":"'User Defined 4'!M1","v":0}]
["Measure Description"]
[{"$f":"'User Defined 4'!K4","v":0}]
[]
[]
[]
[]
[]
[]
["Base Case Description"]
[{"$f":"'User Defined 4'!K12","v":0}]
[]
[]
[]
[]
[]
[]
["Proposed Case Description"]
[{"$f":"'User Defined 4'!K21","v":0}]
[]
[]
[]
[]
[]
[]
[]
["Savings & Incentive"]
[{"$f":"'User Defined 4'!F3","v":"Annual Electric Savings"},null,null,null,{"$f":"'User Defined 4'!H3","v":0},{"$f":"'User Defined 4'!I3","v":"kWh"}]
[{"$f":"'User Defined 4'!F4","v":"Annual Fuel Savings"},null,null,null,{"$f":"'User Defined 4'!H4","v":{"$error":"#N/A"}},{"$f":"'User Defined 4'!I4","v":{"$error":"#N/A"}}]
[{"$f":"'User Defined 4'!F5","v":"Incremental Cost"},null,null,null,{"$f":"'User Defined 4'!H5","v":0},{"$f":"'User Defined 4'!I5","v":"$"}]
[{"$f":"'User Defined 4'!F6","v":"Estimated Custom Incentive"},null,null,null,{"$f":"'User Defined 4'!H6","v":{"$error":"#N/A"}},{"$f":"'User Defined 4'!I6","v":"$"}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"PA Impacts"]
[]
[null,null,"Measure Label",null,{"$f":"_xlfn.IFNA('PA Impacts'!E11,\"\")","v":""},{"$f":"_xlfn.IFNA('PA Impacts'!F11,\"\")","v":""},{"$f":"_xlfn.IFNA('PA Impacts'!G11,\"\")","v":""},{"$f":"_xlfn.IFNA('PA Impacts'!H11,\"\")","v":""},{"$f":"_xlfn.IFNA('PA Impacts'!I11,\"\")","v":""}]
["Measure Information",null,"Include in project",null,{"$f":"IF(E1405<>\"\",'PA Impacts'!E12,\"\")","v":""},{"$f":"IF(F1405<>\"\",'PA Impacts'!F12,\"\")","v":""},{"$f":"IF(G1405<>\"\",'PA Impacts'!G12,\"\")","v":""},{"$f":"IF(H1405<>\"\",'PA Impacts'!H12,\"\")","v":""},{"$f":"IF(I1405<>\"\",'PA Impacts'!I12,\"\")","v":""}]
[null,null,"Initiative",null,{"$f":"IF(E1406<>\"\",'PA Impacts'!E13,\"\")","v":""},{"$f":"IF(F1406<>\"\",'PA Impacts'!F13,\"\")","v":""},{"$f":"IF(G1406<>\"\",'PA Impacts'!G13,\"\")","v":""},{"$f":"IF(H1406<>\"\",'PA Impacts'!H13,\"\")","v":""},{"$f":"IF(I1406<>\"\",'PA Impacts'!I13,\"\")","v":""}]
[null,null,"Fuel  Savings Type",null,{"$f":"IF(E1407<>\"\",'PA Impacts'!E14,\"\")","v":""},{"$f":"IF(F1407<>\"\",'PA Impacts'!F14,\"\")","v":""},{"$f":"IF(G1407<>\"\",'PA Impacts'!G14,\"\")","v":""},{"$f":"IF(H1407<>\"\",'PA Impacts'!H14,\"\")","v":""},{"$f":"IF(I1407<>\"\",'PA Impacts'!I14,\"\")","v":""}]
[null,null,"Measure",null,{"$f":"IF(E1408<>\"\",'PA Impacts'!E15,\"\")","v":""},{"$f":"IF(F1408<>\"\",'PA Impacts'!F15,\"\")","v":""},{"$f":"IF(G1408<>\"\",'PA Impacts'!G15,\"\")","v":""},{"$f":"IF(H1408<>\"\",'PA Impacts'!H15,\"\")","v":""},{"$f":"IF(I1408<>\"\",'PA Impacts'!I15,\"\")","v":""}]
[null,null,"Estimated Useful Life (Years)",null,{"$f":"IF(E1409<>\"\",'PA Impacts'!E16,\"\")","v":""},{"$f":"IF(F1409<>\"\",'PA Impacts'!F16,\"\")","v":""},{"$f":"IF(G1409<>\"\",'PA Impacts'!G16,\"\")","v":""},{"$f":"IF(H1409<>\"\",'PA Impacts'!H16,\"\")","v":""},{"$f":"IF(I1409<>\"\",'PA Impacts'!I16,\"\")","v":""}]
[null,null,"Override Life (Optional)",null,{"$f":"IF(E1410<>\"\",'PA Impacts'!E17,\"\")","v":""},{"$f":"IF(F1410<>\"\",'PA Impacts'!F17,\"\")","v":""},{"$f":"IF(G1410<>\"\",'PA Impacts'!G17,\"\")","v":""},{"$f":"IF(H1410<>\"\",'PA Impacts'!H17,\"\")","v":""},{"$f":"IF(I1410<>\"\",'PA Impacts'!I17,\"\")","v":""}]
["Measure Costs",null,"Proposed Cost ($)",null,{"$f":"IF(E1411<>\"\",'PA Impacts'!E18,\"\")","v":""},{"$f":"IF(F1411<>\"\",'PA Impacts'!F18,\"\")","v":""},{"$f":"IF(G1411<>\"\",'PA Impacts'!G18,\"\")","v":""},{"$f":"IF(H1411<>\"\",'PA Impacts'!H18,\"\")","v":""},{"$f":"IF(I1411<>\"\",'PA Impacts'!I18,\"\")","v":""}]
[null,null,"Baseline Cost ($)",null,{"$f":"IF(E1412<>\"\",'PA Impacts'!E19,\"\")","v":""},{"$f":"IF(F1412<>\"\",'PA Impacts'!F19,\"\")","v":""},{"$f":"IF(G1412<>\"\",'PA Impacts'!G19,\"\")","v":""},{"$f":"IF(H1412<>\"\",'PA Impacts'!H19,\"\")","v":""},{"$f":"IF(I1412<>\"\",'PA Impacts'!I19,\"\")","v":""}]
["Gross Electric Energy",null,"Energy (kWh)",null,{"$f":"IF(E1413<>\"\",'PA Impacts'!E20,\"\")","v":""},{"$f":"IF(F1413<>\"\",'PA Impacts'!F20,\"\")","v":""},{"$f":"IF(G1413<>\"\",'PA Impacts'!G20,\"\")","v":""},{"$f":"IF(H1413<>\"\",'PA Impacts'!H20,\"\")","v":""},{"$f":"IF(I1413<>\"\",'PA Impacts'!I20,\"\")","v":""}]
["(Savings and Penalties)",null,"% Summer On Peak",null,{"$f":"IF(E1414<>\"\",'PA Impacts'!E21,\"\")","v":""},{"$f":"IF(F1414<>\"\",'PA Impacts'!F21,\"\")","v":""},{"$f":"IF(G1414<>\"\",'PA Impacts'!G21,\"\")","v":""},{"$f":"IF(H1414<>\"\",'PA Impacts'!H21,\"\")","v":""},{"$f":"IF(I1414<>\"\",'PA Impacts'!I21,\"\")","v":""}]
[null,null,"% Summer Off Peak",null,{"$f":"IF(E1415<>\"\",'PA Impacts'!E22,\"\")","v":""},{"$f":"IF(F1415<>\"\",'PA Impacts'!F22,\"\")","v":""},{"$f":"IF(G1415<>\"\",'PA Impacts'!G22,\"\")","v":""},{"$f":"IF(H1415<>\"\",'PA Impacts'!H22,\"\")","v":""},{"$f":"IF(I1415<>\"\",'PA Impacts'!I22,\"\")","v":""}]
[null,null,"% Winter On Peak",null,{"$f":"IF(E1416<>\"\",'PA Impacts'!E23,\"\")","v":""},{"$f":"IF(F1416<>\"\",'PA Impacts'!F23,\"\")","v":""},{"$f":"IF(G1416<>\"\",'PA Impacts'!G23,\"\")","v":""},{"$f":"IF(H1416<>\"\",'PA Impacts'!H23,\"\")","v":""},{"$f":"IF(I1416<>\"\",'PA Impacts'!I23,\"\")","v":""}]
[null,null,"% Winter Off Peak",null,{"$f":"IF(E1417<>\"\",'PA Impacts'!E24,\"\")","v":""},{"$f":"IF(F1417<>\"\",'PA Impacts'!F24,\"\")","v":""},{"$f":"IF(G1417<>\"\",'PA Impacts'!G24,\"\")","v":""},{"$f":"IF(H1417<>\"\",'PA Impacts'!H24,\"\")","v":""},{"$f":"IF(I1417<>\"\",'PA Impacts'!I24,\"\")","v":""}]
["Gross Electric Capacity (Savings and Penalties)",null,"Summer Peak kW",null,{"$f":"IF(E1418<>\"\",'PA Impacts'!E25,\"\")","v":""},{"$f":"IF(F1418<>\"\",'PA Impacts'!F25,\"\")","v":""},{"$f":"IF(G1418<>\"\",'PA Impacts'!G25,\"\")","v":""},{"$f":"IF(H1418<>\"\",'PA Impacts'!H25,\"\")","v":""},{"$f":"IF(I1418<>\"\",'PA Impacts'!I25,\"\")","v":""}]
[null,null,"Winter Peak kW",null,{"$f":"IF(E1419<>\"\",'PA Impacts'!E26,\"\")","v":""},{"$f":"IF(F1419<>\"\",'PA Impacts'!F26,\"\")","v":""},{"$f":"IF(G1419<>\"\",'PA Impacts'!G26,\"\")","v":""},{"$f":"IF(H1419<>\"\",'PA Impacts'!H26,\"\")","v":""},{"$f":"IF(I1419<>\"\",'PA Impacts'!I26,\"\")","v":""}]
["Gross Natural Gas",null,"Heating Season (Therms)",null,{"$f":"IF(E1420<>\"\",'PA Impacts'!E27,\"\")","v":""},{"$f":"IF(F1420<>\"\",'PA Impacts'!F27,\"\")","v":""},{"$f":"IF(G1420<>\"\",'PA Impacts'!G27,\"\")","v":""},{"$f":"IF(H1420<>\"\",'PA Impacts'!H27,\"\")","v":""},{"$f":"IF(I1420<>\"\",'PA Impacts'!I27,\"\")","v":""}]
[null,null,"Year Round (Therms)",null,{"$f":"IF(E1421<>\"\",'PA Impacts'!E28,\"\")","v":""},{"$f":"IF(F1421<>\"\",'PA Impacts'!F28,\"\")","v":""},{"$f":"IF(G1421<>\"\",'PA Impacts'!G28,\"\")","v":""},{"$f":"IF(H1421<>\"\",'PA Impacts'!H28,\"\")","v":""},{"$f":"IF(I1421<>\"\",'PA Impacts'!I28,\"\")","v":""}]
[null,null,"Other (Therms)",null,{"$f":"IF(E1422<>\"\",'PA Impacts'!E29,\"\")","v":""},{"$f":"IF(F1422<>\"\",'PA Impacts'!F29,\"\")","v":""},{"$f":"IF(G1422<>\"\",'PA Impacts'!G29,\"\")","v":""},{"$f":"IF(H1422<>\"\",'PA Impacts'!H29,\"\")","v":""},{"$f":"IF(I1422<>\"\",'PA Impacts'!I29,\"\")","v":""}]
["Gross Non-Electric Non-Gas",null,"#2 Oil (MMbtu)",null,{"$f":"IF(E1423<>\"\",'PA Impacts'!E30,\"\")","v":""},{"$f":"IF(F1423<>\"\",'PA Impacts'!F30,\"\")","v":""},{"$f":"IF(G1423<>\"\",'PA Impacts'!G30,\"\")","v":""},{"$f":"IF(H1423<>\"\",'PA Impacts'!H30,\"\")","v":""},{"$f":"IF(I1423<>\"\",'PA Impacts'!I30,\"\")","v":""}]
[null,null,"Propane (MMbtu)",null,{"$f":"IF(E1424<>\"\",'PA Impacts'!E31,\"\")","v":""},{"$f":"IF(F1424<>\"\",'PA Impacts'!F31,\"\")","v":""},{"$f":"IF(G1424<>\"\",'PA Impacts'!G31,\"\")","v":""},{"$f":"IF(H1424<>\"\",'PA Impacts'!H31,\"\")","v":""},{"$f":"IF(I1424<>\"\",'PA Impacts'!I31,\"\")","v":""}]
[null,null,"Water (Gallons)",null,{"$f":"IF(E1425<>\"\",'PA Impacts'!E32,\"\")","v":""},{"$f":"IF(F1425<>\"\",'PA Impacts'!F32,\"\")","v":""},{"$f":"IF(G1425<>\"\",'PA Impacts'!G32,\"\")","v":""},{"$f":"IF(H1425<>\"\",'PA Impacts'!H32,\"\")","v":""},{"$f":"IF(I1425<>\"\",'PA Impacts'!I32,\"\")","v":""}]
[null,null,"Sewer (Gallons)",null,{"$f":"IF(E1426<>\"\",'PA Impacts'!E33,\"\")","v":""},{"$f":"IF(F1426<>\"\",'PA Impacts'!F33,\"\")","v":""},{"$f":"IF(G1426<>\"\",'PA Impacts'!G33,\"\")","v":""},{"$f":"IF(H1426<>\"\",'PA Impacts'!H33,\"\")","v":""},{"$f":"IF(I1426<>\"\",'PA Impacts'!I33,\"\")","v":""}]
[null,null,"Annual $",null,{"$f":"IF(E1427<>\"\",'PA Impacts'!E34,\"\")","v":""},{"$f":"IF(F1427<>\"\",'PA Impacts'!F34,\"\")","v":""},{"$f":"IF(G1427<>\"\",'PA Impacts'!G34,\"\")","v":""},{"$f":"IF(H1427<>\"\",'PA Impacts'!H34,\"\")","v":""},{"$f":"IF(I1427<>\"\",'PA Impacts'!I34,\"\")","v":""}]
[null,null,"One Time $",null,{"$f":"IF(E1428<>\"\",'PA Impacts'!E35,\"\")","v":""},{"$f":"IF(F1428<>\"\",'PA Impacts'!F35,\"\")","v":""},{"$f":"IF(G1428<>\"\",'PA Impacts'!G35,\"\")","v":""},{"$f":"IF(H1428<>\"\",'PA Impacts'!H35,\"\")","v":""},{"$f":"IF(I1428<>\"\",'PA Impacts'!I35,\"\")","v":""}]
[]
[]
["Facility Description"]
[{"$f":"'Project Info'!Q2","v":0}]

{"sheet":"Sheet5","index":30,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":true,"merged":[]}

{"sheet":"Sheet4","index":31,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":true,"merged":[]}

{"sheet":"DX and HP Systems","index":32,"n_rows":83,"n_cols":51,"rows_kept":83,"cut":false,"hidden":true,"merged":[]}
["Savings Summary",null,null,null,null,"Electric Cooling & Heating Systems",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Cooling Load Profiles",null,null,null,null,null,null,null,null,null,null,null,null,"Incremental Cost Estimate"]
["Annual kWh Savings",null,null,{"$f":"SUM(A14:D14)","v":91779.858067418274},null,"Load","Load",null,"Total","Avg. Cooling Performance",null,null,null,"Total","Avg. Heating Performance",null,null,null,null,null,null,"Load","Load",null,"Occupied Profile",null,null,null,"Unocc Profile",null,null,null,null,null,null,null,null,null,null,"Total","Cost Rate","Total"]
["% On Peak",null,null,{"$f":"IF(D2<=0,0,MIN(1,A15+C15))","v":0.45844748858447482},null,"Profile","Profile",null,"Cool","Design",null,"Base",null,"Heat","Design",null,"Base",null,null,null,null,"Profile","Profile",null,"Max OAT","Min OAT","% Load @","%Load @","Max OAT","Min OAT","% Load @","%Load @",null,null,null,null,null,null,"Unit","Units","w/ O&P","Cost"]
["Max kW",null,null,{"$f":"MAX(AY30:AY53,AY60:AY83)","v":14.581263333502919},null,"#","Type",null,"MBH","EER","SEER/IEER","EER","SEER/IEER","MBH","COP",null,"COP",null,null,null,null,"#","Type",null,"°F","°F","Max OAT","Min OAT","°F","°F","Max OAT","Min OAT",null,null,"Baseline"]
["Summer kW",null,null,{"$f":"(SUMPRODUCT(AY30:AY53,L30:L53)+SUMPRODUCT(AY60:AY83,L60:L83))/SUM(L30:L53,L60:L83)","v":10.477152747422176},null,1,"Common OA Temp",null,342,12.629983317943985,15.650877192982454,11.180000000000003,13,148.422,1.0000000000000002,0,1.0000000000000002,0,null,null,null,1,{"$f":"G5","v":"Common OA Temp"},null,95,55,0.85,0,95,75,0.5,0,null,null,"R-13 infill insulation (3.5 inch batt)",null,null,null,"ft²",{"$f":"$D$19","v":0},1.02,{"$f":"AO5*AN5","v":0}]
["Winter kW",null,null,{"$f":"(SUMPRODUCT(AY30:AY53,K30:K53)+SUMPRODUCT(AY60:AY83,K60:K83))/SUM(K30:K53,K60:K83)","v":10.477152747422176},null,2,"Constant Yr-Round",null,54,11.815800000000001,14.099999999999998,11.180000000000003,13,0,1,0,1,0,null,null,null,2,{"$f":"G6","v":"Constant Yr-Round"},null,95,0,0.6,0.6,95,0,0.6,0.6,null,null,"R-7.5 ci insulation (1.5\" polystyrene)",null,null,null,"ft²",{"$f":"$D$19","v":0},1.82,{"$f":"AO6*AN6","v":0}]
["Annual therms Savings",null,null,{"$f":"(SUMPRODUCT($F$30:$F$53,BC30:BC53)+SUMPRODUCT($F$60:$F$83,AZ60:AZ83))/100","v":0},null,3,"Guest Rm OA Temp",null,710,13,13,11.870000000000001,11.870000000000001,620,4,0,3.0388000000000002,0,null,null,null,3,{"$f":"G7","v":"Guest Rm OA Temp"},null,95,55,0.9,0,95,65,0.9,0,null,null,"Total Base Cost",null,null,null,null,null,null,{"$f":"SUM(AP5:AP6)","v":0}]
["Incremental Cost",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Design"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Heating Load Profiles",null,null,null,null,null,null,null,null,null,null,null,null,"R-13 infill insulation (3.5 inch batt)",null,null,null,"ft²",{"$f":"$D$19","v":0},1.02,{"$f":"AO9*AN9","v":0}]
["kWh Savings by Peak Period",null,null,null,null,null,null,null,"DESIGN CASE",null,null,null,null,null,"BASE CASE",null,null,null,null,null,null,"Load","Load",null,"Occupied Profile",null,null,null,"Unocc Profile",null,null,null,null,null,"R-12 ci insulation (2.4\" polystyrene)",null,null,null,"ft²",{"$f":"$D$19","v":0},2.33,{"$f":"AO10*AN10","v":0}]
["Winter","Winter","Summer","Summer",null,"Load","Load",null,"Part Load Cooling Performance Assumptions",null,null,null,null,null,"Part Load Cooling Performance Assumptions",null,null,null,null,null,null,"Profile","Profile",null,"Max OAT","Min OAT","% Load @","%Load @","Max OAT","Min OAT","% Load @","%Load @",null,null,"Total Design Cost",null,null,null,null,null,null,{"$f":"SUM(AP9:AP10)","v":0}]
["On-Peak","Off-Peak","On-Peak","Off-Peak",null,"Profile","Profile",null,0.01,0.42,0.45,0.12,null,"SEER/",0.01,0.42,0.45,0.12,null,"SEER/",null,"#","Type",null,"°F","°F","Max OAT","Min OAT","°F","°F","Max OAT","Min OAT",null,null,null,null,null,null,null,null,"Estimated Incremental Cost",{"$f":"AP11-AP7","v":0}]
["kWh","kWh","kWh","kWh",null,"#","Type",null,1,0.75,0.5,0.25,-0.01,"IEER",1,0.75,0.5,0.25,-0.01,"IEER",null,1,{"$f":"G5","v":"Common OA Temp"},null,55,0,0,0.85,60,0,0,0.65]
[{"$f":"SUMPRODUCT($AY$30:$AY$53,G30:G53)+SUMPRODUCT($AY$60:$AY$83,G60:G83)","v":27994.952141112055},{"$f":"SUMPRODUCT($AY$30:$AY$53,H30:H53)+SUMPRODUCT($AY$60:$AY$83,H60:H83)","v":33107.802681854075},{"$f":"SUMPRODUCT($AY$30:$AY$53,I30:I53)+SUMPRODUCT($AY$60:$AY$83,I60:I83)","v":14081.293292535405},{"$f":"SUMPRODUCT($AY$30:$AY$53,J30:J53)+SUMPRODUCT($AY$60:$AY$83,J60:J83)","v":16595.809951916726},null,1,{"$f":"G5","v":"Common OA Temp"},null,{"$f":"J5","v":12.629983317943985},14.5,17,15,{"$f":"0.5*I14","v":6.3149916589719925},{"$f":"SUMPRODUCT($I$12:$L$12,I14:L14)","v":15.666299833179441},{"$f":"L5","v":11.180000000000003},12.5,13.6,12.3,{"$f":"0.5*O14","v":5.5900000000000016},{"$f":"SUMPRODUCT($I$12:$L$12,O14:R14)","v":12.957799999999999},null,2,{"$f":"G6","v":"Constant Yr-Round"},null,95,0,0,0,95,0,0,0]
[{"$f":"IF(A14<=0,0,A14/SUMIF($A$14:$D$14,\">0\"))","v":0.30502283105022826},{"$f":"IF(B14<=0,0,B14/SUMIF($A$14:$D$14,\">0\"))","v":0.36073059360730586},{"$f":"IF(C14<=0,0,C14/SUMIF($A$14:$D$14,\">0\"))","v":0.15342465753424656},{"$f":"IF(D14<=0,0,D14/SUMIF($A$14:$D$14,\">0\"))","v":0.18082191780821916},null,2,{"$f":"G6","v":"Constant Yr-Round"},null,{"$f":"J6","v":11.815800000000001},13.5,15,13,{"$f":"0.5*I15","v":5.9079000000000006},{"$f":"SUMPRODUCT($I$12:$L$12,I15:L15)","v":14.098158},{"$f":"L6","v":11.180000000000003},12.5,13.6,12.3,{"$f":"0.5*O15","v":5.5900000000000016},{"$f":"SUMPRODUCT($I$12:$L$12,O15:R15)","v":12.957799999999999},null,3,{"$f":"G7","v":"Guest Rm OA Temp"},null,55,0,0,0.9,55,0,0,0.75]
[null,null,null,null,null,3,{"$f":"G7","v":"Guest Rm OA Temp"},null,{"$f":"J7","v":13},{"$f":"I16","v":13},{"$f":"J16","v":13},{"$f":"K16","v":13},{"$f":"L16","v":13},{"$f":"SUMPRODUCT($I$12:$L$12,I16:L16)","v":13.000000000000002},{"$f":"L7","v":11.870000000000001},{"$f":"O16","v":11.870000000000001},{"$f":"P16","v":11.870000000000001},{"$f":"Q16","v":11.870000000000001},{"$f":"R16","v":11.870000000000001},{"$f":"SUMPRODUCT($I$12:$L$12,O16:R16)","v":11.870000000000001},null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Boiler Efficiency"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"OAT","HWST","HWRT","Eff"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,60,110,{"$f":"+AJ18-20","v":90},0.95,"(20°f dT)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,20,130,{"$f":"+AJ19-20","v":110},0.92,"(20°f dT)"]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,"Load Profile",null,null,null,null,null,null,null,null,null,null,null,"Load Profile",null,null,null,null,null,null,null,null,null,null,null,"Load Profile"]
["Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown",null,null,null,null,null,null,1,{"$f":"LOOKUP(M26,$F$5:$F$7,$G$5:$G$7)","v":"Common OA Temp"},null,null,null,null,null,null,null,null,null,null,2,{"$f":"LOOKUP(Y26,$F$5:$F$7,$G$5:$G$7)","v":"Constant Yr-Round"},null,null,null,null,null,null,null,null,null,null,3,{"$f":"LOOKUP(AK26,$F$5:$F$7,$G$5:$G$7)","v":"Guest Rm OA Temp"},null,null,null,null,null,null,null,null,null,null,"End Use",null,"Total"]
["OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Cooling","Cooling","Heating","Heating","Cooling Perf.",null,"Cooling Demand",null,"Heating Perf.",null,"Heating Demand",null,"Cooling","Cooling","Heating","Heating","Cooling Perf.",null,"Cooling Demand",null,"Heating Perf.",null,"Heating Demand",null,"Cooling","Cooling","Heating","Heating","Cooling Perf.",null,"Cooling Demand",null,"Heating Perf.",null,"Heating Demand",null,"Demand Reduction",null,"Demand"]
["Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","%","Load","%","Load","Base","Design","Base","Design","Base","Design","Base","Design","%","Load","%","Load","Base","Design","Base","Design","Base","Design","Base","Design","%","Load","%","Load","Base","Design","Base","Design","Base","Design","Base","Design","Cooling","Heating","Reduction"]
["From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","Load","MBH","Load","MBH","EER","EER","kW","kW","COP","COP","kW","kW","Load","MBH","Load","MBH","EER","EER","kW","kW","COP","COP","kW","kW","Load","MBH","Load","MBH","EER","EER","kW","kW","COP","COP","kW","kW","kW","kW","kW"]
[{"$f":"'Project Info'!A44","v":100},{"$f":"'Project Info'!B44","v":105},{"$f":"'Project Info'!C44","v":102},{"$f":"'Project Info'!D44","v":76},{"$f":"'Project Info'!E44","v":40},{"$f":"'Project Info'!F44","v":0},{"$f":"'Project Info'!G44","v":0},{"$f":"'Project Info'!H44","v":0},{"$f":"'Project Info'!I44","v":0},{"$f":"'Project Info'!J44","v":0},{"$f":"'Project Info'!K44","v":0},{"$f":"'Project Info'!L44","v":0},{"$f":"MAX(0,MIN(1,TREND(OFFSET($V$4,MATCH(M$26,$V$5:$V$7,0),5,1,2),OFFSET($V$4,MATCH(M$26,$V$5:$V$7,0),3,1,2),$C30)))","v":0.99875000000000025},{"$f":"M30*LOOKUP(M$26,$F$5:$F$7,$I$5:$I$7)","v":341.5725000000001},{"$f":"MAX(0,MIN(1,TREND(OFFSET($V$12,MATCH(M$26,$V$13:$V$15,0),5,1,2),OFFSET($V$12,MATCH(M$26,$V$13:$V$15,0),3,1,2),$C30)))","v":0},{"$f":"O30*LOOKUP(M$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(M$26,$F$14:$F$16,0),MATCH(M30,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(M30,$O$13:$S$13,-1),1,2),M30)","v":11.186600000000002},{"$f":"TREND(OFFSET($H$13,MATCH(M$26,$F$14:$F$16,0),MATCH(M30,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(M30,$I$13:$M$13,-1),1,2),M30)","v":12.639333401354264},{"$f":"N30/Q30","v":30.534076484365226},{"$f":"N30/R30","v":27.024566023664008},{"$f":"LOOKUP(M$26,$F$5:$F$7,$Q$5:$Q$7)","v":1.0000000000000002},{"$f":"LOOKUP(M$26,$F$5:$F$7,$O$5:$O$7)","v":1.0000000000000002},{"$f":"P30/U30/3.412","v":0},{"$f":"P30/V30/3.412","v":0},{"$f":"MAX(0,MIN(1,TREND(OFFSET($V$4,MATCH(Y$26,$V$5:$V$7,0),5,1,2),OFFSET($V$4,MATCH(Y$26,$V$5:$V$7,0),3,1,2),$C30)))","v":0.6},{"$f":"Y30*LOOKUP(Y$26,$F$5:$F$7,$I$5:$I$7)","v":32.4},{"$f":"MAX(0,MIN(1,TREND(OFFSET($V$12,MATCH(Y$26,$V$13:$V$15,0),5,1,2),OFFSET($V$12,MATCH(Y$26,$V$13:$V$15,0),3,1,2),$C30)))","v":0},{"$f":"AA30*LOOKUP(Y$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(Y$26,$F$14:$F$16,0),MATCH(Y30,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(Y30,$O$13:$S$13,-1),1,2),Y30)","v":13.16},{"$f":"TREND(OFFSET($H$13,MATCH(Y$26,$F$14:$F$16,0),MATCH(Y30,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(Y30,$I$13:$M$13,-1),1,2),Y30)","v":14.4},{"$f":"Z30/AC30","v":2.4620060790273555},{"$f":"Z30/AD30","v":2.25},{"$f":"LOOKUP(Y$26,$F$5:$F$7,$Q$5:$Q$7)","v":1},{"$f":"LOOKUP(Y$26,$F$5:$F$7,$O$5:$O$7)","v":1},{"$f":"AB30/AG30/3.412","v":0},{"$f":"AB30/AH30/3.412","v":0},{"$f":"MAX(0,MIN(1,TREND(OFFSET($V$4,MATCH(AK$26,$V$5:$V$7,0),5,1,2),OFFSET($V$4,MATCH(AK$26,$V$5:$V$7,0),3,1,2),$C30)))","v":1},{"$f":"AK30*LOOKUP(AK$26,$F$5:$F$7,$I$5:$I$7)","v":710},{"$f":"MAX(0,MIN(1,TREND(OFFSET($V$12,MATCH(AK$26,$V$13:$V$15,0),5,1,2),OFFSET($V$12,MATCH(AK$26,$V$13:$V$15,0),3,1,2),$C30)))","v":0},{"$f":"AM30*LOOKUP(AK$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(AK$26,$F$14:$F$16,0),MATCH(AK30,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(AK30,$O$13:$S$13,-1),1,2),AK30)","v":11.870000000000001},{"$f":"TREND(OFFSET($H$13,MATCH(AK$26,$F$14:$F$16,0),MATCH(AK30,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(AK30,$I$13:$M$13,-1),1,2),AK30)","v":13},{"$f":"AL30/AO30","v":59.81465880370682},{"$f":"AL30/AP30","v":54.615384615384613},{"$f":"LOOKUP(AK$26,$F$5:$F$7,$Q$5:$Q$7)","v":3.0388000000000002},{"$f":"LOOKUP(AK$26,$F$5:$F$7,$O$5:$O$7)","v":4},{"$f":"AN30/AS30/3.412","v":0},{"$f":"AN30/AT30/3.412","v":0},{"$f":"(S30-T30)+(AE30-AF30)+(AQ30-AR30)","v":8.9207907280507808},{"$f":"(W30-X30)+(AI30-AJ30)+(AU30-AV30)","v":0},{"$f":"AW30+AX30","v":8.9207907280507808}]
[{"$f":"'Project Info'!A45","v":95},{"$f":"'Project Info'!B45","v":100},{"$f":"'Project Info'!C45","v":95.219272727272724},{"$f":"'Project Info'!D45","v":74.534025272781079},{"$f":"'Project Info'!E45","v":37.923296058061368},{"$f":"'Project Info'!F45","v":0},{"$f":"'Project Info'!G45","v":0},{"$f":"'Project Info'!H45","v":0},{"$f":"'Project Info'!I45","v":0},{"$f":"'Project Info'!J45","v":0},{"$f":"'Project Info'!K45","v":0},{"$f":"'Project Info'!L45","v":0},{"$f":"MAX(0,MIN(1,TREND(OFFSET($V$4,MATCH(M$26,$V$5:$V$7,0),5,1,2),OFFSET($V$4,MATCH(M$26,$V$5:$V$7,0),3,1,2),$C31)))","v":0.85465954545454537},{"$f":"M31*LOOKUP(M$26,$F$5:$F$7,$I$5:$I$7)","v":292.2935645454545},{"$f":"MAX(0,MIN(1,TREND(OFFSET($V$12,MATCH(M$26,$V$13:$V$15,0),5,1,2),OFFSET($V$12,MATCH(M$26,$V$13:$V$15,0),3,1,2),$C31)))","v":0},{"$f":"O31*LOOKUP(M$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(M$26,$F$14:$F$16,0),MATCH(M31,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(M31,$O$13:$S$13,-1),1,2),M31)","v":11.947397600000002},{"$f":"TREND(OFFSET($H$13,MATCH(M$26,$F$14:$F$16,0),MATCH(M31,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(M31,$I$13:$M$13,-1),1,2),M31)","v":13.717139616254402},{"$f":"N31/Q31","v":24.465040365397602},{"$f":"N31/R31","v":21.308638150704198},{"$f":"LOOKUP(M$26,$F$5:$F$7,$Q$5:$Q$7)","v":1.0000000000000002},{"$f":"LOOKUP(M$26,$F$5:$F$7,$O$5:$O$7)","v":1.0000000000000002},{"$f":"P31/U31/3.412","v":0},{"$f":"P31/V31/3.412","v":0},{"$f":"MAX(0,MIN(1,TREND(OFFSET($V$4,MATCH(Y$26,$V$5:$V$7,0),5,1,2),OFFSET($V$4,MATCH(Y$26,$V$5:$V$7,0),3,1,2),$C31)))","v":0.6},{"$f":"Y31*LOOKUP(Y$26,$F$5:$F$7,$I$5:$I$7)","v":32.4},{"$f":"MAX(0,MIN(1,TREND(OFFSET($V$12,MATCH(Y$26,$V$13:$V$15,0),5,1,2),OFFSET($V$12,MATCH(Y$26,$V$13:$V$15,0),3,1,2),$C31)))","v":0},{"$f":"AA31*LOOKUP(Y$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(Y$26,$F$14:$F$16,0),MATCH(Y31,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(Y31,$O$13:$S$13,-1),1,2),Y31)","v":13.16},{"$f":"TREND(OFFSET($H$13,MATCH(Y$26,$F$14:$F$16,0),MATCH(Y31,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(Y31,$I$13:$M$13,-1),1,2),Y31)","v":14.4},{"$f":"Z31/AC31","v":2.4620060790273555},{"$f":"Z31/AD31","v":2.25},{"$f":"LOOKUP(Y$26,$F$5:$F$7,$Q$5:$Q$7)","v":1},{"$f":"LOOKUP(Y$26,$F$5:$F$7,$O$5:$O$7)","v":1},{"$f":"AB31/AG31/3.412","v":0},{"$f":"AB31/AH31/3.412","v":0},{"$f":"MAX(0,MIN(1,TREND(OFFSET($V$4,MATCH(AK$26,$V$5:$V$7,0),5,1,2),OFFSET($V$4,MATCH(AK$26,$V$5:$V$7,0),3,1,2),$C31)))","v":0.90493363636363622},{"$f":"AK31*LOOKUP(AK$26,$F$5:$F$7,$I$5:$I$7)","v":642.50288181818166},{"$f":"MAX(0,MIN(1,TREND(OFFSET($V$12,MATCH(AK$26,$V$13:$V$15,0),5,1,2),OFFSET($V$12,MATCH(AK$26,$V$13:$V$15,0),3,1,2),$C31)))","v":0},{"$f":"AM31*LOOKUP(AK$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(AK$26,$F$14:$F$16,0),MATCH(AK31,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(AK31,$O$13:$S$13,-1),1,2),AK31)","v":11.870000000000001},{"$f":"TREND(OFFSET($H$13,MATCH(AK$26,$F$14:$F$16,0),MATCH(AK31,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(AK31,$I$13:$M$13,-1),1,2),AK31)","v":13},{"$f":"AL31/AO31","v":54.128296699088594},{"$f":"AL31/AP31","v":49.423298601398592},{"$f":"LOOKUP(AK$26,$F$5:$F$7,$Q$5:$Q$7)","v":3.0388000000000002},{"$f":"LOOKUP(AK$26,$F$5:$F$7,$O$5:$O$7)","v":4},{"$f":"AN31/AS31/3.412","v":0},{"$f":"AN31/AT31/3.412","v":0},8.0734063914107619,0,8.0734063914107619]
[{"$f":"'Project Info'!A46","v":90},{"$f":"'Project Info'!B46","v":95},{"$f":"'Project Info'!C46","v":92.016049160256074},{"$f":"'Project Info'!D46","v":72.911561930607689},{"$f":"'Project Info'!E46","v":36.467095439351091},{"$f":"'Project Info'!F46","v":0},{"$f":"'Project Info'!G46","v":0},{"$f":"'Project Info'!H46","v":0},{"$f":"'Project Info'!I46","v":0},{"$f":"'Project Info'!J46","v":0},{"$f":"'Project Info'!K46","v":0},{"$f":"'Project Info'!L46","v":0},0.78659104465544161,269.01413727216101,0,0,12.30679928421927,14.226296544321871,21.858984701010908,18.909639373399141,1.0000000000000002,1.0000000000000002,0,0,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0.83286110610576181,591.33138533509089,0,0,11.870000000000001,13,49.817302892594007,45.487029641160838,3.0388000000000002,4,0,0,7.4916246580722916,0,7.4916246580722916]
[{"$f":"'Project Info'!A47","v":85},{"$f":"'Project Info'!B47","v":90},{"$f":"'Project Info'!C47","v":87.457811360655285},{"$f":"'Project Info'!D47","v":70.80538329449476},{"$f":"'Project Info'!E47","v":34.679413213566804},{"$f":"'Project Info'!F47","v":0},{"$f":"'Project Info'!G47","v":0},{"$f":"'Project Info'!H47","v":0},{"$f":"'Project Info'!I47","v":0},{"$f":"'Project Info'!J47","v":0},{"$f":"'Project Info'!K47","v":0},{"$f":"'Project Info'!L47","v":0},0.689728491413925,235.88714406356235,0,0,12.76519463777873,15.102715085860748,18.478930463422142,15.618856789823262,1.0000000000000002,1.0000000000000002,0,0,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0.73030075561474384,518.51353648646807,0,0,11.870000000000001,13,43.682690521185172,39.885656652805238,3.0388000000000002,4,0,0,6.8691136210061696,0,6.8691136210061696]
[{"$f":"'Project Info'!A48","v":80},{"$f":"'Project Info'!B48","v":85},{"$f":"'Project Info'!C48","v":82.136788830239965},{"$f":"'Project Info'!D48","v":67.872393622439333},{"$f":"'Project Info'!E48","v":32.296248223809314},{"$f":"'Project Info'!F48","v":0},{"$f":"'Project Info'!G48","v":0},{"$f":"'Project Info'!H48","v":0},{"$f":"'Project Info'!I48","v":0},{"$f":"'Project Info'!J48","v":0},{"$f":"'Project Info'!K48","v":0},{"$f":"'Project Info'!L48","v":0},0.57665676264259935,197.21661282376897,0,0,13.262710244372563,16.233432373574004,14.870008406271939,12.148793199447637,1.0000000000000002,1.0000000000000002,0,0,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0.61057774868039916,433.5102015630834,0,0,11.870000000000001,13,36.521499710453526,33.346938581775646,3.0388000000000002,4,0,0,6.1077824145295381,0,6.1077824145295381]
[{"$f":"'Project Info'!A49","v":75},{"$f":"'Project Info'!B49","v":80},{"$f":"'Project Info'!C49","v":76.988400157585886},{"$f":"'Project Info'!D49","v":65.129261896908645},{"$f":"'Project Info'!E49","v":30.190476812806729},{"$f":"'Project Info'!F49","v":0},{"$f":"'Project Info'!G49","v":0},{"$f":"'Project Info'!H49","v":0},{"$f":"'Project Info'!I49","v":0},{"$f":"'Project Info'!J49","v":0},{"$f":"'Project Info'!K49","v":0},{"$f":"'Project Info'!L49","v":0},0.46725350334870019,159.80069814525547,0,0,13.429718217413239,16.7380280267896,11.899035821768376,9.54716397233239,1.0000000000000002,1.0000000000000002,0,0,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0.49473900354568245,351.26469251743453,0,0,11.870000000000001,13,29.592644693970893,27.020360962879579,3.0388000000000002,4,0,0,5.1361616595546558,0,5.1361616595546558]
[{"$f":"'Project Info'!A50","v":70},{"$f":"'Project Info'!B50","v":75},{"$f":"'Project Info'!C50","v":72.457982050814195},{"$f":"'Project Info'!D50","v":63.604425012889301},{"$f":"'Project Info'!E50","v":29.088683095945193},{"$f":"'Project Info'!F50","v":0},{"$f":"'Project Info'!G50","v":0},{"$f":"'Project Info'!H50","v":0},{"$f":"'Project Info'!I50","v":0},{"$f":"'Project Info'!J50","v":0},{"$f":"'Project Info'!K50","v":0},{"$f":"'Project Info'!L50","v":0},0.37098211857980168,126.87588455429217,0,0,12.929107016614967,15.967856948638413,9.8131978017697747,7.9457052353610251,1.0000000000000002,1.0000000000000002,0,0,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0.39280459614331931,278.89126326175671,0,0,11.870000000000001,13,23.495472894840496,21.453174097058209,3.0388000000000002,4,0,0,4.1217974432183926,0,4.1217974432183926]
[{"$f":"'Project Info'!A51","v":65},{"$f":"'Project Info'!B51","v":70},{"$f":"'Project Info'!C51","v":67.815831070966169},{"$f":"'Project Info'!D51","v":61.631331368130574},{"$f":"'Project Info'!E51","v":27.661514889731574},{"$f":"'Project Info'!F51","v":0},{"$f":"'Project Info'!G51","v":0},{"$f":"'Project Info'!H51","v":0},{"$f":"'Project Info'!I51","v":0},{"$f":"'Project Info'!J51","v":0},{"$f":"'Project Info'!K51","v":0},{"$f":"'Project Info'!L51","v":0},0.27233641025803124,{"$f":"M37*LOOKUP(M$26,$F$5:$F$7,$I$5:$I$7)","v":93.139052308246676},0,{"$f":"O37*LOOKUP(M$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(M$26,$F$14:$F$16,0),MATCH(M37,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(M37,$O$13:$S$13,-1),1,2),M37)","v":12.416149333341762},{"$f":"TREND(OFFSET($H$13,MATCH(M$26,$F$14:$F$16,0),MATCH(M37,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(M37,$I$13:$M$13,-1),1,2),M37)","v":15.17869128206425},{"$f":"N37/Q37","v":7.501444272914414},{"$f":"N37/R37","v":6.1361714641566971},{"$f":"LOOKUP(M$26,$F$5:$F$7,$Q$5:$Q$7)","v":1.0000000000000002},{"$f":"LOOKUP(M$26,$F$5:$F$7,$O$5:$O$7)","v":1.0000000000000002},{"$f":"P37/U37/3.412","v":0},{"$f":"P37/V37/3.412","v":0},0.6,{"$f":"Y37*LOOKUP(Y$26,$F$5:$F$7,$I$5:$I$7)","v":32.4},0,{"$f":"AA37*LOOKUP(Y$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(Y$26,$F$14:$F$16,0),MATCH(Y37,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(Y37,$O$13:$S$13,-1),1,2),Y37)","v":13.16},{"$f":"TREND(OFFSET($H$13,MATCH(Y$26,$F$14:$F$16,0),MATCH(Y37,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(Y37,$I$13:$M$13,-1),1,2),Y37)","v":14.4},{"$f":"Z37/AC37","v":2.4620060790273555},{"$f":"Z37/AD37","v":2.25},{"$f":"LOOKUP(Y$26,$F$5:$F$7,$Q$5:$Q$7)","v":1},{"$f":"LOOKUP(Y$26,$F$5:$F$7,$O$5:$O$7)","v":1},{"$f":"AB37/AG37/3.412","v":0},{"$f":"AB37/AH37/3.412","v":0},0.28835619909673871,{"$f":"AK37*LOOKUP(AK$26,$F$5:$F$7,$I$5:$I$7)","v":204.73290135868447},0,{"$f":"AM37*LOOKUP(AK$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(AK$26,$F$14:$F$16,0),MATCH(AK37,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(AK37,$O$13:$S$13,-1),1,2),AK37)","v":11.870000000000001},{"$f":"TREND(OFFSET($H$13,MATCH(AK$26,$F$14:$F$16,0),MATCH(AK37,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(AK37,$I$13:$M$13,-1),1,2),AK37)","v":13},{"$f":"AL37/AO37","v":17.247927662905177},{"$f":"AL37/AP37","v":15.748684719898806},{"$f":"LOOKUP(AK$26,$F$5:$F$7,$Q$5:$Q$7)","v":3.0388000000000002},{"$f":"LOOKUP(AK$26,$F$5:$F$7,$O$5:$O$7)","v":4},{"$f":"AN37/AS37/3.412","v":0},{"$f":"AN37/AT37/3.412","v":0},{"$f":"(S37-T37)+(AE37-AF37)+(AQ37-AR37)","v":3.0765218307914428},{"$f":"(W37-X37)+(AI37-AJ37)+(AU37-AV37)","v":0},{"$f":"AW37+AX37","v":3.0765218307914428}]
[{"$f":"'Project Info'!A52","v":60},{"$f":"'Project Info'!B52","v":65},{"$f":"'Project Info'!C52","v":62.535961472271332},{"$f":"'Project Info'!D52","v":57.135476922863582},{"$f":"'Project Info'!E52","v":24.623037157728302},{"$f":"'Project Info'!F52","v":0},{"$f":"'Project Info'!G52","v":0},{"$f":"'Project Info'!H52","v":0},{"$f":"'Project Info'!I52","v":0},{"$f":"'Project Info'!J52","v":0},{"$f":"'Project Info'!K52","v":0},{"$f":"'Project Info'!L52","v":0},0.16013918128576599,{"$f":"M38*LOOKUP(M$26,$F$5:$F$7,$I$5:$I$7)","v":54.767599999731971},0,{"$f":"O38*LOOKUP(M$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(M$26,$F$14:$F$16,0),MATCH(M38,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(M38,$O$13:$S$13,-1),1,2),M38)","v":9.9808996401057293},{"$f":"TREND(OFFSET($H$13,MATCH(M$26,$F$14:$F$16,0),MATCH(M38,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(M38,$I$13:$M$13,-1),1,2),M38)","v":11.998300153597199},{"$f":"N38/Q38","v":5.4872408274362536},{"$f":"N38/R38","v":4.5646132617637631},{"$f":"LOOKUP(M$26,$F$5:$F$7,$Q$5:$Q$7)","v":1.0000000000000002},{"$f":"LOOKUP(M$26,$F$5:$F$7,$O$5:$O$7)","v":1.0000000000000002},{"$f":"P38/U38/3.412","v":0},{"$f":"P38/V38/3.412","v":0},0.6,{"$f":"Y38*LOOKUP(Y$26,$F$5:$F$7,$I$5:$I$7)","v":32.4},0,{"$f":"AA38*LOOKUP(Y$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(Y$26,$F$14:$F$16,0),MATCH(Y38,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(Y38,$O$13:$S$13,-1),1,2),Y38)","v":13.16},{"$f":"TREND(OFFSET($H$13,MATCH(Y$26,$F$14:$F$16,0),MATCH(Y38,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(Y38,$I$13:$M$13,-1),1,2),Y38)","v":14.4},{"$f":"Z38/AC38","v":2.4620060790273555},{"$f":"Z38/AD38","v":2.25},{"$f":"LOOKUP(Y$26,$F$5:$F$7,$Q$5:$Q$7)","v":1},{"$f":"LOOKUP(Y$26,$F$5:$F$7,$O$5:$O$7)","v":1},{"$f":"AB38/AG38/3.412","v":0},{"$f":"AB38/AH38/3.412","v":0},0.16955913312610482,{"$f":"AK38*LOOKUP(AK$26,$F$5:$F$7,$I$5:$I$7)","v":120.38698451953442},0,{"$f":"AM38*LOOKUP(AK$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(AK$26,$F$14:$F$16,0),MATCH(AK38,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(AK38,$O$13:$S$13,-1),1,2),AK38)","v":11.870000000000001},{"$f":"TREND(OFFSET($H$13,MATCH(AK$26,$F$14:$F$16,0),MATCH(AK38,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(AK38,$I$13:$M$13,-1),1,2),AK38)","v":13},{"$f":"AL38/AO38","v":10.142121694990262},{"$f":"AL38/AP38","v":9.2605372707334173},{"$f":"LOOKUP(AK$26,$F$5:$F$7,$Q$5:$Q$7)","v":3.0388000000000002},{"$f":"LOOKUP(AK$26,$F$5:$F$7,$O$5:$O$7)","v":4},{"$f":"AN38/AS38/3.412","v":0},{"$f":"AN38/AT38/3.412","v":0},{"$f":"(S38-T38)+(AE38-AF38)+(AQ38-AR38)","v":2.0162180689566909},{"$f":"(W38-X38)+(AI38-AJ38)+(AU38-AV38)","v":0},{"$f":"AW38+AX38","v":2.0162180689566909}]
[{"$f":"'Project Info'!A53","v":55},{"$f":"'Project Info'!B53","v":60},{"$f":"'Project Info'!C53","v":57.125792270740902},{"$f":"'Project Info'!D53","v":52.596971157053673},{"$f":"'Project Info'!E53","v":21.818001539159841},{"$f":"'Project Info'!F53","v":0},{"$f":"'Project Info'!G53","v":0},{"$f":"'Project Info'!H53","v":0},{"$f":"'Project Info'!I53","v":0},{"$f":"'Project Info'!J53","v":0},{"$f":"'Project Info'!K53","v":0},{"$f":"'Project Info'!L53","v":0},4.5173085753244413E-2,{"$f":"M39*LOOKUP(M$26,$F$5:$F$7,$I$5:$I$7)","v":15.449195327609589},0,{"$f":"O39*LOOKUP(M$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(M$26,$F$14:$F$16,0),MATCH(M39,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(M39,$O$13:$S$13,-1),1,2),M39)","v":7.0138900207856549},{"$f":"TREND(OFFSET($H$13,MATCH(M$26,$F$14:$F$16,0),MATCH(M39,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(M39,$I$13:$M$13,-1),1,2),M39)","v":8.1579866973073045},{"$f":"N39/Q39","v":2.2026571961958226},{"$f":"N39/R39","v":1.8937509830346848},{"$f":"LOOKUP(M$26,$F$5:$F$7,$Q$5:$Q$7)","v":1.0000000000000002},{"$f":"LOOKUP(M$26,$F$5:$F$7,$O$5:$O$7)","v":1.0000000000000002},{"$f":"P39/U39/3.412","v":0},{"$f":"P39/V39/3.412","v":0},0.6,{"$f":"Y39*LOOKUP(Y$26,$F$5:$F$7,$I$5:$I$7)","v":32.4},0,{"$f":"AA39*LOOKUP(Y$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(Y$26,$F$14:$F$16,0),MATCH(Y39,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(Y39,$O$13:$S$13,-1),1,2),Y39)","v":13.16},{"$f":"TREND(OFFSET($H$13,MATCH(Y$26,$F$14:$F$16,0),MATCH(Y39,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(Y39,$I$13:$M$13,-1),1,2),Y39)","v":14.4},{"$f":"Z39/AC39","v":2.4620060790273555},{"$f":"Z39/AD39","v":2.25},{"$f":"LOOKUP(Y$26,$F$5:$F$7,$Q$5:$Q$7)","v":1},{"$f":"LOOKUP(Y$26,$F$5:$F$7,$O$5:$O$7)","v":1},{"$f":"AB39/AG39/3.412","v":0},{"$f":"AB39/AH39/3.412","v":0},4.783032609167015E-2,{"$f":"AK39*LOOKUP(AK$26,$F$5:$F$7,$I$5:$I$7)","v":33.959531525085808},0,{"$f":"AM39*LOOKUP(AK$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(AK$26,$F$14:$F$16,0),MATCH(AK39,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(AK39,$O$13:$S$13,-1),1,2),AK39)","v":11.870000000000001},{"$f":"TREND(OFFSET($H$13,MATCH(AK$26,$F$14:$F$16,0),MATCH(AK39,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(AK39,$I$13:$M$13,-1),1,2),AK39)","v":13},{"$f":"AL39/AO39","v":2.860954635643286},{"$f":"AL39/AP39","v":2.6122716557758312},{"$f":"LOOKUP(AK$26,$F$5:$F$7,$Q$5:$Q$7)","v":3.0388000000000002},{"$f":"LOOKUP(AK$26,$F$5:$F$7,$O$5:$O$7)","v":4},{"$f":"AN39/AS39/3.412","v":0},{"$f":"AN39/AT39/3.412","v":0},{"$f":"(S39-T39)+(AE39-AF39)+(AQ39-AR39)","v":0.76959527205594802},{"$f":"(W39-X39)+(AI39-AJ39)+(AU39-AV39)","v":0},{"$f":"AW39+AX39","v":0.76959527205594802}]
[{"$f":"'Project Info'!A54","v":50},{"$f":"'Project Info'!B54","v":55},{"$f":"'Project Info'!C54","v":52.235698854337961},{"$f":"'Project Info'!D54","v":48.022768090099298},{"$f":"'Project Info'!E54","v":19.246640192796217},{"$f":"'Project Info'!F54","v":0},{"$f":"'Project Info'!G54","v":0},{"$f":"'Project Info'!H54","v":0},{"$f":"'Project Info'!I54","v":0},{"$f":"'Project Info'!J54","v":0},{"$f":"'Project Info'!K54","v":0},{"$f":"'Project Info'!L54","v":0},0,0,4.2721017705686037E-2,6.3407388899133332,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,1.8583642701973422,1.8583642701973422,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,4.5234018747196902E-2,28.045091623262081,11.870000000000001,13,0,0,3.0388000000000002,4,2.7048658012161582,2.0548865491839159,0.21200607902735547,0.64997925203224227,0.86198533105959774]
[{"$f":"'Project Info'!A55","v":45},{"$f":"'Project Info'!B55","v":50},{"$f":"'Project Info'!C55","v":47.459170258371508},{"$f":"'Project Info'!D55","v":43.465397050422162},{"$f":"'Project Info'!E55","v":16.894183241713304},{"$f":"'Project Info'!F55","v":0},{"$f":"'Project Info'!G55","v":0},{"$f":"'Project Info'!H55","v":0},{"$f":"'Project Info'!I55","v":0},{"$f":"'Project Info'!J55","v":0},{"$f":"'Project Info'!K55","v":0},{"$f":"'Project Info'!L55","v":0},0,0,0.11654009600698578,17.297114129548845,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,5.0694941763038806,5.0694941763038806,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.12339539577210257,76.505145378703588,11.870000000000001,13,0,0,3.0388000000000002,4,7.3786940735213005,5.6055938876541314,0.21200607902735547,1.7731001858671691,1.9851062648945246]
[{"$f":"'Project Info'!A56","v":40},{"$f":"'Project Info'!B56","v":45},{"$f":"'Project Info'!C56","v":42.677030404888129},{"$f":"'Project Info'!D56","v":38.812544504634097},{"$f":"'Project Info'!E56","v":14.690265649465921},{"$f":"'Project Info'!F56","v":0},{"$f":"'Project Info'!G56","v":0},{"$f":"'Project Info'!H56","v":0},{"$f":"'Project Info'!I56","v":0},{"$f":"'Project Info'!J56","v":0},{"$f":"'Project Info'!K56","v":0},{"$f":"'Project Info'!L56","v":0},0,0,0.19044589374263798,28.266360441069814,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,8.2843963778047502,8.2843963778047502,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.20164859337455787,125.02212789222588,11.870000000000001,13,0,0,3.0388000000000002,4,12.058012955481312,9.1604724422791541,0.21200607902735547,2.8975405132021574,3.1095465922295129]
[{"$f":"'Project Info'!A57","v":35},{"$f":"'Project Info'!B57","v":40},{"$f":"'Project Info'!C57","v":37.333046773755832},{"$f":"'Project Info'!D57","v":33.904706919479686},{"$f":"'Project Info'!E57","v":12.53841602318813},{"$f":"'Project Info'!F57","v":0},{"$f":"'Project Info'!G57","v":0},{"$f":"'Project Info'!H57","v":0},{"$f":"'Project Info'!I57","v":0},{"$f":"'Project Info'!J57","v":0},{"$f":"'Project Info'!K57","v":0},{"$f":"'Project Info'!L57","v":0},0,0,0.27303473167831893,40.524360945159451,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,11.87701082800687,11.87701082800687,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.28909559824763176,179.2392709135317,11.870000000000001,13,0,0,3.0388000000000002,4,17.287095390581509,13.133006368224773,0.21200607902735547,4.1540890223567359,4.3660951013840918]
[{"$f":"'Project Info'!A58","v":30},{"$f":"'Project Info'!B58","v":35},{"$f":"'Project Info'!C58","v":32.638179845662044},{"$f":"'Project Info'!D58","v":29.547170928664851},{"$f":"'Project Info'!E58","v":10.728972818165861},{"$f":"'Project Info'!F58","v":0},{"$f":"'Project Info'!G58","v":0},{"$f":"'Project Info'!H58","v":0},{"$f":"'Project Info'!I58","v":0},{"$f":"'Project Info'!J58","v":0},{"$f":"'Project Info'!K58","v":0},{"$f":"'Project Info'!L58","v":0},0,0,0.34559176602158659,51.293421096455923,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,15.033241821939011,15.033241821939011,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.36592069343462108,226.87082992946506,11.870000000000001,13,0,0,3.0388000000000002,4,21.881017805651929,16.623009226953769,0.21200607902735547,5.2580085786981599,5.4700146577255158]
[{"$f":"'Project Info'!A59","v":25},{"$f":"'Project Info'!B59","v":30},{"$f":"'Project Info'!C59","v":27.529264646850947},{"$f":"'Project Info'!D59","v":24.652717392657845},{"$f":"'Project Info'!E59","v":8.8041305482613303},{"$f":"'Project Info'!F59","v":0},{"$f":"'Project Info'!G59","v":0},{"$f":"'Project Info'!H59","v":0},{"$f":"'Project Info'!I59","v":0},{"$f":"'Project Info'!J59","v":0},{"$f":"'Project Info'!K59","v":0},{"$f":"'Project Info'!L59","v":0},0,0,0.42454772818503078,63.012222912678638,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,18.467826176048835,18.467826176048835,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.44952112396062083,278.70309685558493,11.870000000000001,13,0,0,3.0388000000000002,4,26.880086023766797,20.420801352255637,0.21200607902735547,6.4592846715111598,6.6712907505385157]
[{"$f":"'Project Info'!A60","v":20},{"$f":"'Project Info'!B60","v":25},{"$f":"'Project Info'!C60","v":22.998111483544687},{"$f":"'Project Info'!D60","v":20.383306659827422},{"$f":"'Project Info'!E60","v":7.246164547543378},{"$f":"'Project Info'!F60","v":0},{"$f":"'Project Info'!G60","v":0},{"$f":"'Project Info'!H60","v":0},{"$f":"'Project Info'!I60","v":0},{"$f":"'Project Info'!J60","v":0},{"$f":"'Project Info'!K60","v":0},{"$f":"'Project Info'!L60","v":0},0,0,0.49457464070885476,73.405757323289635,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,21.513996870835175,21.513996870835175,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.52366726663290519,324.67370531240124,11.870000000000001,13,0,0,3.0388000000000002,4,31.313814689955322,23.789105019959059,0.21200607902735547,7.5247096699962626,7.7367157490236185]
[{"$f":"'Project Info'!A61","v":15},{"$f":"'Project Info'!B61","v":20},{"$f":"'Project Info'!C61","v":17.808510327474309},{"$f":"'Project Info'!D61","v":15.420865796304254},{"$f":"'Project Info'!E61","v":5.5490484131518292},{"$f":"'Project Info'!F61","v":0},{"$f":"'Project Info'!G61","v":0},{"$f":"'Project Info'!H61","v":0},{"$f":"'Project Info'!I61","v":0},{"$f":"'Project Info'!J61","v":0},{"$f":"'Project Info'!K61","v":0},{"$f":"'Project Info'!L61","v":0},0,0,0.57477756766630606,85.30963614816848,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,25.002824193484312,25.002824193484312,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.60858801282314767,377.32456795035154,11.870000000000001,13,0,0,3.0388000000000002,4,36.39183403348266,27.646876315236778,0.21200607902735547,8.7449577182458818,8.9569637972732377]
[{"$f":"'Project Info'!A62","v":10},{"$f":"'Project Info'!B62","v":15},{"$f":"'Project Info'!C62","v":12.269931130346862},{"$f":"'Project Info'!D62","v":10.318264913023604},{"$f":"'Project Info'!E62","v":3.9082824916941998},{"$f":"'Project Info'!F62","v":0},{"$f":"'Project Info'!G62","v":0},{"$f":"'Project Info'!H62","v":0},{"$f":"'Project Info'!I62","v":0},{"$f":"'Project Info'!J62","v":0},{"$f":"'Project Info'!K62","v":0},{"$f":"'Project Info'!L62","v":0},0,0,0.66037379162191201,98.013998900107424,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,28.726259935553166,28.726259935553166,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.69921930877614225,433.51597144120819,11.870000000000001,13,0,0,3.0388000000000002,4,41.811328027885864,31.764065902784893,0.21200607902735547,10.047262125100971,10.259268204128327]
[{"$f":"'Project Info'!A63","v":5},{"$f":"'Project Info'!B63","v":10},{"$f":"'Project Info'!C63","v":7.3137581369917548},{"$f":"'Project Info'!D63","v":5.7052382449247707},{"$f":"'Project Info'!E63","v":2.5019418419888937},{"$f":"'Project Info'!F63","v":0},{"$f":"'Project Info'!G63","v":0},{"$f":"'Project Info'!H63","v":0},{"$f":"'Project Info'!I63","v":0},{"$f":"'Project Info'!J63","v":0},{"$f":"'Project Info'!K63","v":0},{"$f":"'Project Info'!L63","v":0},0,0,0.73696919242830916,109.3824414785945,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,32.058159870631442,32.058159870631442,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.78032032139468033,483.79859926470181,11.870000000000001,13,0,0,3.0388000000000002,4,46.660938156534392,35.448314717519182,0.21200607902735547,11.212623439015211,11.424629518042567]
[{"$f":"'Project Info'!A64","v":0},{"$f":"'Project Info'!B64","v":5},{"$f":"'Project Info'!C64","v":2.6119461836144886},{"$f":"'Project Info'!D64","v":1.2699770062067783},{"$f":"'Project Info'!E64","v":1.2046477897733283},{"$f":"'Project Info'!F64","v":0},{"$f":"'Project Info'!G64","v":0},{"$f":"'Project Info'!H64","v":0},{"$f":"'Project Info'!I64","v":0},{"$f":"'Project Info'!J64","v":0},{"$f":"'Project Info'!K64","v":0},{"$f":"'Project Info'!L64","v":0},0,0,0.80963355898050327,120.16743209100426,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,35.219059815651882,35.219059815651882,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.85725906244994476,531.50061871896571,11.870000000000001,13,0,0,3.0388000000000002,4,51.261656271634585,38.943480269560794,0.21200607902735547,12.318176002073791,12.530182081101147]
[{"$f":"'Project Info'!A65","v":-5},{"$f":"'Project Info'!B65","v":0},{"$f":"'Project Info'!C65","v":-1.6731398516793925},{"$f":"'Project Info'!D65","v":-2.7083318773557807},{"$f":"'Project Info'!E65","v":7.9391832815876459E-2},{"$f":"'Project Info'!F65","v":0},{"$f":"'Project Info'!G65","v":0},{"$f":"'Project Info'!H65","v":0},{"$f":"'Project Info'!I65","v":0},{"$f":"'Project Info'!J65","v":0},{"$f":"'Project Info'!K65","v":0},{"$f":"'Project Info'!L65","v":0},0,0,0.87585761588959044,129.99653906556478,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,38.099806291197169,38.099806291197169,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.9273786521183901,574.97476431340181,11.870000000000001,13,0,0,3.0388000000000002,4,55.454608508522462,42.128866083924521,0.21200607902735547,13.325742424597941,13.537748503625297]
[{"$f":"'Project Info'!A66","v":-10},{"$f":"'Project Info'!B66","v":-5},{"$f":"'Project Info'!C66","v":-6.5729865085377277},{"$f":"'Project Info'!D66","v":-7.2465935998252222},{"$f":"'Project Info'!E66","v":-1.168423365310433},{"$f":"'Project Info'!F66","v":0},{"$f":"'Project Info'!G66","v":0},{"$f":"'Project Info'!H66","v":0},{"$f":"'Project Info'!I66","v":0},{"$f":"'Project Info'!J66","v":0},{"$f":"'Project Info'!K66","v":0},{"$f":"'Project Info'!L66","v":0},0,0,0.95158251876831024,141.23578060063014,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,41.393839566421484,41.393839566421484,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,1,620,11.870000000000001,13,0,0,3.0388000000000002,4,59.79715877850839,45.427901524032826,0.21200607902735547,14.369257254475563,14.581263333502919]
[{"$f":"'Project Info'!A67","v":-15},{"$f":"'Project Info'!B67","v":-10},{"$f":"'Project Info'!C67","v":-15.32570353422995},{"$f":"'Project Info'!D67","v":-15.707838211108999},{"$f":"'Project Info'!E67","v":-3.4051318156661381},{"$f":"'Project Info'!F67","v":0},{"$f":"'Project Info'!G67","v":0},{"$f":"'Project Info'!H67","v":0},{"$f":"'Project Info'!I67","v":0},{"$f":"'Project Info'!J67","v":0},{"$f":"'Project Info'!K67","v":0},{"$f":"'Project Info'!L67","v":0},0,0,1,148.422,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,43.499999999999993,43.499999999999993,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,1,620,11.870000000000001,13,0,0,3.0388000000000002,4,59.79715877850839,45.427901524032826,0.21200607902735547,14.369257254475563,14.581263333502919]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,"Load Profile",null,null,null,null,null,null,null,null,null,null,null,"Load Profile",null,null,null,null,null,null,null,null,null,null,null,"Load Profile"]
["Unoccupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown",null,null,null,null,null,null,1,{"$f":"LOOKUP(M56,$F$5:$F$7,$G$5:$G$7)","v":"Common OA Temp"},null,null,null,null,null,null,null,null,null,null,2,{"$f":"LOOKUP(Y56,$F$5:$F$7,$G$5:$G$7)","v":"Constant Yr-Round"},null,null,null,null,null,null,null,null,null,null,3,{"$f":"LOOKUP(AK56,$F$5:$F$7,$G$5:$G$7)","v":"Guest Rm OA Temp"},null,null,null,null,null,null,null,null,null,null,"End Use",null,"Total"]
["OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Cooling","Cooling","Heating","Heating","Cooling Perf.",null,"Cooling Demand",null,"Heating Perf.",null,"Heating Demand",null,"Cooling","Cooling","Heating","Heating","Cooling Perf.",null,"Cooling Demand",null,"Heating Perf.",null,"Heating Demand",null,"Cooling","Cooling","Heating","Heating","Cooling Perf.",null,"Cooling Demand",null,"Heating Perf.",null,"Heating Demand",null,"Demand Reduction",null,"Demand"]
["Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","%","Load","%","Load","Base","Design","Base","Design","Base","Design","Base","Design","%","Load","%","Load","Base","Design","Base","Design","Base","Design","Base","Design","%","Load","%","Load","Base","Design","Base","Design","Base","Design","Base","Design","Cooling","Heating","Reduction"]
["From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","Load","MBH","Load","MBH","EER","EER","kW","kW","COP","COP","kW","kW","Load","MBH","Load","MBH","EER","EER","kW","kW","COP","COP","kW","kW","Load","MBH","Load","MBH","EER","EER","kW","kW","COP","COP","kW","kW","kW","kW","kW"]
[{"$f":"'Project Info'!A74","v":100},{"$f":"'Project Info'!B74","v":105},{"$f":"'Project Info'!C74","v":102},{"$f":"'Project Info'!D74","v":76},{"$f":"'Project Info'!E74","v":40},{"$f":"'Project Info'!F74","v":0},{"$f":"'Project Info'!G74","v":0},{"$f":"'Project Info'!H74","v":0},{"$f":"'Project Info'!I74","v":0},{"$f":"'Project Info'!J74","v":0},{"$f":"'Project Info'!K74","v":0},{"$f":"'Project Info'!L74","v":0},{"$f":"MAX(0,MIN(1,TREND(OFFSET($V$4,MATCH(M$26,$V$5:$V$7,0),9,1,2),OFFSET($V$4,MATCH(M$26,$V$5:$V$7,0),7,1,2),$C60)))","v":0.67499999999999982},{"$f":"M60*LOOKUP(M$26,$F$5:$F$7,$I$5:$I$7)","v":230.84999999999994},{"$f":"MAX(0,TREND(OFFSET($V$12,MATCH(M$26,$V$13:$V$15,0),9,1,2),OFFSET($V$12,MATCH(M$26,$V$13:$V$15,0),7,1,2),$C60))","v":0},{"$f":"O60*LOOKUP(M$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(M$26,$F$14:$F$16,0),MATCH(M60,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(M60,$O$13:$S$13,-1),1,2),M60)","v":12.830000000000002},{"$f":"TREND(OFFSET($H$13,MATCH(M$26,$F$14:$F$16,0),MATCH(M60,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(M60,$I$13:$M$13,-1),1,2),M60)","v":15.25},{"$f":"N60/Q60","v":17.992985190958684},{"$f":"N60/R60","v":15.137704918032783},{"$f":"LOOKUP(M$26,$F$5:$F$7,$Q$5:$Q$7)","v":1.0000000000000002},{"$f":"LOOKUP(M$26,$F$5:$F$7,$O$5:$O$7)","v":1.0000000000000002},{"$f":"P60/U60/3.412","v":0},{"$f":"P60/V60/3.412","v":0},{"$f":"MAX(0,MIN(1,TREND(OFFSET($V$4,MATCH(Y$26,$V$5:$V$7,0),9,1,2),OFFSET($V$4,MATCH(Y$26,$V$5:$V$7,0),7,1,2),$C60)))","v":0.6},{"$f":"Y60*LOOKUP(Y$26,$F$5:$F$7,$I$5:$I$7)","v":32.4},{"$f":"MAX(0,MIN(1,TREND(OFFSET($V$12,MATCH(Y$26,$V$13:$V$15,0),9,1,2),OFFSET($V$12,MATCH(Y$26,$V$13:$V$15,0),7,1,2),$C60)))","v":0},{"$f":"AA60*LOOKUP(Y$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(Y$26,$F$14:$F$16,0),MATCH(Y60,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(Y60,$O$13:$S$13,-1),1,2),Y60)","v":13.16},{"$f":"TREND(OFFSET($H$13,MATCH(Y$26,$F$14:$F$16,0),MATCH(Y60,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(Y60,$I$13:$M$13,-1),1,2),Y60)","v":14.4},{"$f":"Z60/AC60","v":2.4620060790273555},{"$f":"Z60/AD60","v":2.25},{"$f":"LOOKUP(Y$26,$F$5:$F$7,$Q$5:$Q$7)","v":1},{"$f":"LOOKUP(Y$26,$F$5:$F$7,$O$5:$O$7)","v":1},{"$f":"AB60/AG60/3.412","v":0},{"$f":"AB60/AH60/3.412","v":0},{"$f":"MAX(0,MIN(1,TREND(OFFSET($V$4,MATCH(AK$26,$V$5:$V$7,0),9,1,2),OFFSET($V$4,MATCH(AK$26,$V$5:$V$7,0),7,1,2),$C60)))","v":1},{"$f":"AK60*LOOKUP(AK$26,$F$5:$F$7,$I$5:$I$7)","v":710},{"$f":"MAX(0,MIN(1,TREND(OFFSET($V$12,MATCH(AK$26,$V$13:$V$15,0),9,1,2),OFFSET($V$12,MATCH(AK$26,$V$13:$V$15,0),7,1,2),$C60)))","v":0},{"$f":"AM60*LOOKUP(AK$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(AK$26,$F$14:$F$16,0),MATCH(AK60,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(AK60,$O$13:$S$13,-1),1,2),AK60)","v":11.870000000000001},{"$f":"TREND(OFFSET($H$13,MATCH(AK$26,$F$14:$F$16,0),MATCH(AK60,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(AK60,$I$13:$M$13,-1),1,2),AK60)","v":13},{"$f":"AL60/AO60","v":59.81465880370682},{"$f":"AL60/AP60","v":54.615384615384613},{"$f":"LOOKUP(AK$26,$F$5:$F$7,$Q$5:$Q$7)","v":3.0388000000000002},{"$f":"LOOKUP(AK$26,$F$5:$F$7,$O$5:$O$7)","v":4},{"$f":"AN60/AS60/3.412","v":0},{"$f":"AN60/AT60/3.412","v":0},{"$f":"(S60-T60)+(AE60-AF60)+(AQ60-AR60)","v":8.2665605402754636},{"$f":"(W60-X60)+(AI60-AJ60)+(AU60-AV60)","v":0},{"$f":"AW60+AX60","v":8.2665605402754636}]
[{"$f":"'Project Info'!A75","v":95},{"$f":"'Project Info'!B75","v":100},{"$f":"'Project Info'!C75","v":95.219272727272724},{"$f":"'Project Info'!D75","v":74.534025272781079},{"$f":"'Project Info'!E75","v":37.923296058061368},{"$f":"'Project Info'!F75","v":0},{"$f":"'Project Info'!G75","v":0},{"$f":"'Project Info'!H75","v":0},{"$f":"'Project Info'!I75","v":0},{"$f":"'Project Info'!J75","v":0},{"$f":"'Project Info'!K75","v":0},{"$f":"'Project Info'!L75","v":0},{"$f":"MAX(0,MIN(1,TREND(OFFSET($V$4,MATCH(M$26,$V$5:$V$7,0),9,1,2),OFFSET($V$4,MATCH(M$26,$V$5:$V$7,0),7,1,2),$C61)))","v":0.50548181818181792},{"$f":"M61*LOOKUP(M$26,$F$5:$F$7,$I$5:$I$7)","v":172.87478181818173},{"$f":"MAX(0,TREND(OFFSET($V$12,MATCH(M$26,$V$13:$V$15,0),9,1,2),OFFSET($V$12,MATCH(M$26,$V$13:$V$15,0),7,1,2),$C61))","v":0},{"$f":"O61*LOOKUP(M$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(M$26,$F$14:$F$16,0),MATCH(M61,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(M61,$O$13:$S$13,-1),1,2),M61)","v":13.575880000000002},{"$f":"TREND(OFFSET($H$13,MATCH(M$26,$F$14:$F$16,0),MATCH(M61,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(M61,$I$13:$M$13,-1),1,2),M61)","v":16.945181818181819},{"$f":"N61/Q61","v":12.733965077636345},{"$f":"N61/R61","v":10.202002178146639},{"$f":"LOOKUP(M$26,$F$5:$F$7,$Q$5:$Q$7)","v":1.0000000000000002},{"$f":"LOOKUP(M$26,$F$5:$F$7,$O$5:$O$7)","v":1.0000000000000002},{"$f":"P61/U61/3.412","v":0},{"$f":"P61/V61/3.412","v":0},{"$f":"MAX(0,MIN(1,TREND(OFFSET($V$4,MATCH(Y$26,$V$5:$V$7,0),9,1,2),OFFSET($V$4,MATCH(Y$26,$V$5:$V$7,0),7,1,2),$C61)))","v":0.6},{"$f":"Y61*LOOKUP(Y$26,$F$5:$F$7,$I$5:$I$7)","v":32.4},{"$f":"MAX(0,MIN(1,TREND(OFFSET($V$12,MATCH(Y$26,$V$13:$V$15,0),9,1,2),OFFSET($V$12,MATCH(Y$26,$V$13:$V$15,0),7,1,2),$C61)))","v":0},{"$f":"AA61*LOOKUP(Y$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(Y$26,$F$14:$F$16,0),MATCH(Y61,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(Y61,$O$13:$S$13,-1),1,2),Y61)","v":13.16},{"$f":"TREND(OFFSET($H$13,MATCH(Y$26,$F$14:$F$16,0),MATCH(Y61,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(Y61,$I$13:$M$13,-1),1,2),Y61)","v":14.4},{"$f":"Z61/AC61","v":2.4620060790273555},{"$f":"Z61/AD61","v":2.25},{"$f":"LOOKUP(Y$26,$F$5:$F$7,$Q$5:$Q$7)","v":1},{"$f":"LOOKUP(Y$26,$F$5:$F$7,$O$5:$O$7)","v":1},{"$f":"AB61/AG61/3.412","v":0},{"$f":"AB61/AH61/3.412","v":0},{"$f":"MAX(0,MIN(1,TREND(OFFSET($V$4,MATCH(AK$26,$V$5:$V$7,0),9,1,2),OFFSET($V$4,MATCH(AK$26,$V$5:$V$7,0),7,1,2),$C61)))","v":0.90657818181818128},{"$f":"AK61*LOOKUP(AK$26,$F$5:$F$7,$I$5:$I$7)","v":643.67050909090869},{"$f":"MAX(0,MIN(1,TREND(OFFSET($V$12,MATCH(AK$26,$V$13:$V$15,0),9,1,2),OFFSET($V$12,MATCH(AK$26,$V$13:$V$15,0),7,1,2),$C61)))","v":0},{"$f":"AM61*LOOKUP(AK$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(AK$26,$F$14:$F$16,0),MATCH(AK61,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(AK61,$O$13:$S$13,-1),1,2),AK61)","v":11.870000000000001},{"$f":"TREND(OFFSET($H$13,MATCH(AK$26,$F$14:$F$16,0),MATCH(AK61,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(AK61,$I$13:$M$13,-1),1,2),AK61)","v":13},{"$f":"AL61/AO61","v":54.226664624339399},{"$f":"AL61/AP61","v":49.513116083916053},{"$f":"LOOKUP(AK$26,$F$5:$F$7,$Q$5:$Q$7)","v":3.0388000000000002},{"$f":"LOOKUP(AK$26,$F$5:$F$7,$O$5:$O$7)","v":4},{"$f":"AN61/AS61/3.412","v":0},{"$f":"AN61/AT61/3.412","v":0},7.4575175189404082,0,7.4575175189404082]
[{"$f":"'Project Info'!A76","v":90},{"$f":"'Project Info'!B76","v":95},{"$f":"'Project Info'!C76","v":92.016049160256074},{"$f":"'Project Info'!D76","v":72.911561930607689},{"$f":"'Project Info'!E76","v":36.467095439351091},{"$f":"'Project Info'!F76","v":0},{"$f":"'Project Info'!G76","v":0},{"$f":"'Project Info'!H76","v":0},{"$f":"'Project Info'!I76","v":0},{"$f":"'Project Info'!J76","v":0},{"$f":"'Project Info'!K76","v":0},{"$f":"'Project Info'!L76","v":0},0.42540122900640176,145.48722032018941,0,0,13.212086390833289,16.403209832051214,11.011676431447668,8.8694360317157699,1.0000000000000002,1.0000000000000002,0,0,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0.81048147480768207,575.44184711345429,0,0,11.870000000000001,13,48.478672882346608,44.264757470265714,3.0388000000000002,4,0,0,6.5681618908401482,0,6.5681618908401482]
[{"$f":"'Project Info'!A77","v":85},{"$f":"'Project Info'!B77","v":90},{"$f":"'Project Info'!C77","v":87.457811360655285},{"$f":"'Project Info'!D77","v":70.80538329449476},{"$f":"'Project Info'!E77","v":34.679413213566804},{"$f":"'Project Info'!F77","v":0},{"$f":"'Project Info'!G77","v":0},{"$f":"'Project Info'!H77","v":0},{"$f":"'Project Info'!I77","v":0},{"$f":"'Project Info'!J77","v":0},{"$f":"'Project Info'!K77","v":0},{"$f":"'Project Info'!L77","v":0},0.31144528401638194,106.51428713360262,0,0,12.619515476885185,15.491562272131056,8.4404418956260141,6.875632377324477,1.0000000000000002,1.0000000000000002,0,0,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0.67373434081965811,478.35138198195727,0,0,11.870000000000001,13,40.299189720468178,36.796260152458252,3.0388000000000002,4,0,0,5.2797451653388183,0,5.2797451653388183]
[{"$f":"'Project Info'!A78","v":80},{"$f":"'Project Info'!B78","v":85},{"$f":"'Project Info'!C78","v":82.136788830239965},{"$f":"'Project Info'!D78","v":67.872393622439333},{"$f":"'Project Info'!E78","v":32.296248223809314},{"$f":"'Project Info'!F78","v":0},{"$f":"'Project Info'!G78","v":0},{"$f":"'Project Info'!H78","v":0},{"$f":"'Project Info'!I78","v":0},{"$f":"'Project Info'!J78","v":0},{"$f":"'Project Info'!K78","v":0},{"$f":"'Project Info'!L78","v":0},0.17841972075599877,61.019544498551582,0,0,10.452678177972121,12.608941068125905,5.8376947476622414,4.8393869214602532,1.0000000000000002,1.0000000000000002,0,0,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0.51410366490719883,365.0136020841112,0,0,11.870000000000001,13,30.750935306159324,28.077969391085478,3.0388000000000002,4,0,0,3.8832798203031893,0,3.8832798203031893]
[{"$f":"'Project Info'!A79","v":75},{"$f":"'Project Info'!B79","v":80},{"$f":"'Project Info'!C79","v":76.988400157585886},{"$f":"'Project Info'!D79","v":65.129261896908645},{"$f":"'Project Info'!E79","v":30.190476812806729},{"$f":"'Project Info'!F79","v":0},{"$f":"'Project Info'!G79","v":0},{"$f":"'Project Info'!H79","v":0},{"$f":"'Project Info'!I79","v":0},{"$f":"'Project Info'!J79","v":0},{"$f":"'Project Info'!K79","v":0},{"$f":"'Project Info'!L79","v":0},4.9710003939646974E-2,17.000821347359263,0,0,7.1309774093655056,8.3095373599667965,2.384080101702629,2.0459407799602451,1.0000000000000002,1.0000000000000002,0,0,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0.35965200472757641,255.35292335657925,0,0,11.870000000000001,13,21.512461950849136,19.642532565890711,3.0388000000000002,4,0,0,2.4200747857281644,0,2.4200747857281644]
[{"$f":"'Project Info'!A80","v":70},{"$f":"'Project Info'!B80","v":75},{"$f":"'Project Info'!C80","v":72.457982050814195},{"$f":"'Project Info'!D80","v":63.604425012889301},{"$f":"'Project Info'!E80","v":29.088683095945193},{"$f":"'Project Info'!F80","v":0},{"$f":"'Project Info'!G80","v":0},{"$f":"'Project Info'!H80","v":0},{"$f":"'Project Info'!I80","v":0},{"$f":"'Project Info'!J80","v":0},{"$f":"'Project Info'!K80","v":0},{"$f":"'Project Info'!L80","v":0},0,{"$f":"M66*LOOKUP(M$26,$F$5:$F$7,$I$5:$I$7)","v":0},{"$f":"MAX(0,TREND(OFFSET($V$12,MATCH(M$26,$V$13:$V$15,0),9,1,2),OFFSET($V$12,MATCH(M$26,$V$13:$V$15,0),7,1,2),$C66))","v":0},{"$f":"O66*LOOKUP(M$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(M$26,$F$14:$F$16,0),MATCH(M66,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(M66,$O$13:$S$13,-1),1,2),M66)","v":5.8480769230769241},{"$f":"TREND(OFFSET($H$13,MATCH(M$26,$F$14:$F$16,0),MATCH(M66,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(M66,$I$13:$M$13,-1),1,2),M66)","v":6.6490304413192236},{"$f":"N66/Q66","v":0},{"$f":"N66/R66","v":0},{"$f":"LOOKUP(M$26,$F$5:$F$7,$Q$5:$Q$7)","v":1.0000000000000002},{"$f":"LOOKUP(M$26,$F$5:$F$7,$O$5:$O$7)","v":1.0000000000000002},{"$f":"P66/U66/3.412","v":0},{"$f":"P66/V66/3.412","v":0},0.6,{"$f":"Y66*LOOKUP(Y$26,$F$5:$F$7,$I$5:$I$7)","v":32.4},0,{"$f":"AA66*LOOKUP(Y$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(Y$26,$F$14:$F$16,0),MATCH(Y66,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(Y66,$O$13:$S$13,-1),1,2),Y66)","v":13.16},{"$f":"TREND(OFFSET($H$13,MATCH(Y$26,$F$14:$F$16,0),MATCH(Y66,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(Y66,$I$13:$M$13,-1),1,2),Y66)","v":14.4},{"$f":"Z66/AC66","v":2.4620060790273555},{"$f":"Z66/AD66","v":2.25},{"$f":"LOOKUP(Y$26,$F$5:$F$7,$Q$5:$Q$7)","v":1},{"$f":"LOOKUP(Y$26,$F$5:$F$7,$O$5:$O$7)","v":1},{"$f":"AB66/AG66/3.412","v":0},{"$f":"AB66/AH66/3.412","v":0},0.2237394615244257,{"$f":"AK66*LOOKUP(AK$26,$F$5:$F$7,$I$5:$I$7)","v":158.85501768234224},0,{"$f":"AM66*LOOKUP(AK$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(AK$26,$F$14:$F$16,0),MATCH(AK66,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(AK66,$O$13:$S$13,-1),1,2),AK66)","v":11.870000000000001},{"$f":"TREND(OFFSET($H$13,MATCH(AK$26,$F$14:$F$16,0),MATCH(AK66,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(AK66,$I$13:$M$13,-1),1,2),AK66)","v":13},{"$f":"AL66/AO66","v":13.382899552008611},{"$f":"AL66/AP66","v":12.219616744795557},{"$f":"LOOKUP(AK$26,$F$5:$F$7,$Q$5:$Q$7)","v":3.0388000000000002},{"$f":"LOOKUP(AK$26,$F$5:$F$7,$O$5:$O$7)","v":4},{"$f":"AN66/AS66/3.412","v":0},{"$f":"AN66/AT66/3.412","v":0},{"$f":"(S66-T66)+(AE66-AF66)+(AQ66-AR66)","v":1.3752888862404098},{"$f":"(W66-X66)+(AI66-AJ66)+(AU66-AV66)","v":0},{"$f":"AW66+AX66","v":1.3752888862404098}]
[{"$f":"'Project Info'!A81","v":65},{"$f":"'Project Info'!B81","v":70},{"$f":"'Project Info'!C81","v":67.815831070966169},{"$f":"'Project Info'!D81","v":61.631331368130574},{"$f":"'Project Info'!E81","v":27.661514889731574},{"$f":"'Project Info'!F81","v":0},{"$f":"'Project Info'!G81","v":0},{"$f":"'Project Info'!H81","v":0},{"$f":"'Project Info'!I81","v":0},{"$f":"'Project Info'!J81","v":0},{"$f":"'Project Info'!K81","v":0},{"$f":"'Project Info'!L81","v":0},0,{"$f":"M67*LOOKUP(M$26,$F$5:$F$7,$I$5:$I$7)","v":0},{"$f":"MAX(0,TREND(OFFSET($V$12,MATCH(M$26,$V$13:$V$15,0),9,1,2),OFFSET($V$12,MATCH(M$26,$V$13:$V$15,0),7,1,2),$C67))","v":0},{"$f":"O67*LOOKUP(M$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(M$26,$F$14:$F$16,0),MATCH(M67,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(M67,$O$13:$S$13,-1),1,2),M67)","v":5.8480769230769241},{"$f":"TREND(OFFSET($H$13,MATCH(M$26,$F$14:$F$16,0),MATCH(M67,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(M67,$I$13:$M$13,-1),1,2),M67)","v":6.6490304413192236},{"$f":"N67/Q67","v":0},{"$f":"N67/R67","v":0},{"$f":"LOOKUP(M$26,$F$5:$F$7,$Q$5:$Q$7)","v":1.0000000000000002},{"$f":"LOOKUP(M$26,$F$5:$F$7,$O$5:$O$7)","v":1.0000000000000002},{"$f":"P67/U67/3.412","v":0},{"$f":"P67/V67/3.412","v":0},0.6,{"$f":"Y67*LOOKUP(Y$26,$F$5:$F$7,$I$5:$I$7)","v":32.4},0,{"$f":"AA67*LOOKUP(Y$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(Y$26,$F$14:$F$16,0),MATCH(Y67,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(Y67,$O$13:$S$13,-1),1,2),Y67)","v":13.16},{"$f":"TREND(OFFSET($H$13,MATCH(Y$26,$F$14:$F$16,0),MATCH(Y67,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(Y67,$I$13:$M$13,-1),1,2),Y67)","v":14.4},{"$f":"Z67/AC67","v":2.4620060790273555},{"$f":"Z67/AD67","v":2.25},{"$f":"LOOKUP(Y$26,$F$5:$F$7,$Q$5:$Q$7)","v":1},{"$f":"LOOKUP(Y$26,$F$5:$F$7,$O$5:$O$7)","v":1},{"$f":"AB67/AG67/3.412","v":0},{"$f":"AB67/AH67/3.412","v":0},8.4474932128985047E-2,{"$f":"AK67*LOOKUP(AK$26,$F$5:$F$7,$I$5:$I$7)","v":59.977201811579384},0,{"$f":"AM67*LOOKUP(AK$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(AK$26,$F$14:$F$16,0),MATCH(AK67,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(AK67,$O$13:$S$13,-1),1,2),AK67)","v":11.870000000000001},{"$f":"TREND(OFFSET($H$13,MATCH(AK$26,$F$14:$F$16,0),MATCH(AK67,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(AK67,$I$13:$M$13,-1),1,2),AK67)","v":13},{"$f":"AL67/AO67","v":5.0528392427615314},{"$f":"AL67/AP67","v":4.6136309085830298},{"$f":"LOOKUP(AK$26,$F$5:$F$7,$Q$5:$Q$7)","v":3.0388000000000002},{"$f":"LOOKUP(AK$26,$F$5:$F$7,$O$5:$O$7)","v":4},{"$f":"AN67/AS67/3.412","v":0},{"$f":"AN67/AT67/3.412","v":0},{"$f":"(S67-T67)+(AE67-AF67)+(AQ67-AR67)","v":0.65121441320585705},{"$f":"(W67-X67)+(AI67-AJ67)+(AU67-AV67)","v":0},{"$f":"AW67+AX67","v":0.65121441320585705}]
[{"$f":"'Project Info'!A82","v":60},{"$f":"'Project Info'!B82","v":65},{"$f":"'Project Info'!C82","v":62.535961472271332},{"$f":"'Project Info'!D82","v":57.135476922863582},{"$f":"'Project Info'!E82","v":24.623037157728302},{"$f":"'Project Info'!F82","v":0},{"$f":"'Project Info'!G82","v":0},{"$f":"'Project Info'!H82","v":0},{"$f":"'Project Info'!I82","v":0},{"$f":"'Project Info'!J82","v":0},{"$f":"'Project Info'!K82","v":0},{"$f":"'Project Info'!L82","v":0},0,{"$f":"M68*LOOKUP(M$26,$F$5:$F$7,$I$5:$I$7)","v":0},{"$f":"MAX(0,TREND(OFFSET($V$12,MATCH(M$26,$V$13:$V$15,0),9,1,2),OFFSET($V$12,MATCH(M$26,$V$13:$V$15,0),7,1,2),$C68))","v":0},{"$f":"O68*LOOKUP(M$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(M$26,$F$14:$F$16,0),MATCH(M68,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(M68,$O$13:$S$13,-1),1,2),M68)","v":5.8480769230769241},{"$f":"TREND(OFFSET($H$13,MATCH(M$26,$F$14:$F$16,0),MATCH(M68,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(M68,$I$13:$M$13,-1),1,2),M68)","v":6.6490304413192236},{"$f":"N68/Q68","v":0},{"$f":"N68/R68","v":0},{"$f":"LOOKUP(M$26,$F$5:$F$7,$Q$5:$Q$7)","v":1.0000000000000002},{"$f":"LOOKUP(M$26,$F$5:$F$7,$O$5:$O$7)","v":1.0000000000000002},{"$f":"P68/U68/3.412","v":0},{"$f":"P68/V68/3.412","v":0},0.6,{"$f":"Y68*LOOKUP(Y$26,$F$5:$F$7,$I$5:$I$7)","v":32.4},0,{"$f":"AA68*LOOKUP(Y$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(Y$26,$F$14:$F$16,0),MATCH(Y68,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(Y68,$O$13:$S$13,-1),1,2),Y68)","v":13.16},{"$f":"TREND(OFFSET($H$13,MATCH(Y$26,$F$14:$F$16,0),MATCH(Y68,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(Y68,$I$13:$M$13,-1),1,2),Y68)","v":14.4},{"$f":"Z68/AC68","v":2.4620060790273555},{"$f":"Z68/AD68","v":2.25},{"$f":"LOOKUP(Y$26,$F$5:$F$7,$Q$5:$Q$7)","v":1},{"$f":"LOOKUP(Y$26,$F$5:$F$7,$O$5:$O$7)","v":1},{"$f":"AB68/AG68/3.412","v":0},{"$f":"AB68/AH68/3.412","v":0},0,{"$f":"AK68*LOOKUP(AK$26,$F$5:$F$7,$I$5:$I$7)","v":0},0,{"$f":"AM68*LOOKUP(AK$26,$F$5:$F$7,$N$5:$N$7)","v":0},{"$f":"TREND(OFFSET($N$13,MATCH(AK$26,$F$14:$F$16,0),MATCH(AK68,$O$13:$S$13,-1),1,2),OFFSET($N$13,0,MATCH(AK68,$O$13:$S$13,-1),1,2),AK68)","v":11.870000000000001},{"$f":"TREND(OFFSET($H$13,MATCH(AK$26,$F$14:$F$16,0),MATCH(AK68,$I$13:$M$13,-1),1,2),OFFSET($H$13,0,MATCH(AK68,$I$13:$M$13,-1),1,2),AK68)","v":13},{"$f":"AL68/AO68","v":0},{"$f":"AL68/AP68","v":0},{"$f":"LOOKUP(AK$26,$F$5:$F$7,$Q$5:$Q$7)","v":3.0388000000000002},{"$f":"LOOKUP(AK$26,$F$5:$F$7,$O$5:$O$7)","v":4},{"$f":"AN68/AS68/3.412","v":0},{"$f":"AN68/AT68/3.412","v":0},{"$f":"(S68-T68)+(AE68-AF68)+(AQ68-AR68)","v":0.21200607902735547},{"$f":"(W68-X68)+(AI68-AJ68)+(AU68-AV68)","v":0},{"$f":"AW68+AX68","v":0.21200607902735547}]
[{"$f":"'Project Info'!A83","v":55},{"$f":"'Project Info'!B83","v":60},{"$f":"'Project Info'!C83","v":57.125792270740902},{"$f":"'Project Info'!D83","v":52.596971157053673},{"$f":"'Project Info'!E83","v":21.818001539159841},{"$f":"'Project Info'!F83","v":0},{"$f":"'Project Info'!G83","v":0},{"$f":"'Project Info'!H83","v":0},{"$f":"'Project Info'!I83","v":0},{"$f":"'Project Info'!J83","v":0},{"$f":"'Project Info'!K83","v":0},{"$f":"'Project Info'!L83","v":0},0,0,3.1137250400306904E-2,4.621452978914351,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,1.3544703924133501,1.3544703924133501,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0,0,11.870000000000001,13,0,0,3.0388000000000002,4,0,0,0.21200607902735547,0,0.21200607902735547]
[{"$f":"'Project Info'!A84","v":50},{"$f":"'Project Info'!B84","v":55},{"$f":"'Project Info'!C84","v":52.235698854337961},{"$f":"'Project Info'!D84","v":48.022768090099298},{"$f":"'Project Info'!E84","v":19.246640192796217},{"$f":"'Project Info'!F84","v":0},{"$f":"'Project Info'!G84","v":0},{"$f":"'Project Info'!H84","v":0},{"$f":"'Project Info'!I84","v":0},{"$f":"'Project Info'!J84","v":0},{"$f":"'Project Info'!K84","v":0},{"$f":"'Project Info'!L84","v":0},0,0,8.4113262411338763E-2,12.484258633615722,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,3.6589269148932355,3.6589269148932355,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,3.7695015622664307E-2,23.370909686051871,11.870000000000001,13,0,0,3.0388000000000002,4,2.2540548343468121,1.712405457653273,0.21200607902735547,0.54164937669353908,0.75365545572089454]
[{"$f":"'Project Info'!A85","v":45},{"$f":"'Project Info'!B85","v":50},{"$f":"'Project Info'!C85","v":47.459170258371508},{"$f":"'Project Info'!D85","v":43.465397050422162},{"$f":"'Project Info'!E85","v":16.894183241713304},{"$f":"'Project Info'!F85","v":0},{"$f":"'Project Info'!G85","v":0},{"$f":"'Project Info'!H85","v":0},{"$f":"'Project Info'!I85","v":0},{"$f":"'Project Info'!J85","v":0},{"$f":"'Project Info'!K85","v":0},{"$f":"'Project Info'!L85","v":0},0,0,0.13585898886764203,20.164462845713164,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,5.909866015742427,5.909866015742427,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.10282949647675232,63.754287815586444,11.870000000000001,13,0,0,3.0388000000000002,4,6.1489117279344283,4.6713282397117855,0.21200607902735547,1.4775834882226428,1.6895895672499983]
[{"$f":"'Project Info'!A86","v":40},{"$f":"'Project Info'!B86","v":45},{"$f":"'Project Info'!C86","v":42.677030404888129},{"$f":"'Project Info'!D86","v":38.812544504634097},{"$f":"'Project Info'!E86","v":14.690265649465921},{"$f":"'Project Info'!F86","v":0},{"$f":"'Project Info'!G86","v":0},{"$f":"'Project Info'!H86","v":0},{"$f":"'Project Info'!I86","v":0},{"$f":"'Project Info'!J86","v":0},{"$f":"'Project Info'!K86","v":0},{"$f":"'Project Info'!L86","v":0},0,0,0.18766550394704523,27.853689426828346,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,8.1634494216964661,8.1634494216964661,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.16804049447879832,104.18510657685496,11.870000000000001,13,0,0,3.0388000000000002,4,10.048344129567766,7.6337270352326323,0.21200607902735547,2.4146170943351342,2.6266231733624896]
[{"$f":"'Project Info'!A87","v":35},{"$f":"'Project Info'!B87","v":40},{"$f":"'Project Info'!C87","v":37.333046773755832},{"$f":"'Project Info'!D87","v":33.904706919479686},{"$f":"'Project Info'!E87","v":12.53841602318813},{"$f":"'Project Info'!F87","v":0},{"$f":"'Project Info'!G87","v":0},{"$f":"'Project Info'!H87","v":0},{"$f":"'Project Info'!I87","v":0},{"$f":"'Project Info'!J87","v":0},{"$f":"'Project Info'!K87","v":0},{"$f":"'Project Info'!L87","v":0},0,0,0.24555865995097842,36.446307427244115,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,10.681801707867558,10.681801707867558,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.24091299853969328,149.36605909460982,11.870000000000001,13,0,0,3.0388000000000002,4,14.405912825484597,10.94417197352065,0.21200607902735547,3.4617408519639472,3.6737469309913027]
[{"$f":"'Project Info'!A88","v":30},{"$f":"'Project Info'!B88","v":35},{"$f":"'Project Info'!C88","v":32.638179845662044},{"$f":"'Project Info'!D88","v":29.547170928664851},{"$f":"'Project Info'!E88","v":10.728972818165861},{"$f":"'Project Info'!F88","v":0},{"$f":"'Project Info'!G88","v":0},{"$f":"'Project Info'!H88","v":0},{"$f":"'Project Info'!I88","v":0},{"$f":"'Project Info'!J88","v":0},{"$f":"'Project Info'!K88","v":0},{"$f":"'Project Info'!L88","v":0},0,0,0.29641971833866115,43.995207435260767,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,12.894257747731759,12.894257747731759,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.30493391119551766,189.05902494122094,11.870000000000001,13,0,0,3.0388000000000002,4,18.234181504709944,13.852507689128146,0.21200607902735547,4.3816738155817987,4.5936798946091546]
[{"$f":"'Project Info'!A89","v":25},{"$f":"'Project Info'!B89","v":30},{"$f":"'Project Info'!C89","v":27.529264646850947},{"$f":"'Project Info'!D89","v":24.652717392657845},{"$f":"'Project Info'!E89","v":8.8041305482613303},{"$f":"'Project Info'!F89","v":0},{"$f":"'Project Info'!G89","v":0},{"$f":"'Project Info'!H89","v":0},{"$f":"'Project Info'!I89","v":0},{"$f":"'Project Info'!J89","v":0},{"$f":"'Project Info'!K89","v":0},{"$f":"'Project Info'!L89","v":0},0,0,0.35176629965911471,52.209857728005126,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,15.301834035171487,15.301834035171487,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.3746009366338508,232.25258071298751,11.870000000000001,13,0,0,3.0388000000000002,4,22.400071686472341,17.017334460213036,0.21200607902735547,5.3827372262593052,5.5947433052866611]
[{"$f":"'Project Info'!A90","v":20},{"$f":"'Project Info'!B90","v":25},{"$f":"'Project Info'!C90","v":22.998111483544687},{"$f":"'Project Info'!D90","v":20.383306659827422},{"$f":"'Project Info'!E90","v":7.246164547543378},{"$f":"'Project Info'!F90","v":0},{"$f":"'Project Info'!G90","v":0},{"$f":"'Project Info'!H90","v":0},{"$f":"'Project Info'!I90","v":0},{"$f":"'Project Info'!J90","v":0},{"$f":"'Project Info'!K90","v":0},{"$f":"'Project Info'!L90","v":0},0,0,0.40085379226159917,59.49552155505107,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,17.437139963379561,17.437139963379561,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.43638938886075435,270.56142109366772,11.870000000000001,13,0,0,3.0388000000000002,4,26.094845574962768,19.824254183299217,0.21200607902735547,6.270591391663551,6.4825974706909069]
[{"$f":"'Project Info'!A91","v":15},{"$f":"'Project Info'!B91","v":20},{"$f":"'Project Info'!C91","v":17.808510327474309},{"$f":"'Project Info'!D91","v":15.420865796304254},{"$f":"'Project Info'!E91","v":5.5490484131518292},{"$f":"'Project Info'!F91","v":0},{"$f":"'Project Info'!G91","v":0},{"$f":"'Project Info'!H91","v":0},{"$f":"'Project Info'!I91","v":0},{"$f":"'Project Info'!J91","v":0},{"$f":"'Project Info'!K91","v":0},{"$f":"'Project Info'!L91","v":0},0,0,0.45707447145236157,67.839907201902406,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,19.882739508177725,19.882739508177725,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.50715667735262304,314.43713995862629,11.870000000000001,13,0,0,3.0388000000000002,4,30.326528361235553,23.039063596030648,0.21200607902735547,7.2874647652049056,7.4994708442322615]
[{"$f":"'Project Info'!A92","v":10},{"$f":"'Project Info'!B92","v":15},{"$f":"'Project Info'!C92","v":12.269931130346862},{"$f":"'Project Info'!D92","v":10.318264913023604},{"$f":"'Project Info'!E92","v":3.9082824916941998},{"$f":"'Project Info'!F92","v":0},{"$f":"'Project Info'!G92","v":0},{"$f":"'Project Info'!H92","v":0},{"$f":"'Project Info'!I92","v":0},{"$f":"'Project Info'!J92","v":0},{"$f":"'Project Info'!K92","v":0},{"$f":"'Project Info'!L92","v":0},0,0,0.51707574608790896,76.745416385859627,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,22.492794954824038,22.492794954824038,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.58268275731345187,361.26330953434018,11.870000000000001,13,0,0,3.0388000000000002,4,34.842773356571556,26.470054918987412,0.21200607902735547,8.3727184375841439,8.5847245166114998]
[{"$f":"'Project Info'!A93","v":5},{"$f":"'Project Info'!B93","v":10},{"$f":"'Project Info'!C93","v":7.3137581369917548},{"$f":"'Project Info'!D93","v":5.7052382449247707},{"$f":"'Project Info'!E93","v":2.5019418419888937},{"$f":"'Project Info'!F93","v":0},{"$f":"'Project Info'!G93","v":0},{"$f":"'Project Info'!H93","v":0},{"$f":"'Project Info'!I93","v":0},{"$f":"'Project Info'!J93","v":0},{"$f":"'Project Info'!K93","v":0},{"$f":"'Project Info'!L93","v":0},0,0,0.5707676201825892,84.714471722740257,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,24.828391477942628,24.828391477942628,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.65026693449556694,403.16549938725149,11.870000000000001,13,0,0,3.0388000000000002,4,38.884115130445331,29.540262264599317,0.21200607902735547,9.3438528658460136,9.5558589448733695]
[{"$f":"'Project Info'!A94","v":0},{"$f":"'Project Info'!B94","v":5},{"$f":"'Project Info'!C94","v":2.6119461836144886},{"$f":"'Project Info'!D94","v":1.2699770062067783},{"$f":"'Project Info'!E94","v":1.2046477897733283},{"$f":"'Project Info'!F94","v":8760},{"$f":"'Project Info'!G94","v":2672},{"$f":"'Project Info'!H94","v":3160},{"$f":"'Project Info'!I94","v":1344},{"$f":"'Project Info'!J94","v":1584},{"$f":"'Project Info'!K94","v":88},{"$f":"'Project Info'!L94","v":264},0,0,0.62170391634417632,92.274538671635341,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,27.044120360971668,27.044120360971668,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.7143825520416206,442.9171822658048,11.870000000000001,13,0,0,3.0388000000000002,4,42.71804689302882,32.452900224634,0.21200607902735547,10.26514666839482,10.477152747422176]
[{"$f":"'Project Info'!A95","v":-5},{"$f":"'Project Info'!B95","v":0},{"$f":"'Project Info'!C95","v":-1.6731398516793925},{"$f":"'Project Info'!D95","v":-2.7083318773557807},{"$f":"'Project Info'!E95","v":7.9391832815876459E-2},{"$f":"'Project Info'!F95","v":0},{"$f":"'Project Info'!G95","v":0},{"$f":"'Project Info'!H95","v":0},{"$f":"'Project Info'!I95","v":0},{"$f":"'Project Info'!J95","v":0},{"$f":"'Project Info'!K95","v":0},{"$f":"'Project Info'!L95","v":0},0,0,0.66812568172652664,99.164549933214531,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,29.063467155103901,29.063467155103901,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.77281554343199166,479.1456369278348,11.870000000000001,13,0,0,3.0388000000000002,4,46.21217375710205,35.107388403270427,0.21200607902735547,11.104785353831623,11.316791432858979]
[{"$f":"'Project Info'!A96","v":-10},{"$f":"'Project Info'!B96","v":-5},{"$f":"'Project Info'!C96","v":-6.5729865085377277},{"$f":"'Project Info'!D96","v":-7.2465935998252222},{"$f":"'Project Info'!E96","v":-1.168423365310433},{"$f":"'Project Info'!F96","v":0},{"$f":"'Project Info'!G96","v":0},{"$f":"'Project Info'!H96","v":0},{"$f":"'Project Info'!I96","v":0},{"$f":"'Project Info'!J96","v":0},{"$f":"'Project Info'!K96","v":0},{"$f":"'Project Info'!L96","v":0},0,0,0.72120735384249191,107.04303787201033,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,31.372519892148389,31.372519892148389,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.83963163420733267,520.5716132085463,11.870000000000001,13,0,0,3.0388000000000002,4,50.207586146154348,38.142703195233466,0.21200607902735547,12.064882950920882,12.276889029948238]
[{"$f":"'Project Info'!A97","v":-15},{"$f":"'Project Info'!B97","v":-10},{"$f":"'Project Info'!C97","v":-15.32570353422995},{"$f":"'Project Info'!D97","v":-15.707838211108999},{"$f":"'Project Info'!E97","v":-3.4051318156661381},{"$f":"'Project Info'!F97","v":0},{"$f":"'Project Info'!G97","v":0},{"$f":"'Project Info'!H97","v":0},{"$f":"'Project Info'!I97","v":0},{"$f":"'Project Info'!J97","v":0},{"$f":"'Project Info'!K97","v":0},{"$f":"'Project Info'!L97","v":0},0,0,0.81602845495415766,121.11657534120599,5.8480769230769241,6.6490304413192236,0,0,1.0000000000000002,1.0000000000000002,35.497237790505849,35.497237790505849,0.6,32.4,0,0,13.16,14.4,2.4620060790273555,2.25,1,1,0,0,0,0,0.95898686637586295,594.57185715303501,11.870000000000001,13,0,0,3.0388000000000002,4,57.344689915181682,43.56476092856353,0.21200607902735547,13.779928986618152,13.991935065645508]

{"sheet":"High Efficiency VRF Systems","index":33,"n_rows":148,"n_cols":38,"rows_kept":148,"cut":false,"hidden":true,"merged":[[17,29,17,30],[19,7,19,8],[20,7,20,8],[21,7,21,8],[22,7,22,8],[28,7,28,8],[23,7,23,8],[24,7,24,8],[25,7,25,8],[26,7,26,8],[27,7,27,8]]}
["Savings Summary",null,null,null,null,"Measure Summary",null,null,null,"Measure Description",null,null,null,null,null,null,null,null,null,null,"Review Notes"]
["Annual kWh Savings",null,null,{"$f":"SUM(A14:D14)","v":46382.788347077643},null,"Annual kWh Savings",null,{"$f":"D2","v":46382.788347077643},null,null,null,null,null,null,null,null,null,null,null,null,"Assumes the same HVAC/OAT dependent load profile for all systems"]
["% On Peak",null,null,{"$f":"IF(D2<=0,0,MIN(1,A15+C15))","v":0.45844748858447482},null,"Annual Therms Savings",null,{"$f":"D7","v":463.82788347077638},null,null,null,null,null,null,null,null,null,null,null,null,"Savings based on weighted avg (by capacity) of cooling and heating performance for base and proposed equipment"]
["Max kW",null,null,{"$f":"MAX(AF37:AF60,AF67:AF90)","v":22.073020628169189},null,"Incremental Cost",null,45000]
["Summer kW",null,null,{"$f":"(SUMPRODUCT(Q37:Q60,AF37:AF60)+SUMPRODUCT(Q67:Q90,AF67:AF90))/SUM(Q37:Q60,Q67:Q90)","v":5.294838852406123},null,"Incentive",null,{"$f":"IF(AND($C$22>0,$C$23>0),MIN(H4,MAX(0,H2*C22+H3*C23)),\"TBD\")","v":"TBD"},null,"Measure Instructions"]
["Winter kW",null,null,{"$f":"(SUMPRODUCT(P37:P60,AF37:AF60)+SUMPRODUCT(P67:P90,AF67:AF90))/SUM(P37:P60,P67:P90)","v":5.294838852406123},null,"Custom Payback (years)",null,{"$f":"H4/(H2*$B$18+H3*$B$19)","v":{"$error":"#N/A"}}]
["Annual therms Savings",null,null,{"$f":"(SUMPRODUCT($K$37:$K$60,AE37:AE60)+SUMPRODUCT($K$67:$K$90,AE67:AE90))/100","v":463.82788347077638}]
["Incremental Cost",null,null,45000]
[]
["kWh Savings by Peak Period"]
["Winter","Winter","Summer","Summer"]
["On-Peak","Off-Peak","On-Peak","Off-Peak"]
["kWh","kWh","kWh","kWh"]
[{"$f":"SUMPRODUCT($AF$37:$AF$60,L37:L60)+SUMPRODUCT($AF$67:$AF$90,L67:L90)","v":14147.80941362916},{"$f":"SUMPRODUCT($AF$37:$AF$60,M37:M60)+SUMPRODUCT($AF$67:$AF$90,M67:M90)","v":16731.69077360335},{"$f":"SUMPRODUCT($AF$37:$AF$60,N37:N60)+SUMPRODUCT($AF$67:$AF$90,N67:N90)","v":7116.2634176338288},{"$f":"SUMPRODUCT($AF$37:$AF$60,O37:O60)+SUMPRODUCT($AF$67:$AF$90,O67:O90)","v":8387.0247422112989},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"User Inputs - Chiller/Loop Parameters"]
[{"$f":"IF(A14<=0,0,A14/SUMIF($A$14:$D$14,\">0\"))","v":0.30502283105022826},{"$f":"IF(B14<=0,0,B14/SUMIF($A$14:$D$14,\">0\"))","v":0.36073059360730592},{"$f":"IF(C14<=0,0,C14/SUMIF($A$14:$D$14,\">0\"))","v":0.15342465753424656},{"$f":"IF(D14<=0,0,D14/SUMIF($A$14:$D$14,\">0\"))","v":0.18082191780821916},null,"User Inputs",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Incentive Type",null,null,"Custom"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Proposed/Design Performance",null,null,null,null,"Baseline Performance",null,null,null,null,null,null,null,null,"Chiller Quantity",null,null,2,null,null,null,null,"Baseline Code IECC Version",null,null,{"$f":"_xlfn.NUMBERVALUE(MID('Project Info'!C20,1,4))","v":2018}]
["Utility Rates",null,null,null,null,null,"Outdoor","VRF",null,"VRF","Cooling","Heating","Cooling",null,"Heating",null,null,"Cooling",null,"Heating",null,null,null,null,null,null,"Capacity, tons (per Chiller)",null,null,250,null,null,null,null,null,"Base Case Chiler Performace"]
["Elec Rate",{"$f":"'ECM Summary'!$E$31","v":0.1593},"per kWh",null,null,"Line","Unit","Type",null,"Heat","Capacity","Capacity","Full Load",null,"COP","COP",null,"Full Load",null,"COP","COP",null,null,null,null,null,"Chiller Type",null,null,"Water-Cooled Non-Centrifugal",null,null,null,null,null,null,"kW/ton","EER"]
["Gas Rate",{"$f":"'ECM Summary'!$E$32","v":{"$error":"#N/A"}},"per therm",null,null,"#","Tag/#",null,null,"Recovery?","MBH","MBH","EER","IEER","47°F","17°F",null,"EER","IEER","47°F","17°F",null,null,null,null,null,"Design AHRI Full Load Perf.",null,null,0.5,{"$f":"IF(AD18=\"Air-Cooled\", \"EER\", \"kW/ton\")","v":"kW/ton"},"< Units based on Chiller Type",null,null,null,"FL",{"$f":"IF(AD18=G94,OFFSET($G$111,MATCH($AD$17,$G$112:$G$112,-1),MATCH($AL$16,$H$111:$I$111,0)),IF(AD18=G95,OFFSET(#REF!,MATCH($AD$17,#REF!,-1),MATCH($AL$16,#REF!,0)),OFFSET(#REF!,MATCH($AD$17,#REF!,-1),MATCH($AL$16,#REF!,0))))","v":{"$error":"#REF!"}},{"$f":"12/AK19","v":{"$error":"#REF!"}}]
["Fossil Fuel",null,{"$f":"'Project Info'!C21","v":0},null,null,1,"HP-A","HP Air-Cooled",null,"No",250,320,13,18,3.6,2.2999999999999998,null,{"$f":"IF($H20=\"\",\"\",OFFSET($H$116,MATCH($H20,$G$117:$G$121,0),MATCH($K20,$I$115:$L$115,1))-IF(AND($H20=$G$94,$K20<$I$116),0,IF($J20=\"Yes\",0.2,0)))","v":9.5},{"$f":"IF($H20=\"\",\"\",OFFSET($H$125,MATCH($H20,$G$126:$G$130,0),MATCH($K20,$I$124:$L$124,1))-IF(AND($H20=$G$94,$K20<$I$125),0,IF($J20=\"Yes\",0.2,0)))","v":10.6},{"$f":"IF($H20=\"\",\"\",OFFSET($H$134,MATCH($H20,$G$135:$G$139,0),MATCH($L20,$I$133:$L$133,1)))","v":3.2},{"$f":"IF($H20=\"\",\"\",OFFSET($H$143,MATCH($H20,$G$144:$G$148,0),MATCH($L20,$I$142:$L$142,1)))","v":2.0499999999999998},null,null,null,null,null,"Design AHRI IEER/IPLV",null,null,0.44,{"$f":"IF(AD18=\"Air-Cooled\", \"EER\", \"kW/ton\")","v":"kW/ton"},"< Units based on Chiller Type",null,null,null,"IPLV",{"$f":"IF(AD18=G94,OFFSET($K$110,MATCH($AD$17,$K$111:$K$112,-1),MATCH($AL$16,$L$110:$M$110,0)),IF(AD18=G95,OFFSET(#REF!,MATCH($AD$17,#REF!,-1),MATCH($AL$16,$M$116:$M$116,0)),OFFSET(#REF!,MATCH($AD$17,#REF!,-1),MATCH($AL$16,$M$125:$M$125,0))))","v":{"$error":"#REF!"}},{"$f":"12/AK20","v":{"$error":"#REF!"}}]
["Fuel Conversion",null,{"$f":"LOOKUP(C20,'Project Info'!X102:X104,'Project Info'!Z102:Z104)","v":{"$error":"#N/A"}},null,null,2,"HP-B","HP Air-Cooled",null,"No",134,80,12,17,3.5,2.5,null,{"$f":"IF(H21=\"\",\"\",OFFSET($H$116,MATCH($H21,$G$117:$G$121,0),MATCH($K21,$I$115:$L$115,1))-IF(AND($H21=$G$94,$K21<$I$116),0,IF(J21=\"Yes\",0.2,0)))","v":11},12.3,3.3,2.25,null,null,null,null,null,"Max # of Operating Chillers",null,null,null,{"$f":"MAX(1,AD16-1)","v":1},"< Default is N+1 redundancy; if unsure, leave input blank or enter this default value"]
["Elec $/kWh Saved",null,{"$f":"'ECM Summary'!$J$31","v":0.28000000000000003},null,null,3,"HP-Ba","HP Air-Cooled",null,"No",60,66,12,17,3.5,2.5,null,11.1,13,3.3,2.25,null,null,null,null,null,"Peak Plant Load % (@95°F OAT)",null,null,null,0.85,"< Default Peak Plant Load %; if unsure, leave input blank or enter this default value"]
["Gas $/therm Saved",null,{"$f":"'ECM Summary'!$J$32","v":0},null,null,4,null,null,null,null,null,null,null,null,null,null,null,"","","","",null,null,null,null,null,"(% of max operating capacity)"]
[null,null,null,null,null,5,null,null,null,null,null,null,null,null,null,null,null,"","","","",null,null,null,null,null,"Design CHW Temperature",null,null,42]
[null,null,null,null,null,6,null,null,null,null,null,null,null,null,null,null,null,"","","","",null,null,null,null,null,"Design CHW Loop dT",null,null,12]
[null,null,null,null,null,7,null,null,null,null,null,null,null,null,null,null,null,"","","","",null,null,null,null,null,"Design Condenser Fluid Temp(°F)",null,null,95]
[null,null,null,null,null,8,null,null,null,null,null,null,null,null,null,null,null,"","","","",null,null,null,null,null,"Min Condenser Fluid Temp (°F)",null,null,65]
[null,null,null,null,null,9,null,null,null,null,null,null,null,null,null,null,null,"","","","",null,null,null,null,null,"*Cap Ratio = % of Peak Load from 1 Chiller"]
[null,null,null,null,null,10,null,null,null,null,null,null,null,null,null,null,null,"","","",""]
[null,null,null,null,null,"Total or Weighted Avg.",null,null,null,null,{"$f":"SUM(K20:K29)","v":444},{"$f":"SUM(L20:L29)","v":466},{"$f":"SUMPRODUCT(M20:M29,$K$20:$K$29)/SUM($K$20:$K$29)","v":12.563063063063064},{"$f":"SUMPRODUCT(N20:N29,$K$20:$K$29)/SUM($K$20:$K$29)","v":17.563063063063062},{"$f":"SUMPRODUCT(O20:O29,$L$20:$L$29)/SUM($L$20:$L$29)","v":3.5686695278969958},{"$f":"SUMPRODUCT(P20:P29,$L$20:$L$29)/SUM($L$20:$L$29)","v":2.3626609442060085},null,{"$f":"SUMPRODUCT(R20:R29,$K$20:$K$29)/SUM($K$20:$K$29)","v":10.168918918918919},{"$f":"SUMPRODUCT(S20:S29,$K$20:$K$29)/SUM($K$20:$K$29)","v":11.437387387387387},{"$f":"SUMPRODUCT(T20:T29,$L$20:$L$29)/SUM($L$20:$L$29)","v":3.2313304721030041},{"$f":"SUMPRODUCT(U20:U29,$L$20:$L$29)/SUM($L$20:$L$29)","v":2.1126609442060085}]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Line#","Tag"]
[null,null,null,null,null,"Occupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown",null,null,null,null,null,null,1,{"$f":"LOOKUP(R33,$F$20:$F$29,$G$20:$G$29)","v":"HP-A"},null,null,"Cooling Demand",null,null,null,"Heating Demand",null,null,null,"Demand Savings"]
[null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Cooling","Cooling","Heating","Heating","Base","Proposed","Base","Design","Base","Proposed","Base","Design","Cooling","Heating","Total"]
[null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Load","Load","Load","Load","Perf","Perf","Demand","Demand","Perf","Perf","Demand","Demand","Savings","Savings","Savings"]
[null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","%","MBH","%","MBH","EER","EER","kW","kW","COP","COP","kW","kW","kW","kW","kW"]
[null,null,null,null,null,{"$f":"'Project Info'!A44","v":100},{"$f":"'Project Info'!B44","v":105},{"$f":"'Project Info'!C44","v":102},{"$f":"'Project Info'!D44","v":76},{"$f":"'Project Info'!E44","v":40},{"$f":"'Project Info'!F44","v":0},{"$f":"'Project Info'!G44","v":0},{"$f":"'Project Info'!H44","v":0},{"$f":"'Project Info'!I44","v":0},{"$f":"'Project Info'!J44","v":0},{"$f":"'Project Info'!K44","v":0},{"$f":"'Project Info'!L44","v":0},{"$f":"MAX(0,MIN(1,TREND($T$97:$U$97,$R$97:$S$97,H37)))*(H37>=$S$97)","v":1},{"$f":"$K$30*R37","v":444},{"$f":"MAX(0,MIN(1,TREND($AC$97:$AD$97,$AA$97:$AB$97,H37)))*(H37<=$AA$97)","v":0},{"$f":"$L$30*T37","v":0},{"$f":"OFFSET($R$104,MATCH($H37,$R$105:$R$115,-1),MATCH(R37,$S$104:$W$104,-1))*(R37>0)","v":10.168918918918919},{"$f":"OFFSET($R$118,MATCH($H37,$R$119:$R$129,-1),MATCH(R37,$S$118:$W$118,-1))*(R37>0)","v":12.563063063063064},{"$f":"IF(S37>0,S37/V37,0)","v":43.662458471760793},{"$f":"IF(S37>0,S37/W37,0)","v":35.341699533883109},{"$f":"MIN($H$111,TREND($H$111:$I$111,$H$110:$I$110,$H37))*(T37>0)","v":0},{"$f":"MIN($H$112,TREND($H$112:$I$112,$H$110:$I$110,$H37))*(T37>0)","v":0},{"$f":"IF(U37>0,U37/Z37/3.412,0)","v":0},{"$f":"IF(U37>0,U37/AA37/3.412,0)","v":0},{"$f":"X37-Y37","v":8.3207589378776845},{"$f":"AB37-AC37","v":0},{"$f":"AD37+AE37","v":8.3207589378776845}]
[null,null,null,null,null,{"$f":"'Project Info'!A45","v":95},{"$f":"'Project Info'!B45","v":100},{"$f":"'Project Info'!C45","v":95.219272727272724},{"$f":"'Project Info'!D45","v":74.534025272781079},{"$f":"'Project Info'!E45","v":37.923296058061368},{"$f":"'Project Info'!F45","v":0},{"$f":"'Project Info'!G45","v":0},{"$f":"'Project Info'!H45","v":0},{"$f":"'Project Info'!I45","v":0},{"$f":"'Project Info'!J45","v":0},{"$f":"'Project Info'!K45","v":0},{"$f":"'Project Info'!L45","v":0},{"$f":"MAX(0,MIN(1,TREND($T$97:$U$97,$R$97:$S$97,H38)))*(H38>=$S$97)","v":0.95389818181818165},{"$f":"$K$30*R38","v":423.53079272727263},{"$f":"MAX(0,MIN(1,TREND($AC$97:$AD$97,$AA$97:$AB$97,H38)))*(H38<=$AA$97)","v":0},{"$f":"$L$30*T38","v":0},10.168918918918919,12.563063063063064,{"$f":"IF(S38>0,S38/V38,0)","v":41.649539749924486},{"$f":"IF(S38>0,S38/W38,0)","v":33.712382927735575},0,0,{"$f":"IF(U38>0,U38/Z38/3.412,0)","v":0},{"$f":"IF(U38>0,U38/AA38/3.412,0)","v":0},{"$f":"X38-Y38","v":7.9371568221889106},{"$f":"AB38-AC38","v":0},{"$f":"AD38+AE38","v":7.9371568221889106}]
[null,null,null,null,null,{"$f":"'Project Info'!A46","v":90},{"$f":"'Project Info'!B46","v":95},{"$f":"'Project Info'!C46","v":92.016049160256074},{"$f":"'Project Info'!D46","v":72.911561930607689},{"$f":"'Project Info'!E46","v":36.467095439351091},{"$f":"'Project Info'!F46","v":0},{"$f":"'Project Info'!G46","v":0},{"$f":"'Project Info'!H46","v":0},{"$f":"'Project Info'!I46","v":0},{"$f":"'Project Info'!J46","v":0},{"$f":"'Project Info'!K46","v":0},{"$f":"'Project Info'!L46","v":0},0.89695198507121898,398.24668137162121,0,0,10.168918918918919,12.563063063063064,39.163128799335503,31.699807552707028,0,0,0,0,7.4633212466284746,0,7.4633212466284746]
[null,null,null,null,null,{"$f":"'Project Info'!A47","v":85},{"$f":"'Project Info'!B47","v":90},{"$f":"'Project Info'!C47","v":87.457811360655285},{"$f":"'Project Info'!D47","v":70.80538329449476},{"$f":"'Project Info'!E47","v":34.679413213566804},{"$f":"'Project Info'!F47","v":0},{"$f":"'Project Info'!G47","v":0},{"$f":"'Project Info'!H47","v":0},{"$f":"'Project Info'!I47","v":0},{"$f":"'Project Info'!J47","v":0},{"$f":"'Project Info'!K47","v":0},{"$f":"'Project Info'!L47","v":0},0.81591664641164952,362.2669910067724,0,0,10.42966042966043,12.885192885192886,34.734303523107812,28.114983938119714,0,0,0,0,6.6193195849880979,0,6.6193195849880979]
[null,null,null,null,null,{"$f":"'Project Info'!A48","v":80},{"$f":"'Project Info'!B48","v":85},{"$f":"'Project Info'!C48","v":82.136788830239965},{"$f":"'Project Info'!D48","v":67.872393622439333},{"$f":"'Project Info'!E48","v":32.296248223809314},{"$f":"'Project Info'!F48","v":0},{"$f":"'Project Info'!G48","v":0},{"$f":"'Project Info'!H48","v":0},{"$f":"'Project Info'!I48","v":0},{"$f":"'Project Info'!J48","v":0},{"$f":"'Project Info'!K48","v":0},{"$f":"'Project Info'!L48","v":0},0.72132069031537716,320.26638650002747,0,0,10.80972588442101,16.599236431553507,29.62761405093498,19.294043302572202,0,0,0,0,10.333570748362778,0,10.333570748362778]
[null,null,null,null,null,{"$f":"'Project Info'!A49","v":75},{"$f":"'Project Info'!B49","v":80},{"$f":"'Project Info'!C49","v":76.988400157585886},{"$f":"'Project Info'!D49","v":65.129261896908645},{"$f":"'Project Info'!E49","v":30.190476812806729},{"$f":"'Project Info'!F49","v":0},{"$f":"'Project Info'!G49","v":0},{"$f":"'Project Info'!H49","v":0},{"$f":"'Project Info'!I49","v":0},{"$f":"'Project Info'!J49","v":0},{"$f":"'Project Info'!K49","v":0},{"$f":"'Project Info'!L49","v":0},0.62979378057930469,279.62843857721128,0,0,11.079969031531533,17.014217342342342,25.237294236242061,16.434986867207549,0,0,0,0,8.8023073690345122,0,8.8023073690345122]
[null,null,null,null,null,{"$f":"'Project Info'!A50","v":70},{"$f":"'Project Info'!B50","v":75},{"$f":"'Project Info'!C50","v":72.457982050814195},{"$f":"'Project Info'!D50","v":63.604425012889301},{"$f":"'Project Info'!E50","v":29.088683095945193},{"$f":"'Project Info'!F50","v":0},{"$f":"'Project Info'!G50","v":0},{"$f":"'Project Info'!H50","v":0},{"$f":"'Project Info'!I50","v":0},{"$f":"'Project Info'!J50","v":0},{"$f":"'Project Info'!K50","v":0},{"$f":"'Project Info'!L50","v":0},0.54925301423669681,243.86833832109338,0,0,11.364070801570804,17.450479325479325,21.459593360451834,13.974879071947491,0,0,0,0,7.4847142885043425,0,7.4847142885043425]
[null,null,null,null,null,{"$f":"'Project Info'!A51","v":65},{"$f":"'Project Info'!B51","v":70},{"$f":"'Project Info'!C51","v":67.815831070966169},{"$f":"'Project Info'!D51","v":61.631331368130574},{"$f":"'Project Info'!E51","v":27.661514889731574},{"$f":"'Project Info'!F51","v":0},{"$f":"'Project Info'!G51","v":0},{"$f":"'Project Info'!H51","v":0},{"$f":"'Project Info'!I51","v":0},{"$f":"'Project Info'!J51","v":0},{"$f":"'Project Info'!K51","v":0},{"$f":"'Project Info'!L51","v":0},0.46672588570606532,207.226293253493,0,0,12.007271099224223,18.438167073323321,17.258400475931762,11.238985547175771,0,0,0,0,6.0194149287559906,0,6.0194149287559906]
[null,null,null,null,null,{"$f":"'Project Info'!A52","v":60},{"$f":"'Project Info'!B52","v":65},{"$f":"'Project Info'!C52","v":62.535961472271332},{"$f":"'Project Info'!D52","v":57.135476922863582},{"$f":"'Project Info'!E52","v":24.623037157728302},{"$f":"'Project Info'!F52","v":0},{"$f":"'Project Info'!G52","v":0},{"$f":"'Project Info'!H52","v":0},{"$f":"'Project Info'!I52","v":0},{"$f":"'Project Info'!J52","v":0},{"$f":"'Project Info'!K52","v":0},{"$f":"'Project Info'!L52","v":0},0.37286153728482374,165.55052255446174,0,0,12.315149845358178,18.910940588023919,13.442834608858696,8.7542193781362183,0,0,0,0,4.688615230722478,0,4.688615230722478]
[null,null,null,null,null,{"$f":"'Project Info'!A53","v":55},{"$f":"'Project Info'!B53","v":60},{"$f":"'Project Info'!C53","v":57.125792270740902},{"$f":"'Project Info'!D53","v":52.596971157053673},{"$f":"'Project Info'!E53","v":21.818001539159841},{"$f":"'Project Info'!F53","v":0},{"$f":"'Project Info'!G53","v":0},{"$f":"'Project Info'!H53","v":0},{"$f":"'Project Info'!I53","v":0},{"$f":"'Project Info'!J53","v":0},{"$f":"'Project Info'!K53","v":0},{"$f":"'Project Info'!L53","v":0},0.27668075147983828,122.84625365704819,8.9193741762623957E-2,41.564283661382767,12.315149845358178,18.910940588023919,9.9752138788105249,6.4960414361856387,3.2313304721030041,3.5686695278969958,3.7699006176127519,3.4135395971144202,3.4791724426248862,0.35636102049833163,3.8355334631232179]
[null,null,null,null,null,{"$f":"'Project Info'!A54","v":50},{"$f":"'Project Info'!B54","v":55},{"$f":"'Project Info'!C54","v":52.235698854337961},{"$f":"'Project Info'!D54","v":48.022768090099298},{"$f":"'Project Info'!E54","v":19.246640192796217},{"$f":"'Project Info'!F54","v":0},{"$f":"'Project Info'!G54","v":0},{"$f":"'Project Info'!H54","v":0},{"$f":"'Project Info'!I54","v":0},{"$f":"'Project Info'!J54","v":0},{"$f":"'Project Info'!K54","v":0},{"$f":"'Project Info'!L54","v":0},0.18974575741045285,84.247116290241067,0.15587683380448225,72.638604552888722,12.514606598786285,19.217223082457455,6.7319028868563615,4.3839380918227722,3.2313304721030041,3.5686695278969958,6.5883565418183236,5.9655726281840229,2.3479647950335893,0.62278391363430075,2.9707487086678901]
[null,null,null,null,null,{"$f":"'Project Info'!A55","v":45},{"$f":"'Project Info'!B55","v":50},{"$f":"'Project Info'!C55","v":47.459170258371508},{"$f":"'Project Info'!D55","v":43.465397050422162},{"$f":"'Project Info'!E55","v":16.894183241713304},{"$f":"'Project Info'!F55","v":0},{"$f":"'Project Info'!G55","v":0},{"$f":"'Project Info'!H55","v":0},{"$f":"'Project Info'!I55","v":0},{"$f":"'Project Info'!J55","v":0},{"$f":"'Project Info'!K55","v":0},{"$f":"'Project Info'!L55","v":0},0,0,0.22101131465857027,102.99127263089375,0,0,0,0,3.2313304721030041,3.5686695278969958,9.3413582070383914,8.4583386579425177,0,0.88301954909587366,0.88301954909587366]
[null,null,null,null,null,{"$f":"'Project Info'!A56","v":40},{"$f":"'Project Info'!B56","v":45},{"$f":"'Project Info'!C56","v":42.677030404888129},{"$f":"'Project Info'!D56","v":38.812544504634097},{"$f":"'Project Info'!E56","v":14.690265649465921},{"$f":"'Project Info'!F56","v":0},{"$f":"'Project Info'!G56","v":0},{"$f":"'Project Info'!H56","v":0},{"$f":"'Project Info'!I56","v":0},{"$f":"'Project Info'!J56","v":0},{"$f":"'Project Info'!K56","v":0},{"$f":"'Project Info'!L56","v":0},0,0,0.28622231266061637,133.37959769984724,0,0,0,0,3.0701313269004422,3.3948849132723269,12.732785636748275,11.514771504995961,0,1.2180141317523141,1.2180141317523141]
[null,null,null,null,null,{"$f":"'Project Info'!A57","v":35},{"$f":"'Project Info'!B57","v":40},{"$f":"'Project Info'!C57","v":37.333046773755832},{"$f":"'Project Info'!D57","v":33.904706919479686},{"$f":"'Project Info'!E57","v":12.53841602318813},{"$f":"'Project Info'!F57","v":0},{"$f":"'Project Info'!G57","v":0},{"$f":"'Project Info'!H57","v":0},{"$f":"'Project Info'!I57","v":0},{"$f":"'Project Info'!J57","v":0},{"$f":"'Project Info'!K57","v":0},{"$f":"'Project Info'!L57","v":0},0,0,0.35909481672151133,167.33818459222428,0,0,0,0,2.8708596053761744,3.1800552422640043,17.083390805453849,15.422378811040991,0,1.6610119944128581,1.6610119944128581]
[null,null,null,null,null,{"$f":"'Project Info'!A58","v":30},{"$f":"'Project Info'!B58","v":35},{"$f":"'Project Info'!C58","v":32.638179845662044},{"$f":"'Project Info'!D58","v":29.547170928664851},{"$f":"'Project Info'!E58","v":10.728972818165861},{"$f":"'Project Info'!F58","v":0},{"$f":"'Project Info'!G58","v":0},{"$f":"'Project Info'!H58","v":0},{"$f":"'Project Info'!I58","v":0},{"$f":"'Project Info'!J58","v":0},{"$f":"'Project Info'!K58","v":0},{"$f":"'Project Info'!L58","v":0},0,0,0.42311572937733577,197.17192988983848,0,0,0,0,2.695792786376511,2.9913202484450698,21.436286750718175,19.318488957952042,0,2.1177977927661331,2.1177977927661331]
[null,null,null,null,null,{"$f":"'Project Info'!A59","v":25},{"$f":"'Project Info'!B59","v":30},{"$f":"'Project Info'!C59","v":27.529264646850947},{"$f":"'Project Info'!D59","v":24.652717392657845},{"$f":"'Project Info'!E59","v":8.8041305482613303},{"$f":"'Project Info'!F59","v":0},{"$f":"'Project Info'!G59","v":0},{"$f":"'Project Info'!H59","v":0},{"$f":"'Project Info'!I59","v":0},{"$f":"'Project Info'!J59","v":0},{"$f":"'Project Info'!K59","v":0},{"$f":"'Project Info'!L59","v":0},0,0,0.49278275481566891,229.6367637441017,0,0,0,0,2.5052865279258514,2.7859403956745519,26.864266817214066,24.157977623737381,0,2.7062891934766853,2.7062891934766853]
[null,null,null,null,null,{"$f":"'Project Info'!A60","v":20},{"$f":"'Project Info'!B60","v":25},{"$f":"'Project Info'!C60","v":22.998111483544687},{"$f":"'Project Info'!D60","v":20.383306659827422},{"$f":"'Project Info'!E60","v":7.246164547543378},{"$f":"'Project Info'!F60","v":0},{"$f":"'Project Info'!G60","v":0},{"$f":"'Project Info'!H60","v":0},{"$f":"'Project Info'!I60","v":0},{"$f":"'Project Info'!J60","v":0},{"$f":"'Project Info'!K60","v":0},{"$f":"'Project Info'!L60","v":0},0,0,0.55457120704257257,258.43018248183881,0,0,0,0,2.3363244289250247,2.6037867420423546,32.419108036029044,29.089000587323135,0,3.3301074487059097,3.3301074487059097]
[null,null,null,null,null,{"$f":"'Project Info'!A61","v":15},{"$f":"'Project Info'!B61","v":20},{"$f":"'Project Info'!C61","v":17.808510327474309},{"$f":"'Project Info'!D61","v":15.420865796304254},{"$f":"'Project Info'!E61","v":5.5490484131518292},{"$f":"'Project Info'!F61","v":0},{"$f":"'Project Info'!G61","v":0},{"$f":"'Project Info'!H61","v":0},{"$f":"'Project Info'!I61","v":0},{"$f":"'Project Info'!J61","v":0},{"$f":"'Project Info'!K61","v":0},{"$f":"'Project Info'!L61","v":0},0,0,0.62533849553444132,291.40773891904968,0,0,0,0,2.1428094730838598,2.3951632907039029,39.857357401777129,35.657995988873637,0,4.1993614129034924,4.1993614129034924]
[null,null,null,null,null,{"$f":"'Project Info'!A62","v":10},{"$f":"'Project Info'!B62","v":15},{"$f":"'Project Info'!C62","v":12.269931130346862},{"$f":"'Project Info'!D62","v":10.318264913023604},{"$f":"'Project Info'!E62","v":3.9082824916941998},{"$f":"'Project Info'!F62","v":0},{"$f":"'Project Info'!G62","v":0},{"$f":"'Project Info'!H62","v":0},{"$f":"'Project Info'!I62","v":0},{"$f":"'Project Info'!J62","v":0},{"$f":"'Project Info'!K62","v":0},{"$f":"'Project Info'!L62","v":0},0,0,0.70086457549527026,326.60289218079595,0,0,0,0,1.9362814805615036,2.1725108222643019,49.435907625175986,44.060462865548025,0,5.3754447596279604,5.3754447596279604]
[null,null,null,null,null,{"$f":"'Project Info'!A63","v":5},{"$f":"'Project Info'!B63","v":10},{"$f":"'Project Info'!C63","v":7.3137581369917548},{"$f":"'Project Info'!D63","v":5.7052382449247707},{"$f":"'Project Info'!E63","v":2.5019418419888937},{"$f":"'Project Info'!F63","v":0},{"$f":"'Project Info'!G63","v":0},{"$f":"'Project Info'!H63","v":0},{"$f":"'Project Info'!I63","v":0},{"$f":"'Project Info'!J63","v":0},{"$f":"'Project Info'!K63","v":0},{"$f":"'Project Info'!L63","v":0},0,0,0.76844875267738533,358.09711874766157,0,0,0,0,1.7514708238064238,1.9732712498561782,59.92235828824704,53.186941350911169,0,6.7354169373358701,6.7354169373358701]
[null,null,null,null,null,{"$f":"'Project Info'!A64","v":0},{"$f":"'Project Info'!B64","v":5},{"$f":"'Project Info'!C64","v":2.6119461836144886},{"$f":"'Project Info'!D64","v":1.2699770062067783},{"$f":"'Project Info'!E64","v":1.2046477897733283},{"$f":"'Project Info'!F64","v":0},{"$f":"'Project Info'!G64","v":0},{"$f":"'Project Info'!H64","v":0},{"$f":"'Project Info'!I64","v":0},{"$f":"'Project Info'!J64","v":0},{"$f":"'Project Info'!K64","v":0},{"$f":"'Project Info'!L64","v":0},0,0,0.83256437022343899,387.97499652412256,0,0,0,0,1.5761450318682573,1.7842570640337159,72.143720932524914,63.729027403273584,0,8.4146935292513305,8.4146935292513305]
[null,null,null,null,null,{"$f":"'Project Info'!A65","v":-5},{"$f":"'Project Info'!B65","v":0},{"$f":"'Project Info'!C65","v":-1.6731398516793925},{"$f":"'Project Info'!D65","v":-2.7083318773557807},{"$f":"'Project Info'!E65","v":7.9391832815876459E-2},{"$f":"'Project Info'!F65","v":0},{"$f":"'Project Info'!G65","v":0},{"$f":"'Project Info'!H65","v":0},{"$f":"'Project Info'!I65","v":0},{"$f":"'Project Info'!J65","v":0},{"$f":"'Project Info'!K65","v":0},{"$f":"'Project Info'!L65","v":0},0,0,0.89099736161381016,415.20477051203551,0,0,0,0,1.4163585261315834,1.6119953793530892,85.917199176077773,75.490016381572076,0,10.427182794505697,10.427182794505697]
[null,null,null,null,null,{"$f":"'Project Info'!A66","v":-10},{"$f":"'Project Info'!B66","v":-5},{"$f":"'Project Info'!C66","v":-6.5729865085377277},{"$f":"'Project Info'!D66","v":-7.2465935998252222},{"$f":"'Project Info'!E66","v":-1.168423365310433},{"$f":"'Project Info'!F66","v":0},{"$f":"'Project Info'!G66","v":0},{"$f":"'Project Info'!H66","v":0},{"$f":"'Project Info'!I66","v":0},{"$f":"'Project Info'!J66","v":0},{"$f":"'Project Info'!K66","v":0},{"$f":"'Project Info'!L66","v":0},0,0,0.95781345238915105,446.34106881334441,0,0,0,0,1.2336482212517372,1.4150201417883979,106.0392114971124,92.447507129486198,0,13.591704367626207,13.591704367626207]
[null,null,null,null,null,{"$f":"'Project Info'!A67","v":-15},{"$f":"'Project Info'!B67","v":-10},{"$f":"'Project Info'!C67","v":-15.32570353422995},{"$f":"'Project Info'!D67","v":-15.707838211108999},{"$f":"'Project Info'!E67","v":-3.4051318156661381},{"$f":"'Project Info'!F67","v":0},{"$f":"'Project Info'!G67","v":0},{"$f":"'Project Info'!H67","v":0},{"$f":"'Project Info'!I67","v":0},{"$f":"'Project Info'!J67","v":0},{"$f":"'Project Info'!K67","v":0},{"$f":"'Project Info'!L67","v":0},0,0,1,466,0,0,0,0,0.90726829382016683,1.0631584130016289,150.53627327001996,128.46325264185077,0,22.073020628169189,22.073020628169189]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Line#","Tag"]
[null,null,null,null,null,"Unoccupied Hours",null,null,null,null,"Bin Hours - Peak Period Breakdown",null,null,null,null,null,null,1,{"$f":"LOOKUP(R63,$F$20:$F$29,$G$20:$G$29)","v":"HP-A"},null,null,"Cooling Demand",null,null,null,"Heating Demand",null,null,null,"Demand Savings"]
[null,null,null,null,null,"OA Drybulb",null,"Average Bin Conditions",null,null,"Total","Winter","Winter","Summer","Summer","Winter","Summer","Cooling","Cooling","Heating","Heating","Base","Proposed","Base","Design","Base","Proposed","Base","Design","Cooling","Heating","Total"]
[null,null,null,null,null,"Bin Range",null,"OA db","OA wb","OA Enth","Bin","On-Peak","Off-Peak","On-Peak","Off-Peak","Demand","Demand","Load","Load","Load","Load","Perf","Perf","Demand","Demand","Perf","Perf","Demand","Demand","Savings","Savings","Savings"]
[null,null,null,null,null,"From","To","°F","°F","Btu/lb","Hours","Hours","Hours","Hours","Hours","Hours","Hours","%","MBH","%","MBH","EER","EER","kW","kW","COP","COP","kW","kW","kW","kW","kW"]
[null,null,null,null,null,{"$f":"'Project Info'!A74","v":100},{"$f":"'Project Info'!B74","v":105},{"$f":"'Project Info'!C74","v":102},{"$f":"'Project Info'!D74","v":76},{"$f":"'Project Info'!E74","v":40},{"$f":"'Project Info'!F74","v":0},{"$f":"'Project Info'!G74","v":0},{"$f":"'Project Info'!H74","v":0},{"$f":"'Project Info'!I74","v":0},{"$f":"'Project Info'!J74","v":0},{"$f":"'Project Info'!K74","v":0},{"$f":"'Project Info'!L74","v":0},{"$f":"MAX(0,MIN(1,TREND($X$97:$Y$97,$V$97:$W$97,H67)))*(H67>=$W$97)","v":0.53166666666666662},{"$f":"$K$30*R67","v":236.05999999999997},{"$f":"MAX(0,MIN(1,TREND($AG$97:$AH$97,$AE$97:$AF$97,H67)))*(H67<=$AE$97)","v":0},{"$f":"$L$30*T67","v":0},{"$f":"OFFSET($R$104,MATCH($H67,$R$105:$R$115,-1),MATCH(R67,$S$104:$W$104,-1))*(R67>0)","v":10.306947936308402},{"$f":"OFFSET($R$118,MATCH($H67,$R$119:$R$129,-1),MATCH(R67,$S$118:$W$118,-1))*(R67>0)","v":15.827178923109155},{"$f":"IF(S67>0,S67/V67,0)","v":22.902997226601752},{"$f":"IF(S67>0,S67/W67,0)","v":14.914850027715955},{"$f":"MIN($H$111,TREND($H$111:$I$111,$H$110:$I$110,$H67))*(T67>0)","v":0},{"$f":"MIN($H$112,TREND($H$112:$I$112,$H$110:$I$110,$H67))*(T67>0)","v":0},{"$f":"IF(U67>0,U67/Z67/3.412,0)","v":0},{"$f":"IF(U67>0,U67/AA67/3.412,0)","v":0},{"$f":"X67-Y67","v":7.9881471988857964},{"$f":"AB67-AC67","v":0},{"$f":"AD67+AE67","v":7.9881471988857964}]
[null,null,null,null,null,{"$f":"'Project Info'!A75","v":95},{"$f":"'Project Info'!B75","v":100},{"$f":"'Project Info'!C75","v":95.219272727272724},{"$f":"'Project Info'!D75","v":74.534025272781079},{"$f":"'Project Info'!E75","v":37.923296058061368},{"$f":"'Project Info'!F75","v":0},{"$f":"'Project Info'!G75","v":0},{"$f":"'Project Info'!H75","v":0},{"$f":"'Project Info'!I75","v":0},{"$f":"'Project Info'!J75","v":0},{"$f":"'Project Info'!K75","v":0},{"$f":"'Project Info'!L75","v":0},{"$f":"MAX(0,MIN(1,TREND($X$97:$Y$97,$V$97:$W$97,H68)))*(H68>=$W$97)","v":0.45255818181818175},{"$f":"$K$30*R68","v":200.9358327272727},{"$f":"MAX(0,MIN(1,TREND($AG$97:$AH$97,$AE$97:$AF$97,H68)))*(H68<=$AE$97)","v":0},{"$f":"$L$30*T68","v":0},10.673129865977087,16.389481842954062,{"$f":"IF(S68>0,S68/V68,0)","v":18.826326977225225},{"$f":"IF(S68>0,S68/W68,0)","v":12.260047916869089},0,0,{"$f":"IF(U68>0,U68/Z68/3.412,0)","v":0},{"$f":"IF(U68>0,U68/AA68/3.412,0)","v":0},{"$f":"X68-Y68","v":6.5662790603561358},{"$f":"AB68-AC68","v":0},{"$f":"AD68+AE68","v":6.5662790603561358}]
[null,null,null,null,null,{"$f":"'Project Info'!A76","v":90},{"$f":"'Project Info'!B76","v":95},{"$f":"'Project Info'!C76","v":92.016049160256074},{"$f":"'Project Info'!D76","v":72.911561930607689},{"$f":"'Project Info'!E76","v":36.467095439351091},{"$f":"'Project Info'!F76","v":0},{"$f":"'Project Info'!G76","v":0},{"$f":"'Project Info'!H76","v":0},{"$f":"'Project Info'!I76","v":0},{"$f":"'Project Info'!J76","v":0},{"$f":"'Project Info'!K76","v":0},{"$f":"'Project Info'!L76","v":0},0.41518724020298758,184.3431346501265,0,0,10.673129865977087,16.389481842954062,17.271703517612032,11.247648730846041,0,0,0,0,6.0240547867659906,0,6.0240547867659906]
[null,null,null,null,null,{"$f":"'Project Info'!A77","v":85},{"$f":"'Project Info'!B77","v":90},{"$f":"'Project Info'!C77","v":87.457811360655285},{"$f":"'Project Info'!D77","v":70.80538329449476},{"$f":"'Project Info'!E77","v":34.679413213566804},{"$f":"'Project Info'!F77","v":0},{"$f":"'Project Info'!G77","v":0},{"$f":"'Project Info'!H77","v":0},{"$f":"'Project Info'!I77","v":0},{"$f":"'Project Info'!J77","v":0},{"$f":"'Project Info'!K77","v":0},{"$f":"'Project Info'!L77","v":0},0.36200779920764503,160.73146284819438,0,0,10.915700999294748,16.761970066657565,14.724795307106623,9.589055594838273,0,0,0,0,5.1357397122683501,0,5.1357397122683501]
[null,null,null,null,null,{"$f":"'Project Info'!A78","v":80},{"$f":"'Project Info'!B78","v":85},{"$f":"'Project Info'!C78","v":82.136788830239965},{"$f":"'Project Info'!D78","v":67.872393622439333},{"$f":"'Project Info'!E78","v":32.296248223809314},{"$f":"'Project Info'!F78","v":0},{"$f":"'Project Info'!G78","v":0},{"$f":"'Project Info'!H78","v":0},{"$f":"'Project Info'!I78","v":0},{"$f":"'Project Info'!J78","v":0},{"$f":"'Project Info'!K78","v":0},{"$f":"'Project Info'!L78","v":0},0.29992920301946624,133.16856614064301,0,0,11.169554510906254,17.151783324021693,11.922459934334322,7.7641236263832472,0,0,0,0,4.1583363079510747,0,4.1583363079510747]
[null,null,null,null,null,{"$f":"'Project Info'!A79","v":75},{"$f":"'Project Info'!B79","v":80},{"$f":"'Project Info'!C79","v":76.988400157585886},{"$f":"'Project Info'!D79","v":65.129261896908645},{"$f":"'Project Info'!E79","v":30.190476812806729},{"$f":"'Project Info'!F79","v":0},{"$f":"'Project Info'!G79","v":0},{"$f":"'Project Info'!H79","v":0},{"$f":"'Project Info'!I79","v":0},{"$f":"'Project Info'!J79","v":0},{"$f":"'Project Info'!K79","v":0},{"$f":"'Project Info'!L79","v":0},0.23986466850516863,106.49991281629487,0,0,11.64149451049887,17.876486588332519,9.1483024555178911,5.9575416170314126,0,0,0,0,3.1907608384864785,0,3.1907608384864785]
[null,null,null,null,null,{"$f":"'Project Info'!A80","v":70},{"$f":"'Project Info'!B80","v":75},{"$f":"'Project Info'!C80","v":72.457982050814195},{"$f":"'Project Info'!D80","v":63.604425012889301},{"$f":"'Project Info'!E80","v":29.088683095945193},{"$f":"'Project Info'!F80","v":0},{"$f":"'Project Info'!G80","v":0},{"$f":"'Project Info'!H80","v":0},{"$f":"'Project Info'!I80","v":0},{"$f":"'Project Info'!J80","v":0},{"$f":"'Project Info'!K80","v":0},{"$f":"'Project Info'!L80","v":0},0.18700979059283229,83.03234702321754,0,0,11.918672951225034,18.302117221388052,6.9665765109095679,4.5367618412029973,0,0,0,0,2.4298146697065706,0,2.4298146697065706]
[null,null,null,null,null,{"$f":"'Project Info'!A81","v":65},{"$f":"'Project Info'!B81","v":70},{"$f":"'Project Info'!C81","v":67.815831070966169},{"$f":"'Project Info'!D81","v":61.631331368130574},{"$f":"'Project Info'!E81","v":27.661514889731574},{"$f":"'Project Info'!F81","v":0},{"$f":"'Project Info'!G81","v":0},{"$f":"'Project Info'!H81","v":0},{"$f":"'Project Info'!I81","v":0},{"$f":"'Project Info'!J81","v":0},{"$f":"'Project Info'!K81","v":0},{"$f":"'Project Info'!L81","v":0},0.13285136249460539,58.986004947604791,0,0,12.209372291498816,18.748510324348739,4.831207005512951,3.1461702251084724,0,0,0,0,1.6850367804044786,0,1.6850367804044786]
[null,null,null,null,null,{"$f":"'Project Info'!A82","v":60},{"$f":"'Project Info'!B82","v":65},{"$f":"'Project Info'!C82","v":62.535961472271332},{"$f":"'Project Info'!D82","v":57.135476922863582},{"$f":"'Project Info'!E82","v":24.623037157728302},{"$f":"'Project Info'!F82","v":0},{"$f":"'Project Info'!G82","v":0},{"$f":"'Project Info'!H82","v":0},{"$f":"'Project Info'!I82","v":0},{"$f":"'Project Info'!J82","v":0},{"$f":"'Project Info'!K82","v":0},{"$f":"'Project Info'!L82","v":0},0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,{"$f":"'Project Info'!A83","v":55},{"$f":"'Project Info'!B83","v":60},{"$f":"'Project Info'!C83","v":57.125792270740902},{"$f":"'Project Info'!D83","v":52.596971157053673},{"$f":"'Project Info'!E83","v":21.818001539159841},{"$f":"'Project Info'!F83","v":0},{"$f":"'Project Info'!G83","v":0},{"$f":"'Project Info'!H83","v":0},{"$f":"'Project Info'!I83","v":0},{"$f":"'Project Info'!J83","v":0},{"$f":"'Project Info'!K83","v":0},{"$f":"'Project Info'!L83","v":0},0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,{"$f":"'Project Info'!A84","v":50},{"$f":"'Project Info'!B84","v":55},{"$f":"'Project Info'!C84","v":52.235698854337961},{"$f":"'Project Info'!D84","v":48.022768090099298},{"$f":"'Project Info'!E84","v":19.246640192796217},{"$f":"'Project Info'!F84","v":0},{"$f":"'Project Info'!G84","v":0},{"$f":"'Project Info'!H84","v":0},{"$f":"'Project Info'!I84","v":0},{"$f":"'Project Info'!J84","v":0},{"$f":"'Project Info'!K84","v":0},{"$f":"'Project Info'!L84","v":0},0,0,2.7643011456620292E-2,12.881643338785056,0,0,0,0,3.2313304721030041,3.5686695278969958,1.1683712769930938,1.0579275218858692,0,0.11044375510722459,0.11044375510722459]
[null,null,null,null,null,{"$f":"'Project Info'!A85","v":45},{"$f":"'Project Info'!B85","v":50},{"$f":"'Project Info'!C85","v":47.459170258371508},{"$f":"'Project Info'!D85","v":43.465397050422162},{"$f":"'Project Info'!E85","v":16.894183241713304},{"$f":"'Project Info'!F85","v":0},{"$f":"'Project Info'!G85","v":0},{"$f":"'Project Info'!H85","v":0},{"$f":"'Project Info'!I85","v":0},{"$f":"'Project Info'!J85","v":0},{"$f":"'Project Info'!K85","v":0},{"$f":"'Project Info'!L85","v":0},0,0,7.5408297416284853E-2,35.140266595988741,0,0,0,0,3.2313304721030041,3.5686695278969958,3.1872391648211433,2.8859559437087654,0,0.30128322111237793,0.30128322111237793]
[null,null,null,null,null,{"$f":"'Project Info'!A86","v":40},{"$f":"'Project Info'!B86","v":45},{"$f":"'Project Info'!C86","v":42.677030404888129},{"$f":"'Project Info'!D86","v":38.812544504634097},{"$f":"'Project Info'!E86","v":14.690265649465921},{"$f":"'Project Info'!F86","v":0},{"$f":"'Project Info'!G86","v":0},{"$f":"'Project Info'!H86","v":0},{"$f":"'Project Info'!I86","v":0},{"$f":"'Project Info'!J86","v":0},{"$f":"'Project Info'!K86","v":0},{"$f":"'Project Info'!L86","v":0},0,0,0.12322969595111866,57.425038313221293,0,0,0,0,3.0701313269004422,3.3948849132723269,5.481953129516306,4.957551276548342,0,0.52440185296796393,0.52440185296796393]
[null,null,null,null,null,{"$f":"'Project Info'!A87","v":35},{"$f":"'Project Info'!B87","v":40},{"$f":"'Project Info'!C87","v":37.333046773755832},{"$f":"'Project Info'!D87","v":33.904706919479686},{"$f":"'Project Info'!E87","v":12.53841602318813},{"$f":"'Project Info'!F87","v":0},{"$f":"'Project Info'!G87","v":0},{"$f":"'Project Info'!H87","v":0},{"$f":"'Project Info'!I87","v":0},{"$f":"'Project Info'!J87","v":0},{"$f":"'Project Info'!K87","v":0},{"$f":"'Project Info'!L87","v":0},0,0,0.17666953226244164,82.32800203429781,0,0,0,0,2.8708596053761744,3.1800552422640043,8.4047848159185925,7.5875905862318831,0,0.81719422968670941,0.81719422968670941]
[null,null,null,null,null,{"$f":"'Project Info'!A88","v":30},{"$f":"'Project Info'!B88","v":35},{"$f":"'Project Info'!C88","v":32.638179845662044},{"$f":"'Project Info'!D88","v":29.547170928664851},{"$f":"'Project Info'!E88","v":10.728972818165861},{"$f":"'Project Info'!F88","v":0},{"$f":"'Project Info'!G88","v":0},{"$f":"'Project Info'!H88","v":0},{"$f":"'Project Info'!I88","v":0},{"$f":"'Project Info'!J88","v":0},{"$f":"'Project Info'!K88","v":0},{"$f":"'Project Info'!L88","v":0},0,0,0.22361820154337952,104.20608191921485,0,0,0,0,2.695792786376511,2.9913202484450698,11.329155496105125,10.2098916617215,0,1.1192638343836254,1.1192638343836254]
[null,null,null,null,null,{"$f":"'Project Info'!A89","v":25},{"$f":"'Project Info'!B89","v":30},{"$f":"'Project Info'!C89","v":27.529264646850947},{"$f":"'Project Info'!D89","v":24.652717392657845},{"$f":"'Project Info'!E89","v":8.8041305482613303},{"$f":"'Project Info'!F89","v":0},{"$f":"'Project Info'!G89","v":0},{"$f":"'Project Info'!H89","v":0},{"$f":"'Project Info'!I89","v":0},{"$f":"'Project Info'!J89","v":0},{"$f":"'Project Info'!K89","v":0},{"$f":"'Project Info'!L89","v":0},0,0,0.27470735353149051,128.01362674567457,0,0,0,0,2.5052865279258514,2.7859403956745519,14.975791197646959,13.467139494709539,0,1.5086517029374207,1.5086517029374207]
[null,null,null,null,null,{"$f":"'Project Info'!A90","v":20},{"$f":"'Project Info'!B90","v":25},{"$f":"'Project Info'!C90","v":22.998111483544687},{"$f":"'Project Info'!D90","v":20.383306659827422},{"$f":"'Project Info'!E90","v":7.246164547543378},{"$f":"'Project Info'!F90","v":0},{"$f":"'Project Info'!G90","v":0},{"$f":"'Project Info'!H90","v":0},{"$f":"'Project Info'!I90","v":0},{"$f":"'Project Info'!J90","v":0},{"$f":"'Project Info'!K90","v":0},{"$f":"'Project Info'!L90","v":0},0,0,0.32001888516455312,149.12880048668177,0,0,0,0,2.3363244289250247,2.6037867420423546,18.707654995371566,16.785995053997741,0,1.9216599413738251,1.9216599413738251]
[null,null,null,null,null,{"$f":"'Project Info'!A91","v":15},{"$f":"'Project Info'!B91","v":20},{"$f":"'Project Info'!C91","v":17.808510327474309},{"$f":"'Project Info'!D91","v":15.420865796304254},{"$f":"'Project Info'!E91","v":5.5490484131518292},{"$f":"'Project Info'!F91","v":0},{"$f":"'Project Info'!G91","v":0},{"$f":"'Project Info'!H91","v":0},{"$f":"'Project Info'!I91","v":0},{"$f":"'Project Info'!J91","v":0},{"$f":"'Project Info'!K91","v":0},{"$f":"'Project Info'!L91","v":0},0,0,0.3719148967252569,173.31234187396973,0,0,0,0,2.1428094730838598,2.3951632907039029,23.704833570424533,21.207298111877002,0,2.4975354585475316,2.4975354585475316]
[null,null,null,null,null,{"$f":"'Project Info'!A92","v":10},{"$f":"'Project Info'!B92","v":15},{"$f":"'Project Info'!C92","v":12.269931130346862},{"$f":"'Project Info'!D92","v":10.318264913023604},{"$f":"'Project Info'!E92","v":3.9082824916941998},{"$f":"'Project Info'!F92","v":0},{"$f":"'Project Info'!G92","v":0},{"$f":"'Project Info'!H92","v":0},{"$f":"'Project Info'!I92","v":0},{"$f":"'Project Info'!J92","v":0},{"$f":"'Project Info'!K92","v":0},{"$f":"'Project Info'!L92","v":0},0,0,0.42730068869653137,199.12212093258361,0,0,0,0,1.9362814805615036,2.1725108222643019,30.139913063302423,26.862630506660086,0,3.2772825566423371,3.2772825566423371]
[null,null,null,null,null,{"$f":"'Project Info'!A93","v":5},{"$f":"'Project Info'!B93","v":10},{"$f":"'Project Info'!C93","v":7.3137581369917548},{"$f":"'Project Info'!D93","v":5.7052382449247707},{"$f":"'Project Info'!E93","v":2.5019418419888937},{"$f":"'Project Info'!F93","v":0},{"$f":"'Project Info'!G93","v":0},{"$f":"'Project Info'!H93","v":0},{"$f":"'Project Info'!I93","v":0},{"$f":"'Project Info'!J93","v":0},{"$f":"'Project Info'!K93","v":0},{"$f":"'Project Info'!L93","v":0},0,0,0.4768624186300825,222.21788708161844,0,0,0,0,1.7514708238064238,1.9732712498561782,37.184939924482201,33.005263400798093,0,4.1796765236841082,4.1796765236841082]
[null,null,null,null,null,{"$f":"'Project Info'!A94","v":0},{"$f":"'Project Info'!B94","v":5},{"$f":"'Project Info'!C94","v":2.6119461836144886},{"$f":"'Project Info'!D94","v":1.2699770062067783},{"$f":"'Project Info'!E94","v":1.2046477897733283},{"$f":"'Project Info'!F94","v":8760},{"$f":"'Project Info'!G94","v":2672},{"$f":"'Project Info'!H94","v":3160},{"$f":"'Project Info'!I94","v":1344},{"$f":"'Project Info'!J94","v":1584},{"$f":"'Project Info'!K94","v":88},{"$f":"'Project Info'!L94","v":264},0,0,0.52388053816385516,244.12833078435651,0,0,0,0,1.5761450318682573,1.7842570640337159,45.395518591710825,40.100679739304702,0,5.294838852406123,5.294838852406123]
[null,null,null,null,null,{"$f":"'Project Info'!A95","v":-5},{"$f":"'Project Info'!B95","v":0},{"$f":"'Project Info'!C95","v":-1.6731398516793925},{"$f":"'Project Info'!D95","v":-2.7083318773557807},{"$f":"'Project Info'!E95","v":7.9391832815876459E-2},{"$f":"'Project Info'!F95","v":0},{"$f":"'Project Info'!G95","v":0},{"$f":"'Project Info'!H95","v":0},{"$f":"'Project Info'!I95","v":0},{"$f":"'Project Info'!J95","v":0},{"$f":"'Project Info'!K95","v":0},{"$f":"'Project Info'!L95","v":0},0,0,0.56673139851679399,264.09683170882602,0,0,0,0,1.4163585261315834,1.6119953793530892,54.64884245842395,48.016486244689375,0,6.6323562137345746,6.6323562137345746]
[null,null,null,null,null,{"$f":"'Project Info'!A96","v":-10},{"$f":"'Project Info'!B96","v":-5},{"$f":"'Project Info'!C96","v":-6.5729865085377277},{"$f":"'Project Info'!D96","v":-7.2465935998252222},{"$f":"'Project Info'!E96","v":-1.168423365310433},{"$f":"'Project Info'!F96","v":0},{"$f":"'Project Info'!G96","v":0},{"$f":"'Project Info'!H96","v":0},{"$f":"'Project Info'!I96","v":0},{"$f":"'Project Info'!J96","v":0},{"$f":"'Project Info'!K96","v":0},{"$f":"'Project Info'!L96","v":0},0,0,0.6157298650853773,286.9301171297858,0,0,0,0,1.2336482212517372,1.4150201417883979,68.167250340883129,59.429830464722691,0,8.7374198761604376,8.7374198761604376]
[null,null,null,null,null,{"$f":"'Project Info'!A97","v":-15},{"$f":"'Project Info'!B97","v":-10},{"$f":"'Project Info'!C97","v":-15.32570353422995},{"$f":"'Project Info'!D97","v":-15.707838211108999},{"$f":"'Project Info'!E97","v":-3.4051318156661381},{"$f":"'Project Info'!F97","v":0},{"$f":"'Project Info'!G97","v":0},{"$f":"'Project Info'!H97","v":0},{"$f":"'Project Info'!I97","v":0},{"$f":"'Project Info'!J97","v":0},{"$f":"'Project Info'!K97","v":0},{"$f":"'Project Info'!L97","v":0},0,0,0.70325703534229955,327.71777846951159,0,0,0,0,0.90726829382016683,1.0631584130016289,105.8656932513525,90.342686203336811,0,15.523007048015685,15.523007048015685]
[]
[null,null,null,null,null,null,"VRF System Types",null,null,"VRF Heat Recovery?"]
[null,null,null,null,null,null,{"$f":"G117","v":"AC - Cooling Only"},null,null,"No",null,null,null,null,null,null,null,"VRF System Cooling Load Profile",null,null,null,null,null,null,null,null,"VRF System Heating Load Profile"]
[null,null,null,null,null,null,{"$f":"G118","v":"HP Air-Cooled"},null,null,"Yes",null,null,null,null,null,null,null,"Occupied Profile",null,null,null,"Unocc Profile",null,null,null,null,"Occupied Profile",null,null,null,"Unocc Profile"]
[null,null,null,null,null,null,{"$f":"G119","v":"HP Water Source"},null,null,null,null,null,null,null,null,null,null,"Max OAT","Min OAT","% Load @","%Load @","Max OAT","Min OAT","% Load @","%Load @",null,"Max OAT","Min OAT","% Load @","%Load @","Max OAT","Min OAT","% Load @","%Load @"]
[null,null,null,null,null,null,{"$f":"G120","v":"HP Ground Water"},null,null,null,null,null,null,null,null,null,null,"°F","°F","Max OAT","Min OAT","°F","°F","Max OAT","Min OAT",null,"°F","°F","Max OAT","Min OAT","°F","°F","Max OAT","Min OAT"]
[null,null,null,null,null,null,{"$f":"G121","v":"HP Ground Source"},null,null,null,null,null,null,null,null,null,null,95,50,0.95,0.15,95,65,0.45,0.1,null,60,5,0.05,0.8,55,5,0,0.5]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,95,55,{"$f":"T97*$K$30","v":421.79999999999995},{"$f":"U97*$K$30","v":66.599999999999994},95,65,{"$f":"X97*$K$30","v":199.8},{"$f":"Y97*$K$30","v":44.400000000000006},null,55,5,{"$f":"AC97*$L$30","v":23.3},{"$f":"AD97*$L$30","v":372.8},55,5,{"$f":"AG97*$L$30","v":0},{"$f":"AH97*$L$30","v":233}]
[null,null,null,null,null,null,null,"Part Load Cooling Performance Assumptions",null,null,null,null,null,null,null,null,null,"Bin Model EFLH Cooling",null,null,{"$f":"SUMPRODUCT(R37:R60,K37:K60)+SUMPRODUCT(R67:R90,K67:K90)","v":0}]
[null,null,null,null,null,null,null,0.02,0.61699999999999999,0.23799999999999999,0.125,null,null,"IEER"]
[null,null,null,null,null,null,null,1,0.75,0.5,0.25,-0.01,"IEER","Calculated",null,null,null,"OAT Perf. Impact",null,5.0000000000000001E-3,"% improvement per °F OAT reduction"]
[null,null,null,null,null,null,"Base",{"$f":"R30","v":10.168918918918919},{"$f":"IF(H102=0,0,($M102/$H102)*I$105*$H102)","v":11.079969031531533},12.007271099224223,12.514606598786285,{"$f":"K102*0.75","v":9.3859549490897134},{"$f":"S30","v":11.437387387387387},{"$f":"SUMPRODUCT(H102:K102,$H$100:$K$100)","v":11.461775617296984},{"$f":"1-N102/M102","v":-2.1323252490765832E-3}]
[null,null,null,null,null,null,"Proposed",{"$f":"M30","v":12.563063063063064},17.014217342342342,18.438167073323321,19.217223082457455,{"$f":"K103*0.75","v":14.412917311843092},{"$f":"N30","v":17.563063063063062},{"$f":"SUMPRODUCT(H103:K103,$H$100:$K$100)","v":17.539470010244617},{"$f":"1-N103/M103","v":1.3433336049486488E-3},null,null,"Baseline Cooling Performance Table"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"OAT",1,0.75,0.5,0.25,-0.01]
[null,null,null,null,null,null,"PL EER Factors",null,0.96875,1.0498263888888888,1.0941840277777777,null,null,null,null,null,null,105,{"$f":"S106","v":10.168918918918919},{"$f":"T106","v":10.306947936308402},{"$f":"U106","v":10.673129865977087},{"$f":"V106","v":10.882266607640249},{"$f":"W106","v":10.882266607640249}]
[null,null,null,null,null,null,null,null,0.75,0.5,0.25,null,null,null,null,null,null,95,{"$f":"H102","v":10.168918918918919},{"$f":"$T$109/(1-($R$109-$R106)*$T$101)","v":10.306947936308402},{"$f":"$U$111/(1-($R$111-$R106)*$T$101)","v":10.673129865977087},{"$f":"$V$112/(1-($R$112-$R106)*$T$101)","v":10.882266607640249},{"$f":"V106","v":10.882266607640249}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,90,{"$f":"$S$106/(1-($R$106-$R107)*$T$101)","v":10.42966042966043},{"$f":"$T$109/(1-($R$109-$R107)*$T$101)","v":10.552351458601459},{"$f":"$U$111/(1-($R$111-$R107)*$T$101)","v":10.915700999294748},11.124094754476697,11.124094754476697]
[null,null,null,null,null,null,null,"Heating Performance - COP vs. OAT°F",null,null,null,null,null,null,null,null,null,85,10.70412517780939,{"$f":"$T$109/(1-($R$109-$R108)*$T$101)","v":10.80972588442101},{"$f":"$U$111/(1-($R$111-$R108)*$T$101)","v":11.169554510906254},11.376915089805713,11.376915089805713]
[null,null,null,null,null,null,null,"OAT (°F)",null,null,null,null,null,null,null,null,null,80,10.993425858290722,{"$f":"I102","v":11.079969031531533},{"$f":"$U$111/(1-($R$111-$R109)*$T$101)","v":11.43549628497545},11.64149451049887,11.64149451049887]
[null,null,null,null,null,null,null,47,17,null,null,null,null,null,null,null,null,75,11.298798798798799,{"$f":"$T$109/(1-($R$109-$R110)*$T$101)","v":11.364070801570804},{"$f":"$U$111/(1-($R$111-$R110)*$T$101)","v":11.714410828511438},11.918672951225034,11.918672951225034]
[null,null,null,null,null,null,"Base",{"$f":"T30","v":3.2313304721030041},{"$f":"U30","v":2.1126609442060085},null,null,null,null,null,null,null,null,70,11.621621621621623,{"$f":"$T$109/(1-($R$109-$R111)*$T$101)","v":11.663125296348984},{"$f":"J102","v":12.007271099224223},12.209372291498816,12.209372291498816]
[null,null,null,null,null,null,"Proposed",{"$f":"O30","v":3.5686695278969958},{"$f":"P30","v":2.3626609442060085},null,null,null,null,null,null,null,null,65,11.963434022257552,{"$f":"$T$109/(1-($R$109-$R112)*$T$101)","v":11.978344898953008},{"$f":"$U$111/(1-($R$111-$R112)*$T$101)","v":12.315149845358178},{"$f":"K102","v":12.514606598786285},12.514606598786285,"< Min Cond Temp"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,60,{"$f":"S112","v":11.963434022257552},{"$f":"T112","v":11.978344898953008},12.315149845358178,12.514606598786285,12.514606598786285]
[null,null,null,null,null,null,"Baseline EER",null,null,null,null,null,null,null,null,null,null,55,{"$f":"S113","v":11.963434022257552},11.978344898953008,12.315149845358178,12.514606598786285,12.514606598786285]
[null,null,null,null,null,null,null,"MBH ≥",0,65,135,240,null,null,null,null,null,-20,{"$f":"S114","v":11.963434022257552},{"$f":"T114","v":11.978344898953008},{"$f":"U114","v":12.315149845358178},{"$f":"V114","v":12.514606598786285},{"$f":"W114","v":12.514606598786285}]
[null,null,null,null,null,null,null,"MBH <",65,135,240,1000]
[null,null,null,null,null,null,"AC - Cooling Only",null,11.1,11.2,11,10,null,null,null,null,null,"Proposed Cooling Performance Table"]
[null,null,null,null,null,null,"HP Air-Cooled",null,11.1,11,10.6,9.5,null,null,null,null,null,"OAT",1,0.75,0.5,0.25,-0.01]
[null,null,null,null,null,null,"HP Water Source",null,12,12,10,10,null,null,null,null,null,105,{"$f":"S120","v":12.563063063063064},{"$f":"T120","v":15.827178923109155},{"$f":"U120","v":16.389481842954062},{"$f":"V120","v":16.710628767354311},{"$f":"W120","v":16.710628767354311}]
[null,null,null,null,null,null,"HP Ground Water",null,16.2,16.2,13.8,13.8,null,null,null,null,null,95,{"$f":"H103","v":12.563063063063064},{"$f":"$T$123/(1-($R$123-$R120)*$T$101)","v":15.827178923109155},{"$f":"$U$125/(1-($R$125-$R120)*$T$101)","v":16.389481842954062},{"$f":"$V$126/(1-($R$126-$R120)*$T$101)","v":16.710628767354311},{"$f":"V120","v":16.710628767354311}]
[null,null,null,null,null,null,"HP Ground Source",null,13.4,13.4,11,11,null,null,null,null,null,90,{"$f":"$S$120/(1-($R$120-$R121)*$T$101)","v":12.885192885192886},{"$f":"$T$123/(1-($R$123-$R121)*$T$101)","v":16.204016516516514},{"$f":"$U$125/(1-($R$125-$R121)*$T$101)","v":16.761970066657565},17.081976073295515,{"$f":"V121","v":17.081976073295515}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,85,13.224276908487436,{"$f":"$T$123/(1-($R$123-$R122)*$T$101)","v":16.599236431553507},{"$f":"$U$125/(1-($R$125-$R122)*$T$101)","v":17.151783324021693},17.470202802234049,17.470202802234049]
[null,null,null,null,null,null,"Baseline IEER",null,null,null,null,null,null,null,null,null,null,80,13.581689797906014,{"$f":"I103","v":17.014217342342342},{"$f":"$U$125/(1-($R$125-$R123)*$T$101)","v":17.56015911745078},17.876486588332519,17.876486588332519]
[null,null,null,null,null,null,null,"MBH ≥",0,65,135,240,null,null,null,null,null,75,13.958958958958959,{"$f":"$T$123/(1-($R$123-$R124)*$T$101)","v":17.450479325479325},{"$f":"$U$125/(1-($R$125-$R124)*$T$101)","v":17.988455681291047},18.302117221388052,18.302117221388052]
[null,null,null,null,null,null,null,"MBH <",65,135,240,1000,null,null,null,null,null,70,14.357786357786358,{"$f":"$T$123/(1-($R$123-$R125)*$T$101)","v":17.909702465623518},{"$f":"J103","v":18.438167073323321},18.748510324348739,18.748510324348739]
[null,null,null,null,null,null,"AC - Cooling Only",null,13,13.1,12.9,11.6,null,null,null,null,null,65,14.780074191838899,{"$f":"$T$123/(1-($R$123-$R126)*$T$101)","v":18.393748478207936},{"$f":"$U$125/(1-($R$125-$R126)*$T$101)","v":18.910940588023919},{"$f":"K103","v":19.217223082457455},19.217223082457455,"< Min Cond Temp"]
[null,null,null,null,null,null,"HP Air-Cooled",null,13,12.3,11.8,10.6,null,null,null,null,null,60,{"$f":"S126","v":14.780074191838899},{"$f":"T126","v":18.393748478207936},18.910940588023919,19.217223082457455,19.217223082457455]
[null,null,null,null,null,null,"HP Water Source",null,{"$f":"I119","v":12},12,10,10,null,null,null,null,null,55,{"$f":"S127","v":14.780074191838899},18.393748478207936,18.910940588023919,19.217223082457455,19.217223082457455]
[null,null,null,null,null,null,"HP Ground Water",null,16.2,16.2,13.8,13.8,null,null,null,null,null,-20,{"$f":"S128","v":14.780074191838899},{"$f":"T128","v":18.393748478207936},{"$f":"U128","v":18.910940588023919},{"$f":"V128","v":19.217223082457455},{"$f":"W128","v":19.217223082457455}]
[null,null,null,null,null,null,"HP Ground Source",null,13.4,13.4,11,11]
[]
[null,null,null,null,null,null,"Baseline COP 47"]
[null,null,null,null,null,null,null,"MBH ≥",0,65,135,240]
[null,null,null,null,null,null,null,"MBH <",65,135,240,1000]
[null,null,null,null,null,null,"AC - Cooling Only",null,0,0,0,0]
[null,null,null,null,null,null,"HP Air-Cooled",null,{"$f":"7.7/3.412","v":2.2567409144196953},3.3,3.2,3.2]
[null,null,null,null,null,null,"HP Water Source",null,4.2,4.2,3.9,3.9]
[null,null,null,null,null,null,"HP Ground Water",null,3.6,3.6,3.3,3.3]
[null,null,null,null,null,null,"HP Ground Source",null,3.1,3.1,2.8,2.8]
[]
[null,null,null,null,null,null,"Baseline COP 17"]
[null,null,null,null,null,null,null,"MBH ≥",0,65,135,240]
[null,null,null,null,null,null,null,"MBH <",65,135,240,1000]
[null,null,null,null,null,null,"AC - Cooling Only",null,0,0,0,0]
[null,null,null,null,null,null,"HP Air-Cooled",null,{"$f":"7.7/3.412","v":2.2567409144196953},2.25,2.0499999999999998,2.0499999999999998]
[null,null,null,null,null,null,"HP Water Source",null,4.2,4.2,3.9,3.9]
[null,null,null,null,null,null,"HP Ground Water",null,3.6,3.6,3.3,3.3]
[null,null,null,null,null,null,"HP Ground Source",null,3.1,3.1,2.8,2.8]

{"sheet":"Sheet2","index":34,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":true,"merged":[]}

{"sheet":"Sheet1","index":35,"n_rows":90,"n_cols":25,"rows_kept":90,"cut":false,"hidden":true,"merged":[]}
[]
[]
[null,null,"EER",null,10,10]
[null,null,"IEER",null,11,12]
[]
[null,null,0.02,1,{"$f":"E3","v":10},10]
[null,null,0.61699999999999999,0.75,11,11.5]
[null,null,0.23799999999999999,0.5,11.5,12.5]
[null,null,0.125,0.25,10.3,11]
[null,null,null,"IEER",{"$f":"SUMPRODUCT($C$6:$C$9,E6:E9)","v":11.0115},{"$f":"SUMPRODUCT($C$6:$C$9,F6:F9)","v":11.645499999999998},{"$f":"SUMPRODUCT($C$6:$C$9,G6:G9)","v":0},{"$f":"SUMPRODUCT($C$6:$C$9,H6:H9)","v":0},{"$f":"SUMPRODUCT($C$6:$C$9,I6:I9)","v":0}]
[]
[]
[]
[null,null,"Sample Air Cooled Chiller"]
[]
[null,null,"% Load","OAT","kW/ton"]
[null,null,1,95,1.2,1.25,1.2,1.2629999999999999,1.224,1.1759999999999999,1.23]
[null,null,0.75,85,0.95199999999999996,1,0.98399999999999999,1.0620000000000001,0.97599999999999998,0.98399999999999999,0.95499999999999996]
[null,null,0.5,75,0.77400000000000002,0.98399999999999999,0.83899999999999997,0.88900000000000001,0.82799999999999996,0.84499999999999997,0.92]
[null,null,0.25,65,0.67800000000000005,1.2,0.76900000000000002,0.78900000000000003,0.755,0.75,0.93]
[]
[null,null,null,"FL",{"$f":"E17","v":1.2},1.25,1.2,1.2629999999999999,1.224,1.1759999999999999,1.23]
[null,null,null,"Avg PL",{"$f":"SUMPRODUCT(E17:E20,$C$6:$C$9)","v":0.88034599999999996},1.026192,0.92693500000000006,0.99072099999999996,0.9181109999999999,0.925508,0.94904499999999992]
[null,null,null,"EER",{"$f":"12/E22","v":10},9.6,10,9.5011876484560585,9.8039215686274517,10.204081632653061,9.7560975609756095]
[null,null,null,"IEER",13.631004173359111,11.693718134618083,12.945891567369879,12.112390874928462,13.070315027267947,12.965852267079269,12.644289786048081]
[null,null,null,"IEER/EER",{"$f":"E25/E24","v":1.3631004173359111},{"$f":"F25/F24","v":1.2180956390227169},1.2945891567369878,1.2748291395862204,1.3331721327813304,1.2706535221737685,1.2960397030699282]
[null,null,null,"IEER -EER",{"$f":"E25-E24","v":3.631004173359111},{"$f":"F25-F24","v":2.0937181346180829},2.9458915673698787,2.6112032264724032,3.2663934586404952,2.7617706344262078,2.888192225072471]
[]
[null,null,"% Load",null,"EER"]
[null,null,1,null,{"$f":"12/E17","v":10},{"$f":"12/F17","v":9.6},10,9.5011876484560585,9.8039215686274517,10.204081632653061,9.7560975609756095]
[null,null,0.75,null,{"$f":"12/E18","v":12.605042016806724},{"$f":"12/F18","v":12},12.195121951219512,11.299435028248586,12.295081967213115,12.195121951219512,12.565445026178011]
[null,null,0.5,null,{"$f":"12/E19","v":15.503875968992247},{"$f":"12/F19","v":12.195121951219512},14.30274135876043,13.498312710911136,14.492753623188406,14.201183431952662,13.043478260869565]
[null,null,0.25,null,{"$f":"12/E20","v":17.699115044247787},{"$f":"12/F20","v":10},15.604681404421326,15.20912547528517,15.894039735099337,16,12.903225806451612]
[]
[null,null,null,1,{"$f":"E30/(E$25/E$24)","v":7.3362166666666662},{"$f":"F30/(F$25/F$24)","v":7.8811545600000006},7.7244583333333345,7.4529106320396172,7.3538302575932333,8.0305775371373027,7.527622446956177,{"$f":"AVERAGE(E35:K35)","v":7.6152529191037619}]
[null,null,null,0.75,{"$f":"E31/(E$25)","v":0.92473319327731107},{"$f":"F31/(F$25)","v":1.026192},0.94200711382113833,0.93288229755178897,0.94068749999999979,0.94055691056910573,0.99376439790575921,{"$f":"AVERAGE(E36:K36)","v":0.95726048758930049}]
[null,null,null,0.5,{"$f":"E32/(E$25)","v":1.1373979328165373},1.0428780487804878,1.1048092967818834,1.114421822272216,1.1088297101449274,1.0952757396449704,1.031570652173913,{"$f":"AVERAGE(E37:K37)","v":1.0907404575164195}]
[null,null,null,0.25,{"$f":"E33/(E$25)","v":1.2984454277286135},0.85516000000000003,1.2053771131339404,1.2556666666666665,1.2160410596026487,1.2340106666666666,1.0204784946236558,{"$f":"AVERAGE(E38:K38)","v":1.1550256326317416}]
[]
[null,null,null,null,{"$f":"E24/(E$25-E$24)","v":2.7540590763763322},{"$f":"F24/(F$25-F$24)","v":4.5851444094938527},3.3945580722538606,3.6386243522269455,3.0014515069191754,3.6947607109209075,3.3779252905269517]
[null,null,null,null,{"$f":"E25/(E$25-E$24)","v":3.7540590763763322},5.5851444094938527,4.3945580722538606,4.6386243522269455,4.0014515069191754,4.6947607109209075,4.3779252905269521]
[null,null,null,null,0.37540590763763321,0.58178587598894294,0.43945580722538607,0.48821521307188592,0.40814805370575585,0.46008654967024898,0.44873734227901252]
[null,null,null,null,1,1,1,1,1,1,1]
[]
[]
[null,null,null,null,10,13,13,14]
[null,null,null,null,13.6,16,18,17]
[]
[null,null,0.02,1,{"$f":"E46","v":10},{"$f":"F46","v":13},{"$f":"G46","v":13},{"$f":"H46","v":14}]
[null,null,0.61699999999999999,0.75,{"$f":"$L36*(E$47/E$46)","v":1.3018742631214486},{"$f":"$L36*(F$47/F$46)","v":1.1781667539560623},{"$f":"$L36*(G$47/G$46)","v":1.3254375982005699},{"$f":"$L36*(H$47/H$46)","v":1.1623877349298648}]
[null,null,0.23799999999999999,0.5,{"$f":"$L37*(E$47/E$46)","v":1.4834070222223303},1.3424497938663624,1.5102560180996576,1.3244705555556522,null,null,null,null,null,null,null,"IPLV Part Load Coefficients"]
[null,null,0.125,0.25,1.5708348603791684,1.4215700093929129,1.5992662605670269,1.4025311253385433,null,null,null,null,null,null,null,"EER",11.2,11.2,11.2,11.2,null,{"$f":"12/Q52","v":1.0714285714285714},{"$f":"12/R52","v":1.0714285714285714},1.0714285714285714,1.0714285714285714]
[null,null,null,null,{"$f":"E49*$C$49+E50*$C$50+E51*$C$51+E52*$C$52","v":1.5526616491822445},{"$f":"F49*$C$49+F50*$C$50+F51*$C$51+F52*$C$52","v":1.4841281893051987},{"$f":"G49*$C$49+G50*$C$50+G51*$C$51+G52*$C$52","v":1.6371442129683487},{"$f":"H49*$C$49+H50*$C$50+H51*$C$51+H52*$C$52","v":1.4877336153412897},null,null,null,null,null,null,null,"IPLV",12.8,14,16,18,null,0.9375,0.8571428571428571,0.75,0.66666666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,0.01,{"$f":"Q52","v":11.2},{"$f":"R52","v":11.2},{"$f":"S52","v":11.2},{"$f":"T52","v":11.2},null,1.0714285714285714,1.0714285714285714,1.0714285714285714,1.0714285714285714]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.75,0.42,12.2,{"$f":"Q55*($R$53/$Q$53)","v":13.34375},{"$f":"R55*($S$53/$R$53)","v":15.25},{"$f":"S55*($T$53/$S$53)","v":17.15625},null,0.98360655737704927,0.89929742388758782,0.78688524590163933,0.69945355191256831]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.5,0.45,13.2,{"$f":"Q56*($R$53/$Q$53)","v":14.4375},{"$f":"R56*($S$53/$R$53)","v":16.5},{"$f":"S56*($T$53/$S$53)","v":18.5625},null,0.90909090909090917,0.83116883116883122,0.72727272727272729,0.64646464646464652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.25,0.12,13.6,{"$f":"Q57*($R$53/$Q$53)","v":14.875},{"$f":"R57*($S$53/$R$53)","v":17},{"$f":"S57*($T$53/$S$53)","v":19.125},null,0.88235294117647056,0.80672268907563027,0.70588235294117652,0.62745098039215685]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"IEER",{"$f":"SUMPRODUCT($P$54:$P$57,Q54:Q57)","v":12.807999999999998},{"$f":"SUMPRODUCT($P$54:$P$57,R54:R57)","v":13.998250000000001},{"$f":"SUMPRODUCT($P$54:$P$57,S54:S57)","v":15.981999999999999},{"$f":"SUMPRODUCT($P$54:$P$57,T54:T57)","v":17.96575},null,{"$f":"SUMPRODUCT($P$54:$P$57,V54:V57)","v":0.9388023018447319},{"$f":"SUMPRODUCT($P$54:$P$57,W54:W57)","v":0.8592519004621223},{"$f":"SUMPRODUCT($P$54:$P$57,X54:X57)","v":0.75318469861864268},{"$f":"SUMPRODUCT($P$54:$P$57,Y54:Y57)","v":0.67068798607371416}]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"Q53/Q52","v":1.142857142857143},{"$f":"R53/R52","v":1.25},{"$f":"S53/S52","v":1.4285714285714286},{"$f":"T53/T52","v":1.6071428571428572},null,{"$f":"V53/V52","v":0.875},{"$f":"W53/W52","v":0.79999999999999993},{"$f":"X53/X52","v":0.70000000000000007},{"$f":"Y53/Y52","v":0.62222222222222223}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"Q54/Q$54","v":1},1,1,1,null,{"$f":"V54/V$54","v":1},1,1,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.0892857142857142,1.19140625,1.361607142857143,1.5318080357142858,null,0.91803278688524603,0.83934426229508197,0.73442622950819669,0.65282331511839709]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.1785714285714286,1.2890625,1.4732142857142858,1.6573660714285716,null,0.84848484848484862,0.77575757575757587,0.67878787878787883,0.60336700336700344]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.2142857142857144,1.328125,1.517857142857143,1.7075892857142858,null,0.82352941176470584,0.75294117647058822,0.65882352941176481,0.58562091503267977]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,null,null,null,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.75,{"$f":"Q62/Q$60","v":0.95312499999999978},0.953125,0.95312500000000011,0.953125,0.75,{"$f":"V62/V$60","v":1.0491803278688525},1.0491803278688525,1.0491803278688523,1.0491803278688525]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.5,1.0312499999999998,1.03125,1.03125,1.03125,0.5,0.96969696969696983,0.96969696969696995,0.96969696969696961,0.96969696969696983]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.25,1.0625,1.0625,1.0625,1.0625,0.25,0.94117647058823528,0.94117647058823539,0.94117647058823539,0.94117647058823528]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"IEER Part Load Coefficients"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"EER",11.2,11.2,11.2,11.2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"IPLV",12.8,14,16,18]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,0.02,{"$f":"Q73","v":11.2},{"$f":"R73","v":11.2},{"$f":"S73","v":11.2},{"$f":"T73","v":11.2}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.75,0.61699999999999999,12.4,{"$f":"Q76*($R$74/$Q$74)","v":13.5625},{"$f":"Q76*($S$74/$Q$74)","v":15.5},{"$f":"S76*($T$74/$S$74)","v":17.4375}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.5,0.23799999999999999,13.4,{"$f":"Q77*($R$74/$Q$74)","v":14.65625},16.8,19]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.25,0.125,13.9,{"$f":"Q78*($R$74/$Q$74)","v":15.203125},17.5,20]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"IEER",{"$f":"SUMPRODUCT($P$75:$P$78,Q75:Q78)","v":12.801500000000001},{"$f":"SUMPRODUCT($P$75:$P$78,R75:R78)","v":13.980640625000001},{"$f":"SUMPRODUCT($P$75:$P$78,S75:S78)","v":15.9734},{"$f":"SUMPRODUCT($P$75:$P$78,T75:T78)","v":18.0049375}]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"Q74/Q73","v":1.142857142857143},{"$f":"R74/R73","v":1.25},{"$f":"S74/S73","v":1.4285714285714286},{"$f":"T74/T73","v":1.6071428571428572}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"Q75/Q$54","v":1},{"$f":"R75/R$54","v":1},{"$f":"S75/S$54","v":1},{"$f":"T75/T$54","v":1}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"Q76/Q$75","v":1.1071428571428572},{"$f":"R76/R$75","v":1.2109375},{"$f":"S76/S$75","v":1.3839285714285716},{"$f":"T76/T$75","v":1.556919642857143}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"Q77/Q$75","v":1.1964285714285716},1.30859375,1.5000000000000002,1.6964285714285716]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.2410714285714286,1.357421875,1.5625,1.7857142857142858]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.75,{"$f":"Q83/Q$60","v":0.96874999999999989},0.96875,0.96875000000000011,0.96875000000000011,{"$f":"AVERAGE(Q88:T88)","v":0.96875}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.5,1.046875,1.046875,1.05,1.0555555555555556,{"$f":"AVERAGE(Q89:T89)","v":1.0498263888888888}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.25,1.0859374999999998,1.0859375,1.09375,1.1111111111111112,{"$f":"AVERAGE(Q90:T90)","v":1.0941840277777777}]

{"sheet":"Sheet3","index":36,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":true,"merged":[]}

{"sheet":"ERV Eff Calculator","index":37,"n_rows":60,"n_cols":25,"rows_kept":60,"cut":false,"hidden":true,"merged":[[0,0,0,9],[1,11,1,24],[3,16,3,23]]}
["Heat Recovery Effectiveness Calculation"]
["Summer",null,null,null,null,null,null,null,null,null,null,"Return Air Relative Humidity and Enthalpy Calcs"]
[]
[null,"Effectiveness",null,"=",{"$f":"(B11-G11)/(B11-G9)","v":0.5538461538461541},null,null,null,null,null,null,null,null,null,null,"RH","Deg F"]
[null,null,null,null,null,null,null,null,null,null,null,"RA Temperature",75," Deg F",null,null,30,40,50,60,70,80,90,100,"Check"]
[null,"(Thi - Tho)/(Thi - Tci)",null,null,null,null,null,null,null,null,null,"RA Humidity Ratio",0.6,"%",null,0.1,4.0000000000000002E-4,5.9999999999999995E-4,8.9999999999999998E-4,1.1000000000000001E-3,1.6000000000000001E-3,2.3E-3,3.0000000000000001E-3,4.1000000000000003E-3,{"$f":"FORECAST($M$5,OFFSET(Q6:X6,0,MATCH($M$5,$Q$5:$X$5,1)-1,1,2),OFFSET($Q$5:$X$5,0,MATCH($M$5,$Q$5:$X$5,1)-1,1,2))","v":1.9499999999999999E-3}]
["Heat Exchanger",null,null,null,null,null,null,null,null,null,null,"Relat. Humidity",{"$f":"FORECAST($M$6,OFFSET($Y$6:$Y$14,MATCH($M$6,$P$6:$P$14,1)-1,0,2),OFFSET($P$6:$P$14,MATCH($M$6,$P$6:$P$14,1)-1,0,2))","v":1.1300000000000001E-2},"lb/lb",null,0.2,6.9999999999999999E-4,1E-3,1.4E-3,2.3E-3,3.0000000000000001E-3,4.3E-3,6.0000000000000001E-3,8.3000000000000001E-3,3.6500000000000005E-3]
[null,null,null,null,null,null,null,null,null,null,null,"Retun Air Enthalpy",{"$f":"(0.24*M5)+(M7*(1061+0.444*M5))","v":30.365590000000001},"Btu/lb",null,0.3,1E-3,1.6000000000000001E-3,2E-3,3.0999999999999999E-3,4.8999999999999998E-3,6.6E-3,9.2999999999999992E-3,1.24E-2,5.7499999999999999E-3]
["EA",null,"Tco",null,null,null,75,"Tci",null,"RA",null,null,null,null,null,0.4,1.2999999999999999E-3,2E-3,2.8999999999999998E-3,4.3E-3,6.3E-3,8.8999999999999999E-3,1.2200000000000001E-2,1.66E-2,7.5999999999999991E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.5,1.6999999999999999E-3,2.5999999999999999E-3,3.7000000000000002E-3,5.5999999999999999E-3,7.9000000000000008E-3,1.12E-2,1.54E-2,2.1000000000000001E-2,9.5499999999999995E-3]
["OA",88,"Thi",null,null,null,80.8,"Tho",null,"SA",null,null,null,null,null,0.6,2E-3,3.0999999999999999E-3,4.5999999999999999E-3,6.8999999999999999E-3,9.4000000000000004E-3,1.32E-2,1.83E-2,2.52E-2,1.1300000000000001E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.7,2.3999999999999998E-3,3.7000000000000002E-3,5.4000000000000003E-3,7.7000000000000002E-3,1.12E-2,1.54E-2,2.1700000000000001E-2,2.9700000000000001E-2,1.3299999999999999E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.8,2.7000000000000001E-3,4.1000000000000003E-3,6.0000000000000001E-3,8.8999999999999999E-3,1.26E-2,1.7899999999999999E-2,2.47E-2,"-",1.525E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.9,3.0000000000000001E-3,4.7000000000000002E-3,6.8999999999999999E-3,0.01,1.43E-2,0.02,2.7199999999999998E-2,"-",1.7149999999999999E-2]
[]
["Winter",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Source:","http://www.engineeringtoolbox.com/water-vapor-air-d_854.html"]
[]
[null,"Effectiveness",null,"=",{"$f":"(G23-C23)/(G23-C25)","v":0.54933333333333334}]
[]
[null,"(Thi - Tho)/(Thi - Tci)"]
["Heat Exchanger"]
[]
["EA",null,28.8,"Tho",null,"Thi",70,null,null,"RA"]
[]
["OA",null,-5,"Tci",null,"Tco",null,null,null,"SA"]
[]
[]
[]
[]
["Summer"]
[]
[null,"Effectiveness",null,"=",{"$f":"(B39-G39)/(B39-G37)","v":0.6000000000000002}]
[]
[null,"(Thi - Tho)/(Thi - Tci)"]
["Heat Exchanger"]
[]
["EA",null,"Tco",null,null,null,76,"Tci",null,"RA"]
[]
["OA",88,"Thi",null,null,null,80.8,"Tho",null,"SA"]
[]
[]
[]
[]
["Winter"]
[]
[null,"Effectiveness",null,"=",{"$f":"(G51-C51)/(G51-C53)","v":0.53055555555555556}]
[]
[null,"(Thi - Tho)/(Thi - Tci)"]
["Heat Exchanger"]
[]
["EA",null,28.8,"Tho",null,"Thi",67,null,null,"RA"]
[]
["OA",null,-5,"Tci",null,"Tco",null,null,null,"SA"]
[]
[]
[]
["Tci  cold fluid temp entering heat exchanger (F)"]
["Tco  cold fluid temp leaving heat exchanger (F)"]
["Thi  hot fluid temp entering heat exchanger (F)"]
["Tho  hot fluid temp leaving heat exchanger (F)"]

{"sheet":"AirCooled Chiller Sample Data","index":38,"n_rows":51,"n_cols":20,"rows_kept":51,"cut":false,"hidden":true,"merged":[]}
["Chiller Part Load Data"]
["CH-1","York YVAA0213ARM46BA"]
[null,"tons",null,"CHWT","OAT","Rated kW",{"$f":"G4*B4","v":216}]
["Rating",180,null,44,95,"kW/ton",1.2,{"$f":"(G4*B4*3413)/(B4*12000)","v":0.34129999999999999}]
[null,"tons","PLR","CHWT","OAT","dT","kW/ton","kW"]
[null,180,{"$f":"B6/$B$4","v":1},44,95,{"$f":"E6-D6","v":51},1.2,{"$f":"G6*B6","v":216},{"$f":"G6/G6","v":1},{"$f":"G6-G6","v":0},null,null,null,null,"OAT",1,0.75,0.5,0.25,"AVG"]
[null,180,1,44,85,{"$f":"E7-D7","v":41},1.026,{"$f":"G7*B7","v":184.68},{"$f":"G7/G6","v":0.85500000000000009},{"$f":"G6-G7","v":0.17399999999999993},null,null,null,null,95,{"$f":"I6","v":1},{"$f":"I10","v":1},{"$f":"I14","v":1},{"$f":"I18","v":1},{"$f":"AVERAGE(P7:S7)","v":1}]
[null,180,1,44,75,31,0.88200000000000001,158.76,{"$f":"G8/G6","v":0.73499999999999999},{"$f":"G6-G8","v":0.31799999999999995},null,null,null,null,85,{"$f":"I7","v":0.85500000000000009},{"$f":"I11","v":0.84924174843889377},{"$f":"I15","v":0.84428442844284424},{"$f":"I19","v":0.85034013605442182},{"$f":"AVERAGE(P8:S8)","v":0.8497165782340399}]
[null,180,1,44,65,21,0.70599999999999996,127.08,{"$f":"G9/G6","v":0.58833333333333337},{"$f":"G6-G9","v":0.49399999999999999},null,null,null,null,75,{"$f":"I8","v":0.73499999999999999},{"$f":"I12","v":0.71810883140053527},{"$f":"I16","v":0.69666966696669674},{"$f":"I20","v":0.70408163265306123},{"$f":"AVERAGE(P9:S9)","v":0.71346503275507334}]
[null,135,0.75,44,95,51,1.121,151.33500000000001,{"$f":"G10/G10","v":1},{"$f":"G10-G10","v":0},null,null,null,null,65,{"$f":"I9","v":0.58833333333333337},{"$f":"I13","v":0.60124888492417483},{"$f":"I17","v":0.57785778577857783},{"$f":"I21","v":0.57653061224489799},{"$f":"AVERAGE(P10:S10)","v":0.58599265407024603}]
[null,135,0.75,44,85,{"$f":"E11-D11","v":41},0.95199999999999996,128.51999999999998,{"$f":"G11/G10","v":0.84924174843889377},{"$f":"G10-G11","v":0.16900000000000004}]
[null,135,0.75,44,75,{"$f":"E12-D12","v":31},0.80500000000000005,108.67500000000001,{"$f":"G12/G10","v":0.71810883140053527},{"$f":"G10-G12","v":0.31599999999999995}]
[null,135,0.75,44,65,21,0.67400000000000004,90.990000000000009,{"$f":"G13/G10","v":0.60124888492417483},{"$f":"G10-G13","v":0.44699999999999995}]
[null,90,0.5,44,95,51,1.111,99.99,{"$f":"G14/G14","v":1},{"$f":"G14-G14","v":0}]
[null,90,0.5,44,85,41,0.93799999999999994,84.42,{"$f":"G15/G14","v":0.84428442844284424},{"$f":"G14-G15","v":0.17300000000000004}]
[null,90,0.5,44,75,31,0.77400000000000002,69.66,{"$f":"G16/G14","v":0.69666966696669674},{"$f":"G14-G16","v":0.33699999999999997}]
[null,90,0.5,44,65,21,0.64200000000000002,57.78,{"$f":"G17/G14","v":0.57785778577857783},{"$f":"G14-G17","v":0.46899999999999997}]
[null,45,0.25,44,95,51,1.1759999999999999,52.919999999999995,{"$f":"G18/G18","v":1},{"$f":"G18-G18","v":0}]
[null,45,0.25,44,85,41,1,45,{"$f":"G19/G18","v":0.85034013605442182},{"$f":"G18-G19","v":0.17599999999999993}]
[null,45,0.25,44,75,31,0.82799999999999996,37.26,{"$f":"G20/G18","v":0.70408163265306123},{"$f":"G18-G20","v":0.34799999999999998}]
[null,45,0.25,44,65,21,0.67800000000000005,30.51,{"$f":"G21/G18","v":0.57653061224489799},{"$f":"G18-G21","v":0.49799999999999989}]
[]
[]
[]
[null,"eQuest Curve Coefficients"]
[null,null,"Const","PLR","PLR^2","dT","dT^2","PLR*dT"]
[null,"Proposed",0.10173031,-5.3528260000000001E-2,0.30710577999999999,-2.0752800000000001E-3,2.9430000000000001E-5,1.3215569999999999E-2]
[null,"Base",1.040687E-2,1.0518330300000001,-9.4624589999999995E-2,1.63543E-3,-7.79E-6,-6.0324E-4]
[]
[]
["Base Case Chiller Part Load Data"]
[]
[null,"tons",null,"CHWT","OAT","Rated kW",{"$f":"G34*B34","v":225.625}]
["Rating",180.5,null,44,95,"kW/ton",1.25,{"$f":"(G34*B34*3413)/(B34*12000)","v":0.35552083333333334}]
[null,"tons","PLR","CHWT","OAT","dT","kW/ton","kW"]
[null,180.5,{"$f":"B36/$B$34","v":1},44,95,{"$f":"E36-D36","v":51},1.25,{"$f":"G36*B36","v":225.625},{"$f":"G36/G36","v":1},{"$f":"G36-G36","v":0},null,null,null,null,"OAT",1,0.75,0.5,0.25]
[null,184.5,1.0221606648199446,44,85,41,1.071,{"$f":"G37*B37","v":197.59949999999998},{"$f":"G37/G36","v":0.85680000000000001},{"$f":"G36-G37","v":0.17900000000000005},null,null,null,null,95,{"$f":"G36","v":1.25},{"$f":"G40","v":1.143},{"$f":"G44","v":1.2769999999999999},{"$f":"G48","v":1.121}]
[null,187.8,1.040443213296399,44,75,31,0.92300000000000004,173.33940000000001,{"$f":"G38/G36","v":0.73840000000000006},{"$f":"G36-G38","v":0.32699999999999996},null,null,null,null,85,{"$f":"G37","v":1.071},{"$f":"G41","v":1},{"$f":"G45","v":1.081},{"$f":"G49","v":0.97599999999999998}]
[null,188.9,1.0465373961218838,44,65,21,0.85099999999999998,160.75389999999999,{"$f":"G39/G36","v":0.68079999999999996},{"$f":"G36-G39","v":0.39900000000000002},null,null,null,null,75,{"$f":"G38","v":0.92300000000000004},{"$f":"G42","v":0.90200000000000002},{"$f":"G46","v":0.98399999999999999},{"$f":"G50","v":0.94499999999999995}]
[null,135.4,0.75013850415512473,44,95,51,1.143,154.76220000000001,{"$f":"G40/G40","v":1},{"$f":"G40-G40","v":0},null,null,null,null,65,{"$f":"G39","v":0.85099999999999998},{"$f":"G43","v":0.86299999999999999},{"$f":"G47","v":0.94499999999999995},{"$f":"G51","v":1.2}]
[null,138.4,0.76675900277008313,44,85,41,1,138.4,{"$f":"G41/G40","v":0.87489063867016625},{"$f":"G40-G41","v":0.14300000000000002}]
[null,115.7,0.64099722991689756,44,75,31,0.90200000000000002,104.3614,{"$f":"G42/G40","v":0.78915135608048992},{"$f":"G40-G42","v":0.24099999999999999}]
[null,141.69999999999999,0.78504155124653729,44,65,21,0.86299999999999999,122.2871,{"$f":"G43/G40","v":0.75503062117235342},{"$f":"G40-G43","v":0.28000000000000003}]
[null,90.3,0.50027700831024924,44,95,51,1.2769999999999999,115.31309999999999,{"$f":"G44/G44","v":1},{"$f":"G44-G44","v":0}]
[null,92.3,0.51135734072022154,44,85,41,1.081,99.776299999999992,{"$f":"G45/G44","v":0.84651527016444794},{"$f":"G44-G45","v":0.19599999999999995}]
[null,86,0.47645429362880887,44,75,31,0.98399999999999999,84.623999999999995,{"$f":"G46/G44","v":0.77055599060297575},{"$f":"G44-G46","v":0.29299999999999993}]
[null,94.4,0.52299168975069255,44,65,21,0.94499999999999995,89.207999999999998,{"$f":"G47/G44","v":0.74001566170712607},{"$f":"G44-G47","v":0.33199999999999996}]
[null,45.1,0.24986149584487535,44,95,51,1.121,50.557099999999998,{"$f":"G48/G48","v":1},{"$f":"G48-G48","v":0}]
[null,46.1,0.25540166204986148,44,85,41,0.97599999999999998,44.993600000000001,{"$f":"G49/G48","v":0.87065120428189113},{"$f":"G48-G49","v":0.14500000000000002}]
[null,41.1,0.22770083102493074,44,75,31,0.94499999999999995,38.839500000000001,{"$f":"G50/G48","v":0.84299732381801962},{"$f":"G48-G50","v":0.17600000000000005}]
[null,47.2,0.26149584487534627,44,65,21,1.2,56.64,{"$f":"G51/G48","v":1.0704727921498662},{"$f":"G48-G51","v":-7.8999999999999959E-2}]