{"text_format":"1","workbook":"xlsx","n_sheets":36,"sheets":["Instructions","Project Info","Measure Summary","Building Shell Inputs","BldgShell1-AirSealing","BldgShell2-Insulation","Compressed Air Inputs","CompAir1-Storage","CompAir2-Nozzle","CompAir3-LPFilter","CompAir4-ZeroLossDrain","CompAir5-LeakRepair","CompAir6-NewCompressor","CompAir7-NewAirDryer","Hot Water Inputs","HW1-Showerheads","HW2-SteamTraps","HW3-WaterHeater","HVAC Inputs","HVAC1-BoilerReset","HVAC2-DCV","HVAC3-Economizer","HVAC4-DuctInsulation","HVAC5-DuctSealing","HVAC6-HotelOccSensor","HVAC7-DHW_PipeInsulation","HVAC8-SpaceHtgPipeInsulation","HVAC9-WifiTstat","HVAC10-HeatPumps","HVAC11-Unitary&Split","HVAC12-Chillers","HVAC13-ProgTstats","HVAC14-PTHP","HVAC15-CircPumps","Motors and Drives Inputs","Appliances Inputs"],"not_rendered":{"charts":0,"images":1,"macros":1,"external_links":2,"defined_names":109,"comments":11,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Instructions","index":0,"n_rows":40,"n_cols":14,"rows_kept":40,"cut":false,"hidden":false,"merged":[[22,1,32,10],[3,12,7,16],[2,12,2,16],[21,1,21,10],[3,1,7,10],[2,1,2,10],[10,1,13,10],[9,1,9,10],[15,1,15,10],[16,1,19,10],[9,12,9,16],[10,13,10,16],[11,13,11,16]]}
[null,"Version date:","2026-03-20"]
[]
[null,"NHSaves Technical Reference Manual Calculation Tool Overview",null,null,null,null,null,null,null,null,null,null,"Link to NHSaves eTRM"]
[null,"This tool provides energy savings calculations for commercial retrofit energy conservation measures (ECMs) listed in the New Hampshire Technical Reference Manual.  The savings calculations do not include food service or lighting measures."]
[]
[]
[]
[]
[]
[null,"Step 1: Enter General Project Information",null,null,null,null,null,null,null,null,null,null,"Key"]
[null,"General project information must be entered as the first step in the \"Project Info\" worksheet when starting any new project. ",null,null,null,null,null,null,null,null,null,null,null,"Input Cells"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Calculation Cells"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Guidance/Information Cells"]
[]
[]
[null,"Step 2: Select ECMs"]
[null,"Select energy efficiency measures to be analyzed in the \"Measure Summary\" tab by choosing \"Yes\" for each ECM associated with the project (this highlights all input cells needed for user to fill in and enables the calculation worksheet to become visible for that measure)"]
[]
[]
[]
[]
[null,"Step 3: Enter input data"]
[null,"The tool covers 32 ECMs with automated savings calculations based on the applicable user inputs. There are six sheets to be used to enter the relevant calculation inputs for each measure.\n\n- Building Shell, HW & HVAC Inputs\n- Compressed Air Inputs\n- Hot Water Inputs\n- Heat Pump Inputs\n- Motors and Drives Inputs\n- Appliances Inputs\n\nThese are all ORANGE colored tabs, while the sheets containing the calculations (and no inputs) are GREY."]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"Version Notes: "]
[null,"2026-03-20","Updated VFD & Air Sealing calcs ",null,null,"Amir E. "]

{"sheet":"Project Info","index":1,"n_rows":44,"n_cols":27,"rows_kept":44,"cut":false,"hidden":false,"merged":[[0,1,0,2],[6,8,28,14],[5,8,5,14],[5,1,5,5],[7,1,7,2],[8,1,8,2],[9,1,9,2],[10,1,10,2],[11,1,11,2],[12,1,12,2],[13,1,13,2],[6,1,6,2],[20,1,20,2],[16,1,16,2],[17,1,17,2],[19,1,19,2],[25,1,25,2],[26,1,26,2],[18,1,18,2],[21,1,21,2],[22,1,22,2],[23,1,23,2],[24,1,24,2]]}
[null,"Key"]
[null,null,"Input Cells"]
[null,null,"Calculation Cells"]
[null,null,"Guidance/Information Cells"]
[]
[null,"Project Contact Information",null,null,null,null,null,null,"Project Description (include existing and proposed case)",null,null,null,null,null,null,null,"Building Type",null,null,"Weather Data Locations",null,null,"HVAC Type",null,"Heating Fuel Types",null,"DHW Fuel "]
[null,"Field",null,"Customer","Electric Utility","Gas Utility",null,null,null,null,null,null,null,null,null,null,"Community College",null,null,"Berlin",null,null,"CV Econ",null,"Gas",null,"Gas"]
[null,"Company:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"High School",null,null,"Concord",null,null,"CV nonecon",null,"Propane",null,"Propane "]
[null,"Contact Name:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hospital",null,null,"Keene",null,null,"VAV",null,"Fuel Oil",null,"Fuel Oil"]
[null,"Contact Email Address: ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hotel",null,null,"Laconia",null,null,"Unknown",null,"Electric",null,"Electric Resistance"]
[null,"Contact Phone:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Large Office",null,null,"Lebanon",null,null,null,null,null,null,"Electric Heat Pump"]
[null,"Account #:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Large Retail",null,null,"Manchester",null,null,"Cooling Type",null,"Heating Type"]
[null,"Application #:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"University",null,null,"Portsmouth",null,null,"Packaged DX AHU",null,"Gas-fired"]
[null,"Calculations completed by:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Assembly",null,null,null,null,null,"AHU with CHW",null,"Hot water boiler"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Auto Repair",null,null,"Electric Utilities",null,null,"Zone heat pump",null,"Steam boiler"]
[null,"Site Information",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Big Box Retail",null," ","Eversource",null,null,"FCU/Chilled beam with CHW",null,"Heat pump"]
[null,"Site Name:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Dormitory",null,null,"NH Electric Co-op",null,null,"Other",null,"Electric resistance"]
[null,"Street Address:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Fast Food Restaurant",null,null,"Liberty"]
[null,"City,  Zip code:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Full Service Restaurant",null,null,"Unitil"]
[null,"Building Type:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Grocery",null,null,"Municipal Electric"]
[null,"Weather Data:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Light Industrial"]
[null,"HVAC Type:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Motel",null,null,"Gas Utilies"]
[null,"Cooling System Type:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Primary School",null,null,"Liberty"]
[null,"Space Heating Fuel:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Religious",null,null,"Unitil"]
[null,"Space Heating System Type:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Small Office",null,null,"Municipal Gas"]
[null,"Space Heating Boiler Type:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Small Retail",null,null,"N/A"]
[null,"Domestic Water Heater Fuel Type:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Warehouse"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Other"]
[null,"Billing Data"]
[null,"(may be entered for Liberty customers when helpful)"]
[null,"Month","Electric (kWh)",{"$f":"D24","v":0}]
[null,"Jan"]
[null,"Feb"]
[null,"Mar"]
[null,"Apr"]
[null,"May"]
[null,"Jun"]
[null,"Jul"]
[null,"Aug"]
[null,"Sep"]
[null,"Oct"]
[null,"Nov"]
[null,"Dec"]
[null,"Total",{"$f":"SUM(C32:C43)","v":0},{"$f":"SUM(D32:D43)","v":0}]

{"sheet":"Measure Summary","index":2,"n_rows":40,"n_cols":20,"rows_kept":40,"cut":false,"hidden":false,"merged":[[0,0,0,1],[5,15,5,19],[0,3,0,10],[1,3,2,10]]}
["Key",null,null,"Instructions"]
[null,"Input Cells",null,"Please select \"Yes\" or \"No\" on the  ORANGE cells in this sheet to include the energy savings of the facility's project measures.  Then complete the measure specific information on each of the associated ORANGE tabs. "]
[null,"Calculation Cells"]
[null,"Guidance/Information Cells"]
[]
[null,"Summary of TRM Measures",null,null,null,null,null,null,null,null,null,null,null,null,null,"Conversion Table"]
[null,"Energy Conservation Measures (ECM)",null,null,"Calculate","Annual Savings",null,null,"Heating","Water","Measure Life","Review","Input",null,null,"Fuel","MMBtu","=","Conversion Factor","Unit"]
[null,"Measure Name","Measure TRM Category","#","ECM?","kWh","Summer kW","Winter kW",{"$f":"IF('Project Info'!D24=\"Electric\",\"kWh\",IF('Project Info'!D24=\"Gas\",\"therms\",IF('Project Info'!D24=\"Fuel Oil\",\"gallons of oil\",IF('Project Info'!D24=\"Propane\",\"gallons of propane\",\"\"))))","v":""},"gallons","Years","Notes","Sheet",null,null,"Electric",1,null,{"$f":"1000000/3412","v":293.08323563892145},"kWh"]
[null,"Air Sealing","Building Shell",1,"No",{"$f":"IF(E9=\"Yes\",'BldgShell1-AirSealing'!D7,0)","v":0},{"$f":"IF(E9=\"Yes\",('BldgShell1-AirSealing'!D6*'BldgShell1-AirSealing'!D11/100),0)","v":0},{"$f":"IF(E9=\"Yes\",('BldgShell1-AirSealing'!D6*'BldgShell1-AirSealing'!D13/100),0)","v":0},{"$f":"IF('Project Info'!D24=\"\",0,IF(E9=\"Yes\",'BldgShell1-AirSealing'!D8*VLOOKUP('Project Info'!$D$24,'Measure Summary'!$P$8:$T$11,4,FALSE),0))","v":0},0,{"$f":"IF(E9=\"Yes\",'BldgShell1-AirSealing'!D9,\"\")","v":""},{"$f":"IF(AND(E9=\"Yes\",OR(F9>0,I9>0)),\"TRM calculates heating savings only.\",IF(AND(E9=\"Yes\",OR(F9=0,I9=0)),\"Check Inputs. Measure selected, but no savings are calculated.\",\"\"))","v":""},"Building Shell Inputs",null,null,"Gas",1,null,10,"therms"]
[null,"Insulation","Building Shell",2,"No",{"$f":"IF(E10=\"Yes\",'BldgShell2-Insulation'!D7,0)","v":0},{"$f":"IF(E10=\"Yes\",('BldgShell2-Insulation'!D6*'BldgShell2-Insulation'!D11/100),0)","v":0},{"$f":"IF(E10=\"Yes\",('BldgShell2-Insulation'!D6*'BldgShell1-AirSealing'!D13/100),0)","v":0},{"$f":"IF('Project Info'!D24=\"\",0,IF(E10=\"Yes\",'BldgShell2-Insulation'!D8*VLOOKUP('Project Info'!$D$24,'Measure Summary'!$P$8:$T$11,4,FALSE),0))","v":0},0,{"$f":"IF(E10=\"Yes\",'BldgShell2-Insulation'!D10,\"\")","v":""},{"$f":"IF(AND(E10=\"Yes\",OR(F10>0,I10>0)),\"TRM calculates heating savings only.\",IF(AND(E10=\"Yes\",OR(F10=0,I10=0)),\"Check Inputs. Measure selected, but no savings are calculated.\",\"\"))","v":""},"Building Shell Inputs",null,null,"Fuel Oil",1,null,7.1429,"gallons of #2 Fuel Oil"]
[null,"Adding Compressor Storage","Compressed Air",1,"No",{"$f":"IF(E11=\"Yes\",'CompAir1-Storage'!D7,0)","v":0},{"$f":"IF(E11=\"Yes\",'CompAir1-Storage'!D6*'CompAir1-Storage'!D10/100,0)","v":0},{"$f":"IF(E11=\"Yes\",'CompAir1-Storage'!D6*'CompAir1-Storage'!D11/100,0)","v":0},0,0,{"$f":"IF(E11=\"Yes\",'CompAir1-Storage'!D9,\"\")","v":""},{"$f":"IF(OR(AND(E11=\"No\",F11>0),AND(E11=\"No\",I11>0)),\"Check inputs. Measure not selected, but shows savings.\",IF(AND(E11=\"Yes\",AND(F11=0,I11=0)),\"Check Inputs. Measure selected, but no savings are calculated.\",\"\"))","v":""},"Compressed Air Inputs",null,null,"Propane",1,null,10.917,"gallons of propane"]
[null,"Air Nozzle","Compressed Air",2,"No",{"$f":"IF(E12=\"Yes\",'CompAir2-Nozzle'!D7,0)","v":0},{"$f":"IF(E12=\"Yes\",'CompAir2-Nozzle'!D6*'CompAir2-Nozzle'!D10/100,0)","v":0},{"$f":"IF(E12=\"Yes\",'CompAir2-Nozzle'!D6*'CompAir2-Nozzle'!D11/100,0)","v":0},0,0,{"$f":"IF(E12=\"Yes\",'CompAir2-Nozzle'!D9,\"\")","v":""},"","Compressed Air Inputs"]
[null,"Low Pressure Drop Filter","Compressed Air",3,"No",{"$f":"IF(E13=\"Yes\",'CompAir3-LPFilter'!D7,0)","v":0},{"$f":"IF(E13=\"Yes\",'CompAir3-LPFilter'!D6*'CompAir3-LPFilter'!D10/100,0)","v":0},{"$f":"IF(E13=\"Yes\",'CompAir3-LPFilter'!D6*'CompAir3-LPFilter'!D11/100,0)","v":0},0,0,{"$f":"IF(E13=\"Yes\",'CompAir3-LPFilter'!D9,\"\")","v":""},"","Compressed Air Inputs",null,null,"Header",{"$f":"'Project Info'!E8&\" / \"&'Project Info'!F8&\" / \"&'Project Info'!D8","v":" /  / "}]
[null,"Zero Loss Condensate Drain","Compressed Air",4,"No",{"$f":"IF(E14=\"Yes\",'CompAir4-ZeroLossDrain'!D7,0)","v":0},{"$f":"IF(E14=\"Yes\",'CompAir4-ZeroLossDrain'!D6*'CompAir4-ZeroLossDrain'!D10/100,0)","v":0},{"$f":"IF(E14=\"Yes\",'CompAir4-ZeroLossDrain'!D6*'CompAir4-ZeroLossDrain'!D11/100,0)","v":0},0,0,{"$f":"IF(E14=\"Yes\",'CompAir4-ZeroLossDrain'!D9,\"\")","v":""},"","Compressed Air Inputs"]
[null,"Compressed Air Leak Detection & Repair","Compressed Air",5,"No",{"$f":"IF(E15=\"Yes\",'CompAir5-LeakRepair'!D7,0)","v":0},{"$f":"IF(E15=\"Yes\",'CompAir5-LeakRepair'!D6*'CompAir5-LeakRepair'!D10/100,0)","v":0},{"$f":"IF(E15=\"Yes\",'CompAir5-LeakRepair'!D6*'CompAir5-LeakRepair'!D11/100,0)","v":0},0,0,{"$f":"IF(E15=\"Yes\",'CompAir5-LeakRepair'!D9,\"\")","v":""},{"$f":"IF(OR(AND(E15=\"No\",F15>0),AND(E15=\"No\",I15>0)),\"Check inputs. Measure not selected, but shows savings.\",IF(AND(E15=\"Yes\",AND(F15=0,I15=0)),\"Check Inputs. Measure selected, but no savings are calculated.\",\"\"))","v":""},"Compressed Air Inputs"]
[null,"New Air Compressor","Compressed Air",6,"No",{"$f":"IF(E16=\"Yes\",'CompAir6-NewCompressor'!D7,0)","v":0},{"$f":"IF(E16=\"Yes\",'CompAir6-NewCompressor'!D6*'CompAir6-NewCompressor'!D10/100,0)","v":0},{"$f":"IF(E16=\"Yes\",'CompAir6-NewCompressor'!D6*'CompAir6-NewCompressor'!D11/100,0)","v":0},0,0,{"$f":"IF(E16=\"Yes\",'CompAir6-NewCompressor'!D9,\"\")","v":""},"","Compressed Air Inputs"]
[null,"New Refrigerated Air Dryer","Compressed Air",7,"No",{"$f":"IF(E17=\"Yes\",'CompAir7-NewAirDryer'!D7,0)","v":0},{"$f":"IF(E17=\"Yes\",'CompAir7-NewAirDryer'!D6*'CompAir7-NewAirDryer'!D10/100,0)","v":0},{"$f":"IF(E17=\"Yes\",'CompAir7-NewAirDryer'!D6*'CompAir7-NewAirDryer'!D11/100,0)","v":0},0,0,{"$f":"IF(E17=\"Yes\",'CompAir7-NewAirDryer'!D9,\"\")","v":""},"","Compressed Air Inputs"]
[null,"Showerheads (Low-Flow & Thermostatic Shut-Off Valve)","Hot Water",1,"No",{"$f":"IF('Project Info'!D27=\"\",0,IF(E18=\"Yes\",'HW1-Showerheads'!D7,0))","v":0},{"$f":"IF('Project Info'!D27=\"\",0,IF(E18=\"Yes\",'HW1-Showerheads'!D6*'HW1-Showerheads'!D11/100,0))","v":0},{"$f":"IF('Project Info'!D27=\"\",0,IF(E18=\"Yes\",'HW1-Showerheads'!D6*'HW1-Showerheads'!D12/100,0))","v":0},{"$f":"IF('Project Info'!D27=\"\",0,IF(E18=\"Yes\",'HW1-Showerheads'!D8*VLOOKUP('Project Info'!$D$24,'Measure Summary'!$P$8:$T$11,4,FALSE),0))","v":0},{"$f":"IF(E18=\"Yes\",'HW1-Showerheads'!D9,0)","v":0},{"$f":"IF(E18=\"Yes\",'HW1-Showerheads'!D10,\"\")","v":""},"","Hot Water Inputs"]
[null,"Steam Traps","Hot Water",2,"No",{"$f":"IF(E19=\"Yes\",'HW2-SteamTraps'!D7,0)","v":0},{"$f":"IF(E19=\"Yes\",'HW2-SteamTraps'!D6*'HW2-SteamTraps'!D10/100,0)","v":0},{"$f":"IF(E19=\"Yes\",'HW2-SteamTraps'!D6*'HW2-SteamTraps'!D11/100,0)","v":0},{"$f":"IF(E19=\"Yes\",'HW2-SteamTraps'!D8*VLOOKUP('Project Info'!$D$24,'Measure Summary'!$P$8:$T$11,4,FALSE),0)","v":0},0,{"$f":"IF(E19=\"Yes\",'HW2-SteamTraps'!D9,\"\")","v":""},{"$f":"IF(OR(AND(E19=\"No\",F19>0),AND(E19=\"No\",I19>0)),\"Check inputs. Measure not selected, but shows savings.\",IF(AND(E19=\"Yes\",AND(F19=0,I19=0)),\"Check Inputs. Measure selected, but no savings are calculated.\",\"\"))","v":""},"Hot Water Inputs"]
[null,"Water Heaters","Hot Water",3,"No",{"$f":"'HW3-WaterHeater'!D7","v":0},{"$f":"IF(E20=\"Yes\",'HW3-WaterHeater'!D6*'HW3-WaterHeater'!D10/100,0)","v":0},{"$f":"IF(E20=\"Yes\",'HW3-WaterHeater'!D6*'HW3-WaterHeater'!D11/100,0)","v":0},{"$f":"IF('Project Info'!D27=\"\",0,(IF(E20=\"Yes\",('HW3-WaterHeater'!D8*VLOOKUP('Project Info'!$D$24,'Measure Summary'!$P$8:$T$11,4,FALSE)),0)))","v":0},0,{"$f":"IF(E20=\"Yes\",'HW3-WaterHeater'!D9,\"\")","v":""},"","Hot Water Inputs"]
[null,"Boiler Reset Controls","HVAC",1,"No",{"$f":"IF(E21=\"Yes\",'HVAC1-BoilerReset'!D7,0)","v":0},{"$f":"IF(E21=\"Yes\",'HVAC1-BoilerReset'!D6*'HVAC1-BoilerReset'!D10/100,0)","v":0},{"$f":"IF(E21=\"Yes\",'HVAC1-BoilerReset'!D6*'HVAC1-BoilerReset'!D11/100,0)","v":0},{"$f":"IF(E21=\"Yes\",'HVAC1-BoilerReset'!D8*VLOOKUP('Project Info'!$D$24,'Measure Summary'!$P$8:$T$11,4,FALSE),0)","v":0},0,{"$f":"IF(E21=\"Yes\",'HVAC1-BoilerReset'!D9,\"\")","v":""},"","HVAC Inputs"]
[null,"Demand Control Ventilation","HVAC",2,"No",{"$f":"IF(E22=\"Yes\",'HVAC2-DCV'!D7,0)","v":0},{"$f":"IF(E22=\"Yes\",'HVAC2-DCV'!D6*'HVAC2-DCV'!D10/100,0)","v":0},{"$f":"IF(E22=\"Yes\",'HVAC2-DCV'!D6*'HVAC2-DCV'!D11/100,0)","v":0},{"$f":"IF('Project Info'!D24=\"\",0,IF(E22=\"Yes\",'HVAC2-DCV'!D8*VLOOKUP('Project Info'!$D$24,'Measure Summary'!$P$8:$T$11,4,FALSE),0))","v":0},0,{"$f":"IF(E22=\"Yes\",'HVAC2-DCV'!D9,\"\")","v":""},{"$f":"IF(AND(E22=\"Yes\",OR(F22>0,I22>0)),\"TRM calculates cooling savings only.\",IF(AND(E22=\"Yes\",OR(F22=0,I22=0)),\"Check Inputs. Measure selected, but no savings are calculated.\",\"\"))","v":""},"HVAC Inputs"]
[null,"Dual Enthalpy Economizer Controls","HVAC",3,"No",{"$f":"IF(E23=\"Yes\",'HVAC3-Economizer'!D7,0)","v":0},{"$f":"IF(E23=\"Yes\",'HVAC3-Economizer'!D6*'HVAC3-Economizer'!D10/100,0)","v":0},{"$f":"IF(E23=\"Yes\",'HVAC3-Economizer'!D6*'HVAC3-Economizer'!D11/100,0)","v":0},{"$f":"IF(E23=\"Yes\",IF('HVAC3-Economizer'!D8=0,0,'HVAC3-Economizer'!D8*VLOOKUP('Project Info'!$D$24,'Measure Summary'!$P$8:$T$11,4,FALSE)),0)","v":0},0,{"$f":"IF(E23=\"Yes\",'HVAC3-Economizer'!D9,\"\")","v":""},"","HVAC Inputs"]
[null,"Duct Insulation","HVAC",4,"No",{"$f":"IF(E24=\"Yes\",'HVAC4-DuctInsulation'!D7,0)","v":0},{"$f":"IF(E24=\"Yes\",'HVAC4-DuctInsulation'!D6*'HVAC4-DuctInsulation'!D10/100,0)","v":0},{"$f":"IF(E24=\"Yes\",'HVAC4-DuctInsulation'!D6*'HVAC4-DuctInsulation'!D11/100,0)","v":0},{"$f":"IF(E24=\"Yes\",IF('HVAC4-DuctInsulation'!D8=0,0,'HVAC4-DuctInsulation'!D8*VLOOKUP('Project Info'!$D$24,'Measure Summary'!$P$8:$T$11,4,FALSE)),0)","v":0},0,{"$f":"IF(E24=\"Yes\",'HVAC4-DuctInsulation'!D9,\"\")","v":""},"","HVAC Inputs"]
[null,"Duct Sealing","HVAC",5,"No",{"$f":"IF(E25=\"Yes\",'HVAC5-DuctSealing'!D7,0)","v":0},{"$f":"IF(E25=\"Yes\",'HVAC5-DuctSealing'!D6*'HVAC5-DuctSealing'!D10/100,0)","v":0},{"$f":"IF(E25=\"Yes\",'HVAC5-DuctSealing'!D6*'HVAC5-DuctSealing'!D11/100,0)","v":0},{"$f":"IF(E25=\"Yes\",IF('HVAC5-DuctSealing'!D8=0,0,'HVAC5-DuctSealing'!D8*VLOOKUP('Project Info'!$D$24,'Measure Summary'!$P$8:$T$11,4,FALSE)),0)","v":0},0,{"$f":"IF(E25=\"Yes\",'HVAC5-DuctSealing'!D9,\"\")","v":""},{"$f":"IF(OR(AND(E25=\"No\",F25>0),AND(E25=\"No\",I25>0)),\"Check inputs. Measure not selected, but shows savings.\",IF(AND(E25=\"Yes\",AND(F25=0,I25=0)),\"Check Inputs. Measure selected, but no savings are calculated.\",\"\"))","v":""},"HVAC Inputs"]
[null,"Hotel Occupancy Sensor","HVAC",6,"No",{"$f":"IF(E26=\"Yes\",'HVAC6-HotelOccSensor'!D7,0)","v":0},{"$f":"IF(E26=\"Yes\",'HVAC6-HotelOccSensor'!D6*'HVAC6-HotelOccSensor'!D10/100,0)","v":0},{"$f":"IF(E26=\"Yes\",'HVAC6-HotelOccSensor'!D6*'HVAC6-HotelOccSensor'!D11/100,0)","v":0},{"$f":"IF('Project Info'!D24=\"\",0,IF(E26=\"Yes\",'HVAC6-HotelOccSensor'!D8*VLOOKUP('Project Info'!$D$24,'Measure Summary'!$P$8:$T$11,4,FALSE),0))","v":0},0,{"$f":"IF(E26=\"Yes\",'HVAC6-HotelOccSensor'!D9,\"\")","v":""},{"$f":"IF(AND(E26=\"Yes\",OR(F26>0,I26>0)),\"TRM calculates electric savings only.\",IF(AND(E26=\"Yes\",OR(F26=0,I26=0)),\"Check Inputs. Measure selected, but no savings are calculated.\",\"\"))","v":""},"HVAC Inputs"]
[null,"Domestic Hot Water Pipe Insulation","HVAC",7,"No",{"$f":"IF(E27=\"Yes\",'HVAC7-DHW_PipeInsulation'!D7,0)","v":0},{"$f":"IF(E27=\"Yes\",'HVAC7-DHW_PipeInsulation'!D6*'HVAC7-DHW_PipeInsulation'!D10/100,0)","v":0},{"$f":"IF(E27=\"Yes\",'HVAC7-DHW_PipeInsulation'!D6*'HVAC7-DHW_PipeInsulation'!D11/100,0)","v":0},{"$f":"IF(E27=\"Yes\",IF('HVAC7-DHW_PipeInsulation'!D8=0,0,'HVAC7-DHW_PipeInsulation'!D8*VLOOKUP('Project Info'!$D$24,'Measure Summary'!$P$8:$T$11,4,FALSE)),0)","v":0},0,{"$f":"IF(E27=\"Yes\",'HVAC7-DHW_PipeInsulation'!D9,\"\")","v":""},"","HVAC Inputs"]
[null,"Space Heating - Steam or Hot Water Pipe Insulation","HVAC",8,"No",{"$f":"IF(E28=\"Yes\",'HVAC8-SpaceHtgPipeInsulation'!D7,0)","v":0},{"$f":"IF(E28=\"Yes\",'HVAC8-SpaceHtgPipeInsulation'!D6*'HVAC7-DHW_PipeInsulation'!D10/100,0)","v":0},{"$f":"IF(E28=\"Yes\",'HVAC8-SpaceHtgPipeInsulation'!D6*'HVAC8-SpaceHtgPipeInsulation'!D11/100,0)","v":0},{"$f":"IF(E28=\"Yes\",IF('HVAC8-SpaceHtgPipeInsulation'!D8=0,0,'HVAC8-SpaceHtgPipeInsulation'!D8*VLOOKUP('Project Info'!$D$24,'Measure Summary'!$P$8:$T$11,4,FALSE)),0)","v":0},0,{"$f":"IF(E28=\"Yes\",'HVAC8-SpaceHtgPipeInsulation'!D9,\"\")","v":""},{"$f":"IF(OR(AND(E28=\"No\",F28>0),AND(E28=\"No\",I28>0)),\"Check inputs. Measure not selected, but shows savings.\",IF(AND(E28=\"Yes\",AND(F28=0,I28=0)),\"Check Inputs. Measure selected, but no savings are calculated.\",\"\"))","v":""},"HVAC Inputs"]
[null,"Thermostat - WiFi Communicating","HVAC",9,"No",{"$f":"IF(E29=\"Yes\",'HVAC9-WifiTstat'!D7,0)","v":0},{"$f":"IF(E29=\"Yes\",'HVAC9-WifiTstat'!D6*'HVAC9-WifiTstat'!D10/100,0)","v":0},{"$f":"IF(E29=\"Yes\",'HVAC9-WifiTstat'!D6*'HVAC9-WifiTstat'!D11/100,0)","v":0},{"$f":"IF('Project Info'!D24=\"\",0,IF(E29=\"Yes\",'HVAC9-WifiTstat'!D8*VLOOKUP('Project Info'!$D$24,'Measure Summary'!$P$8:$T$11,4,FALSE),0))","v":0},0,{"$f":"IF(E29=\"Yes\",'HVAC9-WifiTstat'!D9,\"\")","v":""},{"$f":"IF(AND(E29=\"Yes\",OR(F29>0,I29>0)),\"TRM calculates heating savings only.\",IF(AND(E29=\"Yes\",OR(F29=0,I29=0)),\"Check Inputs. Measure selected, but no savings are calculated.\",\"\"))","v":""},"HVAC Inputs"]
[null,"Heat Pumps","HVAC",10,"No",{"$f":"IF(E30=\"Yes\",'HVAC10-HeatPumps'!C6,0)","v":0},{"$f":"IF(E30=\"Yes\",'HVAC10-HeatPumps'!C5,0)","v":0},{"$f":"IF(E30=\"Yes\",'HVAC10-HeatPumps'!C4,0)","v":0},0,0,{"$f":"IF(E30=\"Yes\",'HVAC10-HeatPumps'!C7,\"\")","v":""},{"$f":"IF(OR(AND(E30=\"No\",F30>0),AND(E30=\"No\",I30>0)),\"Check inputs. Measure not selected, but shows savings.\",IF(AND(E30=\"Yes\",AND(F30=0,I30=0)),\"Check Inputs. Measure selected, but no savings are calculated.\",\"\"))","v":""},"HVAC Inputs"]
[null,"Unitary-Split","HVAC",11,"No",{"$f":"IF(E31=\"Yes\",'HVAC11-Unitary&Split'!D6,0)","v":0},{"$f":"IF(E31=\"Yes\",'HVAC11-Unitary&Split'!D5,0)","v":0},{"$f":"IF(E31=\"Yes\",'HVAC11-Unitary&Split'!D4,0)","v":0},0,0,{"$f":"IF(E31=\"Yes\",'HVAC11-Unitary&Split'!D7,\"\")","v":""},"","HVAC Inputs"]
[null,"Chillers","HVAC",12,"No",{"$f":"IF(E32=\"Yes\",'HVAC12-Chillers'!D6,0)","v":0},{"$f":"IF(E32=\"Yes\",'HVAC12-Chillers'!D5,0)","v":0},{"$f":"IF(E32=\"Yes\",'HVAC12-Chillers'!D4,0)","v":0},0,0,{"$f":"IF(E32=\"Yes\",'HVAC12-Chillers'!D7,\"\")","v":""},{"$f":"IF(OR(AND(E32=\"No\",F32>0),AND(E32=\"No\",I32>0)),\"Check inputs. Measure not selected, but shows savings.\",IF(AND(E32=\"Yes\",AND(F32=0,I32=0)),\"Check Inputs. Measure selected, but no savings are calculated.\",\"\"))","v":""},"HVAC Inputs"]
[null,"Programmable Thermostat","HVAC",13,"No",0,0,0,{"$f":"IF(E33=\"Yes\",IF('HVAC13-ProgTstats'!D8=0,0,'HVAC13-ProgTstats'!D8*VLOOKUP('Project Info'!$D$24,'Measure Summary'!$P$8:$T$11,4,FALSE)),0)","v":0},0,{"$f":"IF(E33=\"Yes\",'HVAC13-ProgTstats'!D9,\"\")","v":""},{"$f":"IF(OR(AND(E33=\"No\",F33>0),AND(E33=\"No\",I33>0)),\"Check inputs. Measure not selected, but shows savings.\",IF(AND(E33=\"Yes\",AND(F33=0,I33=0)),\"Check Inputs if gas, measure selected,and no savings calculated.\",\"\"))","v":""},"HVAC Inputs"]
[null,"Packaged Terminal Heat Pump (PTHP)","HVAC",14,"No",{"$f":"IF(E34=\"Yes\",'HVAC14-PTHP'!D8,0)","v":0},{"$f":"IF(E34=\"Yes\",'HVAC14-PTHP'!D6, 0)","v":0},{"$f":"IF(E34=\"Yes\",'HVAC14-PTHP'!D7,0)","v":0},0,0,{"$f":"IF(E34=\"Yes\",'HVAC14-PTHP'!D9,\"\")","v":""},{"$f":"IF(OR(AND(E34=\"No\",F34>0),AND(E34=\"No\",I34>0)),\"Check inputs. Measure not selected, but shows savings.\",IF(AND(E34=\"Yes\",AND(F34=0,I34=0)),\"Check Inputs. Measure selected, no savings are calculated.\",\"\"))","v":""},"HVAC Inputs"]
[null,"Circulator Pumps","HVAC",15,"No",{"$f":"IF(E35=\"Yes\",'HVAC15-CircPumps'!D8,0)","v":0},{"$f":"IF(E35=\"Yes\",'HVAC15-CircPumps'!D7*'HVAC15-CircPumps'!D10/100,0)","v":0},{"$f":"IF(E35=\"Yes\",'HVAC15-CircPumps'!D7*'HVAC15-CircPumps'!D11/100,0)","v":0},0,0,{"$f":"IF(E35=\"Yes\",'HVAC15-CircPumps'!D9,\"\")","v":""},"","HVAC Inputs"]
[null,"Variable Frequency Drive","Motors and Drives",1,"No",{"$f":"IF(E36=\"Yes\",'Motors and Drives Inputs'!E33,0)","v":0},{"$f":"IF(E36=\"Yes\",'Motors and Drives Inputs'!K27,0)","v":0},{"$f":"IF(E36=\"Yes\",'Motors and Drives Inputs'!J27,0)","v":0},{"$f":"IF('Motors and Drives Inputs'!E34=0,0,(IF(E36=\"Yes\",'Motors and Drives Inputs'!E34*VLOOKUP('Project Info'!$D$24,'Measure Summary'!$P$8:$T$11,4,FALSE),0)))","v":0},0,{"$f":"IF(E36=\"Yes\",'Motors and Drives Inputs'!E35,\"\")","v":""},"","Motors and Drives"]
[null,"Air Purifiers","Appliances",1,"No",{"$f":"IF(E37=\"Yes\",'Appliances Inputs'!D39,0)","v":0},{"$f":"IF(E37=\"Yes\",'Appliances Inputs'!D38*'Appliances Inputs'!D42/100,0)","v":0},{"$f":"IF(E37=\"Yes\",'Appliances Inputs'!D38*'Appliances Inputs'!D43/100,0)","v":0},0,0,{"$f":"IF(E37=\"Yes\",'Appliances Inputs'!D41,\"\")","v":""},"","Appliances"]
[null,"Dehumidifiers","Appliances",2,"No",{"$f":"IF(E38=\"Yes\",'Appliances Inputs'!P32,0)","v":0},{"$f":"IF(E38=\"Yes\",'Appliances Inputs'!P31*'Appliances Inputs'!P35/100,0)","v":0},{"$f":"IF(E38=\"Yes\",'Appliances Inputs'!P31*'Appliances Inputs'!P36/100,0)","v":0},0,0,{"$f":"IF(E38=\"Yes\",'Appliances Inputs'!P34,\"\")","v":""},"","Appliances"]
[null,"Total",null,null,{"$f":"COUNTIF(E9:E38,\"Yes\")","v":0},{"$f":"SUM(F9:F38)","v":0},{"$f":"SUM(G9:G38)","v":0},{"$f":"SUM(H9:H38)","v":0},{"$f":"SUM(I9:I38)","v":0},{"$f":"SUM(J9:J38)","v":0}]
[null,"% savings of total annual usage",null,null,null,{"$f":"IFERROR(F39/'Project Info'!C44,\"\")","v":""},null,null,{"$f":"IFERROR(IF(I8=\"kWh\",I39/'Project Info'!C44,I39/'Project Info'!D44),\"\")","v":""}]

{"sheet":"Building Shell Inputs","index":3,"n_rows":23,"n_cols":13,"rows_kept":23,"cut":false,"hidden":false,"merged":[[10,1,11,10],[0,0,1,11],[3,2,3,9],[4,2,7,9],[3,11,3,12]]}
["Building Shell Measures: Input Sheet"]
[]
[]
[null,null,"Instructions",null,null,null,null,null,null,null,null,"Key"]
[null,null,"Please fill out all  ORANGE cells in this sheet with the facility's building shell information and as applicable to the measure selection on the \"Measure Summary\" tab. Measures referenced by this sheet include Air Sealing and Insulation.",null,null,null,null,null,null,null,null,null,"Input Cells"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Calculation Cells"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Guidance/Information Cells"]
[]
[]
[]
[null,"Table 1: General ECM Questions"]
[]
[null,"Building Shell ECM1 - Air Sealing",null,null,null,null,null,null,null,null,"Inputs"]
[null,"Table 2 has been completed?"]
[null,"Pre-install photos of areas to be air sealed submitted to NHSaves?",null,null,null,null,null,null,null,null,null,{"$f":"IF(K15=\"No\",\"Please submit this\",\"\")","v":""}]
[null,"Building Shell ECM2 - Insulation"]
[null,"Table 2 has been completed?"]
[null,"Pre-install photos of areas to be insulated submitted to NHSaves?",null,null,null,null,null,null,null,null,null,{"$f":"IF(K18=\"No\",\"Please submit this\",\"\")","v":""}]
[]
[]
[null,null,"Table 2: Air Sealing and Insulation Measures"]
[null,null,"Room","Height","Floor Area","Air","Insulation","R-value","R-value","Insulated Area"]
[null,null,"Location","(ft)","(sqft)","Sealing","Location?","of existing Insulation","of added Insulation","(sqft)"]

{"sheet":"BldgShell1-AirSealing","index":4,"n_rows":8764,"n_cols":32,"rows_kept":2250,"cut":true,"hidden":true,"merged":[[1,13,1,14],[8,13,8,16],[4,6,15,10],[15,1,15,4],[16,6,19,10],[8,1,9,2],[10,1,11,2],[12,1,13,2],[0,1,1,10],[3,6,3,10],[3,1,3,4],[23,9,23,11],[16,1,16,2],[17,1,17,2],[18,1,18,2],[5,1,7,2],[17,3,17,4],[19,1,19,2],[16,3,16,4],[18,3,18,4],[19,3,19,4]],"bounds":{"rows_first":1000,"rows_last":250,"rows_between":1000,"halvings":1}}
[null,"Measure: Air Sealing"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 3: Insulation kW/kWh factors",null,null,null,null,null,"Table 6: TMY3 Weather Data - HDD60 Calculations"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"kW/kWh Factor",null,null,null,null,"Date",null,null,"Berlin",null,"Concord",null,"Dillant Hopkins/Keene",null,"Lebanon",null,"Pease/Portsmouth"]
[null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,"Electric",7.2999999999999996E-4,null,null,null,null,"Month","Day","Hour","db","HDD60","db","HDD60","db","HDD60","db","HDD60","db","HDD60"]
[null,null,null,"Value","Unit",null,"This measure considers savings associated with air sealing and insulation.\n\nDefinitions:\nAir sealing: Air sealing will decrease the infiltration of outside air through cracks and leaks in the building.\nInsulation: The installation of  insulation in an existing structure.",null,null,null,null,null,null,"Gas Oil Other FF",7.6000000000000004E-4,null,null,null,null,1,1,"01:00:00",20,{"$f":"IF(W5<60,(60-W5)/24,0)","v":1.6666666666666667},12.02,{"$f":"IF(Y5<60,(60-Y5)/24,0)","v":1.9991666666666668},19,{"$f":"IF(AA5<60,(60-AA5)/24,0)","v":1.7083333333333333},33,{"$f":"IF(AC5<60,(60-AC5)/24,0)","v":1.125},32,{"$f":"IF(AE5<60,(60-AE5)/24,0)","v":1.1666666666666667}]
[null,"Total Savings",null,{"$f":"L36","v":{"$error":"#VALUE!"}},"kW",null,null,null,null,null,null,null,null,"Central AC in Electrically Heated Unit",5.9000000000000003E-4,null,null,null,null,1,1,"02:00:00",19,1.7083333333333333,10.94,{"$f":"IF(Y6<60,(60-Y6)/24,0)","v":2.0441666666666669},21,{"$f":"IF(AA6<60,(60-AA6)/24,0)","v":1.625},31,{"$f":"IF(AC6<60,(60-AC6)/24,0)","v":1.2083333333333333},32.9,{"$f":"IF(AE6<60,(60-AE6)/24,0)","v":1.1291666666666667}]
[null,null,null,{"$f":"J36","v":0},"kWh",null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,1,"03:00:00",19,1.7083333333333333,10.039999999999999,2.0816666666666666,21,1.625,31,{"$f":"IF(AC7<60,(60-AC7)/24,0)","v":1.2083333333333333},32.9,1.1291666666666667]
[null,null,null,{"$f":"K36","v":0},"MMBtu",null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,1,"04:00:00",18,1.75,8.9600000000000009,2.1266666666666665,23,1.5416666666666667,30,{"$f":"IF(AC8<60,(60-AC8)/24,0)","v":1.25},32.9,1.1291666666666667]
[null,"Measure Life",null,15,"Years",null,null,null,null,null,null,null,null,"Table 4: Coincidence Factors",null,null,null,null,null,1,1,"05:00:00",17,1.7916666666666667,6.08,2.2466666666666666,23,1.5416666666666667,29,{"$f":"IF(AC9<60,(60-AC9)/24,0)","v":1.2916666666666667},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Measure Name","Fuel","CFsp","CFwp",null,null,1,1,"06:00:00",16,1.8333333333333333,6.08,2.2466666666666666,23,1.5416666666666667,28,{"$f":"IF(AC10<60,(60-AC10)/24,0)","v":1.3333333333333333},32.9,1.1291666666666667]
[null,"CFsp",null,{"$f":"VLOOKUP('Project Info'!D24,$O$11:$Q$14,2,FALSE)*100","v":{"$error":"#N/A"}},"%",null,null,null,null,null,null,null,null,"Air Sealing","Electric",0,0.43,null,null,1,1,"07:00:00",16,1.8333333333333333,5,2.2916666666666665,23,1.5416666666666667,28,{"$f":"IF(AC11<60,(60-AC11)/24,0)","v":1.3333333333333333},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Air Sealing","Gas",0,0,null,null,1,1,"08:00:00",14,1.9166666666666667,5,2.2916666666666665,23,1.5416666666666667,27,{"$f":"IF(AC12<60,(60-AC12)/24,0)","v":1.375},33.979999999999997,1.0841666666666667]
[null,"CFwp",null,{"$f":"VLOOKUP('Project Info'!D24,$O$11:$Q$14,3,FALSE)*100","v":{"$error":"#N/A"}},"%",null,null,null,null,null,null,null,null,"Air Sealing","Fuel Oil",0,0,null,null,1,1,"09:00:00",14,1.9166666666666667,14,1.9166666666666667,25,1.4583333333333333,27,{"$f":"IF(AC13<60,(60-AC13)/24,0)","v":1.375},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Air Sealing","Propane",0,0,null,null,1,1,"10:00:00",16,1.8333333333333333,17.059999999999999,1.7891666666666666,32,1.1666666666666667,29,{"$f":"IF(AC14<60,(60-AC14)/24,0)","v":1.2916666666666667},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Insulation","Electric",0.34,0.17,null,null,1,1,"11:00:00",17,1.7916666666666667,21.92,1.5866666666666667,37,0.95833333333333337,30,{"$f":"IF(AC15<60,(60-AC15)/24,0)","v":1.25},34.880000000000003,1.0466666666666666]
[null,"Building Envelope - Air Sealing and Insulation",null,null,null,null,null,null,null,null,null,null,null,"Insulation","Gas",0,0,null,null,1,1,"12:00:00",17,1.7916666666666667,24.98,1.4591666666666665,39,0.875,36,{"$f":"IF(AC16<60,(60-AC16)/24,0)","v":1},34.880000000000003,1.0466666666666666]
[null,"Measure Code",null,"COM-BS-ASI",null,null,"NOTE: For more information on this measure refer to the NH TRM.",null,null,null,null,null,null,"Insulation","Fuel Oil",0,0,null,null,1,1,"13:00:00",16,1.8333333333333333,26.96,1.3766666666666667,43,0.70833333333333337,39,{"$f":"IF(AC17<60,(60-AC17)/24,0)","v":0.875},34.880000000000003,1.0466666666666666]
[null,"Market",null,"Commercial",null,null,null,null,null,null,null,null,null,"Insulation","Propane",0,0,null,null,1,1,"14:00:00",16,1.8333333333333333,28.04,1.3316666666666668,45,0.625,43,{"$f":"IF(AC18<60,(60-AC18)/24,0)","v":0.70833333333333337},34.880000000000003,1.0466666666666666]
[null,"Program Type",null,"Retrofit",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,1,"15:00:00",18,1.75,28.04,1.3316666666666668,45,0.625,43,{"$f":"IF(AC19<60,(60-AC19)/24,0)","v":0.70833333333333337},34.880000000000003,1.0466666666666666]
[null,"Category",null,"Building Shell",null,null,null,null,null,null,null,null,null,"Table 5: Efficiency Values",null,null,null,null,null,1,1,"16:00:00",16,1.8333333333333333,28.04,1.3316666666666668,45,0.625,39,{"$f":"IF(AC20<60,(60-AC20)/24,0)","v":0.875},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Boiler Type","Efficiency %",null,null,null,null,1,1,"17:00:00",14,1.9166666666666667,26.96,1.3766666666666667,36,1,34,{"$f":"IF(AC21<60,(60-AC21)/24,0)","v":1.0833333333333333},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Gas-fired",0.8,null,null,null,null,1,1,"18:00:00",14,1.9166666666666667,26.96,1.3766666666666667,34,1.0833333333333333,36,{"$f":"IF(AC22<60,(60-AC22)/24,0)","v":1},33.979999999999997,1.0841666666666667]
[null,"Table 1: Calculating Primary Energy Impact (Air Sealing)",null,null,null,null,null,null,null,null,null,null,null,"Condensing",0.9,null,null,null,null,1,1,"19:00:00",12,2,26.06,1.4141666666666666,30,1.25,33,{"$f":"IF(AC23<60,(60-AC23)/24,0)","v":1.125},33.979999999999997,1.0841666666666667]
[null,null,"Height","Area","Delta","Weather","Heating ",null,null,"Savings",null,null,null,"Non-Condensing",0.8,null,null,null,null,1,1,"20:00:00",12,2,26.06,1.4141666666666666,28,1.3333333333333333,30,{"$f":"IF(AC24<60,(60-AC24)/24,0)","v":1.25},32.9,1.1291666666666667]
[null,null,"ft","ft2","ACH","HDD60","System",null,null,"kWh","MMBtu","kW",null,"Electric Resistance",1,null,null,null,null,1,1,"21:00:00",12,2,24.08,1.4966666666666668,28,1.3333333333333333,25,{"$f":"IF(AC25<60,(60-AC25)/24,0)","v":1.4583333333333333},32.9,1.1291666666666667]
[null,1,{"$f":"IF('Building Shell Inputs'!F24=\"Yes\",'Building Shell Inputs'!D24,\"\")","v":""},{"$f":"IF('Building Shell Inputs'!F24=\"Yes\",'Building Shell Inputs'!E24,\"\")","v":""},{"$f":"$O$42","v":9.9999999999999978E-2},{"$f":"IF(OR(ISBLANK(D26)),\"\",IFERROR(VLOOKUP('Project Info'!$D$21,$N$30:$O$36,2,FALSE),\"\"))","v":""},{"$f":"IF('Project Info'!$D$25=$N$22,$O$22,IF('Project Info'!$D$25=$N$25,$O$25,IF('Project Info'!$D$25=$N$26,$O$26,IF(OR('Project Info'!$D$25='Project Info'!$Y$14,'Project Info'!$D$25='Project Info'!$Y$15),IF('Project Info'!$D$26=$N$23,$O$23,$O$24)))))","v":false},null,null,{"$f":"IF('Project Info'!$D$24=\"Electric\",IFERROR(((C26*D26*E26*0.018*F26*24)/G26/3413),0),0)","v":0},{"$f":"IF('Project Info'!$D$24=\"Electric\",0,IFERROR(((C26*D26*E26*0.018*F26*24/G26)/1000000),0))","v":0},{"$f":"+J26/F26/24","v":{"$error":"#VALUE!"}},null,"Heat Pump",3,null,null,null,null,1,1,"22:00:00",7,2.2083333333333335,24.98,1.4591666666666665,27,1.375,23,{"$f":"IF(AC26<60,(60-AC26)/24,0)","v":1.5416666666666667},33.979999999999997,1.0841666666666667]
[null,2,{"$f":"IF('Building Shell Inputs'!F25=\"Yes\",'Building Shell Inputs'!D25,\"\")","v":""},{"$f":"IF('Building Shell Inputs'!F25=\"Yes\",'Building Shell Inputs'!E25,\"\")","v":""},9.9999999999999978E-2,{"$f":"IF(OR(ISBLANK(D27)),\"\",IFERROR(VLOOKUP('Project Info'!$D$21,$N$30:$O$36,2,FALSE),\"\"))","v":""},{"$f":"IF('Project Info'!$D$25=$N$22,$O$22,IF('Project Info'!$D$25=$N$25,$O$25,IF('Project Info'!$D$25=$N$26,$O$26,IF(OR('Project Info'!$D$25='Project Info'!$Y$14,'Project Info'!$D$25='Project Info'!$Y$15),IF('Project Info'!$D$26=$N$23,$O$23,$O$24)))))","v":false},null,null,{"$f":"IF('Project Info'!$D$24=\"Electric\",IFERROR(((C27*D27*E27*0.018*F27*24)/G27/3413),0),0)","v":0},{"$f":"IF('Project Info'!$D$24=\"Electric\",0,IFERROR(((C27*D27*E27*0.018*F27*24/G27)/1000000),0))","v":0},{"$f":"+J27/F27/24","v":{"$error":"#VALUE!"}},null,null,null,null,null,null,null,1,1,"23:00:00",7,2.2083333333333335,24.08,1.4966666666666668,27,1.375,21,{"$f":"IF(AC27<60,(60-AC27)/24,0)","v":1.625},33.979999999999997,1.0841666666666667]
[null,3,{"$f":"IF('Building Shell Inputs'!F26=\"Yes\",'Building Shell Inputs'!D26,\"\")","v":""},{"$f":"IF('Building Shell Inputs'!F26=\"Yes\",'Building Shell Inputs'!E26,\"\")","v":""},9.9999999999999978E-2,{"$f":"IF(OR(ISBLANK(D28)),\"\",IFERROR(VLOOKUP('Project Info'!$D$21,$N$30:$O$36,2,FALSE),\"\"))","v":""},{"$f":"IF('Project Info'!$D$25=$N$22,$O$22,IF('Project Info'!$D$25=$N$25,$O$25,IF('Project Info'!$D$25=$N$26,$O$26,IF(OR('Project Info'!$D$25='Project Info'!$Y$14,'Project Info'!$D$25='Project Info'!$Y$15),IF('Project Info'!$D$26=$N$23,$O$23,$O$24)))))","v":false},null,null,{"$f":"IF('Project Info'!$D$24=\"Electric\",IFERROR(((C28*D28*E28*0.018*F28*24)/G28/3413),0),0)","v":0},{"$f":"IF('Project Info'!$D$24=\"Electric\",0,IFERROR(((C28*D28*E28*0.018*F28*24/G28)/1000000),0))","v":0},{"$error":"#VALUE!"},null,"Table 7: HDD60 Summary Table",null,null,null,null,null,1,1,1,9,2.125,24.98,1.4591666666666665,27,1.375,23,{"$f":"IF(AC28<60,(60-AC28)/24,0)","v":1.5416666666666667},32.9,1.1291666666666667]
[null,4,{"$f":"IF('Building Shell Inputs'!F27=\"Yes\",'Building Shell Inputs'!D27,\"\")","v":""},{"$f":"IF('Building Shell Inputs'!F27=\"Yes\",'Building Shell Inputs'!E27,\"\")","v":""},9.9999999999999978E-2,{"$f":"IF(OR(ISBLANK(D29)),\"\",IFERROR(VLOOKUP('Project Info'!$D$21,$N$30:$O$36,2,FALSE),\"\"))","v":""},{"$f":"IF('Project Info'!$D$25=$N$22,$O$22,IF('Project Info'!$D$25=$N$25,$O$25,IF('Project Info'!$D$25=$N$26,$O$26,IF(OR('Project Info'!$D$25='Project Info'!$Y$14,'Project Info'!$D$25='Project Info'!$Y$15),IF('Project Info'!$D$26=$N$23,$O$23,$O$24)))))","v":false},null,null,{"$f":"IF('Project Info'!$D$24=\"Electric\",IFERROR(((C29*D29*E29*0.018*F29*24)/G29/3413),0),0)","v":0},{"$f":"IF('Project Info'!$D$24=\"Electric\",0,IFERROR(((C29*D29*E29*0.018*F29*24/G29)/1000000),0))","v":0},{"$error":"#VALUE!"},null,"City","HDD60",null,null,null,null,1,2,"01:00:00",10,2.0833333333333335,24.08,1.4966666666666668,27,1.375,25.306999999999999,{"$f":"IF(AC29<60,(60-AC29)/24,0)","v":1.4455416666666665},32.9,1.1291666666666667]
[null,5,{"$f":"IF('Building Shell Inputs'!F28=\"Yes\",'Building Shell Inputs'!D28,\"\")","v":""},{"$f":"IF('Building Shell Inputs'!F28=\"Yes\",'Building Shell Inputs'!E28,\"\")","v":""},9.9999999999999978E-2,{"$f":"IF(OR(ISBLANK(D30)),\"\",IFERROR(VLOOKUP('Project Info'!$D$21,$N$30:$O$36,2,FALSE),\"\"))","v":""},{"$f":"IF('Project Info'!$D$25=$N$22,$O$22,IF('Project Info'!$D$25=$N$25,$O$25,IF('Project Info'!$D$25=$N$26,$O$26,IF(OR('Project Info'!$D$25='Project Info'!$Y$14,'Project Info'!$D$25='Project Info'!$Y$15),IF('Project Info'!$D$26=$N$23,$O$23,$O$24)))))","v":false},null,null,{"$f":"IF('Project Info'!$D$24=\"Electric\",IFERROR(((C30*D30*E30*0.018*F30*24)/G30/3413),0),0)","v":0},{"$f":"IF('Project Info'!$D$24=\"Electric\",0,IFERROR(((C30*D30*E30*0.018*F30*24/G30)/1000000),0))","v":0},{"$error":"#VALUE!"},null,"Berlin",{"$f":"SUM(X5:X8764)","v":7420.0335949997034},null,null,null,null,1,2,"02:00:00",10,2.0833333333333335,24.08,1.4966666666666668,28,1.3333333333333333,25,{"$f":"IF(AC30<60,(60-AC30)/24,0)","v":1.4583333333333333},32,1.1666666666666667]
[null,6,{"$f":"IF('Building Shell Inputs'!F29=\"Yes\",'Building Shell Inputs'!D29,\"\")","v":""},{"$f":"IF('Building Shell Inputs'!F29=\"Yes\",'Building Shell Inputs'!E29,\"\")","v":""},9.9999999999999978E-2,{"$f":"IF(OR(ISBLANK(D31)),\"\",IFERROR(VLOOKUP('Project Info'!$D$21,$N$30:$O$36,2,FALSE),\"\"))","v":""},{"$f":"IF('Project Info'!$D$25=$N$22,$O$22,IF('Project Info'!$D$25=$N$25,$O$25,IF('Project Info'!$D$25=$N$26,$O$26,IF(OR('Project Info'!$D$25='Project Info'!$Y$14,'Project Info'!$D$25='Project Info'!$Y$15),IF('Project Info'!$D$26=$N$23,$O$23,$O$24)))))","v":false},null,null,{"$f":"IF('Project Info'!$D$24=\"Electric\",IFERROR(((C31*D31*E31*0.018*F31*24)/G31/3413),0),0)","v":0},{"$f":"IF('Project Info'!$D$24=\"Electric\",0,IFERROR(((C31*D31*E31*0.018*F31*24/G31)/1000000),0))","v":0},{"$error":"#VALUE!"},null,"Concord",{"$f":"SUM(Z5:Z8764)","v":6153.5524999997742},null,null,null,null,1,2,"03:00:00",10,2.0833333333333335,23,1.5416666666666667,30,1.25,25,{"$f":"IF(AC31<60,(60-AC31)/24,0)","v":1.4583333333333333},32,1.1666666666666667]
[null,7,{"$f":"IF('Building Shell Inputs'!F30=\"Yes\",'Building Shell Inputs'!D30,\"\")","v":""},{"$f":"IF('Building Shell Inputs'!F30=\"Yes\",'Building Shell Inputs'!E30,\"\")","v":""},9.9999999999999978E-2,{"$f":"IF(OR(ISBLANK(D32)),\"\",IFERROR(VLOOKUP('Project Info'!$D$21,$N$30:$O$36,2,FALSE),\"\"))","v":""},{"$f":"IF('Project Info'!$D$25=$N$22,$O$22,IF('Project Info'!$D$25=$N$25,$O$25,IF('Project Info'!$D$25=$N$26,$O$26,IF(OR('Project Info'!$D$25='Project Info'!$Y$14,'Project Info'!$D$25='Project Info'!$Y$15),IF('Project Info'!$D$26=$N$23,$O$23,$O$24)))))","v":false},null,null,{"$f":"IF('Project Info'!$D$24=\"Electric\",IFERROR(((C32*D32*E32*0.018*F32*24)/G32/3413),0),0)","v":0},{"$f":"IF('Project Info'!$D$24=\"Electric\",0,IFERROR(((C32*D32*E32*0.018*F32*24/G32)/1000000),0))","v":0},{"$error":"#VALUE!"},null,"Keene",{"$f":"SUM(AB5:AB8764)","v":5991.4529120373672},null,null,null,null,1,2,"04:00:00",10,2.0833333333333335,24.08,1.4966666666666668,28,1.3333333333333333,25,{"$f":"IF(AC32<60,(60-AC32)/24,0)","v":1.4583333333333333},32.9,1.1291666666666667]
[null,8,{"$f":"IF('Building Shell Inputs'!F31=\"Yes\",'Building Shell Inputs'!D31,\"\")","v":""},{"$f":"IF('Building Shell Inputs'!F31=\"Yes\",'Building Shell Inputs'!E31,\"\")","v":""},9.9999999999999978E-2,{"$f":"IF(OR(ISBLANK(D33)),\"\",IFERROR(VLOOKUP('Project Info'!$D$21,$N$30:$O$36,2,FALSE),\"\"))","v":""},{"$f":"IF('Project Info'!$D$25=$N$22,$O$22,IF('Project Info'!$D$25=$N$25,$O$25,IF('Project Info'!$D$25=$N$26,$O$26,IF(OR('Project Info'!$D$25='Project Info'!$Y$14,'Project Info'!$D$25='Project Info'!$Y$15),IF('Project Info'!$D$26=$N$23,$O$23,$O$24)))))","v":false},null,null,{"$f":"IF('Project Info'!$D$24=\"Electric\",IFERROR(((C33*D33*E33*0.018*F33*24)/G33/3413),0),0)","v":0},{"$f":"IF('Project Info'!$D$24=\"Electric\",0,IFERROR(((C33*D33*E33*0.018*F33*24/G33)/1000000),0))","v":0},{"$error":"#VALUE!"},null,"Lebanon",{"$f":"SUM(AD5:AD8764)","v":6183.3099613441227},null,null,null,null,1,2,"05:00:00",10,2.0833333333333335,19.04,1.7066666666666668,30,1.25,25,{"$f":"IF(AC33<60,(60-AC33)/24,0)","v":1.4583333333333333},33.979999999999997,1.0841666666666667]
[null,9,{"$f":"IF('Building Shell Inputs'!F32=\"Yes\",'Building Shell Inputs'!D32,\"\")","v":""},{"$f":"IF('Building Shell Inputs'!F32=\"Yes\",'Building Shell Inputs'!E32,\"\")","v":""},9.9999999999999978E-2,{"$f":"IF(OR(ISBLANK(D34)),\"\",IFERROR(VLOOKUP('Project Info'!$D$21,$N$30:$O$36,2,FALSE),\"\"))","v":""},{"$f":"IF('Project Info'!$D$25=$N$22,$O$22,IF('Project Info'!$D$25=$N$25,$O$25,IF('Project Info'!$D$25=$N$26,$O$26,IF(OR('Project Info'!$D$25='Project Info'!$Y$14,'Project Info'!$D$25='Project Info'!$Y$15),IF('Project Info'!$D$26=$N$23,$O$23,$O$24)))))","v":false},null,null,{"$f":"IF('Project Info'!$D$24=\"Electric\",IFERROR(((C34*D34*E34*0.018*F34*24)/G34/3413),0),0)","v":0},{"$f":"IF('Project Info'!$D$24=\"Electric\",0,IFERROR(((C34*D34*E34*0.018*F34*24/G34)/1000000),0))","v":0},{"$error":"#VALUE!"},null,"Portsmouth",{"$f":"SUM(AF5:AF8764)","v":5516.5874999999642},null,null,null,null,1,2,"06:00:00",10,2.0833333333333335,19.940000000000001,1.6691666666666667,30,1.25,23,{"$f":"IF(AC34<60,(60-AC34)/24,0)","v":1.5416666666666667},33.979999999999997,1.0841666666666667]
[null,10,{"$f":"IF('Building Shell Inputs'!F33=\"Yes\",'Building Shell Inputs'!D33,\"\")","v":""},{"$f":"IF('Building Shell Inputs'!F33=\"Yes\",'Building Shell Inputs'!E33,\"\")","v":""},9.9999999999999978E-2,{"$f":"IF(OR(ISBLANK(D35)),\"\",IFERROR(VLOOKUP('Project Info'!$D$21,$N$30:$O$36,2,FALSE),\"\"))","v":""},{"$f":"IF('Project Info'!$D$25=$N$22,$O$22,IF('Project Info'!$D$25=$N$25,$O$25,IF('Project Info'!$D$25=$N$26,$O$26,IF(OR('Project Info'!$D$25='Project Info'!$Y$14,'Project Info'!$D$25='Project Info'!$Y$15),IF('Project Info'!$D$26=$N$23,$O$23,$O$24)))))","v":false},null,null,{"$f":"IF('Project Info'!$D$24=\"Electric\",IFERROR(((C35*D35*E35*0.018*F35*24)/G35/3413),0),0)","v":0},{"$f":"IF('Project Info'!$D$24=\"Electric\",0,IFERROR(((C35*D35*E35*0.018*F35*24/G35)/1000000),0))","v":0},{"$error":"#VALUE!"},null,"Manchester",{"$f":"+O34","v":5516.5874999999642},"same zone as Portsmouth",null,null,null,1,2,"07:00:00",10,2.0833333333333335,24.98,1.4591666666666665,30,1.25,23,{"$f":"IF(AC35<60,(60-AC35)/24,0)","v":1.5416666666666667},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,"Totals",{"$f":"SUM(J26:J35)","v":0},{"$f":"SUM(K26:K35)","v":0},{"$f":"SUM(L26:L35)","v":{"$error":"#VALUE!"}},null,"Laconia",{"$f":"+O32","v":5991.4529120373672},"same zone as Keene",null,null,null,1,2,"08:00:00",10,2.0833333333333335,24.08,1.4966666666666668,30,1.25,25,{"$f":"IF(AC36<60,(60-AC36)/24,0)","v":1.4583333333333333},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2,"09:00:00",12,2,28.94,1.2941666666666667,30,1.25,27,{"$f":"IF(AC37<60,(60-AC37)/24,0)","v":1.375},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 8: ACH determination (TRM)",null,null,null,null,null,1,2,"10:00:00",12,2,33.08,1.1216666666666668,31,1.2083333333333333,28,{"$f":"IF(AC38<60,(60-AC38)/24,0)","v":1.3333333333333333},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Case","ACH default value",null,null,null,null,1,2,"11:00:00",14,1.9166666666666667,37.94,0.9191666666666668,32,1.1666666666666667,30,{"$f":"IF(AC39<60,(60-AC39)/24,0)","v":1.25},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Baseline",0.5,null,null,null,null,1,2,"12:00:00",14,1.9166666666666667,42.08,0.7466666666666667,34,1.0833333333333333,32,{"$f":"IF(AC40<60,(60-AC40)/24,0)","v":1.1666666666666667},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Proposed",0.4,null,null,null,null,1,2,"13:00:00",14,1.9166666666666667,44.96,0.62666666666666659,34,1.0833333333333333,36,{"$f":"IF(AC41<60,(60-AC41)/24,0)","v":1},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Savings",{"$f":"O40-O41","v":9.9999999999999978E-2},null,null,null,null,1,2,"14:00:00",14,1.9166666666666667,44.96,0.62666666666666659,37,0.95833333333333337,36,{"$f":"IF(AC42<60,(60-AC42)/24,0)","v":1},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2,"15:00:00",14,1.9166666666666667,44.96,0.62666666666666659,39,0.875,37,{"$f":"IF(AC43<60,(60-AC43)/24,0)","v":0.95833333333333337},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2,"16:00:00",14,1.9166666666666667,41,0.79166666666666663,39,0.875,36,{"$f":"IF(AC44<60,(60-AC44)/24,0)","v":1},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2,"17:00:00",12,2,37.94,0.9191666666666668,37,0.95833333333333337,36,{"$f":"IF(AC45<60,(60-AC45)/24,0)","v":1},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2,"18:00:00",12,2,37.04,0.95666666666666667,36,1,39,{"$f":"IF(AC46<60,(60-AC46)/24,0)","v":0.875},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2,"19:00:00",10,2.0833333333333335,33.979999999999997,1.0841666666666667,37,0.95833333333333337,39,{"$f":"IF(AC47<60,(60-AC47)/24,0)","v":0.875},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2,"20:00:00",11,2.0416666666666665,33.979999999999997,1.0841666666666667,36,1,36,{"$f":"IF(AC48<60,(60-AC48)/24,0)","v":1},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2,"21:00:00",12,2,32,1.1666666666666667,41,0.79166666666666663,43,{"$f":"IF(AC49<60,(60-AC49)/24,0)","v":0.70833333333333337},28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2,"22:00:00",13,1.9583333333333333,30.02,1.2491666666666668,39,0.875,46,{"$f":"IF(AC50<60,(60-AC50)/24,0)","v":0.58333333333333337},26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2,"23:00:00",14,1.9166666666666667,28.04,1.3316666666666668,39,0.875,48,{"$f":"IF(AC51<60,(60-AC51)/24,0)","v":0.5},26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2,1,14,1.9166666666666667,28.04,1.3316666666666668,37.133800000000001,0.95275833333333326,46,{"$f":"IF(AC52<60,(60-AC52)/24,0)","v":0.58333333333333337},26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"01:00:00",16,1.8333333333333333,26.96,1.3766666666666667,39,0.875,48,{"$f":"IF(AC53<60,(60-AC53)/24,0)","v":0.5},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"02:00:00",16,1.8333333333333333,26.96,1.3766666666666667,41,0.79166666666666663,48,{"$f":"IF(AC54<60,(60-AC54)/24,0)","v":0.5},26.06,1.4141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"03:00:00",16,1.8333333333333333,28.94,1.2941666666666667,43,0.70833333333333337,46,{"$f":"IF(AC55<60,(60-AC55)/24,0)","v":0.58333333333333337},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"04:00:00",16,1.8333333333333333,28.94,1.2941666666666667,45,0.625,50,{"$f":"IF(AC56<60,(60-AC56)/24,0)","v":0.41666666666666669},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"05:00:00",16,1.8333333333333333,30.02,1.2491666666666668,43,0.70833333333333337,48,{"$f":"IF(AC57<60,(60-AC57)/24,0)","v":0.5},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"06:00:00",16,1.8333333333333333,30.92,1.2116666666666667,43,0.70833333333333337,50,{"$f":"IF(AC58<60,(60-AC58)/24,0)","v":0.41666666666666669},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"07:00:00",9,2.125,30.02,1.2491666666666668,45,0.625,50,{"$f":"IF(AC59<60,(60-AC59)/24,0)","v":0.41666666666666669},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"08:00:00",9,2.125,28.94,1.2941666666666667,46,0.58333333333333337,54,{"$f":"IF(AC60<60,(60-AC60)/24,0)","v":0.25},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"09:00:00",16,1.8333333333333333,28.04,1.3316666666666668,47,0.54166666666666663,48,{"$f":"IF(AC61<60,(60-AC61)/24,0)","v":0.5},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"10:00:00",18,1.75,28.94,1.2941666666666667,48,0.5,55,{"$f":"IF(AC62<60,(60-AC62)/24,0)","v":0.20833333333333334},28.04,1.3316666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"11:00:00",19,1.7083333333333333,28.94,1.2941666666666667,50,0.41666666666666669,54,{"$f":"IF(AC63<60,(60-AC63)/24,0)","v":0.25},28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"12:00:00",21,1.625,30.02,1.2491666666666668,57,0.125,50,{"$f":"IF(AC64<60,(60-AC64)/24,0)","v":0.41666666666666669},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"13:00:00",23,1.5416666666666667,30.02,1.2491666666666668,57,0.125,50,{"$f":"IF(AC65<60,(60-AC65)/24,0)","v":0.41666666666666669},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"14:00:00",22,1.5833333333333333,32,1.1666666666666667,59,4.1666666666666664E-2,48,{"$f":"IF(AC66<60,(60-AC66)/24,0)","v":0.5},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"15:00:00",21,1.625,30.92,1.2116666666666667,55,0.20833333333333334,46,{"$f":"IF(AC67<60,(60-AC67)/24,0)","v":0.58333333333333337},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"16:00:00",21,1.625,30.02,1.2491666666666668,52,0.33333333333333331,43,{"$f":"IF(AC68<60,(60-AC68)/24,0)","v":0.70833333333333337},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"17:00:00",16,{"$f":"IF(W69<60,(60-W69)/24,0)","v":1.8333333333333333},26.06,1.4141666666666666,46,0.58333333333333337,39,{"$f":"IF(AC69<60,(60-AC69)/24,0)","v":0.875},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"18:00:00",12,2,26.06,{"$f":"IF(Y70<60,(60-Y70)/24,0)","v":1.4141666666666666},45,{"$f":"IF(AA70<60,(60-AA70)/24,0)","v":0.625},39,{"$f":"IF(AC70<60,(60-AC70)/24,0)","v":0.875},29.84,{"$f":"IF(AE70<60,(60-AE70)/24,0)","v":1.2566666666666666}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"19:00:00",10,2.0833333333333335,24.08,1.4966666666666668,45,0.625,37,{"$f":"IF(AC71<60,(60-AC71)/24,0)","v":0.95833333333333337},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"20:00:00",10,2.0833333333333335,21.92,1.5866666666666667,43,0.70833333333333337,36,{"$f":"IF(AC72<60,(60-AC72)/24,0)","v":1},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"21:00:00",10,2.0833333333333335,19.940000000000001,1.6691666666666667,45,0.625,34.296999999999997,{"$f":"IF(AC73<60,(60-AC73)/24,0)","v":1.0709583333333335},28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"22:00:00",5,2.2916666666666665,19.940000000000001,1.6691666666666667,43,0.70833333333333337,32.508400000000002,{"$f":"IF(AC74<60,(60-AC74)/24,0)","v":1.1454833333333332},28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"23:00:00",1,2.4583333333333335,17.059999999999999,1.7891666666666666,39,0.875,34.296999999999997,{"$f":"IF(AC75<60,(60-AC75)/24,0)","v":1.0709583333333335},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,1,1,2.4583333333333335,14,1.9166666666666667,39,0.875,36,{"$f":"IF(AC76<60,(60-AC76)/24,0)","v":1},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"01:00:00",1,2.4583333333333335,12.02,1.9991666666666668,39,0.875,35,{"$f":"IF(AC77<60,(60-AC77)/24,0)","v":1.0416666666666667},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"02:00:00",3,2.375,12.92,1.9616666666666667,39,0.875,36,{"$f":"IF(AC78<60,(60-AC78)/24,0)","v":1},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"03:00:00",5,2.2916666666666665,14,1.9166666666666667,39,0.875,36,{"$f":"IF(AC79<60,(60-AC79)/24,0)","v":1},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"04:00:00",7,2.2083333333333335,12.92,1.9616666666666667,39,0.875,34,{"$f":"IF(AC80<60,(60-AC80)/24,0)","v":1.0833333333333333},26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"05:00:00",7,2.2083333333333335,10.94,2.0441666666666669,37,0.95833333333333337,36,{"$f":"IF(AC81<60,(60-AC81)/24,0)","v":1},26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"06:00:00",7,2.2083333333333335,8.9600000000000009,2.1266666666666665,37.133800000000001,0.95275833333333326,36,{"$f":"IF(AC82<60,(60-AC82)/24,0)","v":1},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"07:00:00",7,2.2083333333333335,8.06,2.1641666666666666,37,0.95833333333333337,34,{"$f":"IF(AC83<60,(60-AC83)/24,0)","v":1.0833333333333333},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"08:00:00",9,2.125,8.9600000000000009,2.1266666666666665,36,1,34,{"$f":"IF(AC84<60,(60-AC84)/24,0)","v":1.0833333333333333},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"09:00:00",9,2.125,19.04,1.7066666666666668,36,1,34.213500000000003,{"$f":"IF(AC85<60,(60-AC85)/24,0)","v":1.0744374999999999},26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"10:00:00",10,2.0833333333333335,26.06,1.4141666666666666,36,1,34.213500000000003,{"$f":"IF(AC86<60,(60-AC86)/24,0)","v":1.0744374999999999},28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"11:00:00",16,1.8333333333333333,26.96,1.3766666666666667,36,1,34.213500000000003,{"$f":"IF(AC87<60,(60-AC87)/24,0)","v":1.0744374999999999},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"12:00:00",18,1.75,28.04,1.3316666666666668,37,0.95833333333333337,34.129800000000003,{"$f":"IF(AC88<60,(60-AC88)/24,0)","v":1.0779249999999998},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"13:00:00",21,1.625,30.02,1.2491666666666668,37.133800000000001,0.95275833333333326,34.129800000000003,{"$f":"IF(AC89<60,(60-AC89)/24,0)","v":1.0779249999999998},28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"14:00:00",21,1.625,30.92,1.2116666666666667,37.133800000000001,0.95275833333333326,36.349800000000002,{"$f":"IF(AC90<60,(60-AC90)/24,0)","v":0.98542499999999988},28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"15:00:00",21,1.625,32,1.1666666666666667,37.133800000000001,0.95275833333333326,36.349800000000002,{"$f":"IF(AC91<60,(60-AC91)/24,0)","v":0.98542499999999988},28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"16:00:00",21,1.625,30.02,1.2491666666666668,37.133800000000001,0.95275833333333326,43,{"$f":"IF(AC92<60,(60-AC92)/24,0)","v":0.70833333333333337},26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"17:00:00",21,1.625,26.96,1.3766666666666667,39,0.875,43.000999999999998,{"$f":"IF(AC93<60,(60-AC93)/24,0)","v":0.70829166666666676},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"18:00:00",19,1.7083333333333333,26.06,1.4141666666666666,55,0.20833333333333334,45.052900000000001,{"$f":"IF(AC94<60,(60-AC94)/24,0)","v":0.62279583333333333},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"19:00:00",19,1.7083333333333333,26.06,1.4141666666666666,52,0.33333333333333331,45.142299999999999,{"$f":"IF(AC95<60,(60-AC95)/24,0)","v":0.61907083333333335},21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"20:00:00",17,1.7916666666666667,24.08,1.4966666666666668,50,0.41666666666666669,45.142299999999999,{"$f":"IF(AC96<60,(60-AC96)/24,0)","v":0.61907083333333335},20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"21:00:00",18,1.75,23,1.5416666666666667,46,0.58333333333333337,45,{"$f":"IF(AC97<60,(60-AC97)/24,0)","v":0.625},18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"22:00:00",14,1.9166666666666667,19.940000000000001,1.6691666666666667,46,0.58333333333333337,45,{"$f":"IF(AC98<60,(60-AC98)/24,0)","v":0.625},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"23:00:00",14,1.9166666666666667,19.940000000000001,1.6691666666666667,43,0.70833333333333337,43,{"$f":"IF(AC99<60,(60-AC99)/24,0)","v":0.70833333333333337},16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,1,11,2.0416666666666665,21.92,1.5866666666666667,43,0.70833333333333337,39,{"$f":"IF(AC100<60,(60-AC100)/24,0)","v":0.875},15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"01:00:00",8,2.1666666666666665,21.92,1.5866666666666667,39,0.875,39,{"$f":"IF(AC101<60,(60-AC101)/24,0)","v":0.875},14.9,1.8791666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"02:00:00",5,2.2916666666666665,19.940000000000001,1.6691666666666667,39,0.875,37,{"$f":"IF(AC102<60,(60-AC102)/24,0)","v":0.95833333333333337},14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"03:00:00",2,2.4166666666666665,12.02,1.9991666666666668,37,0.95833333333333337,36,{"$f":"IF(AC103<60,(60-AC103)/24,0)","v":1},14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"04:00:00",0,2.5,10.039999999999999,2.0816666666666666,37,0.95833333333333337,32,{"$f":"IF(AC104<60,(60-AC104)/24,0)","v":1.1666666666666667},12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"05:00:00",-6,2.75,8.9600000000000009,2.1266666666666665,36,1,28,{"$f":"IF(AC105<60,(60-AC105)/24,0)","v":1.3333333333333333},12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"06:00:00",-8,2.8333333333333335,8.06,2.1641666666666666,34,1.0833333333333333,27,{"$f":"IF(AC106<60,(60-AC106)/24,0)","v":1.375},12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"07:00:00",-6,2.75,6.98,2.2091666666666665,30,1.25,23,{"$f":"IF(AC107<60,(60-AC107)/24,0)","v":1.5416666666666667},11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"08:00:00",-6,2.75,10.039999999999999,2.0816666666666666,28,1.3333333333333333,21,{"$f":"IF(AC108<60,(60-AC108)/24,0)","v":1.625},11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"09:00:00",-2,2.5833333333333335,17.96,1.7516666666666667,27,1.375,21,{"$f":"IF(AC109<60,(60-AC109)/24,0)","v":1.625},12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"10:00:00",3,2.375,26.96,1.3766666666666667,28,1.3333333333333333,21,{"$f":"IF(AC110<60,(60-AC110)/24,0)","v":1.625},14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"11:00:00",10,2.0833333333333335,30.02,1.2491666666666668,28,1.3333333333333333,23,{"$f":"IF(AC111<60,(60-AC111)/24,0)","v":1.5416666666666667},15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"12:00:00",18,1.75,32,1.1666666666666667,28,1.3333333333333333,25,{"$f":"IF(AC112<60,(60-AC112)/24,0)","v":1.4583333333333333},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"13:00:00",19,1.7083333333333333,32,1.1666666666666667,30,1.25,27,{"$f":"IF(AC113<60,(60-AC113)/24,0)","v":1.375},21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"14:00:00",21,1.625,33.979999999999997,1.0841666666666667,30,1.25,27,{"$f":"IF(AC114<60,(60-AC114)/24,0)","v":1.375},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"15:00:00",21,1.625,33.08,1.1216666666666668,30,1.25,25,{"$f":"IF(AC115<60,(60-AC115)/24,0)","v":1.4583333333333333},24.08,1.4966666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"16:00:00",19,1.7083333333333333,32,1.1666666666666667,28,1.3333333333333333,25,{"$f":"IF(AC116<60,(60-AC116)/24,0)","v":1.4583333333333333},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"17:00:00",19,1.7083333333333333,30.92,1.2116666666666667,28,1.3333333333333333,21,{"$f":"IF(AC117<60,(60-AC117)/24,0)","v":1.625},21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"18:00:00",19,1.7083333333333333,30.92,1.2116666666666667,25,1.4583333333333333,19,{"$f":"IF(AC118<60,(60-AC118)/24,0)","v":1.7083333333333333},21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"19:00:00",19,1.7083333333333333,30.92,1.2116666666666667,23,1.5416666666666667,17,{"$f":"IF(AC119<60,(60-AC119)/24,0)","v":1.7916666666666667},20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"20:00:00",19,1.7083333333333333,32,1.1666666666666667,21,1.625,16,{"$f":"IF(AC120<60,(60-AC120)/24,0)","v":1.8333333333333333},20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"21:00:00",20,1.6666666666666667,32,1.1666666666666667,21,1.625,16,{"$f":"IF(AC121<60,(60-AC121)/24,0)","v":1.8333333333333333},20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"22:00:00",19,1.7083333333333333,32,1.1666666666666667,19,1.7083333333333333,12,{"$f":"IF(AC122<60,(60-AC122)/24,0)","v":2},20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"23:00:00",19,1.7083333333333333,32,1.1666666666666667,18,1.75,10,{"$f":"IF(AC123<60,(60-AC123)/24,0)","v":2.0833333333333335},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,1,19,1.7083333333333333,30.92,1.2116666666666667,16,1.8333333333333333,10,{"$f":"IF(AC124<60,(60-AC124)/24,0)","v":2.0833333333333335},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"01:00:00",18,1.75,32,1.1666666666666667,16,1.8333333333333333,10,{"$f":"IF(AC125<60,(60-AC125)/24,0)","v":2.0833333333333335},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"02:00:00",18,1.75,30.92,1.2116666666666667,16,1.8333333333333333,10,{"$f":"IF(AC126<60,(60-AC126)/24,0)","v":2.0833333333333335},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"03:00:00",19,1.7083333333333333,30.92,1.2116666666666667,12,2,10,{"$f":"IF(AC127<60,(60-AC127)/24,0)","v":2.0833333333333335},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"04:00:00",19,1.7083333333333333,30.92,1.2116666666666667,12,2,12,{"$f":"IF(AC128<60,(60-AC128)/24,0)","v":2},18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"05:00:00",19,1.7083333333333333,30.92,1.2116666666666667,12,2,10,{"$f":"IF(AC129<60,(60-AC129)/24,0)","v":2.0833333333333335},18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"06:00:00",18,1.75,30.92,1.2116666666666667,12,2,10,{"$f":"IF(AC130<60,(60-AC130)/24,0)","v":2.0833333333333335},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"07:00:00",16.374099999999999,1.8177458333333334,30.92,1.2116666666666667,10,2.0833333333333335,12,{"$f":"IF(AC131<60,(60-AC131)/24,0)","v":2},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"08:00:00",15.271800000000001,1.863675,30.92,1.2116666666666667,12,2,10,{"$f":"IF(AC132<60,(60-AC132)/24,0)","v":2.0833333333333335},18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"09:00:00",16.374099999999999,{"$f":"IF(W133<60,(60-W133)/24,0)","v":1.8177458333333334},32,1.1666666666666667,16,1.8333333333333333,12,{"$f":"IF(AC133<60,(60-AC133)/24,0)","v":2},20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"10:00:00",19.388200000000001,1.6921583333333334,33.08,{"$f":"IF(Y134<60,(60-Y134)/24,0)","v":1.1216666666666668},19,{"$f":"IF(AA134<60,(60-AA134)/24,0)","v":1.7083333333333333},18,{"$f":"IF(AC134<60,(60-AC134)/24,0)","v":1.75},23,{"$f":"IF(AE134<60,(60-AE134)/24,0)","v":1.5416666666666667}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"11:00:00",22.046199999999999,1.5814083333333333,35.06,1.0391666666666666,27,1.375,23,{"$f":"IF(AC135<60,(60-AC135)/24,0)","v":1.5416666666666667},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"12:00:00",25,1.4583333333333333,35.06,1.0391666666666666,28,1.3333333333333333,25,{"$f":"IF(AC136<60,(60-AC136)/24,0)","v":1.4583333333333333},26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"13:00:00",25,1.4583333333333333,35.96,1.0016666666666667,28,1.3333333333333333,27,{"$f":"IF(AC137<60,(60-AC137)/24,0)","v":1.375},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"14:00:00",25,1.4583333333333333,37.04,0.95666666666666667,31,1.2083333333333333,28,{"$f":"IF(AC138<60,(60-AC138)/24,0)","v":1.3333333333333333},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"15:00:00",27,1.375,37.04,0.95666666666666667,34,1.0833333333333333,28,{"$f":"IF(AC139<60,(60-AC139)/24,0)","v":1.3333333333333333},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"16:00:00",27,1.375,35.96,1.0016666666666667,34,1.0833333333333333,30,{"$f":"IF(AC140<60,(60-AC140)/24,0)","v":1.25},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"17:00:00",26,1.4166666666666667,35.06,1.0391666666666666,30,1.25,30,{"$f":"IF(AC141<60,(60-AC141)/24,0)","v":1.25},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"18:00:00",25,1.4583333333333333,33.979999999999997,1.0841666666666667,28,1.3333333333333333,28,{"$f":"IF(AC142<60,(60-AC142)/24,0)","v":1.3333333333333333},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"19:00:00",25,1.4583333333333333,33.979999999999997,1.0841666666666667,28,1.3333333333333333,27,{"$f":"IF(AC143<60,(60-AC143)/24,0)","v":1.375},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"20:00:00",24,1.5,32,1.1666666666666667,28,1.3333333333333333,23,{"$f":"IF(AC144<60,(60-AC144)/24,0)","v":1.5416666666666667},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"21:00:00",25,1.4583333333333333,32,1.1666666666666667,28,1.3333333333333333,23,{"$f":"IF(AC145<60,(60-AC145)/24,0)","v":1.5416666666666667},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"22:00:00",21,1.625,32,1.1666666666666667,30,1.25,21,{"$f":"IF(AC146<60,(60-AC146)/24,0)","v":1.625},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"23:00:00",21,1.625,30.92,1.2116666666666667,30,1.25,23,{"$f":"IF(AC147<60,(60-AC147)/24,0)","v":1.5416666666666667},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,1,21,1.625,30.92,1.2116666666666667,27,1.375,21,{"$f":"IF(AC148<60,(60-AC148)/24,0)","v":1.625},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"01:00:00",25,1.4583333333333333,30.02,1.2491666666666668,26,1.4166666666666667,21,{"$f":"IF(AC149<60,(60-AC149)/24,0)","v":1.625},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"02:00:00",25,1.4583333333333333,30.02,1.2491666666666668,25,1.4583333333333333,21,{"$f":"IF(AC150<60,(60-AC150)/24,0)","v":1.625},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"03:00:00",25,1.4583333333333333,28.94,1.2941666666666667,25,1.4583333333333333,23,{"$f":"IF(AC151<60,(60-AC151)/24,0)","v":1.5416666666666667},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"04:00:00",23,1.5416666666666667,28.04,1.3316666666666668,23,1.5416666666666667,25,{"$f":"IF(AC152<60,(60-AC152)/24,0)","v":1.4583333333333333},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"05:00:00",23,1.5416666666666667,26.96,1.3766666666666667,21,1.625,25,{"$f":"IF(AC153<60,(60-AC153)/24,0)","v":1.4583333333333333},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"06:00:00",23,1.5416666666666667,26.06,1.4141666666666666,21,1.625,25,{"$f":"IF(AC154<60,(60-AC154)/24,0)","v":1.4583333333333333},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"07:00:00",21,1.625,24.98,1.4591666666666665,25,1.4583333333333333,25,{"$f":"IF(AC155<60,(60-AC155)/24,0)","v":1.4583333333333333},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"08:00:00",21,1.625,26.06,1.4141666666666666,25,1.4583333333333333,27,{"$f":"IF(AC156<60,(60-AC156)/24,0)","v":1.375},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"09:00:00",22,1.5833333333333333,28.04,1.3316666666666668,27,1.375,27,{"$f":"IF(AC157<60,(60-AC157)/24,0)","v":1.375},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"10:00:00",23,1.5416666666666667,28.04,1.3316666666666668,27,1.375,28,{"$f":"IF(AC158<60,(60-AC158)/24,0)","v":1.3333333333333333},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"11:00:00",25,1.4583333333333333,28.04,1.3316666666666668,30,1.25,30,{"$f":"IF(AC159<60,(60-AC159)/24,0)","v":1.25},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"12:00:00",27,1.375,26.96,1.3766666666666667,34,1.0833333333333333,32,{"$f":"IF(AC160<60,(60-AC160)/24,0)","v":1.1666666666666667},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"13:00:00",27,1.375,26.06,1.4141666666666666,36,1,34,{"$f":"IF(AC161<60,(60-AC161)/24,0)","v":1.0833333333333333},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"14:00:00",27,1.375,24.98,1.4591666666666665,37,0.95833333333333337,34,{"$f":"IF(AC162<60,(60-AC162)/24,0)","v":1.0833333333333333},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"15:00:00",27,1.375,24.08,1.4966666666666668,37,0.95833333333333337,34,{"$f":"IF(AC163<60,(60-AC163)/24,0)","v":1.0833333333333333},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"16:00:00",27,1.375,21.02,1.6241666666666668,37,0.95833333333333337,36,{"$f":"IF(AC164<60,(60-AC164)/24,0)","v":1},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"17:00:00",25,1.4583333333333333,19.04,1.7066666666666668,37,0.95833333333333337,34,{"$f":"IF(AC165<60,(60-AC165)/24,0)","v":1.0833333333333333},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"18:00:00",21,1.625,17.059999999999999,1.7891666666666666,37,0.95833333333333337,34,{"$f":"IF(AC166<60,(60-AC166)/24,0)","v":1.0833333333333333},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"19:00:00",21,1.625,15.08,1.8716666666666668,36,1,34,{"$f":"IF(AC167<60,(60-AC167)/24,0)","v":1.0833333333333333},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"20:00:00",19,1.7083333333333333,14,1.9166666666666667,36,1,32,{"$f":"IF(AC168<60,(60-AC168)/24,0)","v":1.1666666666666667},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"21:00:00",13,1.9583333333333333,12.92,1.9616666666666667,34,1.0833333333333333,30,{"$f":"IF(AC169<60,(60-AC169)/24,0)","v":1.25},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"22:00:00",7,2.2083333333333335,10.94,2.0441666666666669,34,1.0833333333333333,30,{"$f":"IF(AC170<60,(60-AC170)/24,0)","v":1.25},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"23:00:00",3,2.375,10.039999999999999,2.0816666666666666,32,1.1666666666666667,30,{"$f":"IF(AC171<60,(60-AC171)/24,0)","v":1.25},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,1,1,2.4583333333333335,8.06,2.1641666666666666,32,1.1666666666666667,28,{"$f":"IF(AC172<60,(60-AC172)/24,0)","v":1.3333333333333333},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"01:00:00",0,2.5,6.98,2.2091666666666665,30,1.25,28,{"$f":"IF(AC173<60,(60-AC173)/24,0)","v":1.3333333333333333},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"02:00:00",3,2.375,6.08,2.2466666666666666,28,1.3333333333333333,27,{"$f":"IF(AC174<60,(60-AC174)/24,0)","v":1.375},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"03:00:00",5,2.2916666666666665,3.02,2.3741666666666665,28,1.3333333333333333,27,{"$f":"IF(AC175<60,(60-AC175)/24,0)","v":1.375},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"04:00:00",9,2.125,-3.9999999999999147E-2,2.5016666666666665,28,1.3333333333333333,27,{"$f":"IF(AC176<60,(60-AC176)/24,0)","v":1.375},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"05:00:00",9,2.125,-3.9999999999999147E-2,2.5016666666666665,28,1.3333333333333333,27,{"$f":"IF(AC177<60,(60-AC177)/24,0)","v":1.375},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"06:00:00",9,2.125,-0.94000000000000483,2.539166666666667,27,1.375,25,{"$f":"IF(AC178<60,(60-AC178)/24,0)","v":1.4583333333333333},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"07:00:00",10,2.0833333333333335,-2.02,2.5841666666666669,28,1.3333333333333333,25,{"$f":"IF(AC179<60,(60-AC179)/24,0)","v":1.4583333333333333},28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"08:00:00",10,2.0833333333333335,-3.9999999999999147E-2,2.5016666666666665,27,1.375,25,{"$f":"IF(AC180<60,(60-AC180)/24,0)","v":1.4583333333333333},28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"09:00:00",10,2.0833333333333335,5,2.2916666666666665,28,1.3333333333333333,25,{"$f":"IF(AC181<60,(60-AC181)/24,0)","v":1.4583333333333333},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"10:00:00",14,1.9166666666666667,8.9600000000000009,2.1266666666666665,30,1.25,27,{"$f":"IF(AC182<60,(60-AC182)/24,0)","v":1.375},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"11:00:00",19,1.7083333333333333,10.94,2.0441666666666669,30,1.25,28,{"$f":"IF(AC183<60,(60-AC183)/24,0)","v":1.3333333333333333},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"12:00:00",25,1.4583333333333333,14,1.9166666666666667,34,1.0833333333333333,30,{"$f":"IF(AC184<60,(60-AC184)/24,0)","v":1.25},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"13:00:00",28,1.3333333333333333,15.98,1.8341666666666665,34,1.0833333333333333,30,{"$f":"IF(AC185<60,(60-AC185)/24,0)","v":1.25},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"14:00:00",28,1.3333333333333333,17.059999999999999,1.7891666666666666,36,1,32,{"$f":"IF(AC186<60,(60-AC186)/24,0)","v":1.1666666666666667},28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"15:00:00",30,1.25,17.96,1.7516666666666667,36,1,34,{"$f":"IF(AC187<60,(60-AC187)/24,0)","v":1.0833333333333333},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"16:00:00",29,1.2916666666666667,17.96,1.7516666666666667,36,1,32,{"$f":"IF(AC188<60,(60-AC188)/24,0)","v":1.1666666666666667},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"17:00:00",28,1.3333333333333333,14,1.9166666666666667,30,1.25,30,{"$f":"IF(AC189<60,(60-AC189)/24,0)","v":1.25},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"18:00:00",27,1.375,12.02,1.9991666666666668,30,1.25,28,{"$f":"IF(AC190<60,(60-AC190)/24,0)","v":1.3333333333333333},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"19:00:00",27,1.375,10.94,2.0441666666666669,30,1.25,30,{"$f":"IF(AC191<60,(60-AC191)/24,0)","v":1.25},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"20:00:00",25,1.4583333333333333,8.9600000000000009,2.1266666666666665,28,1.3333333333333333,30,{"$f":"IF(AC192<60,(60-AC192)/24,0)","v":1.25},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"21:00:00",25,1.4583333333333333,5,2.2916666666666665,28,1.3333333333333333,30,{"$f":"IF(AC193<60,(60-AC193)/24,0)","v":1.25},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"22:00:00",25,1.4583333333333333,5,2.2916666666666665,27,1.375,28,{"$f":"IF(AC194<60,(60-AC194)/24,0)","v":1.3333333333333333},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"23:00:00",25,1.4583333333333333,8.9600000000000009,2.1266666666666665,25,1.4583333333333333,25,{"$f":"IF(AC195<60,(60-AC195)/24,0)","v":1.4583333333333333},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,1,25,1.4583333333333333,8.9600000000000009,2.1266666666666665,27,1.375,23,{"$f":"IF(AC196<60,(60-AC196)/24,0)","v":1.5416666666666667},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"01:00:00",25,{"$f":"IF(W197<60,(60-W197)/24,0)","v":1.4583333333333333},10.039999999999999,2.0816666666666666,27,1.375,22,{"$f":"IF(AC197<60,(60-AC197)/24,0)","v":1.5833333333333333},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"02:00:00",25,1.4583333333333333,10.039999999999999,{"$f":"IF(Y198<60,(60-Y198)/24,0)","v":2.0816666666666666},27,{"$f":"IF(AA198<60,(60-AA198)/24,0)","v":1.375},21,{"$f":"IF(AC198<60,(60-AC198)/24,0)","v":1.625},24.98,{"$f":"IF(AE198<60,(60-AE198)/24,0)","v":1.4591666666666665}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"03:00:00",25,1.4583333333333333,10.94,2.0441666666666669,27,1.375,21,{"$f":"IF(AC199<60,(60-AC199)/24,0)","v":1.625},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"04:00:00",25,1.4583333333333333,10.94,2.0441666666666669,25,1.4583333333333333,21,{"$f":"IF(AC200<60,(60-AC200)/24,0)","v":1.625},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"05:00:00",23,1.5416666666666667,10.94,2.0441666666666669,23,1.5416666666666667,28,{"$f":"IF(AC201<60,(60-AC201)/24,0)","v":1.3333333333333333},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"06:00:00",22,1.5833333333333333,12.02,1.9991666666666668,21,1.625,28,{"$f":"IF(AC202<60,(60-AC202)/24,0)","v":1.3333333333333333},21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"07:00:00",19,1.7083333333333333,12.02,1.9991666666666668,19,1.7083333333333333,28,{"$f":"IF(AC203<60,(60-AC203)/24,0)","v":1.3333333333333333},21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"08:00:00",18,1.75,12.92,1.9616666666666667,19,1.7083333333333333,28,{"$f":"IF(AC204<60,(60-AC204)/24,0)","v":1.3333333333333333},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"09:00:00",18,1.75,14,1.9166666666666667,23,1.5416666666666667,30,{"$f":"IF(AC205<60,(60-AC205)/24,0)","v":1.25},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"10:00:00",19,1.7083333333333333,15.08,1.8716666666666668,32,1.1666666666666667,32,{"$f":"IF(AC206<60,(60-AC206)/24,0)","v":1.1666666666666667},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"11:00:00",21,1.625,15.98,1.8341666666666665,36,1,36,{"$f":"IF(AC207<60,(60-AC207)/24,0)","v":1},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"12:00:00",22,1.5833333333333333,17.059999999999999,1.7891666666666666,39,0.875,39,{"$f":"IF(AC208<60,(60-AC208)/24,0)","v":0.875},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"13:00:00",21,1.625,17.96,1.7516666666666667,41,0.79166666666666663,39,{"$f":"IF(AC209<60,(60-AC209)/24,0)","v":0.875},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"14:00:00",21,1.625,17.96,1.7516666666666667,43,0.70833333333333337,39,{"$f":"IF(AC210<60,(60-AC210)/24,0)","v":0.875},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"15:00:00",19,1.7083333333333333,19.940000000000001,1.6691666666666667,45,0.625,39,{"$f":"IF(AC211<60,(60-AC211)/24,0)","v":0.875},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"16:00:00",18,1.75,19.940000000000001,1.6691666666666667,43,0.70833333333333337,39,{"$f":"IF(AC212<60,(60-AC212)/24,0)","v":0.875},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"17:00:00",17,1.7916666666666667,19.940000000000001,1.6691666666666667,36,1,36,{"$f":"IF(AC213<60,(60-AC213)/24,0)","v":1},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"18:00:00",16,1.8333333333333333,21.02,1.6241666666666668,36,1,34,{"$f":"IF(AC214<60,(60-AC214)/24,0)","v":1.0833333333333333},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"19:00:00",16,1.8333333333333333,21.02,1.6241666666666668,34,1.0833333333333333,32,{"$f":"IF(AC215<60,(60-AC215)/24,0)","v":1.1666666666666667},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"20:00:00",13,1.9583333333333333,21.92,1.5866666666666667,34,1.0833333333333333,31,{"$f":"IF(AC216<60,(60-AC216)/24,0)","v":1.2083333333333333},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"21:00:00",12,2,23,1.5416666666666667,34,1.0833333333333333,30,{"$f":"IF(AC217<60,(60-AC217)/24,0)","v":1.25},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"22:00:00",10,2.0833333333333335,24.08,1.4966666666666668,36,1,30,{"$f":"IF(AC218<60,(60-AC218)/24,0)","v":1.25},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"23:00:00",10,2.0833333333333335,24.08,1.4966666666666668,34,1.0833333333333333,30,{"$f":"IF(AC219<60,(60-AC219)/24,0)","v":1.25},21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,1,9,2.125,23,1.5416666666666667,34,1.0833333333333333,28,{"$f":"IF(AC220<60,(60-AC220)/24,0)","v":1.3333333333333333},21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"01:00:00",8,2.1666666666666665,19.04,1.7066666666666668,34,1.0833333333333333,30,{"$f":"IF(AC221<60,(60-AC221)/24,0)","v":1.25},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"02:00:00",7,2.2083333333333335,14,1.9166666666666667,34,1.0833333333333333,30,{"$f":"IF(AC222<60,(60-AC222)/24,0)","v":1.25},18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"03:00:00",5,2.2916666666666665,12.02,1.9991666666666668,34,1.0833333333333333,30,{"$f":"IF(AC223<60,(60-AC223)/24,0)","v":1.25},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"04:00:00",4,2.3333333333333335,12.92,1.9616666666666667,34,1.0833333333333333,30,{"$f":"IF(AC224<60,(60-AC224)/24,0)","v":1.25},14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"05:00:00",3,2.375,28.04,1.3316666666666668,34,1.0833333333333333,32,{"$f":"IF(AC225<60,(60-AC225)/24,0)","v":1.1666666666666667},12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"06:00:00",3,2.375,30.92,1.2116666666666667,34,1.0833333333333333,32,{"$f":"IF(AC226<60,(60-AC226)/24,0)","v":1.1666666666666667},14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"07:00:00",1,2.4583333333333335,32,1.1666666666666667,34,1.0833333333333333,32,{"$f":"IF(AC227<60,(60-AC227)/24,0)","v":1.1666666666666667},12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"08:00:00",-2,2.5833333333333335,30.02,1.2491666666666668,34,1.0833333333333333,34,{"$f":"IF(AC228<60,(60-AC228)/24,0)","v":1.0833333333333333},14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"09:00:00",3,2.375,28.04,1.3316666666666668,36,1,37,{"$f":"IF(AC229<60,(60-AC229)/24,0)","v":0.95833333333333337},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"10:00:00",6,2.25,26.96,1.3766666666666667,39,0.875,37,{"$f":"IF(AC230<60,(60-AC230)/24,0)","v":0.95833333333333337},20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"11:00:00",9,2.125,26.96,1.3766666666666667,43,0.70833333333333337,39,{"$f":"IF(AC231<60,(60-AC231)/24,0)","v":0.875},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"12:00:00",10,2.0833333333333335,26.96,1.3766666666666667,43,0.70833333333333337,37,{"$f":"IF(AC232<60,(60-AC232)/24,0)","v":0.95833333333333337},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"13:00:00",12,2,26.96,1.3766666666666667,43,0.70833333333333337,39,{"$f":"IF(AC233<60,(60-AC233)/24,0)","v":0.875},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"14:00:00",14,1.9166666666666667,24.08,1.4966666666666668,43,0.70833333333333337,40,{"$f":"IF(AC234<60,(60-AC234)/24,0)","v":0.83333333333333337},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"15:00:00",14,1.9166666666666667,21.92,1.5866666666666667,43,0.70833333333333337,39,{"$f":"IF(AC235<60,(60-AC235)/24,0)","v":0.875},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"16:00:00",12,2,19.940000000000001,1.6691666666666667,41,0.79166666666666663,39,{"$f":"IF(AC236<60,(60-AC236)/24,0)","v":0.875},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"17:00:00",10,2.0833333333333335,17.059999999999999,1.7891666666666666,43,0.70833333333333337,36,{"$f":"IF(AC237<60,(60-AC237)/24,0)","v":1},20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"18:00:00",3,2.375,14,1.9166666666666667,41,0.79166666666666663,36,{"$f":"IF(AC238<60,(60-AC238)/24,0)","v":1},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"19:00:00",0,2.5,12.92,1.9616666666666667,41,0.79166666666666663,37,{"$f":"IF(AC239<60,(60-AC239)/24,0)","v":0.95833333333333337},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"20:00:00",-4,2.6666666666666665,10.039999999999999,2.0816666666666666,41,0.79166666666666663,37,{"$f":"IF(AC240<60,(60-AC240)/24,0)","v":0.95833333333333337},18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"21:00:00",-6,2.75,8.9600000000000009,2.1266666666666665,39,0.875,36,{"$f":"IF(AC241<60,(60-AC241)/24,0)","v":1},16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"22:00:00",-8,2.8333333333333335,6.98,2.2091666666666665,39,0.875,34,{"$f":"IF(AC242<60,(60-AC242)/24,0)","v":1.0833333333333333},14.9,1.8791666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"23:00:00",-6,2.75,6.98,2.2091666666666665,36,1,34,{"$f":"IF(AC243<60,(60-AC243)/24,0)","v":1.0833333333333333},12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,1,-4,2.6666666666666665,6.08,2.2466666666666666,43,0.70833333333333337,36,{"$f":"IF(AC244<60,(60-AC244)/24,0)","v":1},11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"01:00:00",-8,2.8333333333333335,5,2.2916666666666665,41,0.79166666666666663,43,{"$f":"IF(AC245<60,(60-AC245)/24,0)","v":0.70833333333333337},9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"02:00:00",-8,2.8333333333333335,3.92,2.3366666666666664,39,0.875,39,{"$f":"IF(AC246<60,(60-AC246)/24,0)","v":0.875},7.88,2.1716666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"03:00:00",-6,2.75,3.92,2.3366666666666664,39,0.875,43,{"$f":"IF(AC247<60,(60-AC247)/24,0)","v":0.70833333333333337},6.98,2.2091666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"04:00:00",0,2.5,3.02,2.3741666666666665,39,0.875,43,{"$f":"IF(AC248<60,(60-AC248)/24,0)","v":0.70833333333333337},5.9,2.2541666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"05:00:00",1,2.4583333333333335,3.02,2.3741666666666665,37,0.95833333333333337,43,{"$f":"IF(AC249<60,(60-AC249)/24,0)","v":0.70833333333333337},5,2.2916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"06:00:00",3,2.375,3.02,2.3741666666666665,34,1.0833333333333333,43,{"$f":"IF(AC250<60,(60-AC250)/24,0)","v":0.70833333333333337},3.92,2.3366666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"07:00:00",5,2.2916666666666665,3.02,2.3741666666666665,39,0.875,43,{"$f":"IF(AC251<60,(60-AC251)/24,0)","v":0.70833333333333337},2.84,2.3816666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"08:00:00",7,2.2083333333333335,3.02,2.3741666666666665,37,0.95833333333333337,45,{"$f":"IF(AC252<60,(60-AC252)/24,0)","v":0.625},3.92,2.3366666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"09:00:00",9,2.125,3.92,2.3366666666666664,41,0.79166666666666663,45,{"$f":"IF(AC253<60,(60-AC253)/24,0)","v":0.625},5,2.2916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"10:00:00",12,2,5,2.2916666666666665,45,0.625,45,{"$f":"IF(AC254<60,(60-AC254)/24,0)","v":0.625},6.98,2.2091666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"11:00:00",16,1.8333333333333333,6.98,2.2091666666666665,46,0.58333333333333337,43,{"$f":"IF(AC255<60,(60-AC255)/24,0)","v":0.70833333333333337},8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"12:00:00",25,1.4583333333333333,8.9600000000000009,2.1266666666666665,46,0.58333333333333337,43,{"$f":"IF(AC256<60,(60-AC256)/24,0)","v":0.70833333333333337},10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"13:00:00",27,1.375,10.039999999999999,2.0816666666666666,48,0.5,39,{"$f":"IF(AC257<60,(60-AC257)/24,0)","v":0.875},10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"14:00:00",27,1.375,10.94,2.0441666666666669,48,0.5,39,{"$f":"IF(AC258<60,(60-AC258)/24,0)","v":0.875},10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"15:00:00",27,1.375,12.02,1.9991666666666668,46,0.58333333333333337,39,{"$f":"IF(AC259<60,(60-AC259)/24,0)","v":0.875},10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"16:00:00",26,1.4166666666666667,12.92,1.9616666666666667,41,0.79166666666666663,37,{"$f":"IF(AC260<60,(60-AC260)/24,0)","v":0.95833333333333337},9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"17:00:00",23,{"$f":"IF(W261<60,(60-W261)/24,0)","v":1.5416666666666667},12.92,1.9616666666666667,39,0.875,37,{"$f":"IF(AC261<60,(60-AC261)/24,0)","v":0.95833333333333337},8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"18:00:00",21,1.625,12.92,{"$f":"IF(Y262<60,(60-Y262)/24,0)","v":1.9616666666666667},37,{"$f":"IF(AA262<60,(60-AA262)/24,0)","v":0.95833333333333337},36,{"$f":"IF(AC262<60,(60-AC262)/24,0)","v":1},8.9600000000000009,{"$f":"IF(AE262<60,(60-AE262)/24,0)","v":2.1266666666666665}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"19:00:00",21,1.625,14,1.9166666666666667,37,0.95833333333333337,36,{"$f":"IF(AC263<60,(60-AC263)/24,0)","v":1},8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"20:00:00",19,1.7083333333333333,12.02,1.9991666666666668,39,0.875,36,{"$f":"IF(AC264<60,(60-AC264)/24,0)","v":1},8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"21:00:00",18,1.75,10.94,2.0441666666666669,39,0.875,36,{"$f":"IF(AC265<60,(60-AC265)/24,0)","v":1},8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"22:00:00",18,1.75,12.02,1.9991666666666668,39,0.875,36,{"$f":"IF(AC266<60,(60-AC266)/24,0)","v":1},7.88,2.1716666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"23:00:00",16,1.8333333333333333,12.92,1.9616666666666667,39,0.875,37,{"$f":"IF(AC267<60,(60-AC267)/24,0)","v":0.95833333333333337},8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,1,16,1.8333333333333333,10.94,2.0441666666666669,39,0.875,37,{"$f":"IF(AC268<60,(60-AC268)/24,0)","v":0.95833333333333337},8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"01:00:00",16,1.8333333333333333,10.94,2.0441666666666669,39,0.875,37,{"$f":"IF(AC269<60,(60-AC269)/24,0)","v":0.95833333333333337},9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"02:00:00",14,1.9166666666666667,10.94,2.0441666666666669,39,0.875,36,{"$f":"IF(AC270<60,(60-AC270)/24,0)","v":1},9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"03:00:00",12,2,10.94,2.0441666666666669,39,0.875,36,{"$f":"IF(AC271<60,(60-AC271)/24,0)","v":1},10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"04:00:00",10,2.0833333333333335,10.94,2.0441666666666669,37,0.95833333333333337,34,{"$f":"IF(AC272<60,(60-AC272)/24,0)","v":1.0833333333333333},11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"05:00:00",9,2.125,10.94,2.0441666666666669,37,0.95833333333333337,34,{"$f":"IF(AC273<60,(60-AC273)/24,0)","v":1.0833333333333333},11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"06:00:00",9,2.125,10.94,2.0441666666666669,37,0.95833333333333337,34,{"$f":"IF(AC274<60,(60-AC274)/24,0)","v":1.0833333333333333},12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"07:00:00",9,2.125,10.94,2.0441666666666669,36,1,34,{"$f":"IF(AC275<60,(60-AC275)/24,0)","v":1.0833333333333333},12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"08:00:00",7,2.2083333333333335,12.02,1.9991666666666668,36,1,34,{"$f":"IF(AC276<60,(60-AC276)/24,0)","v":1.0833333333333333},14.9,1.8791666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"09:00:00",10,2.0833333333333335,12.92,1.9616666666666667,36,1,32,{"$f":"IF(AC277<60,(60-AC277)/24,0)","v":1.1666666666666667},15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"10:00:00",12,2,14,1.9166666666666667,36,1,34,{"$f":"IF(AC278<60,(60-AC278)/24,0)","v":1.0833333333333333},16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"11:00:00",12,2,17.059999999999999,1.7891666666666666,34,1.0833333333333333,30,{"$f":"IF(AC279<60,(60-AC279)/24,0)","v":1.25},18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"12:00:00",16,1.8333333333333333,19.04,1.7066666666666668,36,1,30,{"$f":"IF(AC280<60,(60-AC280)/24,0)","v":1.25},21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"13:00:00",18,1.75,21.92,1.5866666666666667,36,1,30,{"$f":"IF(AC281<60,(60-AC281)/24,0)","v":1.25},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"14:00:00",19,1.7083333333333333,23,1.5416666666666667,36,1,30,{"$f":"IF(AC282<60,(60-AC282)/24,0)","v":1.25},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"15:00:00",19,1.7083333333333333,24.08,1.4966666666666668,36,1,31,{"$f":"IF(AC283<60,(60-AC283)/24,0)","v":1.2083333333333333},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"16:00:00",18,1.75,24.98,1.4591666666666665,36,1,30,{"$f":"IF(AC284<60,(60-AC284)/24,0)","v":1.25},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"17:00:00",16,1.8333333333333333,24.08,1.4966666666666668,34,1.0833333333333333,28,{"$f":"IF(AC285<60,(60-AC285)/24,0)","v":1.3333333333333333},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"18:00:00",7,2.2083333333333335,24.08,1.4966666666666668,30,1.25,28,{"$f":"IF(AC286<60,(60-AC286)/24,0)","v":1.3333333333333333},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"19:00:00",3,2.375,24.98,1.4591666666666665,30,1.25,27,{"$f":"IF(AC287<60,(60-AC287)/24,0)","v":1.375},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"20:00:00",0,2.5,24.08,1.4966666666666668,30,1.25,25,{"$f":"IF(AC288<60,(60-AC288)/24,0)","v":1.4583333333333333},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"21:00:00",-2,2.5833333333333335,23,1.5416666666666667,28,1.3333333333333333,21,{"$f":"IF(AC289<60,(60-AC289)/24,0)","v":1.625},26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"22:00:00",-6,2.75,23,1.5416666666666667,28,1.3333333333333333,21,{"$f":"IF(AC290<60,(60-AC290)/24,0)","v":1.625},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"23:00:00",-8,2.8333333333333335,23,1.5416666666666667,27,1.375,19,{"$f":"IF(AC291<60,(60-AC291)/24,0)","v":1.7083333333333333},26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,1,-9,2.875,23,1.5416666666666667,27,1.375,19,{"$f":"IF(AC292<60,(60-AC292)/24,0)","v":1.7083333333333333},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"01:00:00",-9,2.875,23,1.5416666666666667,27,1.375,21,{"$f":"IF(AC293<60,(60-AC293)/24,0)","v":1.625},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"02:00:00",-11,2.9583333333333335,23,1.5416666666666667,25,1.4583333333333333,19,{"$f":"IF(AC294<60,(60-AC294)/24,0)","v":1.7083333333333333},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"03:00:00",-11,2.9583333333333335,24.08,1.4966666666666668,25,1.4583333333333333,19,{"$f":"IF(AC295<60,(60-AC295)/24,0)","v":1.7083333333333333},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"04:00:00",-11,2.9583333333333335,23,1.5416666666666667,25,1.4583333333333333,18,{"$f":"IF(AC296<60,(60-AC296)/24,0)","v":1.75},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"05:00:00",-11,2.9583333333333335,26.96,1.3766666666666667,23,1.5416666666666667,19,{"$f":"IF(AC297<60,(60-AC297)/24,0)","v":1.7083333333333333},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"06:00:00",-9,2.875,26.06,1.4141666666666666,23,1.5416666666666667,19,{"$f":"IF(AC298<60,(60-AC298)/24,0)","v":1.7083333333333333},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"07:00:00",-9,2.875,21.92,1.5866666666666667,25,1.4583333333333333,19,{"$f":"IF(AC299<60,(60-AC299)/24,0)","v":1.7083333333333333},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"08:00:00",-9,2.875,17.96,1.7516666666666667,25,1.4583333333333333,19,{"$f":"IF(AC300<60,(60-AC300)/24,0)","v":1.7083333333333333},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"09:00:00",-8,2.8333333333333335,17.96,1.7516666666666667,23,1.5416666666666667,19,{"$f":"IF(AC301<60,(60-AC301)/24,0)","v":1.7083333333333333},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"10:00:00",1,2.4583333333333335,17.96,1.7516666666666667,23,1.5416666666666667,19,{"$f":"IF(AC302<60,(60-AC302)/24,0)","v":1.7083333333333333},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"11:00:00",7,2.2083333333333335,19.04,1.7066666666666668,21,1.625,19,{"$f":"IF(AC303<60,(60-AC303)/24,0)","v":1.7083333333333333},41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"12:00:00",14,1.9166666666666667,19.940000000000001,1.6691666666666667,21,1.625,21,{"$f":"IF(AC304<60,(60-AC304)/24,0)","v":1.625},44.96,0.62666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"13:00:00",21,1.625,21.02,1.6241666666666668,21,1.625,21,{"$f":"IF(AC305<60,(60-AC305)/24,0)","v":1.625},47.84,0.50666666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"14:00:00",23,1.5416666666666667,21.02,1.6241666666666668,19,1.7083333333333333,19,{"$f":"IF(AC306<60,(60-AC306)/24,0)","v":1.7083333333333333},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"15:00:00",25,1.4583333333333333,23,1.5416666666666667,21,1.625,19,{"$f":"IF(AC307<60,(60-AC307)/24,0)","v":1.7083333333333333},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"16:00:00",23,1.5416666666666667,23,1.5416666666666667,21,1.625,18,{"$f":"IF(AC308<60,(60-AC308)/24,0)","v":1.75},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"17:00:00",23,1.5416666666666667,19.940000000000001,1.6691666666666667,19,1.7083333333333333,16,{"$f":"IF(AC309<60,(60-AC309)/24,0)","v":1.8333333333333333},48.92,0.46166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"18:00:00",21,1.625,19.04,1.7066666666666668,18,1.75,12,{"$f":"IF(AC310<60,(60-AC310)/24,0)","v":2},48.92,0.46166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"19:00:00",21,1.625,17.96,1.7516666666666667,16,1.8333333333333333,10,{"$f":"IF(AC311<60,(60-AC311)/24,0)","v":2.0833333333333335},46.94,0.5441666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"20:00:00",18,1.75,10.039999999999999,2.0816666666666666,14,1.9166666666666667,10,{"$f":"IF(AC312<60,(60-AC312)/24,0)","v":2.0833333333333335},46.94,0.5441666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"21:00:00",19,1.7083333333333333,8.06,2.1641666666666666,12,2,9,{"$f":"IF(AC313<60,(60-AC313)/24,0)","v":2.125},41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"22:00:00",16,1.8333333333333333,3.92,2.3366666666666664,12,2,9,{"$f":"IF(AC314<60,(60-AC314)/24,0)","v":2.125},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"23:00:00",19,1.7083333333333333,1.04,2.4566666666666666,10,2.0833333333333335,7,{"$f":"IF(AC315<60,(60-AC315)/24,0)","v":2.2083333333333335},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,1,19,1.7083333333333333,-3.9999999999999147E-2,2.5016666666666665,9,2.125,5,{"$f":"IF(AC316<60,(60-AC316)/24,0)","v":2.2916666666666665},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"01:00:00",19,1.7083333333333333,-2.02,2.5841666666666669,7,2.2083333333333335,3,{"$f":"IF(AC317<60,(60-AC317)/24,0)","v":2.375},39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"02:00:00",19,1.7083333333333333,-2.02,2.5841666666666669,7,2.2083333333333335,3,{"$f":"IF(AC318<60,(60-AC318)/24,0)","v":2.375},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"03:00:00",21,1.625,-2.92,2.6216666666666666,7,2.2083333333333335,3,{"$f":"IF(AC319<60,(60-AC319)/24,0)","v":2.375},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"04:00:00",21,1.625,-5.98,2.749166666666667,5,2.2916666666666665,3,{"$f":"IF(AC320<60,(60-AC320)/24,0)","v":2.375},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"05:00:00",21,1.625,-7.06,2.7941666666666669,3,2.375,1,{"$f":"IF(AC321<60,(60-AC321)/24,0)","v":2.4583333333333335},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"06:00:00",23,1.5416666666666667,-7.06,2.7941666666666669,3,2.375,1,{"$f":"IF(AC322<60,(60-AC322)/24,0)","v":2.4583333333333335},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"07:00:00",25,1.4583333333333333,-7.06,2.7941666666666669,3,2.375,1,{"$f":"IF(AC323<60,(60-AC323)/24,0)","v":2.4583333333333335},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"08:00:00",25,1.4583333333333333,-5.98,2.749166666666667,3,2.375,1,{"$f":"IF(AC324<60,(60-AC324)/24,0)","v":2.4583333333333335},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"09:00:00",30,{"$f":"IF(W325<60,(60-W325)/24,0)","v":1.25},1.04,2.4566666666666666,5,2.2916666666666665,1,{"$f":"IF(AC325<60,(60-AC325)/24,0)","v":2.4583333333333335},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"10:00:00",30,1.25,5,{"$f":"IF(Y326<60,(60-Y326)/24,0)","v":2.2916666666666665},7,{"$f":"IF(AA326<60,(60-AA326)/24,0)","v":2.2083333333333335},3,{"$f":"IF(AC326<60,(60-AC326)/24,0)","v":2.375},37.94,{"$f":"IF(AE326<60,(60-AE326)/24,0)","v":0.9191666666666668}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"11:00:00",30,1.25,10.039999999999999,2.0816666666666666,9,2.125,5,{"$f":"IF(AC327<60,(60-AC327)/24,0)","v":2.2916666666666665},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"12:00:00",31,1.2083333333333333,15.08,1.8716666666666668,9,2.125,7,{"$f":"IF(AC328<60,(60-AC328)/24,0)","v":2.2083333333333335},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"13:00:00",30,1.25,19.04,1.7066666666666668,10,2.0833333333333335,9,{"$f":"IF(AC329<60,(60-AC329)/24,0)","v":2.125},39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"14:00:00",30,1.25,24.08,1.4966666666666668,10,2.0833333333333335,9,{"$f":"IF(AC330<60,(60-AC330)/24,0)","v":2.125},39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"15:00:00",30,1.25,24.98,1.4591666666666665,10,2.0833333333333335,10,{"$f":"IF(AC331<60,(60-AC331)/24,0)","v":2.0833333333333335},42.98,0.70916666666666683]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"16:00:00",30,1.25,24.98,1.4591666666666665,10,2.0833333333333335,9,{"$f":"IF(AC332<60,(60-AC332)/24,0)","v":2.125},41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"17:00:00",30,1.25,24.98,1.4591666666666665,10,2.0833333333333335,7,{"$f":"IF(AC333<60,(60-AC333)/24,0)","v":2.2083333333333335},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"18:00:00",30,1.25,24.98,1.4591666666666665,9,2.125,7,{"$f":"IF(AC334<60,(60-AC334)/24,0)","v":2.2083333333333335},39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"19:00:00",28,1.3333333333333333,26.06,1.4141666666666666,8,2.1666666666666665,5,{"$f":"IF(AC335<60,(60-AC335)/24,0)","v":2.2916666666666665},39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"20:00:00",27,1.375,26.96,1.3766666666666667,7,2.2083333333333335,3,{"$f":"IF(AC336<60,(60-AC336)/24,0)","v":2.375},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"21:00:00",27,1.375,24.98,1.4591666666666665,7,2.2083333333333335,3,{"$f":"IF(AC337<60,(60-AC337)/24,0)","v":2.375},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"22:00:00",21,1.625,21.92,1.5866666666666667,5,2.2916666666666665,3,{"$f":"IF(AC338<60,(60-AC338)/24,0)","v":2.375},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"23:00:00",18,1.75,19.04,1.7066666666666668,3,2.375,1,{"$f":"IF(AC339<60,(60-AC339)/24,0)","v":2.4583333333333335},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,1,10.633100000000001,2.0569541666666669,24.08,1.4966666666666668,3,2.375,1,{"$f":"IF(AC340<60,(60-AC340)/24,0)","v":2.4583333333333335},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"01:00:00",9,2.125,26.06,1.4141666666666666,3,2.375,3,{"$f":"IF(AC341<60,(60-AC341)/24,0)","v":2.375},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"02:00:00",7,2.2083333333333335,24.98,1.4591666666666665,3,2.375,1,{"$f":"IF(AC342<60,(60-AC342)/24,0)","v":2.4583333333333335},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"03:00:00",9,2.125,21.02,1.6241666666666668,3,2.375,1,{"$f":"IF(AC343<60,(60-AC343)/24,0)","v":2.4583333333333335},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"04:00:00",10,2.0833333333333335,19.04,1.7066666666666668,1,2.4583333333333335,0,{"$f":"IF(AC344<60,(60-AC344)/24,0)","v":2.5},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"05:00:00",10,2.0833333333333335,17.059999999999999,1.7891666666666666,1,2.4583333333333335,0,{"$f":"IF(AC345<60,(60-AC345)/24,0)","v":2.5},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"06:00:00",12,2,17.96,1.7516666666666667,1,2.4583333333333335,0,{"$f":"IF(AC346<60,(60-AC346)/24,0)","v":2.5},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"07:00:00",14,1.9166666666666667,15.98,1.8341666666666665,0,2.5,-2,{"$f":"IF(AC347<60,(60-AC347)/24,0)","v":2.5833333333333335},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"08:00:00",14,1.9166666666666667,15.08,1.8716666666666668,-2,2.5833333333333335,-2,{"$f":"IF(AC348<60,(60-AC348)/24,0)","v":2.5833333333333335},43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"09:00:00",16,1.8333333333333333,19.04,1.7066666666666668,1,2.4583333333333335,0,{"$f":"IF(AC349<60,(60-AC349)/24,0)","v":2.5},53.96,0.25166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"10:00:00",17,1.7916666666666667,24.98,1.4591666666666665,3,2.375,1,{"$f":"IF(AC350<60,(60-AC350)/24,0)","v":2.4583333333333335},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"11:00:00",19,1.7083333333333333,26.96,1.3766666666666667,7,2.2083333333333335,3,{"$f":"IF(AC351<60,(60-AC351)/24,0)","v":2.375},53.96,0.25166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"12:00:00",20,1.6666666666666667,28.94,1.2941666666666667,9,2.125,7,{"$f":"IF(AC352<60,(60-AC352)/24,0)","v":2.2083333333333335},53.96,0.25166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"13:00:00",20,1.6666666666666667,32,1.1666666666666667,12,2,9,{"$f":"IF(AC353<60,(60-AC353)/24,0)","v":2.125},56.84,0.13166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"14:00:00",19,1.7083333333333333,33.08,1.1216666666666668,14,1.9166666666666667,10,{"$f":"IF(AC354<60,(60-AC354)/24,0)","v":2.0833333333333335},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"15:00:00",20,1.6666666666666667,33.979999999999997,1.0841666666666667,12,2,11,{"$f":"IF(AC355<60,(60-AC355)/24,0)","v":2.0416666666666665},59.9,4.1666666666667256E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"16:00:00",19,1.7083333333333333,35.06,1.0391666666666666,16,1.8333333333333333,10,{"$f":"IF(AC356<60,(60-AC356)/24,0)","v":2.0833333333333335},60.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"17:00:00",18,1.75,33.08,1.1216666666666668,12,2,9,{"$f":"IF(AC357<60,(60-AC357)/24,0)","v":2.125},60.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"18:00:00",18,1.75,32,1.1666666666666667,9,2.125,7,{"$f":"IF(AC358<60,(60-AC358)/24,0)","v":2.2083333333333335},60.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"19:00:00",18,1.75,32,1.1666666666666667,7,2.2083333333333335,5,{"$f":"IF(AC359<60,(60-AC359)/24,0)","v":2.2916666666666665},61.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"20:00:00",17,1.7916666666666667,30.92,1.2116666666666667,3,2.375,3,{"$f":"IF(AC360<60,(60-AC360)/24,0)","v":2.375},61.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"21:00:00",18,1.75,30.92,1.2116666666666667,3,2.375,3,{"$f":"IF(AC361<60,(60-AC361)/24,0)","v":2.375},61.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"22:00:00",19,1.7083333333333333,30.92,1.2116666666666667,1,2.4583333333333335,5,{"$f":"IF(AC362<60,(60-AC362)/24,0)","v":2.2916666666666665},61.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"23:00:00",19,1.7083333333333333,30.92,1.2116666666666667,3,2.375,7,{"$f":"IF(AC363<60,(60-AC363)/24,0)","v":2.2083333333333335},61.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,1,19,1.7083333333333333,30.92,1.2116666666666667,3,2.375,7,{"$f":"IF(AC364<60,(60-AC364)/24,0)","v":2.2083333333333335},56.84,0.13166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"01:00:00",19,1.7083333333333333,32,1.1666666666666667,5,2.2916666666666665,7,{"$f":"IF(AC365<60,(60-AC365)/24,0)","v":2.2083333333333335},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"02:00:00",19,1.7083333333333333,26.06,1.4141666666666666,7,2.2083333333333335,10,{"$f":"IF(AC366<60,(60-AC366)/24,0)","v":2.0833333333333335},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"03:00:00",19,1.7083333333333333,26.06,1.4141666666666666,12,2,12,{"$f":"IF(AC367<60,(60-AC367)/24,0)","v":2},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"04:00:00",19,1.7083333333333333,23,1.5416666666666667,16,1.8333333333333333,16,{"$f":"IF(AC368<60,(60-AC368)/24,0)","v":1.8333333333333333},57.92,8.66666666666666E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"05:00:00",19,1.7083333333333333,21.92,1.5866666666666667,16,1.8333333333333333,18,{"$f":"IF(AC369<60,(60-AC369)/24,0)","v":1.75},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"06:00:00",21,1.625,21.02,1.6241666666666668,16,1.8333333333333333,16,{"$f":"IF(AC370<60,(60-AC370)/24,0)","v":1.8333333333333333},56.84,0.13166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"07:00:00",21,1.625,19.940000000000001,1.6691666666666667,19,1.7083333333333333,16,{"$f":"IF(AC371<60,(60-AC371)/24,0)","v":1.8333333333333333},54.86,0.2141666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"08:00:00",20,1.6666666666666667,23,1.5416666666666667,23,1.5416666666666667,16,{"$f":"IF(AC372<60,(60-AC372)/24,0)","v":1.8333333333333333},54.86,0.2141666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"09:00:00",21,1.625,24.08,1.4966666666666668,19,1.7083333333333333,18,{"$f":"IF(AC373<60,(60-AC373)/24,0)","v":1.75},52.88,0.29666666666666658]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"10:00:00",23,1.5416666666666667,26.96,1.3766666666666667,19,1.7083333333333333,19,{"$f":"IF(AC374<60,(60-AC374)/24,0)","v":1.7083333333333333},52.88,0.29666666666666658]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"11:00:00",26,1.4166666666666667,28.04,1.3316666666666668,21,1.625,23,{"$f":"IF(AC375<60,(60-AC375)/24,0)","v":1.5416666666666667},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"12:00:00",28,1.3333333333333333,30.92,1.2116666666666667,25,1.4583333333333333,25,{"$f":"IF(AC376<60,(60-AC376)/24,0)","v":1.4583333333333333},55.94,0.16916666666666677]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"13:00:00",28,1.3333333333333333,33.08,1.1216666666666668,28,1.3333333333333333,27,{"$f":"IF(AC377<60,(60-AC377)/24,0)","v":1.375},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"14:00:00",28,1.3333333333333333,35.06,1.0391666666666666,34,1.0833333333333333,28,{"$f":"IF(AC378<60,(60-AC378)/24,0)","v":1.3333333333333333},53.96,0.25166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"15:00:00",30,1.25,39.92,0.83666666666666656,34,1.0833333333333333,28,{"$f":"IF(AC379<60,(60-AC379)/24,0)","v":1.3333333333333333},50.9,0.37916666666666671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"16:00:00",33,1.125,37.04,0.95666666666666667,36,1,28,{"$f":"IF(AC380<60,(60-AC380)/24,0)","v":1.3333333333333333},50.9,0.37916666666666671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"17:00:00",34,1.0833333333333333,37.04,0.95666666666666667,36,1,28,{"$f":"IF(AC381<60,(60-AC381)/24,0)","v":1.3333333333333333},50.9,0.37916666666666671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"18:00:00",32,1.1666666666666667,37.04,0.95666666666666667,34,1.0833333333333333,23,{"$f":"IF(AC382<60,(60-AC382)/24,0)","v":1.5416666666666667},51.98,0.33416666666666678]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"19:00:00",32,1.1666666666666667,39.020000000000003,0.87416666666666654,27,1.375,19,{"$f":"IF(AC383<60,(60-AC383)/24,0)","v":1.7083333333333333},50.9,0.37916666666666671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"20:00:00",32,1.1666666666666667,35.96,1.0016666666666667,23,1.5416666666666667,18,{"$f":"IF(AC384<60,(60-AC384)/24,0)","v":1.75},50.9,0.37916666666666671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"21:00:00",30,1.25,35.06,1.0391666666666666,20,1.6666666666666667,12,{"$f":"IF(AC385<60,(60-AC385)/24,0)","v":2},51.98,0.33416666666666678]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"22:00:00",28,1.3333333333333333,35.06,1.0391666666666666,18,1.75,9,{"$f":"IF(AC386<60,(60-AC386)/24,0)","v":2.125},50.9,0.37916666666666671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"23:00:00",27,1.375,35.96,1.0016666666666667,14,1.9166666666666667,5,{"$f":"IF(AC387<60,(60-AC387)/24,0)","v":2.2916666666666665},50.9,0.37916666666666671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,1,25,1.4583333333333333,35.06,1.0391666666666666,10,2.0833333333333335,3,{"$f":"IF(AC388<60,(60-AC388)/24,0)","v":2.375},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"01:00:00",25,{"$f":"IF(W389<60,(60-W389)/24,0)","v":1.4583333333333333},35.96,1.0016666666666667,9,2.125,1,{"$f":"IF(AC389<60,(60-AC389)/24,0)","v":2.4583333333333335},50.9,0.37916666666666671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"02:00:00",24,1.5,35.06,{"$f":"IF(Y390<60,(60-Y390)/24,0)","v":1.0391666666666666},5,{"$f":"IF(AA390<60,(60-AA390)/24,0)","v":2.2916666666666665},0,{"$f":"IF(AC390<60,(60-AC390)/24,0)","v":2.5},51.98,{"$f":"IF(AE390<60,(60-AE390)/24,0)","v":0.33416666666666678}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"03:00:00",23,1.5416666666666667,33.979999999999997,1.0841666666666667,1,2.4583333333333335,-4,{"$f":"IF(AC391<60,(60-AC391)/24,0)","v":2.6666666666666665},50.9,0.37916666666666671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"04:00:00",21,1.625,32,1.1666666666666667,0,2.5,-6,{"$f":"IF(AC392<60,(60-AC392)/24,0)","v":2.75},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"05:00:00",21,1.625,33.08,1.1216666666666668,-2,2.5833333333333335,-8,{"$f":"IF(AC393<60,(60-AC393)/24,0)","v":2.8333333333333335},48.92,0.46166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"06:00:00",21,1.625,33.979999999999997,1.0841666666666667,-2,2.5833333333333335,-8,{"$f":"IF(AC394<60,(60-AC394)/24,0)","v":2.8333333333333335},48.92,0.46166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"07:00:00",21,1.625,33.979999999999997,1.0841666666666667,-4,2.6666666666666665,-9,{"$f":"IF(AC395<60,(60-AC395)/24,0)","v":2.875},47.84,0.50666666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"08:00:00",20,1.6666666666666667,33.979999999999997,1.0841666666666667,-4,2.6666666666666665,-9,{"$f":"IF(AC396<60,(60-AC396)/24,0)","v":2.875},47.84,0.50666666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"09:00:00",20,1.6666666666666667,35.06,1.0391666666666666,-4,2.6666666666666665,-9,{"$f":"IF(AC397<60,(60-AC397)/24,0)","v":2.875},48.92,0.46166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"10:00:00",21,1.625,37.94,0.9191666666666668,0,2.5,-8,{"$f":"IF(AC398<60,(60-AC398)/24,0)","v":2.8333333333333335},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"11:00:00",21,1.625,41,0.79166666666666663,0,2.5,-6,{"$f":"IF(AC399<60,(60-AC399)/24,0)","v":2.75},51.98,0.33416666666666678]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"12:00:00",21,1.625,41,0.79166666666666663,1,2.4583333333333335,-4,{"$f":"IF(AC400<60,(60-AC400)/24,0)","v":2.6666666666666665},52.88,0.29666666666666658]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"13:00:00",21,1.625,41,0.79166666666666663,3,2.375,-2,{"$f":"IF(AC401<60,(60-AC401)/24,0)","v":2.5833333333333335},52.88,0.29666666666666658]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"14:00:00",21,1.625,41,0.79166666666666663,5,2.2916666666666665,0,{"$f":"IF(AC402<60,(60-AC402)/24,0)","v":2.5},50.9,0.37916666666666671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"15:00:00",21,1.625,39.92,0.83666666666666656,7,2.2083333333333335,0,{"$f":"IF(AC403<60,(60-AC403)/24,0)","v":2.5},46.94,0.5441666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"16:00:00",20,1.6666666666666667,39.92,0.83666666666666656,3,2.375,0,{"$f":"IF(AC404<60,(60-AC404)/24,0)","v":2.5},44.96,0.62666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"17:00:00",18,1.75,37.94,0.9191666666666668,1,2.4583333333333335,-2,{"$f":"IF(AC405<60,(60-AC405)/24,0)","v":2.5833333333333335},44.96,0.62666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"18:00:00",16,1.8333333333333333,37.04,0.95666666666666667,1,2.4583333333333335,-4,{"$f":"IF(AC406<60,(60-AC406)/24,0)","v":2.6666666666666665},44.96,0.62666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"19:00:00",14,1.9166666666666667,35.96,1.0016666666666667,0,2.5,-6,{"$f":"IF(AC407<60,(60-AC407)/24,0)","v":2.75},43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"20:00:00",11,2.0416666666666665,35.96,1.0016666666666667,0,2.5,-6,{"$f":"IF(AC408<60,(60-AC408)/24,0)","v":2.75},42.98,0.70916666666666683]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"21:00:00",10,2.0833333333333335,35.96,1.0016666666666667,0,2.5,-8,{"$f":"IF(AC409<60,(60-AC409)/24,0)","v":2.8333333333333335},42.98,0.70916666666666683]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"22:00:00",9,2.125,33.08,1.1216666666666668,-2,2.5833333333333335,-9,{"$f":"IF(AC410<60,(60-AC410)/24,0)","v":2.875},41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"23:00:00",3,2.375,32,1.1666666666666667,-2,2.5833333333333335,-9,{"$f":"IF(AC411<60,(60-AC411)/24,0)","v":2.875},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,1,-2,2.5833333333333335,32,1.1666666666666667,-2,2.5833333333333335,-9,{"$f":"IF(AC412<60,(60-AC412)/24,0)","v":2.875},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"01:00:00",-6,2.75,32,1.1666666666666667,-2,2.5833333333333335,-11,{"$f":"IF(AC413<60,(60-AC413)/24,0)","v":2.9583333333333335},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"02:00:00",-13,3.0416666666666665,32,1.1666666666666667,-2,2.5833333333333335,-9,{"$f":"IF(AC414<60,(60-AC414)/24,0)","v":2.875},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"03:00:00",-15,3.125,32,1.1666666666666667,-2,2.5833333333333335,-11,{"$f":"IF(AC415<60,(60-AC415)/24,0)","v":2.9583333333333335},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"04:00:00",-15,3.125,30.02,1.2491666666666668,-4,2.6666666666666665,-15,{"$f":"IF(AC416<60,(60-AC416)/24,0)","v":3.125},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"05:00:00",-15,3.125,30.92,1.2116666666666667,-4,2.6666666666666665,-9,{"$f":"IF(AC417<60,(60-AC417)/24,0)","v":2.875},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"06:00:00",-17,3.2083333333333335,30.92,1.2116666666666667,-4,2.6666666666666665,-13,{"$f":"IF(AC418<60,(60-AC418)/24,0)","v":3.0416666666666665},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"07:00:00",-17,3.2083333333333335,30.02,1.2491666666666668,-6,2.75,-11,{"$f":"IF(AC419<60,(60-AC419)/24,0)","v":2.9583333333333335},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"08:00:00",-17,3.2083333333333335,28.94,1.2941666666666667,-6,2.75,-11,{"$f":"IF(AC420<60,(60-AC420)/24,0)","v":2.9583333333333335},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"09:00:00",-11,2.9583333333333335,32,1.1666666666666667,-2,2.5833333333333335,-9,{"$f":"IF(AC421<60,(60-AC421)/24,0)","v":2.875},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"10:00:00",-4,2.6666666666666665,33.08,1.1216666666666668,0,2.5,-6,{"$f":"IF(AC422<60,(60-AC422)/24,0)","v":2.75},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"11:00:00",3,2.375,33.979999999999997,1.0841666666666667,3,2.375,-2,{"$f":"IF(AC423<60,(60-AC423)/24,0)","v":2.5833333333333335},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"12:00:00",10,2.0833333333333335,33.979999999999997,1.0841666666666667,7,2.2083333333333335,0,{"$f":"IF(AC424<60,(60-AC424)/24,0)","v":2.5},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"13:00:00",16,1.8333333333333333,35.96,1.0016666666666667,9,2.125,3,{"$f":"IF(AC425<60,(60-AC425)/24,0)","v":2.375},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"14:00:00",19,1.7083333333333333,35.96,1.0016666666666667,10,2.0833333333333335,5,{"$f":"IF(AC426<60,(60-AC426)/24,0)","v":2.2916666666666665},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"15:00:00",19,1.7083333333333333,35.06,1.0391666666666666,12,2,7,{"$f":"IF(AC427<60,(60-AC427)/24,0)","v":2.2083333333333335},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"16:00:00",19,1.7083333333333333,35.06,1.0391666666666666,12,2,7,{"$f":"IF(AC428<60,(60-AC428)/24,0)","v":2.2083333333333335},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"17:00:00",18,1.75,33.979999999999997,1.0841666666666667,10,2.0833333333333335,3,{"$f":"IF(AC429<60,(60-AC429)/24,0)","v":2.375},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"18:00:00",18,1.75,33.979999999999997,1.0841666666666667,10,2.0833333333333335,1,{"$f":"IF(AC430<60,(60-AC430)/24,0)","v":2.4583333333333335},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"19:00:00",18,1.75,33.979999999999997,1.0841666666666667,9,2.125,1,{"$f":"IF(AC431<60,(60-AC431)/24,0)","v":2.4583333333333335},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"20:00:00",18,1.75,33.08,1.1216666666666668,7,2.2083333333333335,-2,{"$f":"IF(AC432<60,(60-AC432)/24,0)","v":2.5833333333333335},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"21:00:00",18,1.75,28.04,1.3316666666666668,7,2.2083333333333335,-6,{"$f":"IF(AC433<60,(60-AC433)/24,0)","v":2.75},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"22:00:00",18,1.75,26.06,1.4141666666666666,5,2.2916666666666665,-6,{"$f":"IF(AC434<60,(60-AC434)/24,0)","v":2.75},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"23:00:00",16,1.8333333333333333,24.08,1.4966666666666668,7,2.2083333333333335,-8,{"$f":"IF(AC435<60,(60-AC435)/24,0)","v":2.8333333333333335},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,1,7,2.2083333333333335,23,1.5416666666666667,5,2.2916666666666665,-9,{"$f":"IF(AC436<60,(60-AC436)/24,0)","v":2.875},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"01:00:00",0,2.5,21.92,1.5866666666666667,3,2.375,-9,{"$f":"IF(AC437<60,(60-AC437)/24,0)","v":2.875},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"02:00:00",0,2.5,21.92,1.5866666666666667,1,2.4583333333333335,-9,{"$f":"IF(AC438<60,(60-AC438)/24,0)","v":2.875},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"03:00:00",1,2.4583333333333335,19.940000000000001,1.6691666666666667,1,2.4583333333333335,-11,{"$f":"IF(AC439<60,(60-AC439)/24,0)","v":2.9583333333333335},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"04:00:00",1,2.4583333333333335,19.04,1.7066666666666668,-2,2.5833333333333335,-11,{"$f":"IF(AC440<60,(60-AC440)/24,0)","v":2.9583333333333335},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"05:00:00",1,2.4583333333333335,17.059999999999999,1.7891666666666666,-4,2.6666666666666665,-11,{"$f":"IF(AC441<60,(60-AC441)/24,0)","v":2.9583333333333335},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"06:00:00",3,2.375,15.98,1.8341666666666665,-4,2.6666666666666665,-13,{"$f":"IF(AC442<60,(60-AC442)/24,0)","v":3.0416666666666665},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"07:00:00",5,2.2916666666666665,14,1.9166666666666667,-4,2.6666666666666665,-11,{"$f":"IF(AC443<60,(60-AC443)/24,0)","v":2.9583333333333335},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"08:00:00",7,2.2083333333333335,14,1.9166666666666667,0,2.5,-8,{"$f":"IF(AC444<60,(60-AC444)/24,0)","v":2.8333333333333335},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"09:00:00",9,2.125,17.059999999999999,1.7891666666666666,3,2.375,-6,{"$f":"IF(AC445<60,(60-AC445)/24,0)","v":2.75},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"10:00:00",12,2,19.04,1.7066666666666668,7,2.2083333333333335,-2,{"$f":"IF(AC446<60,(60-AC446)/24,0)","v":2.5833333333333335},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"11:00:00",14,1.9166666666666667,23,1.5416666666666667,9,2.125,1,{"$f":"IF(AC447<60,(60-AC447)/24,0)","v":2.4583333333333335},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"12:00:00",16,1.8333333333333333,23,1.5416666666666667,12,2,5,{"$f":"IF(AC448<60,(60-AC448)/24,0)","v":2.2916666666666665},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"13:00:00",18,1.75,24.98,1.4591666666666665,16,1.8333333333333333,10,{"$f":"IF(AC449<60,(60-AC449)/24,0)","v":2.0833333333333335},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"14:00:00",20,1.6666666666666667,26.96,1.3766666666666667,18,1.75,10,{"$f":"IF(AC450<60,(60-AC450)/24,0)","v":2.0833333333333335},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"15:00:00",22,1.5833333333333333,28.04,1.3316666666666668,19,1.7083333333333333,14,{"$f":"IF(AC451<60,(60-AC451)/24,0)","v":1.9166666666666667},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"16:00:00",22,1.5833333333333333,28.04,1.3316666666666668,19,1.7083333333333333,14,{"$f":"IF(AC452<60,(60-AC452)/24,0)","v":1.9166666666666667},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"17:00:00",21,{"$f":"IF(W453<60,(60-W453)/24,0)","v":1.625},28.94,1.2941666666666667,18,1.75,9,{"$f":"IF(AC453<60,(60-AC453)/24,0)","v":2.125},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"18:00:00",21.414999999999999,1.6077083333333333,28.94,{"$f":"IF(Y454<60,(60-Y454)/24,0)","v":1.2941666666666667},10,{"$f":"IF(AA454<60,(60-AA454)/24,0)","v":2.0833333333333335},3,{"$f":"IF(AC454<60,(60-AC454)/24,0)","v":2.375},35.96,{"$f":"IF(AE454<60,(60-AE454)/24,0)","v":1.0016666666666667}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"19:00:00",22,1.5833333333333333,28.04,1.3316666666666668,9,2.125,0,{"$f":"IF(AC455<60,(60-AC455)/24,0)","v":2.5},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"20:00:00",21,1.625,21.92,1.5866666666666667,5,2.2916666666666665,0,{"$f":"IF(AC456<60,(60-AC456)/24,0)","v":2.5},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"21:00:00",24,1.5,23,1.5416666666666667,3,2.375,-2,{"$f":"IF(AC457<60,(60-AC457)/24,0)","v":2.5833333333333335},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"22:00:00",27,1.375,21.02,1.6241666666666668,1,2.4583333333333335,-4,{"$f":"IF(AC458<60,(60-AC458)/24,0)","v":2.6666666666666665},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"23:00:00",27,1.375,19.940000000000001,1.6691666666666667,0,2.5,-6,{"$f":"IF(AC459<60,(60-AC459)/24,0)","v":2.75},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,1,25,1.4583333333333333,17.96,1.7516666666666667,-2,2.5833333333333335,-4,{"$f":"IF(AC460<60,(60-AC460)/24,0)","v":2.6666666666666665},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"01:00:00",21,1.625,17.96,1.7516666666666667,-2,2.5833333333333335,-4,{"$f":"IF(AC461<60,(60-AC461)/24,0)","v":2.6666666666666665},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"02:00:00",18,1.75,17.96,1.7516666666666667,-2,2.5833333333333335,-4,{"$f":"IF(AC462<60,(60-AC462)/24,0)","v":2.6666666666666665},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"03:00:00",16,1.8333333333333333,19.940000000000001,1.6691666666666667,0,2.5,-2,{"$f":"IF(AC463<60,(60-AC463)/24,0)","v":2.5833333333333335},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"04:00:00",14,1.9166666666666667,19.940000000000001,1.6691666666666667,0,2.5,-2,{"$f":"IF(AC464<60,(60-AC464)/24,0)","v":2.5833333333333335},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"05:00:00",12,2,21.02,1.6241666666666668,0,2.5,-2,{"$f":"IF(AC465<60,(60-AC465)/24,0)","v":2.5833333333333335},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"06:00:00",12,2,21.02,1.6241666666666668,-2,2.5833333333333335,-2,{"$f":"IF(AC466<60,(60-AC466)/24,0)","v":2.5833333333333335},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"07:00:00",10,2.0833333333333335,21.02,1.6241666666666668,-2,2.5833333333333335,-2,{"$f":"IF(AC467<60,(60-AC467)/24,0)","v":2.5833333333333335},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"08:00:00",10,2.0833333333333335,21.02,1.6241666666666668,0,2.5,0,{"$f":"IF(AC468<60,(60-AC468)/24,0)","v":2.5},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"09:00:00",10,2.0833333333333335,21.92,1.5866666666666667,3,2.375,1,{"$f":"IF(AC469<60,(60-AC469)/24,0)","v":2.4583333333333335},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"10:00:00",12,2,30.92,1.2116666666666667,7,2.2083333333333335,1,{"$f":"IF(AC470<60,(60-AC470)/24,0)","v":2.4583333333333335},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"11:00:00",14,1.9166666666666667,35.96,1.0016666666666667,9,2.125,3,{"$f":"IF(AC471<60,(60-AC471)/24,0)","v":2.375},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"12:00:00",16,1.8333333333333333,41,0.79166666666666663,10,2.0833333333333335,7,{"$f":"IF(AC472<60,(60-AC472)/24,0)","v":2.2083333333333335},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"13:00:00",18,1.75,42.98,0.70916666666666683,10,2.0833333333333335,9,{"$f":"IF(AC473<60,(60-AC473)/24,0)","v":2.125},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"14:00:00",19,1.7083333333333333,42.98,0.70916666666666683,14,1.9166666666666667,10,{"$f":"IF(AC474<60,(60-AC474)/24,0)","v":2.0833333333333335},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"15:00:00",19,1.7083333333333333,42.08,0.7466666666666667,16,1.8333333333333333,10,{"$f":"IF(AC475<60,(60-AC475)/24,0)","v":2.0833333333333335},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"16:00:00",16,1.8333333333333333,42.08,0.7466666666666667,18,1.75,12,{"$f":"IF(AC476<60,(60-AC476)/24,0)","v":2},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"17:00:00",12,2,39.92,0.83666666666666656,18,1.75,10,{"$f":"IF(AC477<60,(60-AC477)/24,0)","v":2.0833333333333335},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"18:00:00",9,2.125,39.020000000000003,0.87416666666666654,16,1.8333333333333333,10,{"$f":"IF(AC478<60,(60-AC478)/24,0)","v":2.0833333333333335},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"19:00:00",7,2.2083333333333335,37.94,0.9191666666666668,16,1.8333333333333333,10,{"$f":"IF(AC479<60,(60-AC479)/24,0)","v":2.0833333333333335},39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"20:00:00",3,2.375,37.94,0.9191666666666668,16,1.8333333333333333,10,{"$f":"IF(AC480<60,(60-AC480)/24,0)","v":2.0833333333333335},39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"21:00:00",3,2.375,35.96,1.0016666666666667,16,1.8333333333333333,10,{"$f":"IF(AC481<60,(60-AC481)/24,0)","v":2.0833333333333335},39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"22:00:00",3,2.375,35.06,1.0391666666666666,16,1.8333333333333333,9,{"$f":"IF(AC482<60,(60-AC482)/24,0)","v":2.125},39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"23:00:00",5,2.2916666666666665,33.979999999999997,1.0841666666666667,16,1.8333333333333333,9,{"$f":"IF(AC483<60,(60-AC483)/24,0)","v":2.125},39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,1,1,2.4583333333333335,30.92,1.2116666666666667,16,1.8333333333333333,9,{"$f":"IF(AC484<60,(60-AC484)/24,0)","v":2.125},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"01:00:00",3,2.375,28.04,1.3316666666666668,16,1.8333333333333333,10,{"$f":"IF(AC485<60,(60-AC485)/24,0)","v":2.0833333333333335},39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"02:00:00",3,2.375,26.06,1.4141666666666666,16,1.8333333333333333,10,{"$f":"IF(AC486<60,(60-AC486)/24,0)","v":2.0833333333333335},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"03:00:00",7,2.2083333333333335,24.98,1.4591666666666665,16,1.8333333333333333,10,{"$f":"IF(AC487<60,(60-AC487)/24,0)","v":2.0833333333333335},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"04:00:00",7,2.2083333333333335,21.02,1.6241666666666668,16,1.8333333333333333,12,{"$f":"IF(AC488<60,(60-AC488)/24,0)","v":2},39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"05:00:00",9,2.125,19.04,1.7066666666666668,16,1.8333333333333333,14,{"$f":"IF(AC489<60,(60-AC489)/24,0)","v":1.9166666666666667},39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"06:00:00",9,2.125,17.96,1.7516666666666667,14,1.9166666666666667,12,{"$f":"IF(AC490<60,(60-AC490)/24,0)","v":2},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"07:00:00",9,2.125,15.98,1.8341666666666665,12,2,10,{"$f":"IF(AC491<60,(60-AC491)/24,0)","v":2.0833333333333335},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"08:00:00",9,2.125,15.08,1.8716666666666668,10,2.0833333333333335,9,{"$f":"IF(AC492<60,(60-AC492)/24,0)","v":2.125},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"09:00:00",10,2.0833333333333335,15.98,1.8341666666666665,10,2.0833333333333335,7,{"$f":"IF(AC493<60,(60-AC493)/24,0)","v":2.2083333333333335},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"10:00:00",10,2.0833333333333335,17.059999999999999,1.7891666666666666,12,2,7,{"$f":"IF(AC494<60,(60-AC494)/24,0)","v":2.2083333333333335},42.98,0.70916666666666683]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"11:00:00",14,1.9166666666666667,17.96,1.7516666666666667,12,2,7,{"$f":"IF(AC495<60,(60-AC495)/24,0)","v":2.2083333333333335},43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"12:00:00",14,1.9166666666666667,17.96,1.7516666666666667,12,2,7,{"$f":"IF(AC496<60,(60-AC496)/24,0)","v":2.2083333333333335},43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"13:00:00",14,1.9166666666666667,19.04,1.7066666666666668,12,2,7,{"$f":"IF(AC497<60,(60-AC497)/24,0)","v":2.2083333333333335},43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"14:00:00",12,2,19.04,1.7066666666666668,12,2,7,{"$f":"IF(AC498<60,(60-AC498)/24,0)","v":2.2083333333333335},43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"15:00:00",16,1.8333333333333333,19.04,1.7066666666666668,12,2,7,{"$f":"IF(AC499<60,(60-AC499)/24,0)","v":2.2083333333333335},43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"16:00:00",12,2,17.96,1.7516666666666667,10,2.0833333333333335,5,{"$f":"IF(AC500<60,(60-AC500)/24,0)","v":2.2916666666666665},43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"17:00:00",12,2,15.08,1.8716666666666668,9,2.125,3,{"$f":"IF(AC501<60,(60-AC501)/24,0)","v":2.375},43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"18:00:00",12,2,12.92,1.9616666666666667,7,2.2083333333333335,1,{"$f":"IF(AC502<60,(60-AC502)/24,0)","v":2.4583333333333335},43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"19:00:00",13,1.9583333333333333,10.94,2.0441666666666669,5,2.2916666666666665,1,{"$f":"IF(AC503<60,(60-AC503)/24,0)","v":2.4583333333333335},42.98,0.70916666666666683]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"20:00:00",12,2,10.039999999999999,2.0816666666666666,3,2.375,0,{"$f":"IF(AC504<60,(60-AC504)/24,0)","v":2.5},41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"21:00:00",12,2,8.9600000000000009,2.1266666666666665,1,2.4583333333333335,0,{"$f":"IF(AC505<60,(60-AC505)/24,0)","v":2.5},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"22:00:00",12,2,6.98,2.2091666666666665,0,2.5,-2,{"$f":"IF(AC506<60,(60-AC506)/24,0)","v":2.5833333333333335},39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"23:00:00",12,2,6.08,2.2466666666666666,0,2.5,-2,{"$f":"IF(AC507<60,(60-AC507)/24,0)","v":2.5833333333333335},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,1,12,2,5,2.2916666666666665,0,2.5,-2,{"$f":"IF(AC508<60,(60-AC508)/24,0)","v":2.5833333333333335},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"01:00:00",7,2.2083333333333335,3.92,2.3366666666666664,0,2.5,-2,{"$f":"IF(AC509<60,(60-AC509)/24,0)","v":2.5833333333333335},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"02:00:00",9,2.125,3.02,2.3741666666666665,0,2.5,-2,{"$f":"IF(AC510<60,(60-AC510)/24,0)","v":2.5833333333333335},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"03:00:00",12,2,1.94,2.4191666666666669,0,2.5,-2,{"$f":"IF(AC511<60,(60-AC511)/24,0)","v":2.5833333333333335},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"04:00:00",7,2.2083333333333335,1.04,2.4566666666666666,-2,2.5833333333333335,-2,{"$f":"IF(AC512<60,(60-AC512)/24,0)","v":2.5833333333333335},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"05:00:00",0,2.5,-3.9999999999999147E-2,2.5016666666666665,-2,2.5833333333333335,-4,{"$f":"IF(AC513<60,(60-AC513)/24,0)","v":2.6666666666666665},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"06:00:00",-2,2.5833333333333335,-0.94000000000000483,2.539166666666667,-2,2.5833333333333335,-4,{"$f":"IF(AC514<60,(60-AC514)/24,0)","v":2.6666666666666665},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"07:00:00",-2,2.5833333333333335,-2.02,2.5841666666666669,-2,2.5833333333333335,-6,{"$f":"IF(AC515<60,(60-AC515)/24,0)","v":2.75},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"08:00:00",-2,2.5833333333333335,-2.02,2.5841666666666669,-2,2.5833333333333335,-4,{"$f":"IF(AC516<60,(60-AC516)/24,0)","v":2.6666666666666665},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"09:00:00",2.1229200000000001,{"$f":"IF(W517<60,(60-W517)/24,0)","v":2.4115449999999998},-3.9999999999999147E-2,2.5016666666666665,0,2.5,-2,{"$f":"IF(AC517<60,(60-AC517)/24,0)","v":2.5833333333333335},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"10:00:00",10,2.0833333333333335,1.94,{"$f":"IF(Y518<60,(60-Y518)/24,0)","v":2.4191666666666669},1,{"$f":"IF(AA518<60,(60-AA518)/24,0)","v":2.4583333333333335},0,{"$f":"IF(AC518<60,(60-AC518)/24,0)","v":2.5},33.979999999999997,{"$f":"IF(AE518<60,(60-AE518)/24,0)","v":1.0841666666666667}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"11:00:00",19,1.7083333333333333,5,2.2916666666666665,3,2.375,1,{"$f":"IF(AC519<60,(60-AC519)/24,0)","v":2.4583333333333335},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"12:00:00",19,1.7083333333333333,6.98,2.2091666666666665,7,2.2083333333333335,3,{"$f":"IF(AC520<60,(60-AC520)/24,0)","v":2.375},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"13:00:00",21,1.625,8.06,2.1641666666666666,9,2.125,5,{"$f":"IF(AC521<60,(60-AC521)/24,0)","v":2.2916666666666665},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"14:00:00",23,1.5416666666666667,10.039999999999999,2.0816666666666666,10,2.0833333333333335,7,{"$f":"IF(AC522<60,(60-AC522)/24,0)","v":2.2083333333333335},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"15:00:00",23,1.5416666666666667,10.039999999999999,2.0816666666666666,10,2.0833333333333335,7,{"$f":"IF(AC523<60,(60-AC523)/24,0)","v":2.2083333333333335},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"16:00:00",21,1.625,10.039999999999999,2.0816666666666666,10,2.0833333333333335,7,{"$f":"IF(AC524<60,(60-AC524)/24,0)","v":2.2083333333333335},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"17:00:00",18,1.75,8.9600000000000009,2.1266666666666665,9,2.125,7,{"$f":"IF(AC525<60,(60-AC525)/24,0)","v":2.2083333333333335},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"18:00:00",7,2.2083333333333335,8.06,2.1641666666666666,7,2.2083333333333335,3,{"$f":"IF(AC526<60,(60-AC526)/24,0)","v":2.375},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"19:00:00",3,2.375,6.98,2.2091666666666665,5,2.2916666666666665,3,{"$f":"IF(AC527<60,(60-AC527)/24,0)","v":2.375},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"20:00:00",-2,2.5833333333333335,3.02,2.3741666666666665,0,2.5,1,{"$f":"IF(AC528<60,(60-AC528)/24,0)","v":2.4583333333333335},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"21:00:00",-4,2.6666666666666665,1.04,2.4566666666666666,0,2.5,1,{"$f":"IF(AC529<60,(60-AC529)/24,0)","v":2.4583333333333335},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"22:00:00",-4,2.6666666666666665,-2.02,2.5841666666666669,-2,2.5833333333333335,-4,{"$f":"IF(AC530<60,(60-AC530)/24,0)","v":2.6666666666666665},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"23:00:00",-6,2.75,-7.06,2.7941666666666669,0,2.5,-8,{"$f":"IF(AC531<60,(60-AC531)/24,0)","v":2.8333333333333335},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,1,-8,2.8333333333333335,-5.98,2.749166666666667,-8,2.8333333333333335,-8,{"$f":"IF(AC532<60,(60-AC532)/24,0)","v":2.8333333333333335},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"01:00:00",-9,2.875,-9.0399999999999991,2.8766666666666665,-9,2.875,-11,{"$f":"IF(AC533<60,(60-AC533)/24,0)","v":2.9583333333333335},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"02:00:00",-8,2.8333333333333335,-7.96,2.8316666666666666,-11,2.9583333333333335,-13,{"$f":"IF(AC534<60,(60-AC534)/24,0)","v":3.0416666666666665},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"03:00:00",-9,2.875,-7.96,2.8316666666666666,-9,2.875,-15,{"$f":"IF(AC535<60,(60-AC535)/24,0)","v":3.125},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"04:00:00",-11,2.9583333333333335,-9.0399999999999991,2.8766666666666665,-9,2.875,-13,{"$f":"IF(AC536<60,(60-AC536)/24,0)","v":3.0416666666666665},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"05:00:00",-11,2.9583333333333335,-9.0399999999999991,2.8766666666666665,-11,2.9583333333333335,-13,{"$f":"IF(AC537<60,(60-AC537)/24,0)","v":3.0416666666666665},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"06:00:00",-13,3.0416666666666665,-9.0399999999999991,2.8766666666666665,-11,2.9583333333333335,-13,{"$f":"IF(AC538<60,(60-AC538)/24,0)","v":3.0416666666666665},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"07:00:00",-13,3.0416666666666665,-5.98,2.749166666666667,-10,2.9166666666666665,-15,{"$f":"IF(AC539<60,(60-AC539)/24,0)","v":3.125},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"08:00:00",-13,3.0416666666666665,-5.0800000000000054,2.7116666666666673,-9,2.875,-11,{"$f":"IF(AC540<60,(60-AC540)/24,0)","v":2.9583333333333335},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"09:00:00",-8,2.8333333333333335,-0.94000000000000483,2.539166666666667,-8,2.8333333333333335,-9,{"$f":"IF(AC541<60,(60-AC541)/24,0)","v":2.875},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"10:00:00",0,2.5,3.92,2.3366666666666664,-2,2.5833333333333335,-6,{"$f":"IF(AC542<60,(60-AC542)/24,0)","v":2.75},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"11:00:00",9,2.125,8.9600000000000009,2.1266666666666665,5,2.2916666666666665,0,{"$f":"IF(AC543<60,(60-AC543)/24,0)","v":2.5},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"12:00:00",19,1.7083333333333333,12.02,1.9991666666666668,9,2.125,3,{"$f":"IF(AC544<60,(60-AC544)/24,0)","v":2.375},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"13:00:00",27,1.375,15.98,1.8341666666666665,12,2,7,{"$f":"IF(AC545<60,(60-AC545)/24,0)","v":2.2083333333333335},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"14:00:00",28,1.3333333333333333,19.04,1.7066666666666668,16,1.8333333333333333,10,{"$f":"IF(AC546<60,(60-AC546)/24,0)","v":2.0833333333333335},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"15:00:00",27,1.375,21.92,1.5866666666666667,18,1.75,12,{"$f":"IF(AC547<60,(60-AC547)/24,0)","v":2},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"16:00:00",25,1.4583333333333333,24.08,1.4966666666666668,19,1.7083333333333333,14,{"$f":"IF(AC548<60,(60-AC548)/24,0)","v":1.9166666666666667},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"17:00:00",19,1.7083333333333333,26.06,1.4141666666666666,19,1.7083333333333333,16,{"$f":"IF(AC549<60,(60-AC549)/24,0)","v":1.8333333333333333},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"18:00:00",16,1.8333333333333333,24.98,1.4591666666666665,18,1.75,16,{"$f":"IF(AC550<60,(60-AC550)/24,0)","v":1.8333333333333333},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"19:00:00",12,2,24.98,1.4591666666666665,16,1.8333333333333333,10,{"$f":"IF(AC551<60,(60-AC551)/24,0)","v":2.0833333333333335},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"20:00:00",9,2.125,24.98,1.4591666666666665,16,1.8333333333333333,14,{"$f":"IF(AC552<60,(60-AC552)/24,0)","v":1.9166666666666667},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"21:00:00",9,2.125,26.06,1.4141666666666666,16,1.8333333333333333,14,{"$f":"IF(AC553<60,(60-AC553)/24,0)","v":1.9166666666666667},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"22:00:00",10,2.0833333333333335,24.98,1.4591666666666665,18,1.75,16,{"$f":"IF(AC554<60,(60-AC554)/24,0)","v":1.8333333333333333},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"23:00:00",16,1.8333333333333333,26.06,1.4141666666666666,18,1.75,16,{"$f":"IF(AC555<60,(60-AC555)/24,0)","v":1.8333333333333333},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,1,16,1.8333333333333333,24.98,1.4591666666666665,18,1.75,16,{"$f":"IF(AC556<60,(60-AC556)/24,0)","v":1.8333333333333333},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"01:00:00",18,1.75,21.92,1.5866666666666667,18,1.75,16,{"$f":"IF(AC557<60,(60-AC557)/24,0)","v":1.8333333333333333},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"02:00:00",18,1.75,23,1.5416666666666667,14,1.9166666666666667,16,{"$f":"IF(AC558<60,(60-AC558)/24,0)","v":1.8333333333333333},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"03:00:00",18,1.75,26.96,1.3766666666666667,16,1.8333333333333333,18,{"$f":"IF(AC559<60,(60-AC559)/24,0)","v":1.75},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"04:00:00",18,1.75,26.96,1.3766666666666667,16,1.8333333333333333,18,{"$f":"IF(AC560<60,(60-AC560)/24,0)","v":1.75},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"05:00:00",19,1.7083333333333333,24.08,1.4966666666666668,18,1.75,16,{"$f":"IF(AC561<60,(60-AC561)/24,0)","v":1.8333333333333333},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"06:00:00",19,1.7083333333333333,17.059999999999999,1.7891666666666666,18,1.75,18,{"$f":"IF(AC562<60,(60-AC562)/24,0)","v":1.75},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"07:00:00",19,1.7083333333333333,23,1.5416666666666667,18,1.75,18,{"$f":"IF(AC563<60,(60-AC563)/24,0)","v":1.75},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"08:00:00",19,1.7083333333333333,24.08,1.4966666666666668,18,1.75,18,{"$f":"IF(AC564<60,(60-AC564)/24,0)","v":1.75},26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"09:00:00",21,1.625,26.96,1.3766666666666667,19,1.7083333333333333,18,{"$f":"IF(AC565<60,(60-AC565)/24,0)","v":1.75},28.04,1.3316666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"10:00:00",23,1.5416666666666667,28.94,1.2941666666666667,21,1.625,19,{"$f":"IF(AC566<60,(60-AC566)/24,0)","v":1.7083333333333333},28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"11:00:00",27,1.375,30.02,1.2491666666666668,25,1.4583333333333333,21,{"$f":"IF(AC567<60,(60-AC567)/24,0)","v":1.625},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"12:00:00",30,1.25,28.94,1.2941666666666667,27,1.375,23,{"$f":"IF(AC568<60,(60-AC568)/24,0)","v":1.5416666666666667},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"13:00:00",30,1.25,30.02,1.2491666666666668,28,1.3333333333333333,25,{"$f":"IF(AC569<60,(60-AC569)/24,0)","v":1.4583333333333333},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"14:00:00",30,1.25,30.02,1.2491666666666668,30,1.25,28,{"$f":"IF(AC570<60,(60-AC570)/24,0)","v":1.3333333333333333},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"15:00:00",30,1.25,30.02,1.2491666666666668,32,1.1666666666666667,28,{"$f":"IF(AC571<60,(60-AC571)/24,0)","v":1.3333333333333333},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"16:00:00",30,1.25,28.94,1.2941666666666667,34,1.0833333333333333,30,{"$f":"IF(AC572<60,(60-AC572)/24,0)","v":1.25},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"17:00:00",28,1.3333333333333333,26.96,1.3766666666666667,28,1.3333333333333333,25,{"$f":"IF(AC573<60,(60-AC573)/24,0)","v":1.4583333333333333},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"18:00:00",28,1.3333333333333333,26.06,1.4141666666666666,25,1.4583333333333333,23,{"$f":"IF(AC574<60,(60-AC574)/24,0)","v":1.5416666666666667},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"19:00:00",27,1.375,24.98,1.4591666666666665,21,1.625,19,{"$f":"IF(AC575<60,(60-AC575)/24,0)","v":1.7083333333333333},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"20:00:00",25,1.4583333333333333,23,1.5416666666666667,19,1.7083333333333333,16,{"$f":"IF(AC576<60,(60-AC576)/24,0)","v":1.8333333333333333},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"21:00:00",28,1.3333333333333333,23,1.5416666666666667,16,1.8333333333333333,16,{"$f":"IF(AC577<60,(60-AC577)/24,0)","v":1.8333333333333333},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"22:00:00",27,1.375,21.92,1.5866666666666667,14,1.9166666666666667,10,{"$f":"IF(AC578<60,(60-AC578)/24,0)","v":2.0833333333333335},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"23:00:00",25,1.4583333333333333,17.96,1.7516666666666667,12,2,10,{"$f":"IF(AC579<60,(60-AC579)/24,0)","v":2.0833333333333335},26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,1,21,1.625,15.08,1.8716666666666668,10,2.0833333333333335,10,{"$f":"IF(AC580<60,(60-AC580)/24,0)","v":2.0833333333333335},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"01:00:00",18,{"$f":"IF(W581<60,(60-W581)/24,0)","v":1.75},12.92,1.9616666666666667,10,2.0833333333333335,7,{"$f":"IF(AC581<60,(60-AC581)/24,0)","v":2.2083333333333335},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"02:00:00",15,1.875,10.94,{"$f":"IF(Y582<60,(60-Y582)/24,0)","v":2.0441666666666669},9,{"$f":"IF(AA582<60,(60-AA582)/24,0)","v":2.125},7,{"$f":"IF(AC582<60,(60-AC582)/24,0)","v":2.2083333333333335},25.88,{"$f":"IF(AE582<60,(60-AE582)/24,0)","v":1.4216666666666669}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"03:00:00",11,2.0416666666666665,8.9600000000000009,2.1266666666666665,9,2.125,7,{"$f":"IF(AC583<60,(60-AC583)/24,0)","v":2.2083333333333335},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"04:00:00",9,2.125,6.98,2.2091666666666665,10,2.0833333333333335,9,{"$f":"IF(AC584<60,(60-AC584)/24,0)","v":2.125},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"05:00:00",7,2.2083333333333335,6.08,2.2466666666666666,14,1.9166666666666667,9,{"$f":"IF(AC585<60,(60-AC585)/24,0)","v":2.125},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"06:00:00",7,2.2083333333333335,3.92,2.3366666666666664,21,1.625,12,{"$f":"IF(AC586<60,(60-AC586)/24,0)","v":2},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"07:00:00",7,2.2083333333333335,1.94,2.4191666666666669,25,1.4583333333333333,14,{"$f":"IF(AC587<60,(60-AC587)/24,0)","v":1.9166666666666667},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"08:00:00",10,2.0833333333333335,1.04,2.4566666666666666,25,1.4583333333333333,16,{"$f":"IF(AC588<60,(60-AC588)/24,0)","v":1.8333333333333333},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"09:00:00",12,2,1.94,2.4191666666666669,23,1.5416666666666667,18,{"$f":"IF(AC589<60,(60-AC589)/24,0)","v":1.75},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"10:00:00",17,1.7916666666666667,3.02,2.3741666666666665,23,1.5416666666666667,18,{"$f":"IF(AC590<60,(60-AC590)/24,0)","v":1.75},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"11:00:00",22,1.5833333333333333,5,2.2916666666666665,23,1.5416666666666667,18,{"$f":"IF(AC591<60,(60-AC591)/24,0)","v":1.75},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"12:00:00",27,1.375,6.08,2.2466666666666666,25,1.4583333333333333,18,{"$f":"IF(AC592<60,(60-AC592)/24,0)","v":1.75},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"13:00:00",28,1.3333333333333333,8.9600000000000009,2.1266666666666665,27,1.375,18,{"$f":"IF(AC593<60,(60-AC593)/24,0)","v":1.75},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"14:00:00",28,1.3333333333333333,10.94,2.0441666666666669,27,1.375,19,{"$f":"IF(AC594<60,(60-AC594)/24,0)","v":1.7083333333333333},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"15:00:00",27,1.375,12.02,1.9991666666666668,27,1.375,19,{"$f":"IF(AC595<60,(60-AC595)/24,0)","v":1.7083333333333333},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"16:00:00",25,1.4583333333333333,12.92,1.9616666666666667,27,1.375,21,{"$f":"IF(AC596<60,(60-AC596)/24,0)","v":1.625},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"17:00:00",21,1.625,12.02,1.9991666666666668,27,1.375,23,{"$f":"IF(AC597<60,(60-AC597)/24,0)","v":1.5416666666666667},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"18:00:00",14,1.9166666666666667,10.039999999999999,2.0816666666666666,25,1.4583333333333333,23,{"$f":"IF(AC598<60,(60-AC598)/24,0)","v":1.5416666666666667},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"19:00:00",7,2.2083333333333335,6.08,2.2466666666666666,25,1.4583333333333333,21,{"$f":"IF(AC599<60,(60-AC599)/24,0)","v":1.625},28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"20:00:00",10,2.0833333333333335,-0.94000000000000483,2.539166666666667,25,1.4583333333333333,21,{"$f":"IF(AC600<60,(60-AC600)/24,0)","v":1.625},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"21:00:00",3,2.375,-3.9999999999999147E-2,2.5016666666666665,23,1.5416666666666667,19.075900000000001,{"$f":"IF(AC601<60,(60-AC601)/24,0)","v":1.7051708333333331},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"22:00:00",1,2.4583333333333335,-0.94000000000000483,2.539166666666667,23,1.5416666666666667,21,{"$f":"IF(AC602<60,(60-AC602)/24,0)","v":1.625},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"23:00:00",0,2.5,-0.94000000000000483,2.539166666666667,23,1.5416666666666667,19,{"$f":"IF(AC603<60,(60-AC603)/24,0)","v":1.7083333333333333},26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,1,-4,2.6666666666666665,-5.0800000000000054,2.7116666666666673,23,1.5416666666666667,19,{"$f":"IF(AC604<60,(60-AC604)/24,0)","v":1.7083333333333333},26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"01:00:00",0,2.5,-5.98,2.749166666666667,21,1.625,19,{"$f":"IF(AC605<60,(60-AC605)/24,0)","v":1.7083333333333333},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"02:00:00",-4,2.6666666666666665,-5.98,2.749166666666667,21,1.625,19,{"$f":"IF(AC606<60,(60-AC606)/24,0)","v":1.7083333333333333},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"03:00:00",-9,2.875,-9.0399999999999991,2.8766666666666665,21,1.625,19,{"$f":"IF(AC607<60,(60-AC607)/24,0)","v":1.7083333333333333},21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"04:00:00",-8,2.8333333333333335,-7.06,2.7941666666666669,21,1.625,19,{"$f":"IF(AC608<60,(60-AC608)/24,0)","v":1.7083333333333333},20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"05:00:00",-8,2.8333333333333335,-7.96,2.8316666666666666,21,1.625,19,{"$f":"IF(AC609<60,(60-AC609)/24,0)","v":1.7083333333333333},20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"06:00:00",-8,2.8333333333333335,-9.94,2.9141666666666666,21,1.625,19,{"$f":"IF(AC610<60,(60-AC610)/24,0)","v":1.7083333333333333},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"07:00:00",-9,2.875,-9.94,2.9141666666666666,21,1.625,19,{"$f":"IF(AC611<60,(60-AC611)/24,0)","v":1.7083333333333333},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"08:00:00",-9,2.875,-9.0399999999999991,2.8766666666666665,21,1.625,19,{"$f":"IF(AC612<60,(60-AC612)/24,0)","v":1.7083333333333333},20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"09:00:00",-2,2.5833333333333335,-2.92,2.6216666666666666,23,1.5416666666666667,19,{"$f":"IF(AC613<60,(60-AC613)/24,0)","v":1.7083333333333333},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"10:00:00",5,2.2916666666666665,5,2.2916666666666665,25,1.4583333333333333,21,{"$f":"IF(AC614<60,(60-AC614)/24,0)","v":1.625},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"11:00:00",16,1.8333333333333333,12.92,1.9616666666666667,25,1.4583333333333333,23,{"$f":"IF(AC615<60,(60-AC615)/24,0)","v":1.5416666666666667},26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"12:00:00",21,1.625,19.940000000000001,1.6691666666666667,25,1.4583333333333333,25,{"$f":"IF(AC616<60,(60-AC616)/24,0)","v":1.4583333333333333},28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"13:00:00",25,1.4583333333333333,21.02,1.6241666666666668,25,1.4583333333333333,25,{"$f":"IF(AC617<60,(60-AC617)/24,0)","v":1.4583333333333333},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"14:00:00",27,1.375,21.92,1.5866666666666667,25,1.4583333333333333,21,{"$f":"IF(AC618<60,(60-AC618)/24,0)","v":1.625},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"15:00:00",27,1.375,21.92,1.5866666666666667,27,1.375,23,{"$f":"IF(AC619<60,(60-AC619)/24,0)","v":1.5416666666666667},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"16:00:00",27,1.375,21.92,1.5866666666666667,25,1.4583333333333333,21,{"$f":"IF(AC620<60,(60-AC620)/24,0)","v":1.625},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"17:00:00",19,1.7083333333333333,19.940000000000001,1.6691666666666667,25,1.4583333333333333,19,{"$f":"IF(AC621<60,(60-AC621)/24,0)","v":1.7083333333333333},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"18:00:00",14,1.9166666666666667,17.059999999999999,1.7891666666666666,21,1.625,16,{"$f":"IF(AC622<60,(60-AC622)/24,0)","v":1.8333333333333333},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"19:00:00",7,2.2083333333333335,17.96,1.7516666666666667,19,1.7083333333333333,18,{"$f":"IF(AC623<60,(60-AC623)/24,0)","v":1.75},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"20:00:00",7,2.2083333333333335,19.04,1.7066666666666668,18,1.75,16,{"$f":"IF(AC624<60,(60-AC624)/24,0)","v":1.8333333333333333},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"21:00:00",3,2.375,19.04,1.7066666666666668,16,1.8333333333333333,16,{"$f":"IF(AC625<60,(60-AC625)/24,0)","v":1.8333333333333333},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"22:00:00",5,2.2916666666666665,17.96,1.7516666666666667,16,1.8333333333333333,12,{"$f":"IF(AC626<60,(60-AC626)/24,0)","v":2},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"23:00:00",1,2.4583333333333335,17.059999999999999,1.7891666666666666,16.050999999999998,1.8312083333333333,12,{"$f":"IF(AC627<60,(60-AC627)/24,0)","v":2},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,1,0,2.5,17.059999999999999,1.7891666666666666,14,1.9166666666666667,11,{"$f":"IF(AC628<60,(60-AC628)/24,0)","v":2.0416666666666665},21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"01:00:00",3,2.375,15.08,1.8716666666666668,12,2,10,{"$f":"IF(AC629<60,(60-AC629)/24,0)","v":2.0833333333333335},21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"02:00:00",5,2.2916666666666665,15.08,1.8716666666666668,10,2.0833333333333335,9,{"$f":"IF(AC630<60,(60-AC630)/24,0)","v":2.125},21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"03:00:00",7,2.2083333333333335,10.94,2.0441666666666669,9,2.125,9,{"$f":"IF(AC631<60,(60-AC631)/24,0)","v":2.125},21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"04:00:00",7,2.2083333333333335,8.06,2.1641666666666666,9,2.125,7,{"$f":"IF(AC632<60,(60-AC632)/24,0)","v":2.2083333333333335},20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"05:00:00",7,2.2083333333333335,6.08,2.2466666666666666,9,2.125,5,{"$f":"IF(AC633<60,(60-AC633)/24,0)","v":2.2916666666666665},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"06:00:00",9,2.125,3.92,2.3366666666666664,9,2.125,5,{"$f":"IF(AC634<60,(60-AC634)/24,0)","v":2.2916666666666665},18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"07:00:00",7,2.2083333333333335,1.94,2.4191666666666669,7,2.2083333333333335,3,{"$f":"IF(AC635<60,(60-AC635)/24,0)","v":2.375},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"08:00:00",9,2.125,3.02,2.3741666666666665,7,2.2083333333333335,3,{"$f":"IF(AC636<60,(60-AC636)/24,0)","v":2.375},18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"09:00:00",10,2.0833333333333335,8.9600000000000009,2.1266666666666665,9,2.125,7,{"$f":"IF(AC637<60,(60-AC637)/24,0)","v":2.2083333333333335},18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"10:00:00",14,1.9166666666666667,19.940000000000001,1.6691666666666667,10,2.0833333333333335,7,{"$f":"IF(AC638<60,(60-AC638)/24,0)","v":2.2083333333333335},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"11:00:00",18,1.75,30.02,1.2491666666666668,12,2,9,{"$f":"IF(AC639<60,(60-AC639)/24,0)","v":2.125},20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"12:00:00",21,1.625,30.92,1.2116666666666667,12,2,9,{"$f":"IF(AC640<60,(60-AC640)/24,0)","v":2.125},21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"13:00:00",25,1.4583333333333333,32,1.1666666666666667,16,1.8333333333333333,10,{"$f":"IF(AC641<60,(60-AC641)/24,0)","v":2.0833333333333335},21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"14:00:00",27,1.375,33.08,1.1216666666666668,14,1.9166666666666667,10,{"$f":"IF(AC642<60,(60-AC642)/24,0)","v":2.0833333333333335},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"15:00:00",28,1.3333333333333333,33.08,1.1216666666666668,14,1.9166666666666667,10,{"$f":"IF(AC643<60,(60-AC643)/24,0)","v":2.0833333333333335},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"16:00:00",28,1.3333333333333333,32,1.1666666666666667,12,2,9,{"$f":"IF(AC644<60,(60-AC644)/24,0)","v":2.125},20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"17:00:00",27,{"$f":"IF(W645<60,(60-W645)/24,0)","v":1.375},30.02,1.2491666666666668,10,2.0833333333333335,7,{"$f":"IF(AC645<60,(60-AC645)/24,0)","v":2.2083333333333335},16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"18:00:00",27,1.375,26.06,{"$f":"IF(Y646<60,(60-Y646)/24,0)","v":1.4141666666666666},9,{"$f":"IF(AA646<60,(60-AA646)/24,0)","v":2.125},3,{"$f":"IF(AC646<60,(60-AC646)/24,0)","v":2.375},15.98,{"$f":"IF(AE646<60,(60-AE646)/24,0)","v":1.8341666666666665}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"19:00:00",25,1.4583333333333333,23,1.5416666666666667,9,2.125,1,{"$f":"IF(AC647<60,(60-AC647)/24,0)","v":2.4583333333333335},14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"20:00:00",25,1.4583333333333333,24.08,1.4966666666666668,7,2.2083333333333335,1,{"$f":"IF(AC648<60,(60-AC648)/24,0)","v":2.4583333333333335},12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"21:00:00",23,1.5416666666666667,26.06,1.4141666666666666,5,2.2916666666666665,-8,{"$f":"IF(AC649<60,(60-AC649)/24,0)","v":2.8333333333333335},11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"22:00:00",22,1.5833333333333333,26.06,1.4141666666666666,3,2.375,-8,{"$f":"IF(AC650<60,(60-AC650)/24,0)","v":2.8333333333333335},11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"23:00:00",21,1.625,24.98,1.4591666666666665,3,2.375,-4,{"$f":"IF(AC651<60,(60-AC651)/24,0)","v":2.6666666666666665},10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,1,20,1.6666666666666667,26.06,1.4141666666666666,3,2.375,-2,{"$f":"IF(AC652<60,(60-AC652)/24,0)","v":2.5833333333333335},9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"01:00:00",19,1.7083333333333333,26.96,1.3766666666666667,3,2.375,0,{"$f":"IF(AC653<60,(60-AC653)/24,0)","v":2.5},9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"02:00:00",19,1.7083333333333333,26.96,1.3766666666666667,3,2.375,1,{"$f":"IF(AC654<60,(60-AC654)/24,0)","v":2.4583333333333335},9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"03:00:00",19,1.7083333333333333,28.94,1.2941666666666667,3,2.375,1,{"$f":"IF(AC655<60,(60-AC655)/24,0)","v":2.4583333333333335},9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"04:00:00",19,1.7083333333333333,30.92,1.2116666666666667,3,2.375,1,{"$f":"IF(AC656<60,(60-AC656)/24,0)","v":2.4583333333333335},10.039999999999999,2.0816666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"05:00:00",19,1.7083333333333333,32,1.1666666666666667,1,2.4583333333333335,-4,{"$f":"IF(AC657<60,(60-AC657)/24,0)","v":2.6666666666666665},10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"06:00:00",19,1.7083333333333333,37.04,0.95666666666666667,1,2.4583333333333335,-2,{"$f":"IF(AC658<60,(60-AC658)/24,0)","v":2.5833333333333335},9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"07:00:00",18,1.75,37.04,0.95666666666666667,1,2.4583333333333335,-8,{"$f":"IF(AC659<60,(60-AC659)/24,0)","v":2.8333333333333335},10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"08:00:00",18,1.75,37.04,0.95666666666666667,1,2.4583333333333335,-8,{"$f":"IF(AC660<60,(60-AC660)/24,0)","v":2.8333333333333335},11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"09:00:00",18,1.75,37.04,0.95666666666666667,1,2.4583333333333335,0,{"$f":"IF(AC661<60,(60-AC661)/24,0)","v":2.5},14.9,1.8791666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"10:00:00",19,1.7083333333333333,37.94,0.9191666666666668,7,2.2083333333333335,1,{"$f":"IF(AC662<60,(60-AC662)/24,0)","v":2.4583333333333335},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"11:00:00",19,1.7083333333333333,39.020000000000003,0.87416666666666654,9,2.125,3,{"$f":"IF(AC663<60,(60-AC663)/24,0)","v":2.375},20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"12:00:00",19,1.7083333333333333,39.92,0.83666666666666656,9,2.125,7,{"$f":"IF(AC664<60,(60-AC664)/24,0)","v":2.2083333333333335},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"13:00:00",19,1.7083333333333333,41,0.79166666666666663,10,2.0833333333333335,7,{"$f":"IF(AC665<60,(60-AC665)/24,0)","v":2.2083333333333335},26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"14:00:00",21,1.625,42.08,0.7466666666666667,12,2,9,{"$f":"IF(AC666<60,(60-AC666)/24,0)","v":2.125},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"15:00:00",21,1.625,42.08,0.7466666666666667,12,2,9,{"$f":"IF(AC667<60,(60-AC667)/24,0)","v":2.125},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"16:00:00",19,1.7083333333333333,41,0.79166666666666663,12,2,7,{"$f":"IF(AC668<60,(60-AC668)/24,0)","v":2.2083333333333335},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"17:00:00",18,1.75,39.020000000000003,0.87416666666666654,10,2.0833333333333335,7,{"$f":"IF(AC669<60,(60-AC669)/24,0)","v":2.2083333333333335},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"18:00:00",16,1.8333333333333333,30.02,1.2491666666666668,10,2.0833333333333335,3,{"$f":"IF(AC670<60,(60-AC670)/24,0)","v":2.375},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"19:00:00",9,2.125,28.04,1.3316666666666668,10,2.0833333333333335,3,{"$f":"IF(AC671<60,(60-AC671)/24,0)","v":2.375},21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"20:00:00",1,2.4583333333333335,24.98,1.4591666666666665,10,2.0833333333333335,-2,{"$f":"IF(AC672<60,(60-AC672)/24,0)","v":2.5833333333333335},20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"21:00:00",-4,2.6666666666666665,21.92,1.5866666666666667,9,2.125,-8,{"$f":"IF(AC673<60,(60-AC673)/24,0)","v":2.8333333333333335},18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"22:00:00",-6,2.75,21.02,1.6241666666666668,9,2.125,-9,{"$f":"IF(AC674<60,(60-AC674)/24,0)","v":2.875},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"23:00:00",-8,2.8333333333333335,19.940000000000001,1.6691666666666667,9,2.125,-8,{"$f":"IF(AC675<60,(60-AC675)/24,0)","v":2.8333333333333335},15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,1,-6,2.75,19.04,1.7066666666666668,9,2.125,-9,{"$f":"IF(AC676<60,(60-AC676)/24,0)","v":2.875},15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"01:00:00",-8,2.8333333333333335,15.98,1.8341666666666665,1,2.4583333333333335,-9,{"$f":"IF(AC677<60,(60-AC677)/24,0)","v":2.875},12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"02:00:00",-9,2.875,17.059999999999999,1.7891666666666666,0,2.5,-8,{"$f":"IF(AC678<60,(60-AC678)/24,0)","v":2.8333333333333335},14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"03:00:00",-11,2.9583333333333335,17.059999999999999,1.7891666666666666,-2,2.5833333333333335,-13,{"$f":"IF(AC679<60,(60-AC679)/24,0)","v":3.0416666666666665},11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"04:00:00",-11,2.9583333333333335,15.98,1.8341666666666665,-8,2.8333333333333335,-15,{"$f":"IF(AC680<60,(60-AC680)/24,0)","v":3.125},10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"05:00:00",-11,2.9583333333333335,15.08,1.8716666666666668,-6,2.75,-15,{"$f":"IF(AC681<60,(60-AC681)/24,0)","v":3.125},9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"06:00:00",-11,2.9583333333333335,15.08,1.8716666666666668,-8,2.8333333333333335,-17,{"$f":"IF(AC682<60,(60-AC682)/24,0)","v":3.2083333333333335},9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"07:00:00",-13,3.0416666666666665,12.02,1.9991666666666668,-11,2.9583333333333335,-18,{"$f":"IF(AC683<60,(60-AC683)/24,0)","v":3.25},7.88,2.1716666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"08:00:00",-11,2.9583333333333335,12.92,1.9616666666666667,-9,2.875,-18,{"$f":"IF(AC684<60,(60-AC684)/24,0)","v":3.25},12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"09:00:00",-8,2.8333333333333335,19.04,1.7066666666666668,-4,2.6666666666666665,-9,{"$f":"IF(AC685<60,(60-AC685)/24,0)","v":2.875},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"10:00:00",1,2.4583333333333335,32,1.1666666666666667,12,2,-2,{"$f":"IF(AC686<60,(60-AC686)/24,0)","v":2.5833333333333335},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"11:00:00",10,2.0833333333333335,39.020000000000003,0.87416666666666654,19,1.7083333333333333,7,{"$f":"IF(AC687<60,(60-AC687)/24,0)","v":2.2083333333333335},26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"12:00:00",19,1.7083333333333333,39.92,0.83666666666666656,23,1.5416666666666667,12,{"$f":"IF(AC688<60,(60-AC688)/24,0)","v":2},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"13:00:00",23,1.5416666666666667,41,0.79166666666666663,25,1.4583333333333333,18,{"$f":"IF(AC689<60,(60-AC689)/24,0)","v":1.75},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"14:00:00",25,1.4583333333333333,42.98,0.70916666666666683,28,1.3333333333333333,21,{"$f":"IF(AC690<60,(60-AC690)/24,0)","v":1.625},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"15:00:00",25,1.4583333333333333,44.96,0.62666666666666659,30,1.25,23,{"$f":"IF(AC691<60,(60-AC691)/24,0)","v":1.5416666666666667},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"16:00:00",25,1.4583333333333333,42.08,0.7466666666666667,30,1.25,21,{"$f":"IF(AC692<60,(60-AC692)/24,0)","v":1.625},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"17:00:00",21,1.625,39.92,0.83666666666666656,28,1.3333333333333333,18,{"$f":"IF(AC693<60,(60-AC693)/24,0)","v":1.75},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"18:00:00",18,1.75,35.96,1.0016666666666667,21,1.625,9,{"$f":"IF(AC694<60,(60-AC694)/24,0)","v":2.125},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"19:00:00",10,2.0833333333333335,30.92,1.2116666666666667,19,1.7083333333333333,1,{"$f":"IF(AC695<60,(60-AC695)/24,0)","v":2.4583333333333335},26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"20:00:00",7,2.2083333333333335,26.06,1.4141666666666666,16,1.8333333333333333,7,{"$f":"IF(AC696<60,(60-AC696)/24,0)","v":2.2083333333333335},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"21:00:00",7,2.2083333333333335,24.98,1.4591666666666665,10,2.0833333333333335,1,{"$f":"IF(AC697<60,(60-AC697)/24,0)","v":2.4583333333333335},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"22:00:00",3,2.375,24.98,1.4591666666666665,9,2.125,-2,{"$f":"IF(AC698<60,(60-AC698)/24,0)","v":2.5833333333333335},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"23:00:00",0,2.5,30.02,1.2491666666666668,9,2.125,-2,{"$f":"IF(AC699<60,(60-AC699)/24,0)","v":2.5833333333333335},20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,1,0,2.5,32,1.1666666666666667,5,2.2916666666666665,-6,{"$f":"IF(AC700<60,(60-AC700)/24,0)","v":2.75},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"01:00:00",-2,2.5833333333333335,32,1.1666666666666667,3,2.375,-6,{"$f":"IF(AC701<60,(60-AC701)/24,0)","v":2.75},20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"02:00:00",-4,2.6666666666666665,32,1.1666666666666667,1,2.4583333333333335,-6,{"$f":"IF(AC702<60,(60-AC702)/24,0)","v":2.75},20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"03:00:00",-6,2.75,33.08,1.1216666666666668,0,2.5,-8,{"$f":"IF(AC703<60,(60-AC703)/24,0)","v":2.8333333333333335},18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"04:00:00",-4,2.6666666666666665,33.979999999999997,1.0841666666666667,0,2.5,-8,{"$f":"IF(AC704<60,(60-AC704)/24,0)","v":2.8333333333333335},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"05:00:00",-4,2.6666666666666665,33.979999999999997,1.0841666666666667,-2,2.5833333333333335,-8,{"$f":"IF(AC705<60,(60-AC705)/24,0)","v":2.8333333333333335},16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"06:00:00",-6,2.75,33.979999999999997,1.0841666666666667,-4,2.6666666666666665,-9,{"$f":"IF(AC706<60,(60-AC706)/24,0)","v":2.875},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"07:00:00",-4,2.6666666666666665,35.06,1.0391666666666666,-4,2.6666666666666665,-11,{"$f":"IF(AC707<60,(60-AC707)/24,0)","v":2.9583333333333335},18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"08:00:00",0,2.5,35.06,1.0391666666666666,-5.3227099999999998,2.7217795833333334,-11,{"$f":"IF(AC708<60,(60-AC708)/24,0)","v":2.9583333333333335},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"09:00:00",7,{"$f":"IF(W709<60,(60-W709)/24,0)","v":2.2083333333333335},35.06,1.0391666666666666,1,2.4583333333333335,-6,{"$f":"IF(AC709<60,(60-AC709)/24,0)","v":2.75},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"10:00:00",10,2.0833333333333335,35.06,{"$f":"IF(Y710<60,(60-Y710)/24,0)","v":1.0391666666666666},9,{"$f":"IF(AA710<60,(60-AA710)/24,0)","v":2.125},3,{"$f":"IF(AC710<60,(60-AC710)/24,0)","v":2.375},28.94,{"$f":"IF(AE710<60,(60-AE710)/24,0)","v":1.2941666666666667}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"11:00:00",14,1.9166666666666667,37.94,0.9191666666666668,18,1.75,10,{"$f":"IF(AC711<60,(60-AC711)/24,0)","v":2.0833333333333335},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"12:00:00",16,1.8333333333333333,37.94,0.9191666666666668,25,1.4583333333333333,16,{"$f":"IF(AC712<60,(60-AC712)/24,0)","v":1.8333333333333333},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"13:00:00",18,1.75,35.96,1.0016666666666667,30,1.25,21,{"$f":"IF(AC713<60,(60-AC713)/24,0)","v":1.625},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"14:00:00",20,1.6666666666666667,35.96,1.0016666666666667,32,1.1666666666666667,27,{"$f":"IF(AC714<60,(60-AC714)/24,0)","v":1.375},41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"15:00:00",21,1.625,37.04,0.95666666666666667,34,1.0833333333333333,28,{"$f":"IF(AC715<60,(60-AC715)/24,0)","v":1.3333333333333333},41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"16:00:00",21,1.625,37.04,0.95666666666666667,36,1,30,{"$f":"IF(AC716<60,(60-AC716)/24,0)","v":1.25},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"17:00:00",22,1.5833333333333333,35.96,1.0016666666666667,28,1.3333333333333333,23,{"$f":"IF(AC717<60,(60-AC717)/24,0)","v":1.5416666666666667},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"18:00:00",22,1.5833333333333333,35.96,1.0016666666666667,28,1.3333333333333333,25,{"$f":"IF(AC718<60,(60-AC718)/24,0)","v":1.4583333333333333},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"19:00:00",23,1.5416666666666667,35.06,1.0391666666666666,28,1.3333333333333333,25,{"$f":"IF(AC719<60,(60-AC719)/24,0)","v":1.4583333333333333},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"20:00:00",22,1.5833333333333333,33.979999999999997,1.0841666666666667,27,1.375,23,{"$f":"IF(AC720<60,(60-AC720)/24,0)","v":1.5416666666666667},28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"21:00:00",23,1.5416666666666667,33.979999999999997,1.0841666666666667,27,1.375,19,{"$f":"IF(AC721<60,(60-AC721)/24,0)","v":1.7083333333333333},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"22:00:00",25,1.4583333333333333,33.979999999999997,1.0841666666666667,28,1.3333333333333333,21,{"$f":"IF(AC722<60,(60-AC722)/24,0)","v":1.625},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"23:00:00",25,1.4583333333333333,35.96,1.0016666666666667,28,1.3333333333333333,23,{"$f":"IF(AC723<60,(60-AC723)/24,0)","v":1.5416666666666667},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,1,25,1.4583333333333333,35.06,1.0391666666666666,27,1.375,21,{"$f":"IF(AC724<60,(60-AC724)/24,0)","v":1.625},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"01:00:00",25,1.4583333333333333,35.06,1.0391666666666666,27,1.375,23,{"$f":"IF(AC725<60,(60-AC725)/24,0)","v":1.5416666666666667},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"02:00:00",24,1.5,33.979999999999997,1.0841666666666667,27,1.375,23,{"$f":"IF(AC726<60,(60-AC726)/24,0)","v":1.5416666666666667},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"03:00:00",24,1.5,33.979999999999997,1.0841666666666667,27,1.375,21,{"$f":"IF(AC727<60,(60-AC727)/24,0)","v":1.625},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"04:00:00",25,1.4583333333333333,33.08,1.1216666666666668,28,1.3333333333333333,21.2469,{"$f":"IF(AC728<60,(60-AC728)/24,0)","v":1.6147125000000002},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"05:00:00",25,1.4583333333333333,33.08,1.1216666666666668,30,1.25,21.2469,{"$f":"IF(AC729<60,(60-AC729)/24,0)","v":1.6147125000000002},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"06:00:00",25,1.4583333333333333,35.06,1.0391666666666666,30,1.25,25,{"$f":"IF(AC730<60,(60-AC730)/24,0)","v":1.4583333333333333},18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"07:00:00",25,1.4583333333333333,30.92,1.2116666666666667,28,1.3333333333333333,27,{"$f":"IF(AC731<60,(60-AC731)/24,0)","v":1.375},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"08:00:00",25,1.4583333333333333,26.96,1.3766666666666667,30,1.25,27,{"$f":"IF(AC732<60,(60-AC732)/24,0)","v":1.375},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"09:00:00",25,1.4583333333333333,26.06,1.4141666666666666,30,1.25,25,{"$f":"IF(AC733<60,(60-AC733)/24,0)","v":1.4583333333333333},26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"10:00:00",27,1.375,26.96,1.3766666666666667,34,1.0833333333333333,27,{"$f":"IF(AC734<60,(60-AC734)/24,0)","v":1.375},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"11:00:00",27,1.375,28.04,1.3316666666666668,32,1.1666666666666667,28,{"$f":"IF(AC735<60,(60-AC735)/24,0)","v":1.3333333333333333},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"12:00:00",28,1.3333333333333333,28.94,1.2941666666666667,32,1.1666666666666667,30,{"$f":"IF(AC736<60,(60-AC736)/24,0)","v":1.25},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"13:00:00",28,1.3333333333333333,28.94,1.2941666666666667,36,1,30,{"$f":"IF(AC737<60,(60-AC737)/24,0)","v":1.25},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"14:00:00",27,1.375,28.04,1.3316666666666668,36,1,32,{"$f":"IF(AC738<60,(60-AC738)/24,0)","v":1.1666666666666667},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"15:00:00",27,1.375,26.96,1.3766666666666667,36,1,34,{"$f":"IF(AC739<60,(60-AC739)/24,0)","v":1.0833333333333333},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"16:00:00",26,1.4166666666666667,26.96,1.3766666666666667,36,1,34,{"$f":"IF(AC740<60,(60-AC740)/24,0)","v":1.0833333333333333},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"17:00:00",25,1.4583333333333333,24.98,1.4591666666666665,32,1.1666666666666667,32,{"$f":"IF(AC741<60,(60-AC741)/24,0)","v":1.1666666666666667},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"18:00:00",25,1.4583333333333333,24.98,1.4591666666666665,30,1.25,30,{"$f":"IF(AC742<60,(60-AC742)/24,0)","v":1.25},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"19:00:00",25,1.4583333333333333,23,1.5416666666666667,28,1.3333333333333333,30,{"$f":"IF(AC743<60,(60-AC743)/24,0)","v":1.25},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"20:00:00",23,1.5416666666666667,21.02,1.6241666666666668,28,1.3333333333333333,30,{"$f":"IF(AC744<60,(60-AC744)/24,0)","v":1.25},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"21:00:00",22,1.5833333333333333,19.940000000000001,1.6691666666666667,28,1.3333333333333333,28,{"$f":"IF(AC745<60,(60-AC745)/24,0)","v":1.3333333333333333},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"22:00:00",18,1.75,18.5,1.7291666666666667,29,1.2916666666666667,24,{"$f":"IF(AC746<60,(60-AC746)/24,0)","v":1.5},31.28,1.1966666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"23:00:00",14,1.9166666666666667,17.059999999999999,1.7891666666666666,29,1.2916666666666667,20,{"$f":"IF(AC747<60,(60-AC747)/24,0)","v":1.6666666666666667},27.32,1.3616666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,1,10,2.0833333333333335,15.44,1.8566666666666667,29,1.2916666666666667,16,{"$f":"IF(AC748<60,(60-AC748)/24,0)","v":1.8333333333333333},23.54,1.5191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"01:00:00",5,2.2916666666666665,13.82,1.9241666666666666,29,1.2916666666666667,12,{"$f":"IF(AC749<60,(60-AC749)/24,0)","v":2},19.579999999999998,1.6841666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"02:00:00",1,2.4583333333333335,12.2,1.9916666666666665,29,1.2916666666666667,8,{"$f":"IF(AC750<60,(60-AC750)/24,0)","v":2.1666666666666665},15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"03:00:00",-3,2.625,10.76,2.0516666666666667,29,1.2916666666666667,3,{"$f":"IF(AC751<60,(60-AC751)/24,0)","v":2.375},11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"04:00:00",-8,2.8333333333333335,8.9600000000000009,2.1266666666666665,29,1.2916666666666667,-1,{"$f":"IF(AC752<60,(60-AC752)/24,0)","v":2.5416666666666665},7.88,2.1716666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"05:00:00",-4,2.6666666666666665,8.9600000000000009,2.1266666666666665,29,1.2916666666666667,-3,{"$f":"IF(AC753<60,(60-AC753)/24,0)","v":2.625},5.9,2.2541666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"06:00:00",-6,2.75,8.9600000000000009,2.1266666666666665,29,1.2916666666666667,-2,{"$f":"IF(AC754<60,(60-AC754)/24,0)","v":2.5833333333333335},5.9,2.2541666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"07:00:00",-8,2.8333333333333335,3.02,2.3741666666666665,30,1.25,-3,{"$f":"IF(AC755<60,(60-AC755)/24,0)","v":2.625},6.98,2.2091666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"08:00:00",-6,2.75,8.06,2.1641666666666666,30,1.25,-2,{"$f":"IF(AC756<60,(60-AC756)/24,0)","v":2.5833333333333335},6.98,2.2091666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"09:00:00",0,2.5,10.039999999999999,2.0816666666666666,30,1.25,4,{"$f":"IF(AC757<60,(60-AC757)/24,0)","v":2.3333333333333335},8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"10:00:00",16,1.8333333333333333,14,1.9166666666666667,30,1.25,8,{"$f":"IF(AC758<60,(60-AC758)/24,0)","v":2.1666666666666665},14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"11:00:00",25,1.4583333333333333,17.96,1.7516666666666667,32,1.1666666666666667,14,{"$f":"IF(AC759<60,(60-AC759)/24,0)","v":1.9166666666666667},14.9,1.8791666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"12:00:00",32,1.1666666666666667,21.92,1.5866666666666667,32,1.1666666666666667,12,{"$f":"IF(AC760<60,(60-AC760)/24,0)","v":2},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"13:00:00",34,1.0833333333333333,23,1.5416666666666667,34,1.0833333333333333,16,{"$f":"IF(AC761<60,(60-AC761)/24,0)","v":1.8333333333333333},18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"14:00:00",36,1,24.98,1.4591666666666665,35,1.0416666666666667,17,{"$f":"IF(AC762<60,(60-AC762)/24,0)","v":1.7916666666666667},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"15:00:00",37,0.95833333333333337,24.98,1.4591666666666665,37,0.95833333333333337,19,{"$f":"IF(AC763<60,(60-AC763)/24,0)","v":1.7083333333333333},18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"16:00:00",36,1,24.98,1.4591666666666665,37.133800000000001,0.95275833333333326,19,{"$f":"IF(AC764<60,(60-AC764)/24,0)","v":1.7083333333333333},20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"17:00:00",28,1.3333333333333333,24.08,1.4966666666666668,35,1.0416666666666667,17,{"$f":"IF(AC765<60,(60-AC765)/24,0)","v":1.7916666666666667},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"18:00:00",18,1.75,24.08,1.4966666666666668,35,1.0416666666666667,15,{"$f":"IF(AC766<60,(60-AC766)/24,0)","v":1.875},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"19:00:00",18,1.75,24.08,1.4966666666666668,35,1.0416666666666667,15,{"$f":"IF(AC767<60,(60-AC767)/24,0)","v":1.875},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"20:00:00",16,1.8333333333333333,24.98,1.4591666666666665,35,1.0416666666666667,13,{"$f":"IF(AC768<60,(60-AC768)/24,0)","v":1.9583333333333333},15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"21:00:00",9,2.125,21.92,1.5866666666666667,36,1,11,{"$f":"IF(AC769<60,(60-AC769)/24,0)","v":2.0416666666666665},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"22:00:00",3,2.375,21.92,1.5866666666666667,31.1968,1.2001333333333333,12,{"$f":"IF(AC770<60,(60-AC770)/24,0)","v":2},16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"23:00:00",7,2.2083333333333335,21.92,1.5866666666666667,27,1.375,11,{"$f":"IF(AC771<60,(60-AC771)/24,0)","v":2.0416666666666665},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,1,1,2.4583333333333335,23,1.5416666666666667,27,1.375,11,{"$f":"IF(AC772<60,(60-AC772)/24,0)","v":2.0416666666666665},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"01:00:00",0,{"$f":"IF(W773<60,(60-W773)/24,0)","v":2.5},23,1.5416666666666667,23,1.5416666666666667,12,{"$f":"IF(AC773<60,(60-AC773)/24,0)","v":2},15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"02:00:00",0,2.5,24.08,{"$f":"IF(Y774<60,(60-Y774)/24,0)","v":1.4966666666666668},22,{"$f":"IF(AA774<60,(60-AA774)/24,0)","v":1.5833333333333333},11,{"$f":"IF(AC774<60,(60-AC774)/24,0)","v":2.0416666666666665},16.88,{"$f":"IF(AE774<60,(60-AE774)/24,0)","v":1.7966666666666669}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"03:00:00",0,2.5,24.98,1.4591666666666665,20.181000000000001,1.6591250000000002,12,{"$f":"IF(AC775<60,(60-AC775)/24,0)","v":2},16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"04:00:00",-2,2.5833333333333335,26.06,1.4141666666666666,16,1.8333333333333333,12,{"$f":"IF(AC776<60,(60-AC776)/24,0)","v":2},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"05:00:00",1,2.4583333333333335,24.98,1.4591666666666665,15,1.875,13,{"$f":"IF(AC777<60,(60-AC777)/24,0)","v":1.9583333333333333},18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"06:00:00",7,2.2083333333333335,24.98,1.4591666666666665,11,2.0416666666666665,15,{"$f":"IF(AC778<60,(60-AC778)/24,0)","v":1.875},16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"07:00:00",12,2,24.98,1.4591666666666665,10,2.0833333333333335,16,{"$f":"IF(AC779<60,(60-AC779)/24,0)","v":1.8333333333333333},15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"08:00:00",16,1.8333333333333333,24.08,1.4966666666666668,12.358599999999999,1.9850583333333336,17,{"$f":"IF(AC780<60,(60-AC780)/24,0)","v":1.7916666666666667},16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"09:00:00",28,1.3333333333333333,24.98,1.4591666666666665,17,1.7916666666666667,18,{"$f":"IF(AC781<60,(60-AC781)/24,0)","v":1.75},16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"10:00:00",28,1.3333333333333333,24.98,1.4591666666666665,23,1.5416666666666667,21,{"$f":"IF(AC782<60,(60-AC782)/24,0)","v":1.625},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"11:00:00",28,1.3333333333333333,26.06,1.4141666666666666,32,1.1666666666666667,23,{"$f":"IF(AC783<60,(60-AC783)/24,0)","v":1.5416666666666667},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"12:00:00",28,1.3333333333333333,28.04,1.3316666666666668,37,0.95833333333333337,24,{"$f":"IF(AC784<60,(60-AC784)/24,0)","v":1.5},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"13:00:00",28,1.3333333333333333,28.94,1.2941666666666667,45,0.625,24,{"$f":"IF(AC785<60,(60-AC785)/24,0)","v":1.5},26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"14:00:00",28,1.3333333333333333,28.94,1.2941666666666667,46,0.58333333333333337,23,{"$f":"IF(AC786<60,(60-AC786)/24,0)","v":1.5416666666666667},26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"15:00:00",30,1.25,30.02,1.2491666666666668,49,0.45833333333333331,23,{"$f":"IF(AC787<60,(60-AC787)/24,0)","v":1.5416666666666667},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"16:00:00",30,1.25,30.92,1.2116666666666667,49,0.45833333333333331,23,{"$f":"IF(AC788<60,(60-AC788)/24,0)","v":1.5416666666666667},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"17:00:00",30,1.25,33.08,1.1216666666666668,43,0.70833333333333337,20,{"$f":"IF(AC789<60,(60-AC789)/24,0)","v":1.6666666666666667},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"18:00:00",30,1.25,33.08,1.1216666666666668,35,1.0416666666666667,18,{"$f":"IF(AC790<60,(60-AC790)/24,0)","v":1.75},26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"19:00:00",30,1.25,30.02,1.2491666666666668,33,1.125,17,{"$f":"IF(AC791<60,(60-AC791)/24,0)","v":1.7916666666666667},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"20:00:00",32,1.1666666666666667,28.04,1.3316666666666668,28,1.3333333333333333,17,{"$f":"IF(AC792<60,(60-AC792)/24,0)","v":1.7916666666666667},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"21:00:00",32,1.1666666666666667,24.98,1.4591666666666665,22,1.5833333333333333,16,{"$f":"IF(AC793<60,(60-AC793)/24,0)","v":1.8333333333333333},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"22:00:00",34,1.0833333333333333,24.98,1.4591666666666665,18.210899999999999,1.7412125000000003,15,{"$f":"IF(AC794<60,(60-AC794)/24,0)","v":1.875},21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"23:00:00",34,1.0833333333333333,23,1.5416666666666667,16.050999999999998,1.8312083333333333,13,{"$f":"IF(AC795<60,(60-AC795)/24,0)","v":1.9583333333333333},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,1,34,1.0833333333333333,21.92,1.5866666666666667,15,1.875,11,{"$f":"IF(AC796<60,(60-AC796)/24,0)","v":2.0416666666666665},16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"01:00:00",36,1,23,1.5416666666666667,11,2.0416666666666665,11,{"$f":"IF(AC797<60,(60-AC797)/24,0)","v":2.0416666666666665},16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"02:00:00",34.191699999999997,1.0753458333333334,23,1.5416666666666667,7,2.2083333333333335,9,{"$f":"IF(AC798<60,(60-AC798)/24,0)","v":2.125},15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"03:00:00",34.191699999999997,1.0753458333333334,23,1.5416666666666667,7,2.2083333333333335,8,{"$f":"IF(AC799<60,(60-AC799)/24,0)","v":2.1666666666666665},14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"04:00:00",34.191699999999997,1.0753458333333334,23,1.5416666666666667,4.3533299999999997,2.31861125,7,{"$f":"IF(AC800<60,(60-AC800)/24,0)","v":2.2083333333333335},14.9,1.8791666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"05:00:00",34.191699999999997,1.0753458333333334,21.02,1.6241666666666668,2.3201000000000001,2.403329166666667,6,{"$f":"IF(AC801<60,(60-AC801)/24,0)","v":2.25},11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"06:00:00",34.191699999999997,1.0753458333333334,21.02,1.6241666666666668,1,2.4583333333333335,7,{"$f":"IF(AC802<60,(60-AC802)/24,0)","v":2.2083333333333335},9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"07:00:00",30,1.25,21.02,1.6241666666666668,7.0163699999999996E-2,2.4970765125000001,7,{"$f":"IF(AC803<60,(60-AC803)/24,0)","v":2.2083333333333335},9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"08:00:00",32,1.1666666666666667,21.02,1.6241666666666668,7.0163699999999996E-2,2.4970765125000001,7,{"$f":"IF(AC804<60,(60-AC804)/24,0)","v":2.2083333333333335},10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"09:00:00",34.191699999999997,1.0753458333333334,24.98,1.4591666666666665,7,2.2083333333333335,8,{"$f":"IF(AC805<60,(60-AC805)/24,0)","v":2.1666666666666665},10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"10:00:00",34.191699999999997,1.0753458333333334,26.06,1.4141666666666666,15,1.875,7,{"$f":"IF(AC806<60,(60-AC806)/24,0)","v":2.2083333333333335},10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"11:00:00",37,0.95833333333333337,28.04,1.3316666666666668,19,1.7083333333333333,10,{"$f":"IF(AC807<60,(60-AC807)/24,0)","v":2.0833333333333335},14.9,1.8791666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"12:00:00",41,0.79166666666666663,28.94,1.2941666666666667,23,1.5416666666666667,11,{"$f":"IF(AC808<60,(60-AC808)/24,0)","v":2.0416666666666665},16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"13:00:00",39,0.875,30.92,1.2116666666666667,32,1.1666666666666667,12,{"$f":"IF(AC809<60,(60-AC809)/24,0)","v":2},15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"14:00:00",41,0.79166666666666663,32,1.1666666666666667,33,1.125,12,{"$f":"IF(AC810<60,(60-AC810)/24,0)","v":2},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"15:00:00",41,0.79166666666666663,32,1.1666666666666667,34,1.0833333333333333,14,{"$f":"IF(AC811<60,(60-AC811)/24,0)","v":1.9166666666666667},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"16:00:00",41,0.79166666666666663,32,1.1666666666666667,34,1.0833333333333333,12,{"$f":"IF(AC812<60,(60-AC812)/24,0)","v":2},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"17:00:00",37,0.95833333333333337,30.02,1.2491666666666668,34,1.0833333333333333,9,{"$f":"IF(AC813<60,(60-AC813)/24,0)","v":2.125},16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"18:00:00",28,1.3333333333333333,28.04,1.3316666666666668,32,1.1666666666666667,7,{"$f":"IF(AC814<60,(60-AC814)/24,0)","v":2.2083333333333335},12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"19:00:00",27,1.375,24.08,1.4966666666666668,31,1.2083333333333333,5,{"$f":"IF(AC815<60,(60-AC815)/24,0)","v":2.2916666666666665},11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"20:00:00",25,1.4583333333333333,24.08,1.4966666666666668,30,1.25,4,{"$f":"IF(AC816<60,(60-AC816)/24,0)","v":2.3333333333333335},12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"21:00:00",21,1.625,23,1.5416666666666667,28,1.3333333333333333,3,{"$f":"IF(AC817<60,(60-AC817)/24,0)","v":2.375},11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"22:00:00",18,1.75,21.02,1.6241666666666668,25,1.4583333333333333,1,{"$f":"IF(AC818<60,(60-AC818)/24,0)","v":2.4583333333333335},8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"23:00:00",19,1.7083333333333333,19.04,1.7066666666666668,23,1.5416666666666667,-1,{"$f":"IF(AC819<60,(60-AC819)/24,0)","v":2.5416666666666665},8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,1,16,1.8333333333333333,17.059999999999999,1.7891666666666666,21,1.625,-2,{"$f":"IF(AC820<60,(60-AC820)/24,0)","v":2.5833333333333335},7.88,2.1716666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"01:00:00",18,1.75,8.06,2.1641666666666666,20,1.6666666666666667,-2,{"$f":"IF(AC821<60,(60-AC821)/24,0)","v":2.5833333333333335},5,2.2916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"02:00:00",16,1.8333333333333333,5,2.2916666666666665,20,1.6666666666666667,-3,{"$f":"IF(AC822<60,(60-AC822)/24,0)","v":2.625},3.92,2.3366666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"03:00:00",14,1.9166666666666667,3.02,2.3741666666666665,19,1.7083333333333333,-4,{"$f":"IF(AC823<60,(60-AC823)/24,0)","v":2.6666666666666665},1.94,2.4191666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"04:00:00",10,2.0833333333333335,-3.9999999999999147E-2,2.5016666666666665,18,1.75,-5,{"$f":"IF(AC824<60,(60-AC824)/24,0)","v":2.7083333333333335},0.85999999999999943,2.4641666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"05:00:00",12,2,-2.02,2.5841666666666669,20,1.6666666666666667,-5,{"$f":"IF(AC825<60,(60-AC825)/24,0)","v":2.7083333333333335},-3.9999999999999147E-2,2.5016666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"06:00:00",12,2,-0.94000000000000483,2.539166666666667,21,1.625,-4,{"$f":"IF(AC826<60,(60-AC826)/24,0)","v":2.6666666666666665},-1.1200000000000001,2.5466666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"07:00:00",12,2,-2.02,2.5841666666666669,27,1.375,-4,{"$f":"IF(AC827<60,(60-AC827)/24,0)","v":2.6666666666666665},-1.1200000000000001,2.5466666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"08:00:00",16,1.8333333333333333,-3.9999999999999147E-2,2.5016666666666665,30,1.25,-3,{"$f":"IF(AC828<60,(60-AC828)/24,0)","v":2.625},-3.9999999999999147E-2,2.5016666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"09:00:00",18,1.75,5,2.2916666666666665,31,1.2083333333333333,0,{"$f":"IF(AC829<60,(60-AC829)/24,0)","v":2.5},0.85999999999999943,2.4641666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"10:00:00",25,1.4583333333333333,10.039999999999999,2.0816666666666666,31,1.2083333333333333,4,{"$f":"IF(AC830<60,(60-AC830)/24,0)","v":2.3333333333333335},3.92,2.3366666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"11:00:00",30,1.25,15.98,1.8341666666666665,32,1.1666666666666667,4,{"$f":"IF(AC831<60,(60-AC831)/24,0)","v":2.3333333333333335},5.9,2.2541666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"12:00:00",39,0.875,21.02,1.6241666666666668,33,1.125,8,{"$f":"IF(AC832<60,(60-AC832)/24,0)","v":2.1666666666666665},6.98,2.2091666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"13:00:00",39,0.875,23,1.5416666666666667,36,1,9,{"$f":"IF(AC833<60,(60-AC833)/24,0)","v":2.125},8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"14:00:00",39,0.875,24.98,1.4591666666666665,35,1.0416666666666667,11,{"$f":"IF(AC834<60,(60-AC834)/24,0)","v":2.0416666666666665},10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"15:00:00",39,0.875,26.06,1.4141666666666666,35,1.0416666666666667,12,{"$f":"IF(AC835<60,(60-AC835)/24,0)","v":2},10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"16:00:00",39,0.875,26.06,1.4141666666666666,35,1.0416666666666667,13,{"$f":"IF(AC836<60,(60-AC836)/24,0)","v":1.9583333333333333},10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"17:00:00",39,{"$f":"IF(W837<60,(60-W837)/24,0)","v":0.875},26.06,1.4141666666666666,33,1.125,11,{"$f":"IF(AC837<60,(60-AC837)/24,0)","v":2.0416666666666665},10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"18:00:00",37,0.95833333333333337,24.98,{"$f":"IF(Y838<60,(60-Y838)/24,0)","v":1.4591666666666665},31,{"$f":"IF(AA838<60,(60-AA838)/24,0)","v":1.2083333333333333},8,{"$f":"IF(AC838<60,(60-AC838)/24,0)","v":2.1666666666666665},8.9600000000000009,{"$f":"IF(AE838<60,(60-AE838)/24,0)","v":2.1266666666666665}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"19:00:00",36,1,24.98,1.4591666666666665,30,1.25,7,{"$f":"IF(AC839<60,(60-AC839)/24,0)","v":2.2083333333333335},5,2.2916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"20:00:00",34,1.0833333333333333,24.08,1.4966666666666668,29,1.2916666666666667,4,{"$f":"IF(AC840<60,(60-AC840)/24,0)","v":2.3333333333333335},5,2.2916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"21:00:00",33,1.125,24.08,1.4966666666666668,29,1.2916666666666667,1,{"$f":"IF(AC841<60,(60-AC841)/24,0)","v":2.4583333333333335},3.92,2.3366666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"22:00:00",32.447400000000002,1.1480249999999999,23,1.5416666666666667,30,1.25,1,{"$f":"IF(AC842<60,(60-AC842)/24,0)","v":2.4583333333333335},-3.9999999999999147E-2,2.5016666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"23:00:00",32,1.1666666666666667,24.08,1.4966666666666668,31,1.2083333333333333,-2,{"$f":"IF(AC843<60,(60-AC843)/24,0)","v":2.5833333333333335},1.94,2.4191666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,1,32.447400000000002,1.1480249999999999,24.08,1.4966666666666668,34,1.0833333333333333,-3,{"$f":"IF(AC844<60,(60-AC844)/24,0)","v":2.625},-3.9999999999999147E-2,2.5016666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"01:00:00",32,1.1666666666666667,24.08,1.4966666666666668,34,1.0833333333333333,-4,{"$f":"IF(AC845<60,(60-AC845)/24,0)","v":2.6666666666666665},-4,2.6666666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"02:00:00",32,1.1666666666666667,24.08,1.4966666666666668,35,1.0416666666666667,-5,{"$f":"IF(AC846<60,(60-AC846)/24,0)","v":2.7083333333333335},-4,2.6666666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"03:00:00",32,1.1666666666666667,24.08,1.4966666666666668,34,1.0833333333333333,-7,{"$f":"IF(AC847<60,(60-AC847)/24,0)","v":2.7916666666666665},-5.0800000000000054,2.7116666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"04:00:00",36,1,24.98,1.4591666666666665,35,1.0416666666666667,-8,{"$f":"IF(AC848<60,(60-AC848)/24,0)","v":2.8333333333333335},-9.0399999999999991,2.8766666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"05:00:00",36,1,23,1.5416666666666667,34,1.0833333333333333,-9,{"$f":"IF(AC849<60,(60-AC849)/24,0)","v":2.875},-8.14,2.8391666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"06:00:00",34,1.0833333333333333,24.08,1.4966666666666668,33,1.125,-8,{"$f":"IF(AC850<60,(60-AC850)/24,0)","v":2.8333333333333335},-8.14,2.8391666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"07:00:00",34,1.0833333333333333,24.08,1.4966666666666668,34,1.0833333333333333,-7,{"$f":"IF(AC851<60,(60-AC851)/24,0)","v":2.7916666666666665},-10.119999999999999,2.9216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"08:00:00",30,1.25,24.98,1.4591666666666665,35,1.0416666666666667,-6,{"$f":"IF(AC852<60,(60-AC852)/24,0)","v":2.75},-6.16,2.7566666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"09:00:00",30,1.25,26.06,1.4141666666666666,37,0.95833333333333337,0,{"$f":"IF(AC853<60,(60-AC853)/24,0)","v":2.5},-2.02,2.5841666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"10:00:00",27,1.375,26.96,1.3766666666666667,37,0.95833333333333337,6,{"$f":"IF(AC854<60,(60-AC854)/24,0)","v":2.25},5,2.2916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"11:00:00",25,1.4583333333333333,30.02,1.2491666666666668,41,0.79166666666666663,9,{"$f":"IF(AC855<60,(60-AC855)/24,0)","v":2.125},10.039999999999999,2.0816666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"12:00:00",25,1.4583333333333333,30.92,1.2116666666666667,40,0.83333333333333337,15,{"$f":"IF(AC856<60,(60-AC856)/24,0)","v":1.875},14.9,1.8791666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"13:00:00",24,1.5,33.979999999999997,1.0841666666666667,42,0.75,14,{"$f":"IF(AC857<60,(60-AC857)/24,0)","v":1.9166666666666667},14.9,1.8791666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"14:00:00",23,1.5416666666666667,35.06,1.0391666666666666,42,0.75,17,{"$f":"IF(AC858<60,(60-AC858)/24,0)","v":1.7916666666666667},15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"15:00:00",23,1.5416666666666667,37.04,0.95666666666666667,42,0.75,18,{"$f":"IF(AC859<60,(60-AC859)/24,0)","v":1.75},16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"16:00:00",21,1.625,37.04,0.95666666666666667,42,0.75,16,{"$f":"IF(AC860<60,(60-AC860)/24,0)","v":1.8333333333333333},14.9,1.8791666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"17:00:00",19,1.7083333333333333,35.06,1.0391666666666666,40,0.83333333333333337,15,{"$f":"IF(AC861<60,(60-AC861)/24,0)","v":1.875},15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"18:00:00",18,1.75,33.08,1.1216666666666668,40,0.83333333333333337,15,{"$f":"IF(AC862<60,(60-AC862)/24,0)","v":1.875},14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"19:00:00",16,1.8333333333333333,32,1.1666666666666667,40,0.83333333333333337,15,{"$f":"IF(AC863<60,(60-AC863)/24,0)","v":1.875},10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"20:00:00",16,1.8333333333333333,33.08,1.1216666666666668,38,0.91666666666666663,14,{"$f":"IF(AC864<60,(60-AC864)/24,0)","v":1.9166666666666667},11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"21:00:00",14,1.9166666666666667,32,1.1666666666666667,38,0.91666666666666663,14,{"$f":"IF(AC865<60,(60-AC865)/24,0)","v":1.9166666666666667},12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"22:00:00",12,2,35.96,1.0016666666666667,36,1,14,{"$f":"IF(AC866<60,(60-AC866)/24,0)","v":1.9166666666666667},14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"23:00:00",10,2.0833333333333335,35.06,1.0391666666666666,36,1,12,{"$f":"IF(AC867<60,(60-AC867)/24,0)","v":2},12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,1,7,2.2083333333333335,33.08,1.1216666666666668,36,1,11,{"$f":"IF(AC868<60,(60-AC868)/24,0)","v":2.0416666666666665},14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"01:00:00",7,2.2083333333333335,32,1.1666666666666667,36,1,10,{"$f":"IF(AC869<60,(60-AC869)/24,0)","v":2.0833333333333335},12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"02:00:00",3,2.375,30.92,1.2116666666666667,36,1,8,{"$f":"IF(AC870<60,(60-AC870)/24,0)","v":2.1666666666666665},11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"03:00:00",1,2.4583333333333335,28.94,1.2941666666666667,36,1,7,{"$f":"IF(AC871<60,(60-AC871)/24,0)","v":2.2083333333333335},10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"04:00:00",1,2.4583333333333335,28.04,1.3316666666666668,36,1,6,{"$f":"IF(AC872<60,(60-AC872)/24,0)","v":2.25},9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"05:00:00",0,2.5,28.04,1.3316666666666668,36,1,5,{"$f":"IF(AC873<60,(60-AC873)/24,0)","v":2.2916666666666665},8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"06:00:00",0,2.5,24.08,1.4966666666666668,36,1,6,{"$f":"IF(AC874<60,(60-AC874)/24,0)","v":2.25},6.98,2.2091666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"07:00:00",1,2.4583333333333335,19.04,1.7066666666666668,37,0.95833333333333337,5,{"$f":"IF(AC875<60,(60-AC875)/24,0)","v":2.2916666666666665},6.98,2.2091666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"08:00:00",3,2.375,15.98,1.8341666666666665,35,1.0416666666666667,7,{"$f":"IF(AC876<60,(60-AC876)/24,0)","v":2.2083333333333335},8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"09:00:00",7,2.2083333333333335,14,1.9166666666666667,35,1.0416666666666667,12,{"$f":"IF(AC877<60,(60-AC877)/24,0)","v":2},9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"10:00:00",12,2,15.08,1.8716666666666668,35,1.0416666666666667,15,{"$f":"IF(AC878<60,(60-AC878)/24,0)","v":1.875},14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"11:00:00",16,1.8333333333333333,17.059999999999999,1.7891666666666666,38,0.91666666666666663,17,{"$f":"IF(AC879<60,(60-AC879)/24,0)","v":1.7916666666666667},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"12:00:00",18,1.75,17.96,1.7516666666666667,39,0.875,18,{"$f":"IF(AC880<60,(60-AC880)/24,0)","v":1.75},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"13:00:00",19,1.7083333333333333,19.940000000000001,1.6691666666666667,39,0.875,20,{"$f":"IF(AC881<60,(60-AC881)/24,0)","v":1.6666666666666667},21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"14:00:00",21,1.625,19.940000000000001,1.6691666666666667,40,0.83333333333333337,20,{"$f":"IF(AC882<60,(60-AC882)/24,0)","v":1.6666666666666667},21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"15:00:00",21,1.625,19.940000000000001,1.6691666666666667,40,0.83333333333333337,21,{"$f":"IF(AC883<60,(60-AC883)/24,0)","v":1.625},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"16:00:00",21,1.625,19.04,1.7066666666666668,40,0.83333333333333337,21,{"$f":"IF(AC884<60,(60-AC884)/24,0)","v":1.625},21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"17:00:00",21,1.625,17.96,1.7516666666666667,39,0.875,20,{"$f":"IF(AC885<60,(60-AC885)/24,0)","v":1.6666666666666667},18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"18:00:00",21,1.625,15.98,1.8341666666666665,38,0.91666666666666663,15,{"$f":"IF(AC886<60,(60-AC886)/24,0)","v":1.875},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"19:00:00",21,1.625,14,1.9166666666666667,38,0.91666666666666663,11,{"$f":"IF(AC887<60,(60-AC887)/24,0)","v":2.0416666666666665},14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"20:00:00",25,1.4583333333333333,12.02,1.9991666666666668,38,0.91666666666666663,11,{"$f":"IF(AC888<60,(60-AC888)/24,0)","v":2.0416666666666665},8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"21:00:00",25,1.4583333333333333,8.9600000000000009,2.1266666666666665,37,0.95833333333333337,8,{"$f":"IF(AC889<60,(60-AC889)/24,0)","v":2.1666666666666665},6.98,2.2091666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"22:00:00",23,1.5416666666666667,6.98,2.2091666666666665,35,1.0416666666666667,8,{"$f":"IF(AC890<60,(60-AC890)/24,0)","v":2.1666666666666665},10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"23:00:00",23,1.5416666666666667,8.06,2.1641666666666666,36,1,7,{"$f":"IF(AC891<60,(60-AC891)/24,0)","v":2.2083333333333335},5.9,2.2541666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,1,21,1.625,5,2.2916666666666665,36,1,6,{"$f":"IF(AC892<60,(60-AC892)/24,0)","v":2.25},7.88,2.1716666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"01:00:00",21,1.625,1.04,2.4566666666666666,35,1.0416666666666667,7,{"$f":"IF(AC893<60,(60-AC893)/24,0)","v":2.2083333333333335},7.88,2.1716666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"02:00:00",19,1.7083333333333333,-2.02,2.5841666666666669,35,1.0416666666666667,6,{"$f":"IF(AC894<60,(60-AC894)/24,0)","v":2.25},6.98,2.2091666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"03:00:00",19,1.7083333333333333,1.04,2.4566666666666666,34,1.0833333333333333,6,{"$f":"IF(AC895<60,(60-AC895)/24,0)","v":2.25},3.92,2.3366666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"04:00:00",19,1.7083333333333333,1.04,2.4566666666666666,34,1.0833333333333333,6,{"$f":"IF(AC896<60,(60-AC896)/24,0)","v":2.25},3.92,2.3366666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"05:00:00",19,1.7083333333333333,-3.9999999999999147E-2,2.5016666666666665,35,1.0416666666666667,6,{"$f":"IF(AC897<60,(60-AC897)/24,0)","v":2.25},6.98,2.2091666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"06:00:00",18,1.75,-0.94000000000000483,2.539166666666667,35,1.0416666666666667,8,{"$f":"IF(AC898<60,(60-AC898)/24,0)","v":2.1666666666666665},5.9,2.2541666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"07:00:00",18,1.75,-0.94000000000000483,2.539166666666667,34,1.0833333333333333,7,{"$f":"IF(AC899<60,(60-AC899)/24,0)","v":2.2083333333333335},5.9,2.2541666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"08:00:00",18,1.75,1.94,2.4191666666666669,33,1.125,10,{"$f":"IF(AC900<60,(60-AC900)/24,0)","v":2.0833333333333335},5.9,2.2541666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"09:00:00",19,{"$f":"IF(W901<60,(60-W901)/24,0)","v":1.7083333333333333},8.06,2.1641666666666666,33,1.125,15,{"$f":"IF(AC901<60,(60-AC901)/24,0)","v":1.875},10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"10:00:00",19,1.7083333333333333,10.039999999999999,{"$f":"IF(Y902<60,(60-Y902)/24,0)","v":2.0816666666666666},33,{"$f":"IF(AA902<60,(60-AA902)/24,0)","v":1.125},21,{"$f":"IF(AC902<60,(60-AC902)/24,0)","v":1.625},17.96,{"$f":"IF(AE902<60,(60-AE902)/24,0)","v":1.7516666666666667}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"11:00:00",21,1.625,14,1.9166666666666667,34,1.0833333333333333,24,{"$f":"IF(AC903<60,(60-AC903)/24,0)","v":1.5},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"12:00:00",23,1.5416666666666667,15.98,1.8341666666666665,32,1.1666666666666667,27,{"$f":"IF(AC904<60,(60-AC904)/24,0)","v":1.375},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"13:00:00",23,1.5416666666666667,21.92,1.5866666666666667,32,1.1666666666666667,29,{"$f":"IF(AC905<60,(60-AC905)/24,0)","v":1.2916666666666667},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"14:00:00",25,1.4583333333333333,23,1.5416666666666667,29,1.2916666666666667,29,{"$f":"IF(AC906<60,(60-AC906)/24,0)","v":1.2916666666666667},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"15:00:00",25,1.4583333333333333,23,1.5416666666666667,26,1.4166666666666667,29,{"$f":"IF(AC907<60,(60-AC907)/24,0)","v":1.2916666666666667},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"16:00:00",25,1.4583333333333333,23,1.5416666666666667,24,1.5,31,{"$f":"IF(AC908<60,(60-AC908)/24,0)","v":1.2083333333333333},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"17:00:00",21,1.625,23,1.5416666666666667,21,1.625,31,{"$f":"IF(AC909<60,(60-AC909)/24,0)","v":1.2083333333333333},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"18:00:00",19,1.7083333333333333,21.92,1.5866666666666667,20,1.6666666666666667,30,{"$f":"IF(AC910<60,(60-AC910)/24,0)","v":1.25},28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"19:00:00",18,1.75,21.92,1.5866666666666667,19,1.7083333333333333,30,{"$f":"IF(AC911<60,(60-AC911)/24,0)","v":1.25},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"20:00:00",14,1.9166666666666667,21.92,1.5866666666666667,16,1.8333333333333333,29,{"$f":"IF(AC912<60,(60-AC912)/24,0)","v":1.2916666666666667},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"21:00:00",9,2.125,21.02,1.6241666666666668,14,1.9166666666666667,30,{"$f":"IF(AC913<60,(60-AC913)/24,0)","v":1.25},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"22:00:00",7,2.2083333333333335,19.940000000000001,1.6691666666666667,12,2,29,{"$f":"IF(AC914<60,(60-AC914)/24,0)","v":1.2916666666666667},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"23:00:00",5,2.2916666666666665,19.940000000000001,1.6691666666666667,11,2.0416666666666665,28,{"$f":"IF(AC915<60,(60-AC915)/24,0)","v":1.3333333333333333},29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,1,1,2.4583333333333335,21.02,1.6241666666666668,10,2.0833333333333335,28,{"$f":"IF(AC916<60,(60-AC916)/24,0)","v":1.3333333333333333},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"01:00:00",0,2.5,19.940000000000001,1.6691666666666667,3,2.375,28,{"$f":"IF(AC917<60,(60-AC917)/24,0)","v":1.3333333333333333},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"02:00:00",-2,2.5833333333333335,19.940000000000001,1.6691666666666667,0,2.5,27,{"$f":"IF(AC918<60,(60-AC918)/24,0)","v":1.375},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"03:00:00",-6,2.75,17.96,1.7516666666666667,-1,2.5416666666666665,27,{"$f":"IF(AC919<60,(60-AC919)/24,0)","v":1.375},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"04:00:00",-8,2.8333333333333335,17.059999999999999,1.7891666666666666,-3,2.625,27,{"$f":"IF(AC920<60,(60-AC920)/24,0)","v":1.375},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"05:00:00",-8,2.8333333333333335,17.059999999999999,1.7891666666666666,-2,2.5833333333333335,27,{"$f":"IF(AC921<60,(60-AC921)/24,0)","v":1.375},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"06:00:00",-9,2.875,15.98,1.8341666666666665,0,2.5,29,{"$f":"IF(AC922<60,(60-AC922)/24,0)","v":1.2916666666666667},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"07:00:00",-9,2.875,15.98,1.8341666666666665,3,2.375,29,{"$f":"IF(AC923<60,(60-AC923)/24,0)","v":1.2916666666666667},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"08:00:00",-9,2.875,15.98,1.8341666666666665,3,2.375,29,{"$f":"IF(AC924<60,(60-AC924)/24,0)","v":1.2916666666666667},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"09:00:00",-2,2.5833333333333335,19.940000000000001,1.6691666666666667,2,2.4166666666666665,30,{"$f":"IF(AC925<60,(60-AC925)/24,0)","v":1.25},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"10:00:00",9,2.125,21.92,1.5866666666666667,2,2.4166666666666665,31,{"$f":"IF(AC926<60,(60-AC926)/24,0)","v":1.2083333333333333},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"11:00:00",16,1.8333333333333333,26.06,1.4141666666666666,3,2.375,33,{"$f":"IF(AC927<60,(60-AC927)/24,0)","v":1.125},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"12:00:00",21,1.625,28.04,1.3316666666666668,4,2.3333333333333335,37,{"$f":"IF(AC928<60,(60-AC928)/24,0)","v":0.95833333333333337},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"13:00:00",27,1.375,28.94,1.2941666666666667,5,2.2916666666666665,37,{"$f":"IF(AC929<60,(60-AC929)/24,0)","v":0.95833333333333337},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"14:00:00",27,1.375,30.02,1.2491666666666668,8,2.1666666666666665,37,{"$f":"IF(AC930<60,(60-AC930)/24,0)","v":0.95833333333333337},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"15:00:00",27,1.375,30.92,1.2116666666666667,8,2.1666666666666665,37,{"$f":"IF(AC931<60,(60-AC931)/24,0)","v":0.95833333333333337},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"16:00:00",28,1.3333333333333333,30.02,1.2491666666666668,8,2.1666666666666665,37,{"$f":"IF(AC932<60,(60-AC932)/24,0)","v":0.95833333333333337},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"17:00:00",25,1.4583333333333333,28.04,1.3316666666666668,7,2.2083333333333335,37,{"$f":"IF(AC933<60,(60-AC933)/24,0)","v":0.95833333333333337},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"18:00:00",19,1.7083333333333333,24.98,1.4591666666666665,7,2.2083333333333335,36,{"$f":"IF(AC934<60,(60-AC934)/24,0)","v":1},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"19:00:00",14,1.9166666666666667,24.08,1.4966666666666668,7,2.2083333333333335,36,{"$f":"IF(AC935<60,(60-AC935)/24,0)","v":1},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"20:00:00",12,2,17.96,1.7516666666666667,7,2.2083333333333335,36,{"$f":"IF(AC936<60,(60-AC936)/24,0)","v":1},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"21:00:00",12,2,17.059999999999999,1.7891666666666666,7,2.2083333333333335,35,{"$f":"IF(AC937<60,(60-AC937)/24,0)","v":1.0416666666666667},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"22:00:00",7,2.2083333333333335,19.04,1.7066666666666668,6,2.25,34,{"$f":"IF(AC938<60,(60-AC938)/24,0)","v":1.0833333333333333},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"23:00:00",3,2.375,17.059999999999999,1.7891666666666666,6,2.25,33,{"$f":"IF(AC939<60,(60-AC939)/24,0)","v":1.125},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,1,0,2.5,12.02,1.9991666666666668,6,2.25,32,{"$f":"IF(AC940<60,(60-AC940)/24,0)","v":1.1666666666666667},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"01:00:00",0,2.5,8.9600000000000009,2.1266666666666665,6,2.25,32.049900000000001,{"$f":"IF(AC941<60,(60-AC941)/24,0)","v":1.1645874999999999},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"02:00:00",-2,2.5833333333333335,6.08,2.2466666666666666,6,2.25,32,{"$f":"IF(AC942<60,(60-AC942)/24,0)","v":1.1666666666666667},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"03:00:00",0,2.5,3.92,2.3366666666666664,6,2.25,32,{"$f":"IF(AC943<60,(60-AC943)/24,0)","v":1.1666666666666667},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"04:00:00",0,2.5,1.94,2.4191666666666669,5,2.2916666666666665,32.131399999999999,{"$f":"IF(AC944<60,(60-AC944)/24,0)","v":1.1611916666666666},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"05:00:00",-2,2.5833333333333335,1.94,2.4191666666666669,5,2.2916666666666665,33,{"$f":"IF(AC945<60,(60-AC945)/24,0)","v":1.125},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"06:00:00",0,2.5,3.02,2.3741666666666665,6,2.25,35.201900000000002,{"$f":"IF(AC946<60,(60-AC946)/24,0)","v":1.0332541666666666},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"07:00:00",1,2.4583333333333335,-3.9999999999999147E-2,2.5016666666666665,6,2.25,35,{"$f":"IF(AC947<60,(60-AC947)/24,0)","v":1.0416666666666667},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"08:00:00",1,2.4583333333333335,-3.9999999999999147E-2,2.5016666666666665,5,2.2916666666666665,35,{"$f":"IF(AC948<60,(60-AC948)/24,0)","v":1.0416666666666667},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"09:00:00",7,2.2083333333333335,12.02,1.9991666666666668,6,2.25,36,{"$f":"IF(AC949<60,(60-AC949)/24,0)","v":1},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"10:00:00",10,2.0833333333333335,17.96,1.7516666666666667,7,2.2083333333333335,39,{"$f":"IF(AC950<60,(60-AC950)/24,0)","v":0.875},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"11:00:00",19,1.7083333333333333,24.98,1.4591666666666665,8,2.1666666666666665,40,{"$f":"IF(AC951<60,(60-AC951)/24,0)","v":0.83333333333333337},43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"12:00:00",21,1.625,30.02,1.2491666666666668,8,2.1666666666666665,40,{"$f":"IF(AC952<60,(60-AC952)/24,0)","v":0.83333333333333337},44.96,0.62666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"13:00:00",25,1.4583333333333333,33.979999999999997,1.0841666666666667,9,2.125,39,{"$f":"IF(AC953<60,(60-AC953)/24,0)","v":0.875},42.98,0.70916666666666683]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"14:00:00",28,1.3333333333333333,35.06,1.0391666666666666,9,2.125,39,{"$f":"IF(AC954<60,(60-AC954)/24,0)","v":0.875},42.98,0.70916666666666683]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"15:00:00",28,1.3333333333333333,35.06,1.0391666666666666,9,2.125,29,{"$f":"IF(AC955<60,(60-AC955)/24,0)","v":1.2916666666666667},41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"16:00:00",31,1.2083333333333333,33.08,1.1216666666666668,9,2.125,39,{"$f":"IF(AC956<60,(60-AC956)/24,0)","v":0.875},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"17:00:00",32,1.1666666666666667,30.92,1.2116666666666667,9,2.125,38,{"$f":"IF(AC957<60,(60-AC957)/24,0)","v":0.91666666666666663},39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"18:00:00",25,1.4583333333333333,28.94,1.2941666666666667,9,2.125,38,{"$f":"IF(AC958<60,(60-AC958)/24,0)","v":0.91666666666666663},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"19:00:00",25,1.4583333333333333,26.96,1.3766666666666667,9,2.125,37,{"$f":"IF(AC959<60,(60-AC959)/24,0)","v":0.95833333333333337},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"20:00:00",25,1.4583333333333333,21.02,1.6241666666666668,9,2.125,37,{"$f":"IF(AC960<60,(60-AC960)/24,0)","v":0.95833333333333337},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"21:00:00",27,1.375,24.98,1.4591666666666665,9,2.125,36,{"$f":"IF(AC961<60,(60-AC961)/24,0)","v":1},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"22:00:00",36,1,19.940000000000001,1.6691666666666667,9,2.125,35,{"$f":"IF(AC962<60,(60-AC962)/24,0)","v":1.0416666666666667},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"23:00:00",37,0.95833333333333337,14,1.9166666666666667,7,2.2083333333333335,34,{"$f":"IF(AC963<60,(60-AC963)/24,0)","v":1.0833333333333333},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,1,37,0.95833333333333337,17.059999999999999,1.7891666666666666,6,2.25,33,{"$f":"IF(AC964<60,(60-AC964)/24,0)","v":1.125},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"01:00:00",36,{"$f":"IF(W965<60,(60-W965)/24,0)","v":1},12.92,1.9616666666666667,4,2.3333333333333335,32,{"$f":"IF(AC965<60,(60-AC965)/24,0)","v":1.1666666666666667},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"02:00:00",36,1,10.94,{"$f":"IF(Y966<60,(60-Y966)/24,0)","v":2.0441666666666669},2,{"$f":"IF(AA966<60,(60-AA966)/24,0)","v":2.4166666666666665},30,{"$f":"IF(AC966<60,(60-AC966)/24,0)","v":1.25},35.96,{"$f":"IF(AE966<60,(60-AE966)/24,0)","v":1.0016666666666667}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"03:00:00",34,1.0833333333333333,8.06,2.1641666666666666,-2,2.5833333333333335,29,{"$f":"IF(AC967<60,(60-AC967)/24,0)","v":1.2916666666666667},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"04:00:00",34,1.0833333333333333,8.9600000000000009,2.1266666666666665,-3,2.625,28,{"$f":"IF(AC968<60,(60-AC968)/24,0)","v":1.3333333333333333},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"05:00:00",36,1,12.92,1.9616666666666667,-6,2.75,27,{"$f":"IF(AC969<60,(60-AC969)/24,0)","v":1.375},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"06:00:00",34,1.0833333333333333,10.039999999999999,2.0816666666666666,-5,2.7083333333333335,28,{"$f":"IF(AC970<60,(60-AC970)/24,0)","v":1.3333333333333333},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"07:00:00",34,1.0833333333333333,8.9600000000000009,2.1266666666666665,-5,2.7083333333333335,27,{"$f":"IF(AC971<60,(60-AC971)/24,0)","v":1.375},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"08:00:00",32,1.1666666666666667,6.08,2.2466666666666666,-7,2.7916666666666665,28,{"$f":"IF(AC972<60,(60-AC972)/24,0)","v":1.3333333333333333},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"09:00:00",30,1.25,17.96,1.7516666666666667,-3,2.625,30,{"$f":"IF(AC973<60,(60-AC973)/24,0)","v":1.25},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"10:00:00",30,1.25,23,1.5416666666666667,-1,2.5416666666666665,31,{"$f":"IF(AC974<60,(60-AC974)/24,0)","v":1.2083333333333333},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"11:00:00",28,1.3333333333333333,28.04,1.3316666666666668,3,2.375,33,{"$f":"IF(AC975<60,(60-AC975)/24,0)","v":1.125},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"12:00:00",27,1.375,32,1.1666666666666667,6,2.25,35,{"$f":"IF(AC976<60,(60-AC976)/24,0)","v":1.0416666666666667},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"13:00:00",27,1.375,33.08,1.1216666666666668,9,2.125,38,{"$f":"IF(AC977<60,(60-AC977)/24,0)","v":0.91666666666666663},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"14:00:00",28,1.3333333333333333,35.06,1.0391666666666666,11,2.0416666666666665,38,{"$f":"IF(AC978<60,(60-AC978)/24,0)","v":0.91666666666666663},39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"15:00:00",28,1.3333333333333333,35.06,1.0391666666666666,12,2,38,{"$f":"IF(AC979<60,(60-AC979)/24,0)","v":0.91666666666666663},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"16:00:00",28,1.3333333333333333,35.06,1.0391666666666666,13,1.9583333333333333,39,{"$f":"IF(AC980<60,(60-AC980)/24,0)","v":0.875},39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"17:00:00",27,1.375,32,1.1666666666666667,10,2.0833333333333335,37,{"$f":"IF(AC981<60,(60-AC981)/24,0)","v":0.95833333333333337},37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"18:00:00",27,1.375,30.92,1.2116666666666667,4,2.3333333333333335,33,{"$f":"IF(AC982<60,(60-AC982)/24,0)","v":1.125},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"19:00:00",27,1.375,30.02,1.2491666666666668,-2,2.5833333333333335,31,{"$f":"IF(AC983<60,(60-AC983)/24,0)","v":1.2083333333333333},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"20:00:00",27,1.375,28.94,1.2941666666666667,-5,2.7083333333333335,26,{"$f":"IF(AC984<60,(60-AC984)/24,0)","v":1.4166666666666667},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"21:00:00",25,1.4583333333333333,24.08,1.4966666666666668,-5,2.7083333333333335,26,{"$f":"IF(AC985<60,(60-AC985)/24,0)","v":1.4166666666666667},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"22:00:00",25,1.4583333333333333,19.940000000000001,1.6691666666666667,-6,2.75,25,{"$f":"IF(AC986<60,(60-AC986)/24,0)","v":1.4583333333333333},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"23:00:00",21,1.625,21.92,1.5866666666666667,-8,2.8333333333333335,24,{"$f":"IF(AC987<60,(60-AC987)/24,0)","v":1.5},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,1,19,1.7083333333333333,21.02,1.6241666666666668,-8,2.8333333333333335,24,{"$f":"IF(AC988<60,(60-AC988)/24,0)","v":1.5},28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"01:00:00",19,1.7083333333333333,19.940000000000001,1.6691666666666667,-8,2.8333333333333335,24,{"$f":"IF(AC989<60,(60-AC989)/24,0)","v":1.5},28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"02:00:00",18,1.75,17.96,1.7516666666666667,-8,2.8333333333333335,24,{"$f":"IF(AC990<60,(60-AC990)/24,0)","v":1.5},28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"03:00:00",16,1.8333333333333333,19.940000000000001,1.6691666666666667,-6,2.75,24,{"$f":"IF(AC991<60,(60-AC991)/24,0)","v":1.5},30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"04:00:00",14,1.9166666666666667,17.059999999999999,1.7891666666666666,-5,2.7083333333333335,24,{"$f":"IF(AC992<60,(60-AC992)/24,0)","v":1.5},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"05:00:00",14,1.9166666666666667,15.08,1.8716666666666668,-3,2.625,25,{"$f":"IF(AC993<60,(60-AC993)/24,0)","v":1.4583333333333333},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"06:00:00",14,1.9166666666666667,10.94,2.0441666666666669,-1,2.5416666666666665,27,{"$f":"IF(AC994<60,(60-AC994)/24,0)","v":1.375},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"07:00:00",12,2,8.9600000000000009,2.1266666666666665,1,2.4583333333333335,28,{"$f":"IF(AC995<60,(60-AC995)/24,0)","v":1.3333333333333333},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"08:00:00",14,1.9166666666666667,12.92,1.9616666666666667,3,2.375,29,{"$f":"IF(AC996<60,(60-AC996)/24,0)","v":1.2916666666666667},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"09:00:00",18,1.75,15.98,1.8341666666666665,8,2.1666666666666665,30,{"$f":"IF(AC997<60,(60-AC997)/24,0)","v":1.25},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"10:00:00",23,1.5416666666666667,19.04,1.7066666666666668,15,1.875,31,{"$f":"IF(AC998<60,(60-AC998)/24,0)","v":1.2083333333333333},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"11:00:00",27,1.375,21.02,1.6241666666666668,17,1.7916666666666667,32,{"$f":"IF(AC999<60,(60-AC999)/24,0)","v":1.1666666666666667},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"12:00:00",28,1.3333333333333333,23,1.5416666666666667,25,1.4583333333333333,32,{"$f":"IF(AC1000<60,(60-AC1000)/24,0)","v":1.1666666666666667},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"17:00:00",30,1.25,28.04,1.3316666666666668,33,1.125,34,{"$f":"IF(AC1005<60,(60-AC1005)/24,0)","v":1.0833333333333333},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"22:00:00",25,1.4583333333333333,21.92,1.5866666666666667,32,1.1666666666666667,34,{"$f":"IF(AC1010<60,(60-AC1010)/24,0)","v":1.0833333333333333},34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,12,"07:00:00",27,1.375,12.02,1.9991666666666668,28,1.3333333333333333,16,{"$f":"IF(AC1019<60,(60-AC1019)/24,0)","v":1.8333333333333333},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,12,"15:00:00",48,0.5,26.06,1.4141666666666666,37,0.95833333333333337,14,{"$f":"IF(AC1027<60,(60-AC1027)/24,0)","v":1.9166666666666667},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,12,"21:00:00",39,0.875,17.059999999999999,1.7891666666666666,28,1.3333333333333333,3,{"$f":"IF(AC1033<60,(60-AC1033)/24,0)","v":2.375},7.88,2.1716666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,13,"08:00:00",28,1.3333333333333333,5,2.2916666666666665,16,1.8333333333333333,-2,{"$f":"IF(AC1044<60,(60-AC1044)/24,0)","v":2.5833333333333335},1.94,2.4191666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,13,"11:00:00",30,1.25,23,1.5416666666666667,19,1.7083333333333333,3,{"$f":"IF(AC1047<60,(60-AC1047)/24,0)","v":2.375},7.88,2.1716666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,13,"17:00:00",25,1.4583333333333333,26.06,1.4141666666666666,22,1.5833333333333333,10,{"$f":"IF(AC1053<60,(60-AC1053)/24,0)","v":2.0833333333333335},11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,14,"01:00:00",9,2.125,12.92,1.9616666666666667,18,1.75,-1,{"$f":"IF(AC1061<60,(60-AC1061)/24,0)","v":2.5416666666666665},7.88,2.1716666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,14,"10:00:00",12,2,19.940000000000001,1.6691666666666667,18,1.75,5,{"$f":"IF(AC1070<60,(60-AC1070)/24,0)","v":2.2916666666666665},17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,14,"18:00:00",10,2.0833333333333335,26.06,1.4141666666666666,22,1.5833333333333333,19,{"$f":"IF(AC1078<60,(60-AC1078)/24,0)","v":1.7083333333333333},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,15,"03:00:00",-8,2.8333333333333335,17.96,1.7516666666666667,8,2.1666666666666665,11,{"$f":"IF(AC1087<60,(60-AC1087)/24,0)","v":2.0416666666666665},20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,15,"08:00:00",-8,2.8333333333333335,10.94,2.0441666666666669,11,2.0416666666666665,15,{"$f":"IF(AC1092<60,(60-AC1092)/24,0)","v":1.875},19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,15,"20:00:00",14,1.9166666666666667,23,1.5416666666666667,28,1.3333333333333333,14,{"$f":"IF(AC1104<60,(60-AC1104)/24,0)","v":1.9166666666666667},20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,15,"22:00:00",10,2.0833333333333335,21.02,1.6241666666666668,28,1.3333333333333333,11,{"$f":"IF(AC1106<60,(60-AC1106)/24,0)","v":2.0416666666666665},15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,16,"05:00:00",5,2.2916666666666665,12.02,1.9991666666666668,32,1.1666666666666667,5,{"$f":"IF(AC1113<60,(60-AC1113)/24,0)","v":2.2916666666666665},8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,16,"19:00:00",27,1.375,21.02,1.6241666666666668,28,1.3333333333333333,20,{"$f":"IF(AC1127<60,(60-AC1127)/24,0)","v":1.6666666666666667},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,16,"22:00:00",18,1.75,12.92,1.9616666666666667,25,1.4583333333333333,20,{"$f":"IF(AC1130<60,(60-AC1130)/24,0)","v":1.6666666666666667},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,17,"05:00:00",18,1.75,15.98,1.8341666666666665,14,1.9166666666666667,17,{"$f":"IF(AC1137<60,(60-AC1137)/24,0)","v":1.7916666666666667},24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,17,"15:00:00",32,1.1666666666666667,26.06,1.4141666666666666,28,1.3333333333333333,26,{"$f":"IF(AC1147<60,(60-AC1147)/24,0)","v":1.4166666666666667},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,17,"19:00:00",30,1.25,26.96,1.3766666666666667,25,1.4583333333333333,21,{"$f":"IF(AC1151<60,(60-AC1151)/24,0)","v":1.625},23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,18,"08:00:00",28,1.3333333333333333,28.04,1.3316666666666668,22,1.5833333333333333,7,{"$f":"IF(AC1164<60,(60-AC1164)/24,0)","v":2.2083333333333335},18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,18,"16:00:00",30,1.25,30.92,1.2116666666666667,48,0.5,21,{"$f":"IF(AC1172<60,(60-AC1172)/24,0)","v":1.625},28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,18,"17:00:00",32,1.1666666666666667,30.92,1.2116666666666667,47,0.54166666666666663,19,{"$f":"IF(AC1173<60,(60-AC1173)/24,0)","v":1.7083333333333333},25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,19,"06:00:00",16,1.8333333333333333,28.94,1.2941666666666667,34,1.0833333333333333,0,{"$f":"IF(AC1186<60,(60-AC1186)/24,0)","v":2.5},8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,19,"10:00:00",28,1.3333333333333333,28.94,1.2941666666666667,38,0.91666666666666663,9,{"$f":"IF(AC1190<60,(60-AC1190)/24,0)","v":2.125},14.9,1.8791666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,19,"16:00:00",34,1.0833333333333333,32,1.1666666666666667,58,8.3333333333333329E-2,27,{"$f":"IF(AC1196<60,(60-AC1196)/24,0)","v":1.375},27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,20,"03:00:00",9,2.125,30.02,1.2491666666666668,37,0.95833333333333337,23,{"$f":"IF(AC1207<60,(60-AC1207)/24,0)","v":1.5416666666666667},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,20,"13:00:00",28,1.3333333333333333,37.04,0.95666666666666667,45,0.625,33,{"$f":"IF(AC1217<60,(60-AC1217)/24,0)","v":1.125},41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,20,"20:00:00",16,1.8333333333333333,33.979999999999997,1.0841666666666667,39,0.875,37,{"$f":"IF(AC1224<60,(60-AC1224)/24,0)","v":0.95833333333333337},39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,21,"03:00:00",7,2.2083333333333335,33.979999999999997,1.0841666666666667,38,0.91666666666666663,36,{"$f":"IF(AC1231<60,(60-AC1231)/24,0)","v":1},38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,21,"05:00:00",9,2.125,33.979999999999997,1.0841666666666667,37,0.95833333333333337,35,{"$f":"IF(AC1233<60,(60-AC1233)/24,0)","v":1.0416666666666667},40.28,0.82166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,21,"17:00:00",19,1.7083333333333333,35.06,1.0391666666666666,54,0.25,38,{"$f":"IF(AC1245<60,(60-AC1245)/24,0)","v":0.91666666666666663},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,21,"22:00:00",7,2.2083333333333335,33.979999999999997,1.0841666666666667,53,0.29166666666666669,36.349800000000002,{"$f":"IF(AC1250<60,(60-AC1250)/24,0)","v":0.98542499999999988},39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,22,"10:00:00",1,2.4583333333333335,26.06,1.4141666666666666,50,0.41666666666666669,38,{"$f":"IF(AC1262<60,(60-AC1262)/24,0)","v":0.91666666666666663},42.98,0.70916666666666683]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,22,"15:00:00",9,2.125,35.06,1.0391666666666666,49,0.45833333333333331,47,{"$f":"IF(AC1267<60,(60-AC1267)/24,0)","v":0.54166666666666663},45.86,0.58916666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,22,1,-9,2.875,19.940000000000001,1.6691666666666667,34,1.0833333333333333,35.4298,{"$f":"IF(AC1276<60,(60-AC1276)/24,0)","v":1.0237583333333333},42.98,0.70916666666666683]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,23,"06:00:00",-15,3.125,19.940000000000001,1.6691666666666667,30,1.25,35,{"$f":"IF(AC1282<60,(60-AC1282)/24,0)","v":1.0416666666666667},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,23,"17:00:00",16,1.8333333333333333,30.02,1.2491666666666668,34,1.0833333333333333,43,{"$f":"IF(AC1293<60,(60-AC1293)/24,0)","v":0.70833333333333337},44.96,0.62666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,23,"23:00:00",-8,2.8333333333333335,19.04,1.7066666666666668,29,1.2916666666666667,34.463299999999997,{"$f":"IF(AC1299<60,(60-AC1299)/24,0)","v":1.0640291666666668},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,24,"02:00:00",-9,2.875,19.04,1.7066666666666668,29,1.2916666666666667,36.147799999999997,{"$f":"IF(AC1302<60,(60-AC1302)/24,0)","v":0.99384166666666685},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,24,"13:00:00",25,1.4583333333333333,33.08,1.1216666666666668,30,1.25,43,{"$f":"IF(AC1313<60,(60-AC1313)/24,0)","v":0.70833333333333337},39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,24,"19:00:00",18,1.75,30.02,1.2491666666666668,20,1.6666666666666667,39,{"$f":"IF(AC1319<60,(60-AC1319)/24,0)","v":0.875},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,25,"03:00:00",-2,2.5833333333333335,24.98,1.4591666666666665,11,2.0416666666666665,34,{"$f":"IF(AC1327<60,(60-AC1327)/24,0)","v":1.0833333333333333},39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,25,"12:00:00",21,1.625,30.92,1.2116666666666667,20,1.6666666666666667,38,{"$f":"IF(AC1336<60,(60-AC1336)/24,0)","v":0.91666666666666663},41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,25,"17:00:00",28,1.3333333333333333,26.96,1.3766666666666667,25,1.4583333333333333,42,{"$f":"IF(AC1341<60,(60-AC1341)/24,0)","v":0.75},43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,26,"05:00:00",23,1.5416666666666667,10.039999999999999,2.0816666666666666,17,1.7916666666666667,31,{"$f":"IF(AC1353<60,(60-AC1353)/24,0)","v":1.2083333333333333},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,26,"10:00:00",27,1.375,10.94,2.0441666666666669,37,0.95833333333333337,35,{"$f":"IF(AC1358<60,(60-AC1358)/24,0)","v":1.0416666666666667},36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,26,"14:00:00",30,1.25,21.02,1.6241666666666668,49,0.45833333333333331,40,{"$f":"IF(AC1362<60,(60-AC1362)/24,0)","v":0.83333333333333337},41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,26,1,21,1.625,15.98,1.8341666666666665,37,0.95833333333333337,29,{"$f":"IF(AC1372<60,(60-AC1372)/24,0)","v":1.2916666666666667},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,27,"07:00:00",21,1.625,8.06,2.1641666666666666,30,1.25,23,{"$f":"IF(AC1379<60,(60-AC1379)/24,0)","v":1.5416666666666667},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,27,"14:00:00",39,0.875,32,1.1666666666666667,43,0.70833333333333337,45,{"$f":"IF(AC1386<60,(60-AC1386)/24,0)","v":0.625},53.96,0.25166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,27,1,10,2.0833333333333335,19.04,1.7066666666666668,43,0.70833333333333337,36,{"$f":"IF(AC1396<60,(60-AC1396)/24,0)","v":1},41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,28,"04:00:00",7,2.2083333333333335,14,1.9166666666666667,38,0.91666666666666663,38,{"$f":"IF(AC1400<60,(60-AC1400)/24,0)","v":0.91666666666666663},42.98,0.70916666666666683]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,28,"17:00:00",34,{"$f":"IF(W1413<60,(60-W1413)/24,0)","v":1.0833333333333333},32,1.1666666666666667,34,1.0833333333333333,43,{"$f":"IF(AC1413<60,(60-AC1413)/24,0)","v":0.70833333333333337},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,28,"18:00:00",34,1.0833333333333333,30.02,{"$f":"IF(Y1414<60,(60-Y1414)/24,0)","v":1.2491666666666668},30,{"$f":"IF(AA1414<60,(60-AA1414)/24,0)","v":1.25},40,{"$f":"IF(AC1414<60,(60-AC1414)/24,0)","v":0.83333333333333337},45.86,{"$f":"IF(AE1414<60,(60-AE1414)/24,0)","v":0.58916666666666673}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,1,"02:00:00",11,2.0416666666666665,31.64,1.1816666666666666,30,1.25,35,{"$f":"IF(AC1422<60,(60-AC1422)/24,0)","v":1.0416666666666667},23.18,1.5341666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,1,"11:00:00",22,1.5833333333333333,41,0.79166666666666663,35,1.0416666666666667,39,{"$f":"IF(AC1431<60,(60-AC1431)/24,0)","v":0.875},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,1,"19:00:00",21,1.625,37.94,0.9191666666666668,38,0.91666666666666663,37,{"$f":"IF(AC1439<60,(60-AC1439)/24,0)","v":0.95833333333333337},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,2,"01:00:00",6,2.25,35.96,1.0016666666666667,38,0.91666666666666663,35,{"$f":"IF(AC1445<60,(60-AC1445)/24,0)","v":1.0416666666666667},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,2,"12:00:00",24,1.5,39.020000000000003,0.87416666666666654,45,0.625,39,{"$f":"IF(AC1456<60,(60-AC1456)/24,0)","v":0.875},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,2,"15:00:00",25,1.4583333333333333,39.92,0.83666666666666656,47,0.54166666666666663,46,{"$f":"IF(AC1459<60,(60-AC1459)/24,0)","v":0.58333333333333337},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,3,"05:00:00",5,2.2916666666666665,26.06,1.4141666666666666,37,0.95833333333333337,33,{"$f":"IF(AC1473<60,(60-AC1473)/24,0)","v":1.125},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,3,"12:00:00",26,1.4166666666666667,28.04,1.3316666666666668,37,0.95833333333333337,37,{"$f":"IF(AC1480<60,(60-AC1480)/24,0)","v":0.95833333333333337},6.8,2.2166666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,3,"14:00:00",24,1.5,28.04,1.3316666666666668,39,0.875,39,{"$f":"IF(AC1482<60,(60-AC1482)/24,0)","v":0.875},10.4,2.0666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,3,"22:00:00",16,1.8333333333333333,17.96,1.7516666666666667,33,1.125,37,{"$f":"IF(AC1490<60,(60-AC1490)/24,0)","v":0.95833333333333337},5,2.2916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,4,"07:00:00",9,2.125,14,1.9166666666666667,28,1.3333333333333333,30,{"$f":"IF(AC1499<60,(60-AC1499)/24,0)","v":1.25},1.4,2.4416666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,4,"12:00:00",16,1.8333333333333333,30.02,1.2491666666666668,31,1.2083333333333333,43,{"$f":"IF(AC1504<60,(60-AC1504)/24,0)","v":0.70833333333333337},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,4,1,6,2.25,24.08,1.4966666666666668,34,1.0833333333333333,33,{"$f":"IF(AC1516<60,(60-AC1516)/24,0)","v":1.125},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,5,"09:00:00",13,1.9583333333333333,26.06,1.4141666666666666,38,0.91666666666666663,36,{"$f":"IF(AC1525<60,(60-AC1525)/24,0)","v":1},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,5,"17:00:00",24,1.5,37.94,0.9191666666666668,48,0.5,36,{"$f":"IF(AC1533<60,(60-AC1533)/24,0)","v":1},34.520000000000003,1.0616666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,5,"18:00:00",23,1.5416666666666667,35.06,1.0391666666666666,46,0.58333333333333337,36,{"$f":"IF(AC1534<60,(60-AC1534)/24,0)","v":1},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,6,"08:00:00",21,1.625,30.02,1.2491666666666668,33,1.125,34,{"$f":"IF(AC1548<60,(60-AC1548)/24,0)","v":1.0833333333333333},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,6,"11:00:00",25,1.4583333333333333,30.92,1.2116666666666667,32,1.1666666666666667,36,{"$f":"IF(AC1551<60,(60-AC1551)/24,0)","v":1},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,6,"22:00:00",19,1.7083333333333333,33.979999999999997,1.0841666666666667,30,1.25,30,{"$f":"IF(AC1562<60,(60-AC1562)/24,0)","v":1.25},15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,7,"04:00:00",15,1.875,33.979999999999997,1.0841666666666667,28,1.3333333333333333,29,{"$f":"IF(AC1568<60,(60-AC1568)/24,0)","v":1.2916666666666667},5,2.2916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,7,"12:00:00",19,1.7083333333333333,35.96,1.0016666666666667,28,1.3333333333333333,37,{"$f":"IF(AC1576<60,(60-AC1576)/24,0)","v":0.95833333333333337},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,7,"21:00:00",17,1.7916666666666667,33.979999999999997,1.0841666666666667,20,1.6666666666666667,30,{"$f":"IF(AC1585<60,(60-AC1585)/24,0)","v":1.25},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,8,"05:00:00",14,1.9166666666666667,33.08,1.1216666666666668,18,1.75,26,{"$f":"IF(AC1593<60,(60-AC1593)/24,0)","v":1.4166666666666667},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,8,"06:00:00",14,1.9166666666666667,33.08,1.1216666666666668,18,1.75,25,{"$f":"IF(AC1594<60,(60-AC1594)/24,0)","v":1.4583333333333333},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,8,"19:00:00",12,2,35.06,1.0391666666666666,28,1.3333333333333333,36,{"$f":"IF(AC1607<60,(60-AC1607)/24,0)","v":1},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,8,"23:00:00",9,2.125,33.979999999999997,1.0841666666666667,21,1.625,35,{"$f":"IF(AC1611<60,(60-AC1611)/24,0)","v":1.0416666666666667},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,9,"09:00:00",6,2.25,33.979999999999997,1.0841666666666667,18,1.75,36,{"$f":"IF(AC1621<60,(60-AC1621)/24,0)","v":1},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,9,"16:00:00",11,2.0416666666666665,41,0.79166666666666663,30,1.25,41,{"$f":"IF(AC1628<60,(60-AC1628)/24,0)","v":0.79166666666666663},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,9,"23:00:00",8,2.1666666666666665,35.06,1.0391666666666666,27,1.375,38,{"$f":"IF(AC1635<60,(60-AC1635)/24,0)","v":0.91666666666666663},17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,10,"09:00:00",7,2.2083333333333335,37.04,0.95666666666666667,28,1.3333333333333333,45,{"$f":"IF(AC1645<60,(60-AC1645)/24,0)","v":0.625},15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,10,"16:00:00",27,1.375,41,0.79166666666666663,43,0.70833333333333337,36,{"$f":"IF(AC1652<60,(60-AC1652)/24,0)","v":1},21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,10,"18:00:00",25,1.4583333333333333,37.04,0.95666666666666667,40,0.83333333333333337,28,{"$f":"IF(AC1654<60,(60-AC1654)/24,0)","v":1.3333333333333333},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,11,"06:00:00",-8,2.8333333333333335,24.08,1.4966666666666668,26,1.4166666666666667,12.289899999999999,{"$f":"IF(AC1666<60,(60-AC1666)/24,0)","v":1.9879208333333331},12.2,1.9916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,11,"11:00:00",30,1.25,37.04,0.95666666666666667,34,1.0833333333333333,18,{"$f":"IF(AC1671<60,(60-AC1671)/24,0)","v":1.75},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,11,"20:00:00",20,1.6666666666666667,30.92,1.2116666666666667,33,1.125,18,{"$f":"IF(AC1680<60,(60-AC1680)/24,0)","v":1.75},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,12,"04:00:00",4,2.3333333333333335,21.92,1.5866666666666667,16.050999999999998,1.8312083333333333,10,{"$f":"IF(AC1688<60,(60-AC1688)/24,0)","v":2.0833333333333335},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,12,"10:00:00",27,1.375,33.08,1.1216666666666668,23,1.5416666666666667,16,{"$f":"IF(AC1694<60,(60-AC1694)/24,0)","v":1.8333333333333333},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,12,"21:00:00",23,1.5416666666666667,28.04,1.3316666666666668,16,1.8333333333333333,8,{"$f":"IF(AC1705<60,(60-AC1705)/24,0)","v":2.1666666666666665},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,13,"03:00:00",14,1.9166666666666667,30.92,1.2116666666666667,15,1.875,-2,{"$f":"IF(AC1711<60,(60-AC1711)/24,0)","v":2.5833333333333335},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,13,"06:00:00",10,2.0833333333333335,24.98,1.4591666666666665,11,2.0416666666666665,-5.3857699999999999,{"$f":"IF(AC1714<60,(60-AC1714)/24,0)","v":2.7244070833333329},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,13,"17:00:00",50,0.41666666666666669,39.92,0.83666666666666656,15,1.875,23,{"$f":"IF(AC1725<60,(60-AC1725)/24,0)","v":1.5416666666666667},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,13,"23:00:00",25,1.4583333333333333,32,1.1666666666666667,10,2.0833333333333335,31,{"$f":"IF(AC1731<60,(60-AC1731)/24,0)","v":1.2083333333333333},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,14,"07:00:00",27,1.375,28.04,1.3316666666666668,1,2.4583333333333335,36,{"$f":"IF(AC1739<60,(60-AC1739)/24,0)","v":1},10.4,2.0666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,14,"16:00:00",53,0.29166666666666669,26.06,1.4141666666666666,25,1.4583333333333333,36,{"$f":"IF(AC1748<60,(60-AC1748)/24,0)","v":1},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,14,"21:00:00",46,0.58333333333333337,19.940000000000001,1.6691666666666667,18,1.75,36,{"$f":"IF(AC1753<60,(60-AC1753)/24,0)","v":1},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,15,"09:00:00",43,0.70833333333333337,33.08,1.1216666666666668,36,1,37,{"$f":"IF(AC1765<60,(60-AC1765)/24,0)","v":0.95833333333333337},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,15,"14:00:00",46,0.58333333333333337,50,0.41666666666666669,43,0.70833333333333337,46,{"$f":"IF(AC1770<60,(60-AC1770)/24,0)","v":0.58333333333333337},30.38,1.2341666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,15,"18:00:00",39,0.875,46.94,0.5441666666666668,37,0.95833333333333337,41,{"$f":"IF(AC1774<60,(60-AC1774)/24,0)","v":0.79166666666666663},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,16,"04:00:00",23,1.5416666666666667,32,1.1666666666666667,9,2.125,19,{"$f":"IF(AC1784<60,(60-AC1784)/24,0)","v":1.7083333333333333},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,16,"11:00:00",23,1.5416666666666667,41,0.79166666666666663,25,1.4583333333333333,36,{"$f":"IF(AC1791<60,(60-AC1791)/24,0)","v":1},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,16,"18:00:00",25,1.4583333333333333,28.94,{"$f":"IF(Y1798<60,(60-Y1798)/24,0)","v":1.2941666666666667},26,{"$f":"IF(AA1798<60,(60-AA1798)/24,0)","v":1.4166666666666667},37,{"$f":"IF(AC1798<60,(60-AC1798)/24,0)","v":0.95833333333333337},37.4,{"$f":"IF(AE1798<60,(60-AE1798)/24,0)","v":0.94166666666666676}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,17,"04:00:00",19,1.7083333333333333,17.059999999999999,1.7891666666666666,28,1.3333333333333333,25.162400000000002,{"$f":"IF(AC1808<60,(60-AC1808)/24,0)","v":1.4515666666666664},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,17,"13:00:00",35,1.0416666666666667,33.979999999999997,1.0841666666666667,50,0.41666666666666669,39,{"$f":"IF(AC1817<60,(60-AC1817)/24,0)","v":0.875},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,17,"17:00:00",38,0.91666666666666663,33.979999999999997,1.0841666666666667,56,0.16666666666666666,41,{"$f":"IF(AC1821<60,(60-AC1821)/24,0)","v":0.79166666666666663},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,18,"06:00:00",13,1.9583333333333333,17.96,1.7516666666666667,29,1.2916666666666667,28.001899999999999,{"$f":"IF(AC1834<60,(60-AC1834)/24,0)","v":1.3332541666666666},29.3,1.2791666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,18,"07:00:00",17,1.7916666666666667,19.04,1.7066666666666668,28,1.3333333333333333,28.001899999999999,{"$f":"IF(AC1835<60,(60-AC1835)/24,0)","v":1.3332541666666666},30.38,1.2341666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,18,"15:00:00",46,0.58333333333333337,33.08,1.1216666666666668,43,0.70833333333333337,37,{"$f":"IF(AC1843<60,(60-AC1843)/24,0)","v":0.95833333333333337},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,19,"04:00:00",16,1.8333333333333333,8.9600000000000009,2.1266666666666665,23,1.5416666666666667,28,{"$f":"IF(AC1856<60,(60-AC1856)/24,0)","v":1.3333333333333333},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,19,"08:00:00",24,1.5,19.940000000000001,1.6691666666666667,27,1.375,29,{"$f":"IF(AC1860<60,(60-AC1860)/24,0)","v":1.2916666666666667},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,19,"14:00:00",51,0.375,33.979999999999997,1.0841666666666667,50,0.41666666666666669,33,{"$f":"IF(AC1866<60,(60-AC1866)/24,0)","v":1.125},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,20,"01:00:00",40,0.83333333333333337,24.08,1.4966666666666668,27,1.375,8,{"$f":"IF(AC1877<60,(60-AC1877)/24,0)","v":2.1666666666666665},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,20,"04:00:00",39,0.875,19.940000000000001,1.6691666666666667,25,1.4583333333333333,10,{"$f":"IF(AC1880<60,(60-AC1880)/24,0)","v":2.0833333333333335},21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,20,"18:00:00",33,1.125,30.02,1.2491666666666668,31.1968,1.2001333333333333,36,{"$f":"IF(AC1894<60,(60-AC1894)/24,0)","v":1},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,21,"01:00:00",33,1.125,28.94,1.2941666666666667,32,1.1666666666666667,25,{"$f":"IF(AC1901<60,(60-AC1901)/24,0)","v":1.4583333333333333},37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,21,"03:00:00",33,1.125,28.94,1.2941666666666667,31,1.2083333333333333,23,{"$f":"IF(AC1903<60,(60-AC1903)/24,0)","v":1.5416666666666667},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,21,"15:00:00",38,0.91666666666666663,37.94,0.9191666666666668,41,0.79166666666666663,46,{"$f":"IF(AC1915<60,(60-AC1915)/24,0)","v":0.58333333333333337},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,21,"20:00:00",32,1.1666666666666667,37.04,0.95666666666666667,33,1.125,34,{"$f":"IF(AC1920<60,(60-AC1920)/24,0)","v":1.0833333333333333},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,22,"01:00:00",31,{"$f":"IF(W1925<60,(60-W1925)/24,0)","v":1.2083333333333333},35.06,1.0391666666666666,35,1.0416666666666667,27.324100000000001,{"$f":"IF(AC1925<60,(60-AC1925)/24,0)","v":1.3614958333333333},40.1,0.82916666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,22,"13:00:00",37,0.95833333333333337,42.98,0.70916666666666683,33,1.125,48,{"$f":"IF(AC1937<60,(60-AC1937)/24,0)","v":0.5},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,22,"22:00:00",31,1.2083333333333333,26.96,1.3766666666666667,28,1.3333333333333333,36,{"$f":"IF(AC1946<60,(60-AC1946)/24,0)","v":1},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,23,"06:00:00",24,1.5,21.02,1.6241666666666668,16,1.8333333333333333,28,{"$f":"IF(AC1954<60,(60-AC1954)/24,0)","v":1.3333333333333333},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,23,"12:00:00",28,1.3333333333333333,44.06,0.66416666666666657,37,0.95833333333333337,36,{"$f":"IF(AC1960<60,(60-AC1960)/24,0)","v":1},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,23,"15:00:00",29,1.2916666666666667,46.94,0.5441666666666668,40,0.83333333333333337,39,{"$f":"IF(AC1963<60,(60-AC1963)/24,0)","v":0.875},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,24,"02:00:00",20,1.6666666666666667,24.98,1.4591666666666665,25,1.4583333333333333,34,{"$f":"IF(AC1974<60,(60-AC1974)/24,0)","v":1.0833333333333333},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,24,"08:00:00",21,1.625,32,1.1666666666666667,25,1.4583333333333333,32,{"$f":"IF(AC1980<60,(60-AC1980)/24,0)","v":1.1666666666666667},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,24,"16:00:00",34,1.0833333333333333,48.02,0.49916666666666654,54,0.25,43,{"$f":"IF(AC1988<60,(60-AC1988)/24,0)","v":0.70833333333333337},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,25,"01:00:00",29,1.2916666666666667,28.04,1.3316666666666668,34,1.0833333333333333,27,{"$f":"IF(AC1997<60,(60-AC1997)/24,0)","v":1.375},33.26,1.1141666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,25,"09:00:00",35,1.0416666666666667,35.06,1.0391666666666666,45,0.625,37,{"$f":"IF(AC2005<60,(60-AC2005)/24,0)","v":0.95833333333333337},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,25,"18:00:00",45,0.625,35.06,1.0391666666666666,46,0.58333333333333337,39,{"$f":"IF(AC2014<60,(60-AC2014)/24,0)","v":0.875},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,25,"23:00:00",37,0.95833333333333337,24.08,1.4966666666666668,38,0.91666666666666663,27,{"$f":"IF(AC2019<60,(60-AC2019)/24,0)","v":1.375},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,26,"03:00:00",37,0.95833333333333337,21.02,1.6241666666666668,36,1,19.146799999999999,{"$f":"IF(AC2023<60,(60-AC2023)/24,0)","v":1.7022166666666667},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,26,"13:00:00",45,0.625,51.08,0.37166666666666676,71,0,41,{"$f":"IF(AC2033<60,(60-AC2033)/24,0)","v":0.79166666666666663},62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,26,"20:00:00",32,1.1666666666666667,35.96,1.0016666666666667,45,0.625,28,{"$f":"IF(AC2040<60,(60-AC2040)/24,0)","v":1.3333333333333333},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,27,"03:00:00",19,1.7083333333333333,35.06,1.0391666666666666,32,1.1666666666666667,19.146799999999999,{"$f":"IF(AC2047<60,(60-AC2047)/24,0)","v":1.7022166666666667},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,27,"13:00:00",20,1.6666666666666667,37.94,0.9191666666666668,59,4.1666666666666664E-2,50,{"$f":"IF(AC2057<60,(60-AC2057)/24,0)","v":0.41666666666666669},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,27,"20:00:00",17,1.7916666666666667,39.92,0.83666666666666656,55,0.20833333333333334,39,{"$f":"IF(AC2064<60,(60-AC2064)/24,0)","v":0.875},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,28,"06:00:00",9,2.125,21.92,1.5866666666666667,48,0.5,34,{"$f":"IF(AC2074<60,(60-AC2074)/24,0)","v":1.0833333333333333},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,28,"07:00:00",13,1.9583333333333333,26.96,1.3766666666666667,48,0.5,34,{"$f":"IF(AC2075<60,(60-AC2075)/24,0)","v":1.0833333333333333},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,28,"16:00:00",36,1,55.94,0.16916666666666677,46,0.58333333333333337,37.049100000000003,{"$f":"IF(AC2084<60,(60-AC2084)/24,0)","v":0.95628749999999985},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,28,1,20,1.6666666666666667,44.06,0.66416666666666657,36,1,37.049100000000003,{"$f":"IF(AC2092<60,(60-AC2092)/24,0)","v":0.95628749999999985},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,29,"09:00:00",29,1.2916666666666667,53.96,0.25166666666666665,46,0.58333333333333337,39.075600000000001,{"$f":"IF(AC2101<60,(60-AC2101)/24,0)","v":0.8718499999999999},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,29,"17:00:00",46,0.58333333333333337,75.02,0,46,0.58333333333333337,45,{"$f":"IF(AC2109<60,(60-AC2109)/24,0)","v":0.625},60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,29,"23:00:00",32,1.1666666666666667,64.94,0,42,0.75,30,{"$f":"IF(AC2115<60,(60-AC2115)/24,0)","v":1.25},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,30,"10:00:00",33,1.125,68,0,51,0.375,46,{"$f":"IF(AC2126<60,(60-AC2126)/24,0)","v":0.58333333333333337},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,30,"13:00:00",37,0.95833333333333337,69.98,0,56,0.16666666666666666,55,{"$f":"IF(AC2129<60,(60-AC2129)/24,0)","v":0.20833333333333334},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,30,"19:00:00",31,1.2083333333333333,55.94,0.16916666666666677,48,0.5,37,{"$f":"IF(AC2135<60,(60-AC2135)/24,0)","v":0.95833333333333337},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,31,"03:00:00",26,1.4166666666666667,53.06,0.28916666666666657,40,0.83333333333333337,30,{"$f":"IF(AC2143<60,(60-AC2143)/24,0)","v":1.25},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,31,"12:00:00",41,0.79166666666666663,60.98,0,36,1,54,{"$f":"IF(AC2152<60,(60-AC2152)/24,0)","v":0.25},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,31,"20:00:00",29,1.2916666666666667,50,0.41666666666666669,24,1.5,48,{"$f":"IF(AC2160<60,(60-AC2160)/24,0)","v":0.5},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,1,"05:00:00",36.0077,0.99967916666666667,32,1.1666666666666667,27,1.375,37,{"$f":"IF(AC2169<60,(60-AC2169)/24,0)","v":0.95833333333333337},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,1,"10:00:00",41,0.79166666666666663,33.979999999999997,1.0841666666666667,48,0.5,41,{"$f":"IF(AC2174<60,(60-AC2174)/24,0)","v":0.79166666666666663},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,1,"22:00:00",43,0.70833333333333337,33.979999999999997,1.0841666666666667,37,0.95833333333333337,36,{"$f":"IF(AC2186<60,(60-AC2186)/24,0)","v":1},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,1,1,39,0.875,33.979999999999997,1.0841666666666667,36,1,37,{"$f":"IF(AC2188<60,(60-AC2188)/24,0)","v":0.95833333333333337},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,2,"07:00:00",36,1,32,1.1666666666666667,39,0.875,37.049100000000003,{"$f":"IF(AC2195<60,(60-AC2195)/24,0)","v":0.95628749999999985},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,2,"21:00:00",34.277200000000001,1.0717833333333333,37.94,0.9191666666666668,54,0.25,50,{"$f":"IF(AC2209<60,(60-AC2209)/24,0)","v":0.41666666666666669},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,2,1,34.191699999999997,1.0753458333333334,35.06,1.0391666666666666,48,0.5,52,{"$f":"IF(AC2212<60,(60-AC2212)/24,0)","v":0.33333333333333331},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,3,"07:00:00",34.191699999999997,1.0753458333333334,30.92,1.2116666666666667,50,0.41666666666666669,48,{"$f":"IF(AC2219<60,(60-AC2219)/24,0)","v":0.5},37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,3,"17:00:00",43,0.70833333333333337,37.04,0.95666666666666667,50,0.41666666666666669,46,{"$f":"IF(AC2229<60,(60-AC2229)/24,0)","v":0.58333333333333337},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,3,"21:00:00",36.188299999999998,0.99215416666666678,33.979999999999997,1.0841666666666667,48,0.5,39,{"$f":"IF(AC2233<60,(60-AC2233)/24,0)","v":0.875},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,4,"10:00:00",43,0.70833333333333337,42.98,{"$f":"IF(Y2246<60,(60-Y2246)/24,0)","v":0.70916666666666683},52,{"$f":"IF(AA2246<60,(60-AA2246)/24,0)","v":0.33333333333333331},39,{"$f":"IF(AC2246<60,(60-AC2246)/24,0)","v":0.875},28.4,{"$f":"IF(AE2246<60,(60-AE2246)/24,0)","v":1.3166666666666667}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,4,"18:00:00",39,0.875,44.96,0.62666666666666659,55,0.20833333333333334,45,{"$f":"IF(AC2254<60,(60-AC2254)/24,0)","v":0.625},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,4,"19:00:00",37.037500000000001,0.95677083333333324,37.94,0.9191666666666668,54,0.25,43,{"$f":"IF(AC2255<60,(60-AC2255)/24,0)","v":0.70833333333333337},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,5,"08:00:00",21,1.625,39.92,0.83666666666666656,37,0.95833333333333337,43,{"$f":"IF(AC2268<60,(60-AC2268)/24,0)","v":0.70833333333333337},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,5,"12:00:00",23,1.5416666666666667,42.98,0.70916666666666683,39,0.875,54,{"$f":"IF(AC2272<60,(60-AC2272)/24,0)","v":0.25},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,5,"18:00:00",21,1.625,39.020000000000003,0.87416666666666654,37,0.95833333333333337,54,{"$f":"IF(AC2278<60,(60-AC2278)/24,0)","v":0.25},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,6,"05:00:00",21,1.625,37.94,0.9191666666666668,32,1.1666666666666667,36,{"$f":"IF(AC2289<60,(60-AC2289)/24,0)","v":1},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,6,"15:00:00",28,1.3333333333333333,51.98,0.33416666666666678,48,0.5,66,{"$f":"IF(AC2299<60,(60-AC2299)/24,0)","v":0},37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,6,"22:00:00",34,1.0833333333333333,53.96,0.25166666666666665,39,0.875,41,{"$f":"IF(AC2306<60,(60-AC2306)/24,0)","v":0.79166666666666663},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,7,"05:00:00",22,1.5833333333333333,44.96,0.62666666666666659,46,0.58333333333333337,39,{"$f":"IF(AC2313<60,(60-AC2313)/24,0)","v":0.875},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,7,"07:00:00",27,1.375,44.06,0.66416666666666657,46,0.58333333333333337,43,{"$f":"IF(AC2315<60,(60-AC2315)/24,0)","v":0.70833333333333337},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,7,"19:00:00",39,0.875,48.02,0.49916666666666654,52,0.33333333333333331,52,{"$f":"IF(AC2327<60,(60-AC2327)/24,0)","v":0.33333333333333331},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,7,1,21,1.625,35.96,1.0016666666666667,46,0.58333333333333337,46,{"$f":"IF(AC2332<60,(60-AC2332)/24,0)","v":0.58333333333333337},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,8,"09:00:00",41,0.79166666666666663,42.08,0.7466666666666667,48,0.5,46,{"$f":"IF(AC2341<60,(60-AC2341)/24,0)","v":0.58333333333333337},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,8,"18:00:00",46,0.58333333333333337,46.94,0.5441666666666668,66,0,54,{"$f":"IF(AC2350<60,(60-AC2350)/24,0)","v":0.25},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,9,"02:00:00",28,1.3333333333333333,33.08,1.1216666666666668,54,0.25,28,{"$f":"IF(AC2358<60,(60-AC2358)/24,0)","v":1.3333333333333333},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,9,"08:00:00",41,0.79166666666666663,35.06,1.0391666666666666,37.133800000000001,0.95275833333333326,37,{"$f":"IF(AC2364<60,(60-AC2364)/24,0)","v":0.95833333333333337},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,9,"19:00:00",37,0.95833333333333337,32,1.1666666666666667,32,1.1666666666666667,43,{"$f":"IF(AC2375<60,(60-AC2375)/24,0)","v":0.70833333333333337},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,10,"01:00:00",27,1.375,26.06,1.4141666666666666,34,1.0833333333333333,28,{"$f":"IF(AC2381<60,(60-AC2381)/24,0)","v":1.3333333333333333},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,10,"04:00:00",32,1.1666666666666667,23,1.5416666666666667,34,1.0833333333333333,27,{"$f":"IF(AC2384<60,(60-AC2384)/24,0)","v":1.375},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,10,"15:00:00",37,0.95833333333333337,42.98,0.70916666666666683,45,0.625,66,{"$f":"IF(AC2395<60,(60-AC2395)/24,0)","v":0},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,10,"21:00:00",30,1.25,37.04,0.95666666666666667,34,1.0833333333333333,46,{"$f":"IF(AC2401<60,(60-AC2401)/24,0)","v":0.58333333333333337},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,11,"05:00:00",19,1.7083333333333333,39.020000000000003,0.87416666666666654,27,1.375,27,{"$f":"IF(AC2409<60,(60-AC2409)/24,0)","v":1.375},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,11,"14:00:00",43,0.70833333333333337,59,4.1666666666666664E-2,45,0.625,48,{"$f":"IF(AC2418<60,(60-AC2418)/24,0)","v":0.5},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,11,"19:00:00",36,1,44.96,0.62666666666666659,37,0.95833333333333337,39,{"$f":"IF(AC2423<60,(60-AC2423)/24,0)","v":0.875},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,12,"07:00:00",27,1.375,32,1.1666666666666667,37.133800000000001,0.95275833333333326,36,{"$f":"IF(AC2435<60,(60-AC2435)/24,0)","v":1},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,12,"12:00:00",46,0.58333333333333337,46.04,0.58166666666666667,37,0.95833333333333337,46,{"$f":"IF(AC2440<60,(60-AC2440)/24,0)","v":0.58333333333333337},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,12,"16:00:00",52,0.33333333333333331,51.08,0.37166666666666676,39,0.875,46,{"$f":"IF(AC2444<60,(60-AC2444)/24,0)","v":0.58333333333333337},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,13,"02:00:00",39,0.875,21.92,1.5866666666666667,27,1.375,36,{"$f":"IF(AC2454<60,(60-AC2454)/24,0)","v":1},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,13,"09:00:00",34,1.0833333333333333,44.06,0.66416666666666657,37,0.95833333333333337,39,{"$f":"IF(AC2461<60,(60-AC2461)/24,0)","v":0.875},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,13,"16:00:00",39,0.875,48.92,0.46166666666666661,46,0.58333333333333337,54,{"$f":"IF(AC2468<60,(60-AC2468)/24,0)","v":0.25},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,14,"02:00:00",46,0.58333333333333337,37.94,0.9191666666666668,28,1.3333333333333333,36,{"$f":"IF(AC2478<60,(60-AC2478)/24,0)","v":1},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,14,"06:00:00",45,0.625,37.04,0.95666666666666667,25,1.4583333333333333,28,{"$f":"IF(AC2482<60,(60-AC2482)/24,0)","v":1.3333333333333333},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,14,"19:00:00",39,0.875,41,0.79166666666666663,52,0.33333333333333331,46,{"$f":"IF(AC2495<60,(60-AC2495)/24,0)","v":0.58333333333333337},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,14,"20:00:00",39,0.875,41,0.79166666666666663,50,0.41666666666666669,43,{"$f":"IF(AC2496<60,(60-AC2496)/24,0)","v":0.70833333333333337},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,15,"04:00:00",36,1,41,0.79166666666666663,34,1.0833333333333333,21,{"$f":"IF(AC2504<60,(60-AC2504)/24,0)","v":1.625},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,15,"13:00:00",46,0.58333333333333337,66.02,0,75,0,57,{"$f":"IF(AC2513<60,(60-AC2513)/24,0)","v":0.125},80.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,15,"21:00:00",34,1.0833333333333333,59,4.1666666666666664E-2,61,0,34,{"$f":"IF(AC2521<60,(60-AC2521)/24,0)","v":1.0833333333333333},71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,16,"03:00:00",25,1.4583333333333333,53.06,0.28916666666666657,52,0.33333333333333331,25,{"$f":"IF(AC2527<60,(60-AC2527)/24,0)","v":1.4583333333333333},64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,16,"14:00:00",52,0.33333333333333331,73.040000000000006,0,72,0,66,{"$f":"IF(AC2538<60,(60-AC2538)/24,0)","v":0},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,16,"17:00:00",52,0.33333333333333331,73.040000000000006,0,54,0.25,68,{"$f":"IF(AC2541<60,(60-AC2541)/24,0)","v":0},50.36,0.40166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,17,"07:00:00",30,1.25,30.92,1.2116666666666667,37,0.95833333333333337,34,{"$f":"IF(AC2555<60,(60-AC2555)/24,0)","v":1.0833333333333333},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,17,"14:00:00",68,0,46.94,0.5441666666666668,52,0.33333333333333331,73,{"$f":"IF(AC2562<60,(60-AC2562)/24,0)","v":0},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,17,"16:00:00",57,0.125,46.04,0.58166666666666667,48,0.5,72,{"$f":"IF(AC2564<60,(60-AC2564)/24,0)","v":0},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,17,1,50,0.41666666666666669,32,1.1666666666666667,41,0.79166666666666663,37,{"$f":"IF(AC2572<60,(60-AC2572)/24,0)","v":0.95833333333333337},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,18,"09:00:00",52,0.33333333333333331,37.94,0.9191666666666668,37,0.95833333333333337,55,{"$f":"IF(AC2581<60,(60-AC2581)/24,0)","v":0.20833333333333334},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,18,"14:00:00",59,4.1666666666666664E-2,35.06,1.0391666666666666,45,0.625,68,{"$f":"IF(AC2586<60,(60-AC2586)/24,0)","v":0},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,19,"02:00:00",46,0.58333333333333337,37.04,0.95666666666666667,39,0.875,30,{"$f":"IF(AC2598<60,(60-AC2598)/24,0)","v":1.25},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,19,"11:00:00",72,0,51.08,0.37166666666666676,43,0.70833333333333337,70,{"$f":"IF(AC2607<60,(60-AC2607)/24,0)","v":0},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,19,"19:00:00",75,0,48.92,0.46166666666666661,45,0.625,63,{"$f":"IF(AC2615<60,(60-AC2615)/24,0)","v":0},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,19,"20:00:00",73,0,48.02,0.49916666666666654,45,0.625,55,{"$f":"IF(AC2616<60,(60-AC2616)/24,0)","v":0.20833333333333334},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,20,"10:00:00",41,0.79166666666666663,53.96,{"$f":"IF(Y2630<60,(60-Y2630)/24,0)","v":0.25166666666666665},52,{"$f":"IF(AA2630<60,(60-AA2630)/24,0)","v":0.33333333333333331},75,{"$f":"IF(AC2630<60,(60-AC2630)/24,0)","v":0},53.6,{"$f":"IF(AE2630<60,(60-AE2630)/24,0)","v":0.26666666666666661}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,20,"13:00:00",46,0.58333333333333337,60.98,0,57,0.125,81,{"$f":"IF(AC2633<60,(60-AC2633)/24,0)","v":0},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,20,1,27,1.375,42.98,0.70916666666666683,50,0.41666666666666669,45,{"$f":"IF(AC2644<60,(60-AC2644)/24,0)","v":0.625},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,21,"06:00:00",28,1.3333333333333333,42.98,0.70916666666666683,46,0.58333333333333337,37,{"$f":"IF(AC2650<60,(60-AC2650)/24,0)","v":0.95833333333333337},37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,21,"14:00:00",50,0.41666666666666669,69.98,0,43,0.70833333333333337,54,{"$f":"IF(AC2658<60,(60-AC2658)/24,0)","v":0.25},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,21,"23:00:00",46,0.58333333333333337,48.92,0.46166666666666661,39,0.875,30,{"$f":"IF(AC2667<60,(60-AC2667)/24,0)","v":1.25},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,22,"07:00:00",46,0.58333333333333337,44.96,0.62666666666666659,41,0.79166666666666663,32,{"$f":"IF(AC2675<60,(60-AC2675)/24,0)","v":1.1666666666666667},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,22,"08:00:00",50,0.41666666666666669,50,0.41666666666666669,42,0.75,37,{"$f":"IF(AC2676<60,(60-AC2676)/24,0)","v":0.95833333333333337},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,22,"21:00:00",48,0.5,46.94,0.5441666666666668,41,0.79166666666666663,54,{"$f":"IF(AC2689<60,(60-AC2689)/24,0)","v":0.25},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,23,"01:00:00",45,{"$f":"IF(W2693<60,(60-W2693)/24,0)","v":0.625},39.020000000000003,0.87416666666666654,39,0.875,45,{"$f":"IF(AC2693<60,(60-AC2693)/24,0)","v":0.625},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,23,"11:00:00",46,0.58333333333333337,53.96,0.25166666666666665,45,0.625,45,{"$f":"IF(AC2703<60,(60-AC2703)/24,0)","v":0.625},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,23,"18:00:00",52,0.33333333333333331,50,0.41666666666666669,45,0.625,46,{"$f":"IF(AC2710<60,(60-AC2710)/24,0)","v":0.58333333333333337},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,24,"01:00:00",34,1.0833333333333333,35.06,1.0391666666666666,41,0.79166666666666663,50,{"$f":"IF(AC2717<60,(60-AC2717)/24,0)","v":0.41666666666666669},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,24,"11:00:00",46,0.58333333333333337,48.92,0.46166666666666661,46,0.58333333333333337,57,{"$f":"IF(AC2727<60,(60-AC2727)/24,0)","v":0.125},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,24,"18:00:00",43,0.70833333333333337,55.94,0.16916666666666677,46,0.58333333333333337,61,{"$f":"IF(AC2734<60,(60-AC2734)/24,0)","v":0},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,24,"20:00:00",37,0.95833333333333337,48.02,0.49916666666666654,46,0.58333333333333337,54,{"$f":"IF(AC2736<60,(60-AC2736)/24,0)","v":0.25},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,25,"08:00:00",30,1.25,48.92,0.46166666666666661,41,0.79166666666666663,43,{"$f":"IF(AC2748<60,(60-AC2748)/24,0)","v":0.70833333333333337},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,25,"13:00:00",46,0.58333333333333337,71.06,0,55,0.20833333333333334,46,{"$f":"IF(AC2753<60,(60-AC2753)/24,0)","v":0.58333333333333337},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,25,"22:00:00",37,0.95833333333333337,64.94,0,39,0.875,43,{"$f":"IF(AC2762<60,(60-AC2762)/24,0)","v":0.70833333333333337},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,26,"06:00:00",37.054099999999998,0.9560791666666667,60.08,0,39,0.875,37,{"$f":"IF(AC2770<60,(60-AC2770)/24,0)","v":0.95833333333333337},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,26,"12:00:00",45,0.625,73.040000000000006,0,36,1,63,{"$f":"IF(AC2776<60,(60-AC2776)/24,0)","v":0},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,26,"23:00:00",41,0.79166666666666663,55.94,0.16916666666666677,34,1.0833333333333333,55,{"$f":"IF(AC2787<60,(60-AC2787)/24,0)","v":0.20833333333333334},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,27,"05:00:00",41.1663,0.78473749999999998,51.98,0.33416666666666678,34,1.0833333333333333,52,{"$f":"IF(AC2793<60,(60-AC2793)/24,0)","v":0.33333333333333331},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,27,"08:00:00",45,0.625,53.96,0.25166666666666665,36,1,50,{"$f":"IF(AC2796<60,(60-AC2796)/24,0)","v":0.41666666666666669},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,27,"19:00:00",46,0.58333333333333337,53.96,0.25166666666666665,45,0.625,48,{"$f":"IF(AC2807<60,(60-AC2807)/24,0)","v":0.5},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,28,"01:00:00",36,1,37.04,0.95666666666666667,43,0.70833333333333337,46,{"$f":"IF(AC2813<60,(60-AC2813)/24,0)","v":0.58333333333333337},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,28,"09:00:00",37,{"$f":"IF(W2821<60,(60-W2821)/24,0)","v":0.95833333333333337},55.94,0.16916666666666677,43,0.70833333333333337,48,{"$f":"IF(AC2821<60,(60-AC2821)/24,0)","v":0.5},64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,28,"18:00:00",43,0.70833333333333337,51.98,0.33416666666666678,52,0.33333333333333331,52,{"$f":"IF(AC2830<60,(60-AC2830)/24,0)","v":0.33333333333333331},77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,28,"23:00:00",23,1.5416666666666667,48.92,0.46166666666666661,36,1,39,{"$f":"IF(AC2835<60,(60-AC2835)/24,0)","v":0.875},64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,29,"11:00:00",61,0,57.92,8.66666666666666E-2,61,0,54,{"$f":"IF(AC2847<60,(60-AC2847)/24,0)","v":0.25},77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,29,"16:00:00",73,0,64.040000000000006,0,66,0,59,{"$f":"IF(AC2852<60,(60-AC2852)/24,0)","v":4.1666666666666664E-2},75.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,29,"20:00:00",57,0.125,55.94,0.16916666666666677,54,0.25,45,{"$f":"IF(AC2856<60,(60-AC2856)/24,0)","v":0.625},62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,30,"06:00:00",46,0.58333333333333337,37.04,0.95666666666666667,45,0.625,39,{"$f":"IF(AC2866<60,(60-AC2866)/24,0)","v":0.875},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,30,"13:00:00",79,0,80.06,0,55,0.20833333333333334,48,{"$f":"IF(AC2873<60,(60-AC2873)/24,0)","v":0.5},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,30,"22:00:00",46,0.58333333333333337,67.64,0,36,1,49,{"$f":"IF(AC2882<60,(60-AC2882)/24,0)","v":0.45833333333333331},45.14,0.61916666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,1,"05:00:00",37.301699999999997,0.94576250000000017,51.98,0.33416666666666678,30,1.25,52,{"$f":"IF(AC2889<60,(60-AC2889)/24,0)","v":0.33333333333333331},37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,1,"15:00:00",45,0.625,80.959999999999994,0,52,0.33333333333333331,57,{"$f":"IF(AC2899<60,(60-AC2899)/24,0)","v":0.125},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,1,"19:00:00",39,0.875,75.02,0,46,0.58333333333333337,61,{"$f":"IF(AC2903<60,(60-AC2903)/24,0)","v":0},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,2,"08:00:00",30,1.25,66.92,0,41,0.79166666666666663,45,{"$f":"IF(AC2916<60,(60-AC2916)/24,0)","v":0.625},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,2,"09:00:00",36,1,71.599999999999994,0,43,0.70833333333333337,45,{"$f":"IF(AC2917<60,(60-AC2917)/24,0)","v":0.625},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,2,"17:00:00",37.213900000000002,0.94942083333333327,68,0,46,0.58333333333333337,59,{"$f":"IF(AC2925<60,(60-AC2925)/24,0)","v":4.1666666666666664E-2},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,3,"06:00:00",41,0.79166666666666663,64.040000000000006,0,45,0.625,37,{"$f":"IF(AC2938<60,(60-AC2938)/24,0)","v":0.95833333333333337},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,3,"10:00:00",43,0.70833333333333337,66.92,0,46,0.58333333333333337,42,{"$f":"IF(AC2942<60,(60-AC2942)/24,0)","v":0.75},51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,3,"16:00:00",37.301699999999997,0.94576250000000017,57.02,0.12416666666666654,48,0.5,43,{"$f":"IF(AC2948<60,(60-AC2948)/24,0)","v":0.70833333333333337},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,4,"03:00:00",39,0.875,42.08,0.7466666666666667,34,1.0833333333333333,43,{"$f":"IF(AC2959<60,(60-AC2959)/24,0)","v":0.70833333333333337},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,4,"06:00:00",37,0.95833333333333337,39.92,0.83666666666666656,32,1.1666666666666667,45,{"$f":"IF(AC2962<60,(60-AC2962)/24,0)","v":0.625},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,4,"20:00:00",43,0.70833333333333337,46.04,0.58166666666666667,48,0.5,44,{"$f":"IF(AC2976<60,(60-AC2976)/24,0)","v":0.66666666666666663},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,5,"03:00:00",27,1.375,30.02,1.2491666666666668,34.380299999999998,1.0674875000000001,32,{"$f":"IF(AC2983<60,(60-AC2983)/24,0)","v":1.1666666666666667},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,5,"05:00:00",25,1.4583333333333333,30.02,1.2491666666666668,34,1.0833333333333333,30,{"$f":"IF(AC2985<60,(60-AC2985)/24,0)","v":1.25},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,5,"17:00:00",66,0,53.96,0.25166666666666665,72,0,63,{"$f":"IF(AC2997<60,(60-AC2997)/24,0)","v":0},64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,5,"22:00:00",36,1,50,0.41666666666666669,46,0.58333333333333337,46,{"$f":"IF(AC3002<60,(60-AC3002)/24,0)","v":0.58333333333333337},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,6,"03:00:00",28,1.3333333333333333,42.8,0.71666666666666679,37.133800000000001,0.95275833333333326,45,{"$f":"IF(AC3007<60,(60-AC3007)/24,0)","v":0.625},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,6,"15:00:00",73,0,69.98,0,79,0,55,{"$f":"IF(AC3019<60,(60-AC3019)/24,0)","v":0.20833333333333334},77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,6,1,50,0.41666666666666669,62.06,0,59,4.1666666666666664E-2,40,{"$f":"IF(AC3028<60,(60-AC3028)/24,0)","v":0.83333333333333337},62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,7,"08:00:00",57,0.125,69.98,0,59,4.1666666666666664E-2,37,{"$f":"IF(AC3036<60,(60-AC3036)/24,0)","v":0.95833333333333337},57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,7,"14:00:00",70,0,78.08,0,73,0,46,{"$f":"IF(AC3042<60,(60-AC3042)/24,0)","v":0.58333333333333337},75.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,7,"17:00:00",70,0,69.98,0,73,0,46,{"$f":"IF(AC3045<60,(60-AC3045)/24,0)","v":0.58333333333333337},75.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,8,"04:00:00",41,0.79166666666666663,37.94,0.9191666666666668,50,0.41666666666666669,39,{"$f":"IF(AC3056<60,(60-AC3056)/24,0)","v":0.875},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,8,"10:00:00",46,0.58333333333333337,51.98,0.33416666666666678,55,0.20833333333333334,48,{"$f":"IF(AC3062<60,(60-AC3062)/24,0)","v":0.5},60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,8,"18:00:00",54,0.25,55.94,0.16916666666666677,63,0,61,{"$f":"IF(AC3070<60,(60-AC3070)/24,0)","v":0},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,9,"03:00:00",36,1,50,0.41666666666666669,52,0.33333333333333331,35,{"$f":"IF(AC3079<60,(60-AC3079)/24,0)","v":1.0416666666666667},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,9,"11:00:00",54,0.25,53.96,0.25166666666666665,50,0.41666666666666669,43,{"$f":"IF(AC3087<60,(60-AC3087)/24,0)","v":0.70833333333333337},51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,9,"20:00:00",46,0.58333333333333337,57.92,8.66666666666666E-2,52,0.33333333333333331,43,{"$f":"IF(AC3096<60,(60-AC3096)/24,0)","v":0.70833333333333337},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,10,"01:00:00",46.143500000000003,0.5773541666666665,46.94,0.5441666666666668,48,0.5,40,{"$f":"IF(AC3101<60,(60-AC3101)/24,0)","v":0.83333333333333337},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,10,"05:00:00",45,0.625,42.08,0.7466666666666667,48,0.5,41,{"$f":"IF(AC3105<60,(60-AC3105)/24,0)","v":0.79166666666666663},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,10,"15:00:00",66,0,62.96,0,72,0,46,{"$f":"IF(AC3115<60,(60-AC3115)/24,0)","v":0.58333333333333337},73.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,10,"22:00:00",46,0.58333333333333337,48.92,0.46166666666666661,55,0.20833333333333334,42,{"$f":"IF(AC3122<60,(60-AC3122)/24,0)","v":0.75},57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,11,"05:00:00",36,1,48.92,0.46166666666666661,45,0.625,37.302399999999999,{"$f":"IF(AC3129<60,(60-AC3129)/24,0)","v":0.94573333333333343},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,11,"15:00:00",54,0.25,84.02,0,63,0,64,{"$f":"IF(AC3139<60,(60-AC3139)/24,0)","v":0},64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,11,1,30,1.25,57.02,0.12416666666666654,45,0.625,51,{"$f":"IF(AC3148<60,(60-AC3148)/24,0)","v":0.375},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,12,"04:00:00",34,1.0833333333333333,48.02,0.49916666666666654,40,0.83333333333333337,50,{"$f":"IF(AC3152<60,(60-AC3152)/24,0)","v":0.41666666666666669},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,12,"09:00:00",50,0.41666666666666669,71.959999999999994,0,44.104399999999998,0.66231666666666678,55,{"$f":"IF(AC3157<60,(60-AC3157)/24,0)","v":0.20833333333333334},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,12,"18:00:00",41,0.79166666666666663,84.02,0,45,0.625,63,{"$f":"IF(AC3166<60,(60-AC3166)/24,0)","v":0},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,13,"02:00:00",39.127099999999999,0.86970416666666672,57.02,0.12416666666666654,43,0.70833333333333337,46,{"$f":"IF(AC3174<60,(60-AC3174)/24,0)","v":0.58333333333333337},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,13,"11:00:00",39,0.875,66.92,0,46,0.58333333333333337,61,{"$f":"IF(AC3183<60,(60-AC3183)/24,0)","v":0},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,13,"19:00:00",32,1.1666666666666667,55.04,0.20666666666666669,42,0.75,55,{"$f":"IF(AC3191<60,(60-AC3191)/24,0)","v":0.20833333333333334},41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,14,"01:00:00",36,1,46.04,0.58166666666666667,43,0.70833333333333337,41.143000000000001,{"$f":"IF(AC3197<60,(60-AC3197)/24,0)","v":0.78570833333333334},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,14,"12:00:00",41,0.79166666666666663,68,0,54,0.25,63,{"$f":"IF(AC3208<60,(60-AC3208)/24,0)","v":0},51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,14,"15:00:00",45,0.625,78.98,0,55,0.20833333333333334,64,{"$f":"IF(AC3211<60,(60-AC3211)/24,0)","v":0},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,14,"21:00:00",37.125799999999998,0.95309166666666678,64.94,0,41,0.79166666666666663,50,{"$f":"IF(AC3217<60,(60-AC3217)/24,0)","v":0.41666666666666669},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,15,"05:00:00",34,1.0833333333333333,60.98,0,41,0.79166666666666663,43,{"$f":"IF(AC3225<60,(60-AC3225)/24,0)","v":0.70833333333333337},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,15,"14:00:00",41,0.79166666666666663,89.06,0,55,0.20833333333333334,66,{"$f":"IF(AC3234<60,(60-AC3234)/24,0)","v":0},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,15,"22:00:00",45,0.625,56.48,0.14666666666666681,52,0.33333333333333331,48,{"$f":"IF(AC3242<60,(60-AC3242)/24,0)","v":0.5},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,16,"07:00:00",45,0.625,52.7,0.30416666666666653,46,0.58333333333333337,46,{"$f":"IF(AC3251<60,(60-AC3251)/24,0)","v":0.58333333333333337},51.98,0.33416666666666678]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,16,"12:00:00",61,0,64.94,0,72,0,52,{"$f":"IF(AC3256<60,(60-AC3256)/24,0)","v":0.33333333333333331},66.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,16,1,61,0,53.96,0.25166666666666665,61,0,41.229300000000002,{"$f":"IF(AC3268<60,(60-AC3268)/24,0)","v":0.78211249999999988},66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,17,"02:00:00",55,0.20833333333333334,53.96,{"$f":"IF(Y3270<60,(60-Y3270)/24,0)","v":0.25166666666666665},61,{"$f":"IF(AA3270<60,(60-AA3270)/24,0)","v":0},43,{"$f":"IF(AC3270<60,(60-AC3270)/24,0)","v":0.70833333333333337},66.2,{"$f":"IF(AE3270<60,(60-AE3270)/24,0)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,17,"09:00:00",52,0.33333333333333331,60.98,0,57,0.125,46,{"$f":"IF(AC3277<60,(60-AC3277)/24,0)","v":0.58333333333333337},66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,17,"23:00:00",43,0.70833333333333337,55.94,0.16916666666666677,52,0.33333333333333331,47,{"$f":"IF(AC3291<60,(60-AC3291)/24,0)","v":0.54166666666666663},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,18,"02:00:00",36,1,57.92,8.66666666666666E-2,45,0.625,40.296100000000003,{"$f":"IF(AC3294<60,(60-AC3294)/24,0)","v":0.82099583333333326},51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,18,"09:00:00",34.277200000000001,1.0717833333333333,60.98,0,36,1,54,{"$f":"IF(AC3301<60,(60-AC3301)/24,0)","v":0.25},37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,18,"19:00:00",37,0.95833333333333337,71.959999999999994,0,40,0.83333333333333337,61,{"$f":"IF(AC3311<60,(60-AC3311)/24,0)","v":0},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,18,"23:00:00",32,1.1666666666666667,62.96,0,36,1,49,{"$f":"IF(AC3315<60,(60-AC3315)/24,0)","v":0.45833333333333331},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,19,"12:00:00",43,0.70833333333333337,68,0,42,0.75,50,{"$f":"IF(AC3328<60,(60-AC3328)/24,0)","v":0.41666666666666669},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,19,"20:00:00",37,0.95833333333333337,55.94,0.16916666666666677,36,1,48,{"$f":"IF(AC3336<60,(60-AC3336)/24,0)","v":0.5},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,19,"21:00:00",28,1.3333333333333333,51.08,0.37166666666666676,35,1.0416666666666667,48,{"$f":"IF(AC3337<60,(60-AC3337)/24,0)","v":0.5},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,20,"10:00:00",45,0.625,69.98,0,35,1.0416666666666667,61,{"$f":"IF(AC3350<60,(60-AC3350)/24,0)","v":0},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,20,"14:00:00",45,0.625,73.040000000000006,0,40,0.83333333333333337,61,{"$f":"IF(AC3354<60,(60-AC3354)/24,0)","v":0},57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,20,"20:00:00",39,0.875,64.94,0,37,0.95833333333333337,55,{"$f":"IF(AC3360<60,(60-AC3360)/24,0)","v":0.20833333333333334},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,21,"07:00:00",39,0.875,57.02,0.12416666666666654,35,1.0416666666666667,50,{"$f":"IF(AC3371<60,(60-AC3371)/24,0)","v":0.41666666666666669},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,21,"17:00:00",48,0.5,77,0,54,0.25,57,{"$f":"IF(AC3381<60,(60-AC3381)/24,0)","v":0.125},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,21,1,28,1.3333333333333333,55.94,0.16916666666666677,37.133800000000001,0.95275833333333326,40,{"$f":"IF(AC3388<60,(60-AC3388)/24,0)","v":0.83333333333333337},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,22,"07:00:00",39,0.875,48.92,0.46166666666666661,37.133800000000001,0.95275833333333326,43,{"$f":"IF(AC3395<60,(60-AC3395)/24,0)","v":0.70833333333333337},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,22,"09:00:00",52,{"$f":"IF(W3397<60,(60-W3397)/24,0)","v":0.33333333333333331},44.06,0.66416666666666657,50,0.41666666666666669,48,{"$f":"IF(AC3397<60,(60-AC3397)/24,0)","v":0.5},60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,22,"21:00:00",43,0.70833333333333337,48.02,0.49916666666666654,45,0.625,46,{"$f":"IF(AC3409<60,(60-AC3409)/24,0)","v":0.58333333333333337},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,23,"02:00:00",28.29,1.32125,46.4,0.56666666666666676,36,1,48,{"$f":"IF(AC3414<60,(60-AC3414)/24,0)","v":0.5},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,23,"11:00:00",66,0,75.2,0,61,0,55,{"$f":"IF(AC3423<60,(60-AC3423)/24,0)","v":0.20833333333333334},71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,23,"20:00:00",61,0,57.38,0.10916666666666656,55,0.20833333333333334,50,{"$f":"IF(AC3432<60,(60-AC3432)/24,0)","v":0.41666666666666669},62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,24,"04:00:00",37,0.95833333333333337,27.68,1.3466666666666667,43,0.70833333333333337,43,{"$f":"IF(AC3440<60,(60-AC3440)/24,0)","v":0.70833333333333337},51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,24,"10:00:00",70,0,53.96,0.25166666666666665,60,0,61,{"$f":"IF(AC3446<60,(60-AC3446)/24,0)","v":0},75.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,24,"21:00:00",52,0.33333333333333331,50,0.41666666666666669,62,0,54,{"$f":"IF(AC3457<60,(60-AC3457)/24,0)","v":0.25},68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,25,"03:00:00",36,1,48.38,0.48416666666666658,59,4.1666666666666664E-2,49,{"$f":"IF(AC3463<60,(60-AC3463)/24,0)","v":0.45833333333333331},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,25,"06:00:00",37,0.95833333333333337,48.92,0.46166666666666661,60,0,52,{"$f":"IF(AC3466<60,(60-AC3466)/24,0)","v":0.33333333333333331},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,25,"17:00:00",63,0,51.08,0.37166666666666676,77,0,64,{"$f":"IF(AC3477<60,(60-AC3477)/24,0)","v":0},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,25,"23:00:00",43,0.70833333333333337,46.94,0.5441666666666668,60,0,63,{"$f":"IF(AC3483<60,(60-AC3483)/24,0)","v":0},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,26,"07:00:00",46,0.58333333333333337,44.96,0.62666666666666659,56,0.16666666666666666,52,{"$f":"IF(AC3491<60,(60-AC3491)/24,0)","v":0.33333333333333331},51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,26,"16:00:00",70,0,50,0.41666666666666669,67,0,54,{"$f":"IF(AC3500<60,(60-AC3500)/24,0)","v":0.25},68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,26,"21:00:00",54,0.25,48.92,0.46166666666666661,57,0.125,50,{"$f":"IF(AC3505<60,(60-AC3505)/24,0)","v":0.41666666666666669},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,27,"09:00:00",61,0,53.06,0.28916666666666657,69,0,54,{"$f":"IF(AC3517<60,(60-AC3517)/24,0)","v":0.25},68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,27,"14:00:00",77,0,71.06,0,78,0,65,{"$f":"IF(AC3522<60,(60-AC3522)/24,0)","v":0},71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,27,"18:00:00",73,0,66.92,{"$f":"IF(Y3526<60,(60-Y3526)/24,0)","v":0},77,{"$f":"IF(AA3526<60,(60-AA3526)/24,0)","v":0},66,{"$f":"IF(AC3526<60,(60-AC3526)/24,0)","v":0},60.8,{"$f":"IF(AE3526<60,(60-AE3526)/24,0)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,28,"04:00:00",43,0.70833333333333337,48.92,0.46166666666666661,61,0,39,{"$f":"IF(AC3536<60,(60-AC3536)/24,0)","v":0.875},57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,28,"11:00:00",72,0,55.04,0.20666666666666669,70,0,72,{"$f":"IF(AC3543<60,(60-AC3543)/24,0)","v":0},66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,28,"18:00:00",70,0,55.4,0.19166666666666674,68,0,75,{"$f":"IF(AC3550<60,(60-AC3550)/24,0)","v":0},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,29,"04:00:00",46.038600000000002,0.58172499999999994,44.06,0.66416666666666657,59,4.1666666666666664E-2,42,{"$f":"IF(AC3560<60,(60-AC3560)/24,0)","v":0.75},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,29,"08:00:00",66,0,48.92,0.46166666666666661,64,0,59,{"$f":"IF(AC3564<60,(60-AC3564)/24,0)","v":4.1666666666666664E-2},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,29,"21:00:00",59,4.1666666666666664E-2,44.96,0.62666666666666659,64,0,68,{"$f":"IF(AC3577<60,(60-AC3577)/24,0)","v":0},60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,29,"22:00:00",57,0.125,44.06,0.66416666666666657,64,0,65,{"$f":"IF(AC3578<60,(60-AC3578)/24,0)","v":0},60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,30,"06:00:00",61,0,46.94,0.5441666666666668,61,0,54,{"$f":"IF(AC3586<60,(60-AC3586)/24,0)","v":0.25},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,30,"15:00:00",70,0,68,0,81,0,63,{"$f":"IF(AC3595<60,(60-AC3595)/24,0)","v":0},82.4,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,30,"23:00:00",57,0.125,42.08,0.7466666666666667,64,0,58,{"$f":"IF(AC3603<60,(60-AC3603)/24,0)","v":8.3333333333333329E-2},69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,31,"05:00:00",54,0.25,37.04,0.95666666666666667,63,0,54,{"$f":"IF(AC3609<60,(60-AC3609)/24,0)","v":0.25},64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,31,"16:00:00",61,0,66.92,0,63,0,70,{"$f":"IF(AC3620<60,(60-AC3620)/24,0)","v":0},78.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,31,"19:00:00",64,0,59,4.1666666666666664E-2,63,0,64,{"$f":"IF(AC3623<60,(60-AC3623)/24,0)","v":0},64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,1,"09:00:00",55,0.20833333333333334,73.040000000000006,0,73,0,73,{"$f":"IF(AC3637<60,(60-AC3637)/24,0)","v":0},64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,1,"16:00:00",57,0.125,86,0,73,0,82,{"$f":"IF(AC3644<60,(60-AC3644)/24,0)","v":0},64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,1,"18:00:00",54,0.25,82.94,0,64,0,77,{"$f":"IF(AC3646<60,(60-AC3646)/24,0)","v":0},60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,2,"02:00:00",30,1.25,66.02,{"$f":"IF(Y3654<60,(60-Y3654)/24,0)","v":0},55,{"$f":"IF(AA3654<60,(60-AA3654)/24,0)","v":0.20833333333333334},64,{"$f":"IF(AC3654<60,(60-AC3654)/24,0)","v":0},55.4,{"$f":"IF(AE3654<60,(60-AE3654)/24,0)","v":0.19166666666666674}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,2,"11:00:00",64,0,66.92,0,75,0,75,{"$f":"IF(AC3663<60,(60-AC3663)/24,0)","v":0},57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,2,"16:00:00",64,0,59,4.1666666666666664E-2,76,0,82,{"$f":"IF(AC3668<60,(60-AC3668)/24,0)","v":0},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,3,"04:00:00",54,0.25,53.06,0.28916666666666657,64,0,70,{"$f":"IF(AC3680<60,(60-AC3680)/24,0)","v":0},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,3,"13:00:00",48,0.5,68,0,72,0,70,{"$f":"IF(AC3689<60,(60-AC3689)/24,0)","v":0},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,3,"15:00:00",48,0.5,69.98,0,78,0,75,{"$f":"IF(AC3691<60,(60-AC3691)/24,0)","v":0},57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,3,"22:00:00",38.2042,0.90815833333333329,53.96,0.25166666666666665,64,0,63,{"$f":"IF(AC3698<60,(60-AC3698)/24,0)","v":0},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,4,"12:00:00",52,0.33333333333333331,57.02,0.12416666666666654,68,0,72,{"$f":"IF(AC3712<60,(60-AC3712)/24,0)","v":0},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,4,"15:00:00",52,0.33333333333333331,57.92,8.66666666666666E-2,69,0,72,{"$f":"IF(AC3715<60,(60-AC3715)/24,0)","v":0},60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,5,"02:00:00",45,0.625,55.04,0.20666666666666669,45,0.625,43.011000000000003,{"$f":"IF(AC3726<60,(60-AC3726)/24,0)","v":0.70787499999999992},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,5,"08:00:00",45,0.625,57.92,8.66666666666666E-2,58,8.3333333333333329E-2,54,{"$f":"IF(AC3732<60,(60-AC3732)/24,0)","v":0.25},57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,5,"16:00:00",54,0.25,75.92,0,77,0,77,{"$f":"IF(AC3740<60,(60-AC3740)/24,0)","v":0},62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,6,"01:00:00",46,0.58333333333333337,53.96,0.25166666666666665,57,0.125,61,{"$f":"IF(AC3749<60,(60-AC3749)/24,0)","v":0},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,6,"09:00:00",48,0.5,60.98,0,68,0,66,{"$f":"IF(AC3757<60,(60-AC3757)/24,0)","v":0},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,6,"10:00:00",48,0.5,64.040000000000006,0,72,0,70,{"$f":"IF(AC3758<60,(60-AC3758)/24,0)","v":0},60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,6,"23:00:00",48,0.5,42.08,0.7466666666666667,67,0,64,{"$f":"IF(AC3771<60,(60-AC3771)/24,0)","v":0},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,7,"03:00:00",46.143500000000003,0.5773541666666665,35.96,1.0016666666666667,62,0,63.037300000000002,{"$f":"IF(AC3775<60,(60-AC3775)/24,0)","v":0},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,7,"13:00:00",55,0.20833333333333334,69.98,0,93,0,93,{"$f":"IF(AC3785<60,(60-AC3785)/24,0)","v":0},64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,7,"20:00:00",52,0.33333333333333331,60.08,0,74,0,81,{"$f":"IF(AC3792<60,(60-AC3792)/24,0)","v":0},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,8,"03:00:00",50,0.41666666666666669,53.96,0.25166666666666665,48,0.5,75,{"$f":"IF(AC3799<60,(60-AC3799)/24,0)","v":0},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,8,"13:00:00",54,0.25,68,0,72,0,84,{"$f":"IF(AC3809<60,(60-AC3809)/24,0)","v":0},64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,8,"20:00:00",52,0.33333333333333331,64.94,0,64,0,66,{"$f":"IF(AC3816<60,(60-AC3816)/24,0)","v":0},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,8,"22:00:00",48,0.5,64.94,0,60,0,64,{"$f":"IF(AC3818<60,(60-AC3818)/24,0)","v":0},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,9,"10:00:00",59,4.1666666666666664E-2,69.08,0,52,0.33333333333333331,57,{"$f":"IF(AC3830<60,(60-AC3830)/24,0)","v":0.125},71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,9,"15:00:00",73,0,69.98,0,55,0.20833333333333334,61,{"$f":"IF(AC3835<60,(60-AC3835)/24,0)","v":0},80.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,9,1,48,0.5,57.02,0.12416666666666654,55,0.20833333333333334,55,{"$f":"IF(AC3844<60,(60-AC3844)/24,0)","v":0.20833333333333334},62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,10,"08:00:00",61,0,60.08,0,64,0,59,{"$f":"IF(AC3852<60,(60-AC3852)/24,0)","v":4.1666666666666664E-2},75.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,10,"14:00:00",77,0,69.98,0,86,0,72,{"$f":"IF(AC3858<60,(60-AC3858)/24,0)","v":0},87.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,11,"01:00:00",46.038600000000002,0.58172499999999994,44.96,0.62666666666666659,58,8.3333333333333329E-2,48,{"$f":"IF(AC3869<60,(60-AC3869)/24,0)","v":0.5},69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,11,"07:00:00",52,0.33333333333333331,57.02,0.12416666666666654,62,0,54,{"$f":"IF(AC3875<60,(60-AC3875)/24,0)","v":0.25},71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,11,"10:00:00",73,0,71.959999999999994,0,77,0,68,{"$f":"IF(AC3878<60,(60-AC3878)/24,0)","v":0},82.4,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,11,"21:00:00",54,0.25,62.96,0,69,0,55,{"$f":"IF(AC3889<60,(60-AC3889)/24,0)","v":0.20833333333333334},77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,12,"03:00:00",39,0.875,57.02,0.12416666666666654,58,8.3333333333333329E-2,46,{"$f":"IF(AC3895<60,(60-AC3895)/24,0)","v":0.58333333333333337},62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,12,"11:00:00",64,0,60.08,0,81,0,77,{"$f":"IF(AC3903<60,(60-AC3903)/24,0)","v":0},73.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,12,"20:00:00",55,0.20833333333333334,66.02,0,70,0,64,{"$f":"IF(AC3912<60,(60-AC3912)/24,0)","v":0},64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,13,"01:00:00",57,0.125,60.08,0,63,0,54,{"$f":"IF(AC3917<60,(60-AC3917)/24,0)","v":0.25},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,13,"13:00:00",63,0,82.94,0,82,0,82,{"$f":"IF(AC3929<60,(60-AC3929)/24,0)","v":0},73.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,13,"18:00:00",63,0,75.92,0,80,0,79,{"$f":"IF(AC3934<60,(60-AC3934)/24,0)","v":0},71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,13,"22:00:00",61,0,64.94,0,61,0,64,{"$f":"IF(AC3938<60,(60-AC3938)/24,0)","v":0},66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,14,"07:00:00",61,0,66.02,0,59,4.1666666666666664E-2,70,{"$f":"IF(AC3947<60,(60-AC3947)/24,0)","v":0},68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,14,"14:00:00",63,0,82.04,0,73,0,77,{"$f":"IF(AC3954<60,(60-AC3954)/24,0)","v":0},77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,14,1,59,4.1666666666666664E-2,66.02,0,45,0.625,68,{"$f":"IF(AC3964<60,(60-AC3964)/24,0)","v":0},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,15,"07:00:00",61,0,75.92,0,52,0.33333333333333331,63,{"$f":"IF(AC3971<60,(60-AC3971)/24,0)","v":0},57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,15,"17:00:00",64,0,82.94,0,73,0,72,{"$f":"IF(AC3981<60,(60-AC3981)/24,0)","v":0},69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,15,"21:00:00",63,0,62.96,0,64,0,57,{"$f":"IF(AC3985<60,(60-AC3985)/24,0)","v":0.125},60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,16,"10:00:00",61,0,77,0,69,0,61,{"$f":"IF(AC3998<60,(60-AC3998)/24,0)","v":0},69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,16,"11:00:00",61,0,78.98,0,72,0,64,{"$f":"IF(AC3999<60,(60-AC3999)/24,0)","v":0},68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,16,"19:00:00",63,0,64.94,0,69,0,59,{"$f":"IF(AC4007<60,(60-AC4007)/24,0)","v":4.1666666666666664E-2},60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,17,"08:00:00",61,0,62.96,0,61,0,55,{"$f":"IF(AC4020<60,(60-AC4020)/24,0)","v":0.20833333333333334},64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,17,"12:00:00",70,0,73.040000000000006,0,72,0,72,{"$f":"IF(AC4024<60,(60-AC4024)/24,0)","v":0},69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,17,"18:00:00",70,0,73.94,0,77,0,61,{"$f":"IF(AC4030<60,(60-AC4030)/24,0)","v":0},69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,18,"05:00:00",61,0,46.04,0.58166666666666667,62,0,55,{"$f":"IF(AC4041<60,(60-AC4041)/24,0)","v":0.20833333333333334},60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,18,"08:00:00",64,0,66.02,0,69,0,55,{"$f":"IF(AC4044<60,(60-AC4044)/24,0)","v":0.20833333333333334},60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,18,"22:00:00",63.005299999999998,0,60.08,0,61,0,50,{"$f":"IF(AC4058<60,(60-AC4058)/24,0)","v":0.41666666666666669},57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,19,"05:00:00",63,0,51.98,0.33416666666666678,60,0,46,{"$f":"IF(AC4065<60,(60-AC4065)/24,0)","v":0.58333333333333337},57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,19,"07:00:00",64,0,62.96,0,69,0,48,{"$f":"IF(AC4067<60,(60-AC4067)/24,0)","v":0.5},57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,19,"19:00:00",72,0,82.04,0,72,0,63,{"$f":"IF(AC4079<60,(60-AC4079)/24,0)","v":0},77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,19,1,59,4.1666666666666664E-2,64.94,0,62,0,52.005600000000001,{"$f":"IF(AC4084<60,(60-AC4084)/24,0)","v":0.33309999999999995},62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,20,"05:00:00",61,0,59,4.1666666666666664E-2,65,0,52.005600000000001,{"$f":"IF(AC4089<60,(60-AC4089)/24,0)","v":0.33309999999999995},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,20,"17:00:00",72,{"$f":"IF(W4101<60,(60-W4101)/24,0)","v":0},82.04,0,77,0,73,{"$f":"IF(AC4101<60,(60-AC4101)/24,0)","v":0},71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,21,"02:00:00",59.0351,4.0204166666666673E-2,48.92,0.46166666666666661,62,0,54,{"$f":"IF(AC4110<60,(60-AC4110)/24,0)","v":0.25},62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,21,"10:00:00",73,0,73.94,0,76,0,66,{"$f":"IF(AC4118<60,(60-AC4118)/24,0)","v":0},82.4,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,21,"16:00:00",81,0,80.06,0,91,0,73,{"$f":"IF(AC4124<60,(60-AC4124)/24,0)","v":0},89.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,21,"19:00:00",72,0,75.92,0,89,0,63,{"$f":"IF(AC4127<60,(60-AC4127)/24,0)","v":0},84.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,22,"06:00:00",63,0,66.02,0,71,0,55,{"$f":"IF(AC4138<60,(60-AC4138)/24,0)","v":0.20833333333333334},75.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,22,"12:00:00",81,0,69.98,0,86,0,82,{"$f":"IF(AC4144<60,(60-AC4144)/24,0)","v":0},89.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,22,"20:00:00",70,0,66.02,0,75,0,66,{"$f":"IF(AC4152<60,(60-AC4152)/24,0)","v":0},78.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,23,"05:00:00",63,0,62.06,0,52,0.33333333333333331,54,{"$f":"IF(AC4161<60,(60-AC4161)/24,0)","v":0.25},64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,23,"13:00:00",81,0,60.98,0,78,0,86,{"$f":"IF(AC4169<60,(60-AC4169)/24,0)","v":0},78.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,23,"22:00:00",64,0,53.06,0.28916666666666657,61,0,63,{"$f":"IF(AC4178<60,(60-AC4178)/24,0)","v":0},66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,24,"03:00:00",63,0,48.92,0.46166666666666661,52.050600000000003,0.33122499999999988,57.023299999999999,{"$f":"IF(AC4183<60,(60-AC4183)/24,0)","v":0.1240291666666667},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,24,"07:00:00",68,0,55.04,0.20666666666666669,52.050600000000003,0.33122499999999988,64,{"$f":"IF(AC4187<60,(60-AC4187)/24,0)","v":0},66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,24,"17:00:00",75,0,86,0,72,0,84,{"$f":"IF(AC4197<60,(60-AC4197)/24,0)","v":0},78.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,24,1,63,0,64.040000000000006,0,57,0.125,57,{"$f":"IF(AC4204<60,(60-AC4204)/24,0)","v":0.125},62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,25,"07:00:00",63,0,60.08,0,62,0,64,{"$f":"IF(AC4211<60,(60-AC4211)/24,0)","v":0},64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,25,"17:00:00",79,0,60.98,0,82,0,73,{"$f":"IF(AC4221<60,(60-AC4221)/24,0)","v":0},78.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,26,"02:00:00",63,0,53.06,{"$f":"IF(Y4230<60,(60-Y4230)/24,0)","v":0.28916666666666657},67,{"$f":"IF(AA4230<60,(60-AA4230)/24,0)","v":0},55,{"$f":"IF(AC4230<60,(60-AC4230)/24,0)","v":0.20833333333333334},77,{"$f":"IF(AE4230<60,(60-AE4230)/24,0)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,26,"06:00:00",64,0,53.96,0.25166666666666665,67,0,59.016800000000003,{"$f":"IF(AC4234<60,(60-AC4234)/24,0)","v":4.0966666666666519E-2},77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,26,"11:00:00",73,0,57.92,8.66666666666666E-2,79,0,84,{"$f":"IF(AC4239<60,(60-AC4239)/24,0)","v":0},77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,26,"20:00:00",66,0,57.92,8.66666666666666E-2,69,0,70,{"$f":"IF(AC4248<60,(60-AC4248)/24,0)","v":0},71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,27,"04:00:00",64.077799999999996,0,59,4.1666666666666664E-2,50.082700000000003,0.4132208333333332,55,{"$f":"IF(AC4256<60,(60-AC4256)/24,0)","v":0.20833333333333334},66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,27,"13:00:00",64,0,62.06,0,77,0,91,{"$f":"IF(AC4265<60,(60-AC4265)/24,0)","v":0},80.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,27,"21:00:00",57,0.125,60.08,0,59,4.1666666666666664E-2,70,{"$f":"IF(AC4273<60,(60-AC4273)/24,0)","v":0},66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,28,"03:00:00",48.149099999999997,0.4937875000000001,60.08,0,58,8.3333333333333329E-2,75,{"$f":"IF(AC4279<60,(60-AC4279)/24,0)","v":0},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,28,"14:00:00",70,0,71.959999999999994,0,79,0,81,{"$f":"IF(AC4290<60,(60-AC4290)/24,0)","v":0},84.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,28,"17:00:00",72,{"$f":"IF(W4293<60,(60-W4293)/24,0)","v":0},73.040000000000006,0,85,0,77,{"$f":"IF(AC4293<60,(60-AC4293)/24,0)","v":0},82.4,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,28,"23:00:00",51,0.375,60.98,0,72,0,73,{"$f":"IF(AC4299<60,(60-AC4299)/24,0)","v":0},69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,29,"07:00:00",48.057000000000002,0.49762499999999993,64.94,0,76,0,73,{"$f":"IF(AC4307<60,(60-AC4307)/24,0)","v":0},73.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,29,"16:00:00",79,0,82.94,0,73,0,75,{"$f":"IF(AC4316<60,(60-AC4316)/24,0)","v":0},89.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,29,1,63,0,66.92,0,76,0,68,{"$f":"IF(AC4324<60,(60-AC4324)/24,0)","v":0},69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,30,"09:00:00",73,0,71.959999999999994,0,79,0,70,{"$f":"IF(AC4333<60,(60-AC4333)/24,0)","v":0},82.4,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,30,"14:00:00",68,0,84.02,0,88,0,79,{"$f":"IF(AC4338<60,(60-AC4338)/24,0)","v":0},87.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,1,"02:00:00",49,0.45833333333333331,62.42,0,61,0,60,{"$f":"IF(AC4350<60,(60-AC4350)/24,0)","v":0},57.92,8.66666666666666E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,1,"04:00:00",43,0.70833333333333337,57.92,8.66666666666666E-2,57,0.125,57.023299999999999,{"$f":"IF(AC4352<60,(60-AC4352)/24,0)","v":0.1240291666666667},51.08,0.37166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,1,"11:00:00",75,0,68,0,69,0,81,{"$f":"IF(AC4359<60,(60-AC4359)/24,0)","v":0},71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,2,"01:00:00",56,0.16666666666666666,59,4.1666666666666664E-2,74,0,66,{"$f":"IF(AC4373<60,(60-AC4373)/24,0)","v":0},55.94,0.16916666666666677]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,2,"04:00:00",50,0.41666666666666669,53.06,0.28916666666666657,75,0,58,{"$f":"IF(AC4376<60,(60-AC4376)/24,0)","v":8.3333333333333329E-2},53.96,0.25166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,2,"11:00:00",72,0,73.040000000000006,0,85,0,81,{"$f":"IF(AC4383<60,(60-AC4383)/24,0)","v":0},77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,2,"21:00:00",63,0,60.98,0,72,0,68,{"$f":"IF(AC4393<60,(60-AC4393)/24,0)","v":0},69.08,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,3,"01:00:00",52,0.33333333333333331,53.96,0.25166666666666665,69,0,62,{"$f":"IF(AC4397<60,(60-AC4397)/24,0)","v":0},68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,3,"14:00:00",73,0,82.94,0,78,0,75,{"$f":"IF(AC4410<60,(60-AC4410)/24,0)","v":0},73.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,3,"22:00:00",52,0.33333333333333331,73.94,0,58.0854,7.9774999999999999E-2,51,{"$f":"IF(AC4418<60,(60-AC4418)/24,0)","v":0.375},62.06,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,3,"23:00:00",50,0.41666666666666669,73.94,0,56,0.16666666666666666,52,{"$f":"IF(AC4419<60,(60-AC4419)/24,0)","v":0.33333333333333331},60.08,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,4,"12:00:00",77,0,86,0,76,0,72,{"$f":"IF(AC4432<60,(60-AC4432)/24,0)","v":0},75.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,4,"16:00:00",81,0,89.06,0,78,0,69,{"$f":"IF(AC4436<60,(60-AC4436)/24,0)","v":0},73.040000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,4,"22:00:00",64,0,80.959999999999994,0,57,0.125,62,{"$f":"IF(AC4442<60,(60-AC4442)/24,0)","v":0},60.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,5,"09:00:00",68,0,77,0,73,0,66,{"$f":"IF(AC4453<60,(60-AC4453)/24,0)","v":0},64.040000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,5,"19:00:00",68,0,71.959999999999994,0,69,0,69,{"$f":"IF(AC4463<60,(60-AC4463)/24,0)","v":0},62.06,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,6,"02:00:00",64.070300000000003,0,50,0.41666666666666669,64,0,60.010399999999997,{"$f":"IF(AC4470<60,(60-AC4470)/24,0)","v":0},62.06,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,6,"09:00:00",64,0,68,0,76,0,75,{"$f":"IF(AC4477<60,(60-AC4477)/24,0)","v":0},66.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,6,"11:00:00",64,0,71.959999999999994,0,79,0,75,{"$f":"IF(AC4479<60,(60-AC4479)/24,0)","v":0},69.08,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,6,"20:00:00",55,0.20833333333333334,64.040000000000006,0,72,0,64,{"$f":"IF(AC4488<60,(60-AC4488)/24,0)","v":0},64.040000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,7,"08:00:00",54,0.25,64.040000000000006,0,63,0,60,{"$f":"IF(AC4500<60,(60-AC4500)/24,0)","v":0},68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,7,"13:00:00",77,0,73.040000000000006,0,72,0,73,{"$f":"IF(AC4505<60,(60-AC4505)/24,0)","v":0},71.06,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,7,"22:00:00",66,0,51.98,0.33416666666666678,64,0,68,{"$f":"IF(AC4514<60,(60-AC4514)/24,0)","v":0},66.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,8,"06:00:00",63,0,53.06,0.28916666666666657,61,0,66,{"$f":"IF(AC4522<60,(60-AC4522)/24,0)","v":0},66.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,8,"12:00:00",66,0,78.08,0,67,0,82,{"$f":"IF(AC4528<60,(60-AC4528)/24,0)","v":0},80.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,8,"23:00:00",62,0,69.08,0,68,0,72,{"$f":"IF(AC4539<60,(60-AC4539)/24,0)","v":0},69.08,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,9,"05:00:00",62,0,60.98,0,65,0,66,{"$f":"IF(AC4545<60,(60-AC4545)/24,0)","v":0},66.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,9,"08:00:00",70,0,66.92,0,67,0,72,{"$f":"IF(AC4548<60,(60-AC4548)/24,0)","v":0},68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,9,"19:00:00",66,0,80.959999999999994,0,64,0,69,{"$f":"IF(AC4559<60,(60-AC4559)/24,0)","v":0},71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,10,"01:00:00",55.068100000000001,0.20549583333333329,69.98,0,61,0,60,{"$f":"IF(AC4565<60,(60-AC4565)/24,0)","v":0},57.92,8.66666666666666E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,10,"09:00:00",64,0,78.08,0,74,0,68,{"$f":"IF(AC4573<60,(60-AC4573)/24,0)","v":0},71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,10,"18:00:00",63,0,80.06,0,76,0,70,{"$f":"IF(AC4582<60,(60-AC4582)/24,0)","v":0},78.08,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,10,"23:00:00",57,0.125,66.02,0,59,4.1666666666666664E-2,60,{"$f":"IF(AC4587<60,(60-AC4587)/24,0)","v":0},62.96,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,11,"11:00:00",73,0,68,0,69,0,79,{"$f":"IF(AC4599<60,(60-AC4599)/24,0)","v":0},78.08,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,11,"16:00:00",73,0,73.94,0,67,0,79,{"$f":"IF(AC4604<60,(60-AC4604)/24,0)","v":0},78.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,11,"20:00:00",61,0,66.02,0,58,8.3333333333333329E-2,68,{"$f":"IF(AC4608<60,(60-AC4608)/24,0)","v":0},69.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,12,"06:00:00",52,0.33333333333333331,55.94,0.16916666666666677,52,0.33333333333333331,55,{"$f":"IF(AC4618<60,(60-AC4618)/24,0)","v":0.20833333333333334},60.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,12,"13:00:00",75,0,64.94,0,83,0,81,{"$f":"IF(AC4625<60,(60-AC4625)/24,0)","v":0},78.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,12,"20:00:00",63,0,60.98,0,72,0,72,{"$f":"IF(AC4632<60,(60-AC4632)/24,0)","v":0},66.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,13,"06:00:00",57,0.125,59,4.1666666666666664E-2,66,0,63,{"$f":"IF(AC4642<60,(60-AC4642)/24,0)","v":0},62.96,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,13,"10:00:00",63,0,71.959999999999994,0,79,0,64,{"$f":"IF(AC4646<60,(60-AC4646)/24,0)","v":0},66.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,13,"23:00:00",63,0,59,4.1666666666666664E-2,66,0,61,{"$f":"IF(AC4659<60,(60-AC4659)/24,0)","v":0},62.96,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,13,1,63,0,55.04,0.20666666666666669,65.072199999999995,0,60,{"$f":"IF(AC4660<60,(60-AC4660)/24,0)","v":0},62.96,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,14,"08:00:00",66,0,64.94,0,71,0,73,{"$f":"IF(AC4668<60,(60-AC4668)/24,0)","v":0},68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,14,"17:00:00",75,{"$f":"IF(W4677<60,(60-W4677)/24,0)","v":0},80.06,0,90,0,77,{"$f":"IF(AC4677<60,(60-AC4677)/24,0)","v":0},78.08,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,15,"01:00:00",66,0,62.06,0,73,0,65,{"$f":"IF(AC4685<60,(60-AC4685)/24,0)","v":0},62.06,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,15,"07:00:00",67,0,73.94,0,72,0,68,{"$f":"IF(AC4691<60,(60-AC4691)/24,0)","v":0},68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,15,"18:00:00",66,0,86,0,90,0,75,{"$f":"IF(AC4702<60,(60-AC4702)/24,0)","v":0},82.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,15,"21:00:00",68,0,78.08,0,82,0,73,{"$f":"IF(AC4705<60,(60-AC4705)/24,0)","v":0},71.06,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,16,"11:00:00",75,0,89.06,0,86,0,79,{"$f":"IF(AC4719<60,(60-AC4719)/24,0)","v":0},84.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,16,"18:00:00",70,0,82.04,0,80,0,72,{"$f":"IF(AC4726<60,(60-AC4726)/24,0)","v":0},84.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,16,"20:00:00",61,0,75.02,0,69,0,66.000699999999995,{"$f":"IF(AC4728<60,(60-AC4728)/24,0)","v":0},75.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,17,"04:00:00",54,0.25,60.98,0,58.0854,7.9774999999999999E-2,65,{"$f":"IF(AC4736<60,(60-AC4736)/24,0)","v":0},64.040000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,17,"13:00:00",74,0,87.08,0,84,0,81,{"$f":"IF(AC4745<60,(60-AC4745)/24,0)","v":0},87.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,17,"22:00:00",59,4.1666666666666664E-2,71.06,0,66,0,65,{"$f":"IF(AC4754<60,(60-AC4754)/24,0)","v":0},75.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,18,"03:00:00",54,0.25,62.06,0,64,0,60,{"$f":"IF(AC4759<60,(60-AC4759)/24,0)","v":0},71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,18,"15:00:00",81,0,91.04,0,86,0,86,{"$f":"IF(AC4771<60,(60-AC4771)/24,0)","v":0},91.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,18,"17:00:00",79,0,91.04,0,81,0,87,{"$f":"IF(AC4773<60,(60-AC4773)/24,0)","v":0},89.96,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,18,1,57,0.125,71.959999999999994,0,62,0,64,{"$f":"IF(AC4780<60,(60-AC4780)/24,0)","v":0},75.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,19,"14:00:00",70,0,91.04,0,66,0,73,{"$f":"IF(AC4794<60,(60-AC4794)/24,0)","v":0},89.96,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,19,"17:00:00",70,0,87.98,0,63,0,72,{"$f":"IF(AC4797<60,(60-AC4797)/24,0)","v":0},86,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,20,"04:00:00",54,0.25,60.08,0,47,0.54166666666666663,61,{"$f":"IF(AC4808<60,(60-AC4808)/24,0)","v":0},71.06,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,20,"10:00:00",54,0.25,84.92,0,74,0,61,{"$f":"IF(AC4814<60,(60-AC4814)/24,0)","v":0},89.06,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,20,"18:00:00",54,0.25,73.040000000000006,0,61,0,65,{"$f":"IF(AC4822<60,(60-AC4822)/24,0)","v":0},91.04,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,21,"03:00:00",57,0.125,66.92,0,52,0.33333333333333331,61,{"$f":"IF(AC4831<60,(60-AC4831)/24,0)","v":0},75.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,21,"11:00:00",64,0,82.04,0,63,0,70,{"$f":"IF(AC4839<60,(60-AC4839)/24,0)","v":0},91.04,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,21,"12:00:00",66,0,84.92,0,63,0,73,{"$f":"IF(AC4840<60,(60-AC4840)/24,0)","v":0},91.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,22,"01:00:00",48,0.5,62.96,0,60,0,50,{"$f":"IF(AC4853<60,(60-AC4853)/24,0)","v":0.41666666666666669},69.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,22,"05:00:00",45.085900000000002,0.6214208333333332,60.08,0,57,0.125,46,{"$f":"IF(AC4857<60,(60-AC4857)/24,0)","v":0.58333333333333337},69.08,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,22,"15:00:00",79,0,84.02,0,79,0,82,{"$f":"IF(AC4867<60,(60-AC4867)/24,0)","v":0},75.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,22,"22:00:00",57,0.125,69.08,0,57,0.125,64,{"$f":"IF(AC4874<60,(60-AC4874)/24,0)","v":0},68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,23,"05:00:00",52,0.33333333333333331,66.02,0,57,0.125,55,{"$f":"IF(AC4881<60,(60-AC4881)/24,0)","v":0.20833333333333334},69.08,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,23,"15:00:00",73,0,84.02,0,75,0,72,{"$f":"IF(AC4891<60,(60-AC4891)/24,0)","v":0},91.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,23,"22:00:00",59,4.1666666666666664E-2,71.06,0,58,8.3333333333333329E-2,64,{"$f":"IF(AC4898<60,(60-AC4898)/24,0)","v":0},78.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,23,1,54,0.25,71.06,0,55,0.20833333333333334,62,{"$f":"IF(AC4900<60,(60-AC4900)/24,0)","v":0},75.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,24,"12:00:00",74,0,77,0,68,0,73,{"$f":"IF(AC4912<60,(60-AC4912)/24,0)","v":0},84.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,24,"17:00:00",79,0,73.94,0,65,0,81,{"$f":"IF(AC4917<60,(60-AC4917)/24,0)","v":0},84.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,25,"02:00:00",55.075400000000002,0.20519166666666658,66.92,0,55,0.20833333333333334,69,{"$f":"IF(AC4926<60,(60-AC4926)/24,0)","v":0},66.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,25,"10:00:00",72,0,75.02,{"$f":"IF(Y4934<60,(60-Y4934)/24,0)","v":0},70,{"$f":"IF(AA4934<60,(60-AA4934)/24,0)","v":0},72,{"$f":"IF(AC4934<60,(60-AC4934)/24,0)","v":0},75.92,{"$f":"IF(AE4934<60,(60-AE4934)/24,0)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,25,"16:00:00",70,0,82.94,0,79,0,74,{"$f":"IF(AC4940<60,(60-AC4940)/24,0)","v":0},78.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,26,"03:00:00",62,0,64.94,0,51,0.375,65,{"$f":"IF(AC4951<60,(60-AC4951)/24,0)","v":0},66.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,26,"09:00:00",69,0,75.92,0,67,0,68,{"$f":"IF(AC4957<60,(60-AC4957)/24,0)","v":0},69.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,26,"12:00:00",69,0,82.94,0,74,0,72,{"$f":"IF(AC4960<60,(60-AC4960)/24,0)","v":0},69.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,26,"23:00:00",61,0,68,0,69,0,68,{"$f":"IF(AC4971<60,(60-AC4971)/24,0)","v":0},62.96,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,27,"05:00:00",56,0.16666666666666666,62.96,0,67,0,63,{"$f":"IF(AC4977<60,(60-AC4977)/24,0)","v":0},62.96,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,27,"13:00:00",72,0,86,0,82,0,73,{"$f":"IF(AC4985<60,(60-AC4985)/24,0)","v":0},78.08,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,27,"22:00:00",63,0,68,0,74,0,63,{"$f":"IF(AC4994<60,(60-AC4994)/24,0)","v":0},66.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,28,"03:00:00",50,0.41666666666666669,64.94,0,71,0,56,{"$f":"IF(AC4999<60,(60-AC4999)/24,0)","v":0.16666666666666666},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,28,"15:00:00",72,0,80.959999999999994,0,79,0,81,{"$f":"IF(AC5011<60,(60-AC5011)/24,0)","v":0},78.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,28,"20:00:00",55,0.20833333333333334,73.040000000000006,0,71,0,64,{"$f":"IF(AC5016<60,(60-AC5016)/24,0)","v":0},66.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,28,1,46.219200000000001,0.57419999999999993,64.94,0,65,0,58,{"$f":"IF(AC5020<60,(60-AC5020)/24,0)","v":8.3333333333333329E-2},64.040000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,29,"09:00:00",62,0,69.98,0,68,0,66,{"$f":"IF(AC5029<60,(60-AC5029)/24,0)","v":0},71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,29,"16:00:00",73,0,84.02,0,75,0,79,{"$f":"IF(AC5036<60,(60-AC5036)/24,0)","v":0},75.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,30,"02:00:00",55,0.20833333333333334,62.96,0,60,0,66,{"$f":"IF(AC5046<60,(60-AC5046)/24,0)","v":0},62.06,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,30,"09:00:00",70,0,64.94,0,70,0,72,{"$f":"IF(AC5053<60,(60-AC5053)/24,0)","v":0},69.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,30,"19:00:00",64,0,75.92,0,70,0,70,{"$f":"IF(AC5063<60,(60-AC5063)/24,0)","v":0},66.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,30,"23:00:00",61,0,62.96,0,57,0.125,62,{"$f":"IF(AC5067<60,(60-AC5067)/24,0)","v":0},64.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,31,"12:00:00",64,0,80.959999999999994,0,81,0,64,{"$f":"IF(AC5080<60,(60-AC5080)/24,0)","v":0},75.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,31,"13:00:00",61,0,82.94,0,79,0,64,{"$f":"IF(AC5081<60,(60-AC5081)/24,0)","v":0},75.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,31,"21:00:00",57,0.125,71.06,0,66,0,63,{"$f":"IF(AC5089<60,(60-AC5089)/24,0)","v":0},71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,1,"10:00:00",75,0,66.02,0,79,0,70,{"$f":"IF(AC5102<60,(60-AC5102)/24,0)","v":0},80.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,1,"14:00:00",82,0,73.94,0,85,0,79,{"$f":"IF(AC5106<60,(60-AC5106)/24,0)","v":0},86.9,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,1,"20:00:00",70,0,66.02,0,70,0,61,{"$f":"IF(AC5112<60,(60-AC5112)/24,0)","v":0},75.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,2,"07:00:00",61,0,57.92,8.66666666666666E-2,65,0,52.005600000000001,{"$f":"IF(AC5123<60,(60-AC5123)/24,0)","v":0.33309999999999995},72.86,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,2,"10:00:00",75,0,69.98,{"$f":"IF(Y5126<60,(60-Y5126)/24,0)","v":0},76,{"$f":"IF(AA5126<60,(60-AA5126)/24,0)","v":0},72,{"$f":"IF(AC5126<60,(60-AC5126)/24,0)","v":0},82.94,{"$f":"IF(AE5126<60,(60-AE5126)/24,0)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,2,1,54,0.25,55.04,0.20666666666666669,64,0,54,{"$f":"IF(AC5140<60,(60-AC5140)/24,0)","v":0.25},70.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,3,"07:00:00",59,4.1666666666666664E-2,55.94,0.16916666666666677,61,0,57,{"$f":"IF(AC5147<60,(60-AC5147)/24,0)","v":0.125},69.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,3,"09:00:00",75,0,69.08,0,67,0,66,{"$f":"IF(AC5149<60,(60-AC5149)/24,0)","v":0},70.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,3,"21:00:00",63,0,64.94,0,66,0,63,{"$f":"IF(AC5161<60,(60-AC5161)/24,0)","v":0},71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,4,"02:00:00",61,0,55.04,0.20666666666666669,64,0,57,{"$f":"IF(AC5166<60,(60-AC5166)/24,0)","v":0.125},70.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,4,"07:00:00",63,0,60.08,0,66,0,61,{"$f":"IF(AC5171<60,(60-AC5171)/24,0)","v":0},71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,4,"19:00:00",63,0,75.92,0,68,0,73,{"$f":"IF(AC5183<60,(60-AC5183)/24,0)","v":0},80.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,5,"04:00:00",46.051699999999997,0.5811791666666668,55.04,0.20666666666666669,64,0,61.023099999999999,{"$f":"IF(AC5192<60,(60-AC5192)/24,0)","v":0},73.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,5,"12:00:00",71,0,84.02,0,83,0,81,{"$f":"IF(AC5200<60,(60-AC5200)/24,0)","v":0},69.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,5,"18:00:00",63,0,82.04,0,82,0,81,{"$f":"IF(AC5206<60,(60-AC5206)/24,0)","v":0},63.86,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,5,"21:00:00",50,0.41666666666666669,69.98,0,70,0,64,{"$f":"IF(AC5209<60,(60-AC5209)/24,0)","v":0},56.84,0.13166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,6,"08:00:00",52,0.33333333333333331,64.040000000000006,0,70,0,68,{"$f":"IF(AC5220<60,(60-AC5220)/24,0)","v":0},61.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,6,"14:00:00",64,0,84.92,0,88,0,79,{"$f":"IF(AC5226<60,(60-AC5226)/24,0)","v":0},71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,6,"22:00:00",48.057000000000002,0.49762499999999993,64.94,0,79,0,66,{"$f":"IF(AC5234<60,(60-AC5234)/24,0)","v":0},57.92,8.66666666666666E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,7,"07:00:00",52,0.33333333333333331,62.96,0,73,0,66,{"$f":"IF(AC5243<60,(60-AC5243)/24,0)","v":0},59.9,4.1666666666667256E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,7,"15:00:00",70,0,78.98,0,85,0,73,{"$f":"IF(AC5251<60,(60-AC5251)/24,0)","v":0},74.84,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,7,1,54,0.25,69.08,0,63,0,68,{"$f":"IF(AC5260<60,(60-AC5260)/24,0)","v":0},55.94,0.16916666666666677]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,8,"05:00:00",52.026699999999998,0.33222083333333341,68,0,60,0,66,{"$f":"IF(AC5265<60,(60-AC5265)/24,0)","v":0},52.88,0.29666666666666658]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,8,"09:00:00",59,4.1666666666666664E-2,69.08,0,71,0,70,{"$f":"IF(AC5269<60,(60-AC5269)/24,0)","v":0},70.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,8,"19:00:00",57,0.125,75.02,0,73,0,73,{"$f":"IF(AC5279<60,(60-AC5279)/24,0)","v":0},64.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,9,"02:00:00",55,0.20833333333333334,60.08,0,65.072199999999995,0,57,{"$f":"IF(AC5286<60,(60-AC5286)/24,0)","v":0.125},56.84,0.13166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,9,"11:00:00",72,0,82.94,0,70,0,81,{"$f":"IF(AC5295<60,(60-AC5295)/24,0)","v":0},79.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,9,"18:00:00",72,0,82.94,0,73,0,82,{"$f":"IF(AC5302<60,(60-AC5302)/24,0)","v":0},73.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,10,"04:00:00",46,0.58333333333333337,57.02,0.12416666666666654,72,0,64,{"$f":"IF(AC5312<60,(60-AC5312)/24,0)","v":0},68.900000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,10,"08:00:00",61,0,69.08,0,75,0,73,{"$f":"IF(AC5316<60,(60-AC5316)/24,0)","v":0},73.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,10,"13:00:00",81,0,86,0,82,0,82,{"$f":"IF(AC5321<60,(60-AC5321)/24,0)","v":0},77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,10,"22:00:00",63,0,69.08,0,73,0,75,{"$f":"IF(AC5330<60,(60-AC5330)/24,0)","v":0},62.96,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,11,"06:00:00",64,0,62.06,0,72,0,70,{"$f":"IF(AC5338<60,(60-AC5338)/24,0)","v":0},56.84,0.13166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,11,"15:00:00",79,0,84.02,0,79,0,82,{"$f":"IF(AC5347<60,(60-AC5347)/24,0)","v":0},71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,11,"23:00:00",64,0,71.06,0,69,0,68,{"$f":"IF(AC5355<60,(60-AC5355)/24,0)","v":0},62.96,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,12,"05:00:00",63,0,64.040000000000006,0,67,0,63.037300000000002,{"$f":"IF(AC5361<60,(60-AC5361)/24,0)","v":0},60.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,12,"16:00:00",72,0,77,0,69,0,73,{"$f":"IF(AC5372<60,(60-AC5372)/24,0)","v":0},72.86,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,12,"19:00:00",66,0,69.08,0,66,0,61,{"$f":"IF(AC5375<60,(60-AC5375)/24,0)","v":0},68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,13,"01:00:00",66,{"$f":"IF(W5381<60,(60-W5381)/24,0)","v":0},50,0.41666666666666669,60,0,48.157499999999999,{"$f":"IF(AC5381<60,(60-AC5381)/24,0)","v":0.49343750000000003},65.84,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,13,"09:00:00",70,0,69.08,0,63,0,55,{"$f":"IF(AC5389<60,(60-AC5389)/24,0)","v":0.20833333333333334},69.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,13,"18:00:00",70,0,80.06,0,70,0,68,{"$f":"IF(AC5398<60,(60-AC5398)/24,0)","v":0},73.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,14,"02:00:00",66,0,64.94,0,56,0.16666666666666666,54,{"$f":"IF(AC5406<60,(60-AC5406)/24,0)","v":0.25},69.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,14,"11:00:00",70,0,87.08,0,76,0,70,{"$f":"IF(AC5415<60,(60-AC5415)/24,0)","v":0},77.900000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,14,"16:00:00",72,0,89.96,0,80,0,80,{"$f":"IF(AC5420<60,(60-AC5420)/24,0)","v":0},75.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,15,"04:00:00",52.088999999999999,0.32962500000000006,62.96,0,67,0,61,{"$f":"IF(AC5432<60,(60-AC5432)/24,0)","v":0},59.9,4.1666666666667256E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,15,"06:00:00",54,0.25,64.94,0,66,0,64,{"$f":"IF(AC5434<60,(60-AC5434)/24,0)","v":0},60.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,15,"13:00:00",72,0,91.04,0,70,0,79,{"$f":"IF(AC5441<60,(60-AC5441)/24,0)","v":0},66.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,16,"03:00:00",57.0077,0.12467916666666667,71.06,0,61,0,65,{"$f":"IF(AC5455<60,(60-AC5455)/24,0)","v":0},55.94,0.16916666666666677]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,16,"06:00:00",59,4.1666666666666664E-2,69.08,0,58,8.3333333333333329E-2,67,{"$f":"IF(AC5458<60,(60-AC5458)/24,0)","v":0},55.94,0.16916666666666677]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,16,"13:00:00",70,0,71.959999999999994,0,78,0,82,{"$f":"IF(AC5465<60,(60-AC5465)/24,0)","v":0},74.84,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,16,"23:00:00",59,4.1666666666666664E-2,55.94,0.16916666666666677,64,0,66,{"$f":"IF(AC5475<60,(60-AC5475)/24,0)","v":0},61.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,17,"03:00:00",57,0.125,50,0.41666666666666669,61,0,64.010499999999993,{"$f":"IF(AC5479<60,(60-AC5479)/24,0)","v":0},61.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,17,"16:00:00",75,0,80.959999999999994,0,84,0,77,{"$f":"IF(AC5492<60,(60-AC5492)/24,0)","v":0},75.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,17,1,50,0.41666666666666669,55.94,0.16916666666666677,67,0,66.000699999999995,{"$f":"IF(AC5500<60,(60-AC5500)/24,0)","v":0},68.900000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,18,"01:00:00",48.149099999999997,0.4937875000000001,57.02,0.12416666666666654,66,0,68,{"$f":"IF(AC5501<60,(60-AC5501)/24,0)","v":0},68.900000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,18,"14:00:00",79,0,80.06,0,80,0,73,{"$f":"IF(AC5514<60,(60-AC5514)/24,0)","v":0},68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,18,"18:00:00",72,0,71.959999999999994,0,78,0,64,{"$f":"IF(AC5518<60,(60-AC5518)/24,0)","v":0},66.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,18,1,54,0.25,64.040000000000006,0,62,0,54,{"$f":"IF(AC5524<60,(60-AC5524)/24,0)","v":0.25},65.84,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,19,"11:00:00",73,0,64.94,0,75,0,64,{"$f":"IF(AC5535<60,(60-AC5535)/24,0)","v":0},70.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,19,"21:00:00",63,0,62.96,0,59,4.1666666666666664E-2,52,{"$f":"IF(AC5545<60,(60-AC5545)/24,0)","v":0.33333333333333331},65.84,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,20,"04:00:00",55.075400000000002,0.20519166666666658,60.98,0,48,0.5,43.011000000000003,{"$f":"IF(AC5552<60,(60-AC5552)/24,0)","v":0.70787499999999992},64.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,20,"11:00:00",64,0,73.040000000000006,0,78,0,70,{"$f":"IF(AC5559<60,(60-AC5559)/24,0)","v":0},77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,20,"13:00:00",72,0,78.08,0,83,0,75,{"$f":"IF(AC5561<60,(60-AC5561)/24,0)","v":0},77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,20,"22:00:00",61,0,60.08,0,67,0,59,{"$f":"IF(AC5570<60,(60-AC5570)/24,0)","v":4.1666666666666664E-2},69.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,21,"10:00:00",61,0,73.040000000000006,0,73,0,63,{"$f":"IF(AC5582<60,(60-AC5582)/24,0)","v":0},74.84,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,21,"15:00:00",61,0,78.98,0,89,0,72,{"$f":"IF(AC5587<60,(60-AC5587)/24,0)","v":0},81.86,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,21,1,48,0.5,57.02,0.12416666666666654,64,0,55,{"$f":"IF(AC5596<60,(60-AC5596)/24,0)","v":0.20833333333333334},65.84,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,22,"08:00:00",52,0.33333333333333331,62.96,0,81,0,55,{"$f":"IF(AC5604<60,(60-AC5604)/24,0)","v":0.20833333333333334},65.84,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,22,"14:00:00",70,0,71.959999999999994,0,86,0,77,{"$f":"IF(AC5610<60,(60-AC5610)/24,0)","v":0},60.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,23,"01:00:00",46,0.58333333333333337,46.94,0.5441666666666668,57.023299999999999,0.1240291666666667,63,{"$f":"IF(AC5621<60,(60-AC5621)/24,0)","v":0},57.92,8.66666666666666E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,23,"07:00:00",48.057000000000002,0.49762499999999993,53.06,0.28916666666666657,54,0.25,61,{"$f":"IF(AC5627<60,(60-AC5627)/24,0)","v":0},57.92,8.66666666666666E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,23,"10:00:00",72,0,69.98,0,72,0,68,{"$f":"IF(AC5630<60,(60-AC5630)/24,0)","v":0},64.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,23,"21:00:00",57,0.125,62.06,0,58.0854,7.9774999999999999E-2,64.029899999999998,{"$f":"IF(AC5641<60,(60-AC5641)/24,0)","v":0},55.94,0.16916666666666677]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,24,"03:00:00",45,0.625,50,0.41666666666666669,53,0.29166666666666669,64,{"$f":"IF(AC5647<60,(60-AC5647)/24,0)","v":0},50.9,0.37916666666666671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,24,"11:00:00",63,0,75.92,0,74,0,73,{"$f":"IF(AC5655<60,(60-AC5655)/24,0)","v":0},71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,24,"20:00:00",48,0.5,68,0,64,0,63,{"$f":"IF(AC5664<60,(60-AC5664)/24,0)","v":0},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,25,"01:00:00",43.000999999999998,0.70829166666666676,64.94,0,55,0.20833333333333334,61,{"$f":"IF(AC5669<60,(60-AC5669)/24,0)","v":0},53.96,0.25166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,25,"13:00:00",73,0,66.02,0,82,0,79,{"$f":"IF(AC5681<60,(60-AC5681)/24,0)","v":0},77.900000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,25,"18:00:00",70,0,64.040000000000006,0,75,0,72,{"$f":"IF(AC5686<60,(60-AC5686)/24,0)","v":0},75.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,25,"22:00:00",52.088999999999999,0.32962500000000006,64.040000000000006,0,61,0,68,{"$f":"IF(AC5690<60,(60-AC5690)/24,0)","v":0},68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,26,"08:00:00",54,0.25,62.96,0,69,0,66.000699999999995,{"$f":"IF(AC5700<60,(60-AC5700)/24,0)","v":0},71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,26,"15:00:00",79,0,64.040000000000006,0,84,0,84,{"$f":"IF(AC5707<60,(60-AC5707)/24,0)","v":0},78.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,26,"22:00:00",55,0.20833333333333334,62.96,0,66,0,63.037300000000002,{"$f":"IF(AC5714<60,(60-AC5714)/24,0)","v":0},69.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,27,"08:00:00",61,0,64.040000000000006,0,62,0,66,{"$f":"IF(AC5724<60,(60-AC5724)/24,0)","v":0},73.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,27,"12:00:00",77,0,77,0,80,0,79,{"$f":"IF(AC5728<60,(60-AC5728)/24,0)","v":0},79.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,28,"01:00:00",63,0,64.040000000000006,0,63,0,57,{"$f":"IF(AC5741<60,(60-AC5741)/24,0)","v":0.125},64.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,28,"02:00:00",64,0,62.06,0,64,0,57,{"$f":"IF(AC5742<60,(60-AC5742)/24,0)","v":0.125},64.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,28,"10:00:00",81,0,75.92,0,72,0,72,{"$f":"IF(AC5750<60,(60-AC5750)/24,0)","v":0},78.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,28,"19:00:00",70,0,73.040000000000006,0,68,0,68,{"$f":"IF(AC5759<60,(60-AC5759)/24,0)","v":0},77.900000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,29,"03:00:00",66,0,64.94,0,65,0,57,{"$f":"IF(AC5767<60,(60-AC5767)/24,0)","v":0.125},71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,29,"09:00:00",73,0,66.02,0,70,0,63,{"$f":"IF(AC5773<60,(60-AC5773)/24,0)","v":0},70.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,29,"20:00:00",66,0,60.08,0,65,0,64.029899999999998,{"$f":"IF(AC5784<60,(60-AC5784)/24,0)","v":0},65.84,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,29,"23:00:00",66,0,55.94,0.16916666666666677,58,8.3333333333333329E-2,61,{"$f":"IF(AC5787<60,(60-AC5787)/24,0)","v":0},59.9,4.1666666666667256E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,30,"13:00:00",79,0,57.92,8.66666666666666E-2,70,0,79,{"$f":"IF(AC5801<60,(60-AC5801)/24,0)","v":0},72.86,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,30,"20:00:00",72,0,55.04,0.20666666666666669,57,0.125,59,{"$f":"IF(AC5808<60,(60-AC5808)/24,0)","v":4.1666666666666664E-2},60.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,30,"22:00:00",68,0,53.96,0.25166666666666665,57,0.125,55,{"$f":"IF(AC5810<60,(60-AC5810)/24,0)","v":0.20833333333333334},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,31,"06:00:00",66,0,51.98,0.33416666666666678,60,0,55,{"$f":"IF(AC5818<60,(60-AC5818)/24,0)","v":0.20833333333333334},57.02,0.12416666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,31,"15:00:00",70,0,57.02,0.12416666666666654,69,0,75,{"$f":"IF(AC5827<60,(60-AC5827)/24,0)","v":0},63.86,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,31,1,49,0.45833333333333331,51.62,0.34916666666666679,55,0.20833333333333334,51,{"$f":"IF(AC5836<60,(60-AC5836)/24,0)","v":0.375},65.3,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,1,"05:00:00",39.301299999999998,0.86244583333333347,48.02,0.49916666666666654,46,0.58333333333333337,46,{"$f":"IF(AC5841<60,(60-AC5841)/24,0)","v":0.58333333333333337},69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,1,"17:00:00",82,0,71.959999999999994,0,80,0,84,{"$f":"IF(AC5853<60,(60-AC5853)/24,0)","v":0},84.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,1,"19:00:00",64,0,60.08,0,68,0,64,{"$f":"IF(AC5855<60,(60-AC5855)/24,0)","v":0},78.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,2,"02:00:00",45,0.625,55.04,0.20666666666666669,52,0.33333333333333331,54,{"$f":"IF(AC5862<60,(60-AC5862)/24,0)","v":0.25},73.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,2,"16:00:00",84,0,71.959999999999994,0,88,0,88,{"$f":"IF(AC5876<60,(60-AC5876)/24,0)","v":0},62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,2,"19:00:00",64,0,62.96,0,72,0,72,{"$f":"IF(AC5879<60,(60-AC5879)/24,0)","v":0},60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,3,"06:00:00",46.038600000000002,0.58172499999999994,51.98,0.33416666666666678,54,0.25,54,{"$f":"IF(AC5890<60,(60-AC5890)/24,0)","v":0.25},60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,3,"12:00:00",84,0,68,0,85,0,84,{"$f":"IF(AC5896<60,(60-AC5896)/24,0)","v":0},66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,3,"20:00:00",61,0,66.92,0,68,0,64,{"$f":"IF(AC5904<60,(60-AC5904)/24,0)","v":0},64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,4,"05:00:00",50,0.41666666666666669,62.06,0,59,4.1666666666666664E-2,55,{"$f":"IF(AC5913<60,(60-AC5913)/24,0)","v":0.20833333333333334},64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,4,"13:00:00",90,0,84.02,0,88,0,90,{"$f":"IF(AC5921<60,(60-AC5921)/24,0)","v":0},69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,4,"14:00:00",90,0,84.92,0,88,0,90,{"$f":"IF(AC5922<60,(60-AC5922)/24,0)","v":0},66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,5,"03:00:00",52,0.33333333333333331,60.08,0,61,0,61,{"$f":"IF(AC5935<60,(60-AC5935)/24,0)","v":0},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,5,"07:00:00",55,0.20833333333333334,64.94,0,64,0,66,{"$f":"IF(AC5939<60,(60-AC5939)/24,0)","v":0},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,5,"17:00:00",75,0,75.02,0,80,0,81,{"$f":"IF(AC5949<60,(60-AC5949)/24,0)","v":0},62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,5,1,55,0.20833333333333334,64.040000000000006,0,67,0,66,{"$f":"IF(AC5956<60,(60-AC5956)/24,0)","v":0},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,6,"07:00:00",59,4.1666666666666664E-2,62.06,0,70,0,70,{"$f":"IF(AC5963<60,(60-AC5963)/24,0)","v":0},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,6,"17:00:00",73,0,62.96,0,73,0,72,{"$f":"IF(AC5973<60,(60-AC5973)/24,0)","v":0},60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,6,1,68,0,59,4.1666666666666664E-2,71,0,70,{"$f":"IF(AC5980<60,(60-AC5980)/24,0)","v":0},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,7,"02:00:00",68,0,59,4.1666666666666664E-2,71,0,70,{"$f":"IF(AC5982<60,(60-AC5982)/24,0)","v":0},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,7,"14:00:00",81,0,69.98,0,80,0,81,{"$f":"IF(AC5994<60,(60-AC5994)/24,0)","v":0},71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,7,"19:00:00",73,0,66.02,0,70,0,75,{"$f":"IF(AC5999<60,(60-AC5999)/24,0)","v":0},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,8,"04:00:00",66,0,60.08,0,72,0,72,{"$f":"IF(AC6008<60,(60-AC6008)/24,0)","v":0},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,8,"12:00:00",79,0,82.94,0,79,0,79,{"$f":"IF(AC6016<60,(60-AC6016)/24,0)","v":0},77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,8,"18:00:00",72,0,77,{"$f":"IF(Y6022<60,(60-Y6022)/24,0)","v":0},66,{"$f":"IF(AA6022<60,(60-AA6022)/24,0)","v":0},72,{"$f":"IF(AC6022<60,(60-AC6022)/24,0)","v":0},73.400000000000006,{"$f":"IF(AE6022<60,(60-AE6022)/24,0)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,9,"05:00:00",61,0,55.94,0.16916666666666677,69,0,64.029899999999998,{"$f":"IF(AC6033<60,(60-AC6033)/24,0)","v":0},60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,9,"11:00:00",77,0,69.98,0,79,0,79,{"$f":"IF(AC6039<60,(60-AC6039)/24,0)","v":0},78.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,9,"14:00:00",79,0,68,0,82,0,81,{"$f":"IF(AC6042<60,(60-AC6042)/24,0)","v":0},78.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,10,"01:00:00",55,0.20833333333333334,55.04,0.20666666666666669,70,0,66,{"$f":"IF(AC6053<60,(60-AC6053)/24,0)","v":0},60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,10,"07:00:00",63,0,57.02,0.12416666666666654,70,0,68.048900000000003,{"$f":"IF(AC6059<60,(60-AC6059)/24,0)","v":0},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,10,"15:00:00",64.070300000000003,0,62.06,0,70,0,70,{"$f":"IF(AC6067<60,(60-AC6067)/24,0)","v":0},71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,10,1,63,0,57.92,8.66666666666666E-2,65,0,64,{"$f":"IF(AC6076<60,(60-AC6076)/24,0)","v":0},51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,11,"05:00:00",54.028100000000002,0.24882916666666657,53.96,0.25166666666666665,59,4.1666666666666664E-2,55,{"$f":"IF(AC6081<60,(60-AC6081)/24,0)","v":0.20833333333333334},51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,11,"17:00:00",68,0,60.08,0,71,0,72,{"$f":"IF(AC6093<60,(60-AC6093)/24,0)","v":0},68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,12,"02:00:00",43.155700000000003,0.70184583333333317,35.96,1.0016666666666667,50,0.41666666666666669,48,{"$f":"IF(AC6102<60,(60-AC6102)/24,0)","v":0.5},62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,12,"04:00:00",41,0.79166666666666663,33.08,1.1216666666666668,48,0.5,45.008800000000001,{"$f":"IF(AC6104<60,(60-AC6104)/24,0)","v":0.62463333333333326},62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,12,"11:00:00",66,0,59,4.1666666666666664E-2,68,0,72,{"$f":"IF(AC6111<60,(60-AC6111)/24,0)","v":0},71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,12,"18:00:00",63,0,53.96,0.25166666666666665,67,0,64,{"$f":"IF(AC6118<60,(60-AC6118)/24,0)","v":0},71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,13,"04:00:00",45,0.625,32,1.1666666666666667,52,0.33333333333333331,50,{"$f":"IF(AC6128<60,(60-AC6128)/24,0)","v":0.41666666666666669},68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,13,"11:00:00",72,0,60.08,0,71,0,70,{"$f":"IF(AC6135<60,(60-AC6135)/24,0)","v":0},75.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,13,"21:00:00",57,0.125,41,0.79166666666666663,60,0,59,{"$f":"IF(AC6145<60,(60-AC6145)/24,0)","v":4.1666666666666664E-2},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,14,"01:00:00",50,{"$f":"IF(W6149<60,(60-W6149)/24,0)","v":0.41666666666666669},35.96,1.0016666666666667,55,0.20833333333333334,61,{"$f":"IF(AC6149<60,(60-AC6149)/24,0)","v":0},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,14,"14:00:00",73,0,66.92,0,73,0,75,{"$f":"IF(AC6162<60,(60-AC6162)/24,0)","v":0},73.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,14,"15:00:00",73,0,66.92,0,75,0,75,{"$f":"IF(AC6163<60,(60-AC6163)/24,0)","v":0},71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,14,"23:00:00",63,0,42.98,0.70916666666666683,64,0,66,{"$f":"IF(AC6171<60,(60-AC6171)/24,0)","v":0},60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,15,"12:00:00",72,0,69.08,0,73,0,73,{"$f":"IF(AC6184<60,(60-AC6184)/24,0)","v":0},64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,15,"16:00:00",70,0,71.06,0,76,0,72,{"$f":"IF(AC6188<60,(60-AC6188)/24,0)","v":0},66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,15,"22:00:00",63,0,46.94,0.5441666666666668,66,0,66,{"$f":"IF(AC6194<60,(60-AC6194)/24,0)","v":0},57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,16,"09:00:00",55,0.20833333333333334,55.94,0.16916666666666677,57,0.125,55.072200000000002,{"$f":"IF(AC6205<60,(60-AC6205)/24,0)","v":0.2053249999999999},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,16,"12:00:00",55,0.20833333333333334,69.98,0,60,0,55,{"$f":"IF(AC6208<60,(60-AC6208)/24,0)","v":0.20833333333333334},62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,17,"02:00:00",54,0.25,42.08,0.7466666666666667,54,0.25,55,{"$f":"IF(AC6222<60,(60-AC6222)/24,0)","v":0.20833333333333334},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,17,"09:00:00",52,0.33333333333333331,53.96,0.25166666666666665,54,0.25,52,{"$f":"IF(AC6229<60,(60-AC6229)/24,0)","v":0.33333333333333331},57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,17,"11:00:00",50,0.41666666666666669,69.98,0,57,0.125,52,{"$f":"IF(AC6231<60,(60-AC6231)/24,0)","v":0.33333333333333331},62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,17,"23:00:00",52,0.33333333333333331,50,0.41666666666666669,57,0.125,55,{"$f":"IF(AC6243<60,(60-AC6243)/24,0)","v":0.20833333333333334},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,18,"04:00:00",48,0.5,46.04,0.58166666666666667,55,0.20833333333333334,52,{"$f":"IF(AC6248<60,(60-AC6248)/24,0)","v":0.33333333333333331},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,18,"09:00:00",55,0.20833333333333334,55.04,0.20666666666666669,60,0,57,{"$f":"IF(AC6253<60,(60-AC6253)/24,0)","v":0.125},66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,18,"21:00:00",39,0.875,55.94,0.16916666666666677,52,0.33333333333333331,45,{"$f":"IF(AC6265<60,(60-AC6265)/24,0)","v":0.625},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,19,"06:00:00",30.233000000000001,1.2402916666666666,50,0.41666666666666669,38,0.91666666666666663,41.229300000000002,{"$f":"IF(AC6274<60,(60-AC6274)/24,0)","v":0.78211249999999988},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,19,"14:00:00",68,0,82.94,0,72,0,70,{"$f":"IF(AC6282<60,(60-AC6282)/24,0)","v":0},75.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,19,"20:00:00",45,0.625,66.92,0,54,0.25,54,{"$f":"IF(AC6288<60,(60-AC6288)/24,0)","v":0.25},66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,19,"23:00:00",37.140599999999999,0.95247500000000007,57.92,8.66666666666666E-2,51,0.375,46.103999999999999,{"$f":"IF(AC6291<60,(60-AC6291)/24,0)","v":0.57900000000000007},64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,20,"10:00:00",64,0,78.08,0,66,0,64,{"$f":"IF(AC6302<60,(60-AC6302)/24,0)","v":0},66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,20,"16:00:00",64,0,86,0,70,0,70,{"$f":"IF(AC6308<60,(60-AC6308)/24,0)","v":0},73.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,20,1,57,0.125,60.08,0,59,4.1666666666666664E-2,61,{"$f":"IF(AC6316<60,(60-AC6316)/24,0)","v":0},60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,21,"09:00:00",57,0.125,75.02,0,59,4.1666666666666664E-2,61,{"$f":"IF(AC6325<60,(60-AC6325)/24,0)","v":0},73.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,21,"17:00:00",52.026699999999998,0.33222083333333341,73.040000000000006,0,59,4.1666666666666664E-2,52,{"$f":"IF(AC6333<60,(60-AC6333)/24,0)","v":0.33333333333333331},68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,22,"02:00:00",48,0.5,55.94,{"$f":"IF(Y6342<60,(60-Y6342)/24,0)","v":0.16916666666666677},52.050600000000003,{"$f":"IF(AA6342<60,(60-AA6342)/24,0)","v":0.33122499999999988},48,{"$f":"IF(AC6342<60,(60-AC6342)/24,0)","v":0.5},51.8,{"$f":"IF(AE6342<60,(60-AE6342)/24,0)","v":0.34166666666666679}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,22,"07:00:00",48,0.5,59,4.1666666666666664E-2,47,0.54166666666666663,48,{"$f":"IF(AC6347<60,(60-AC6347)/24,0)","v":0.5},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,22,"11:00:00",54,0.25,64.94,0,52.050600000000003,0.33122499999999988,52,{"$f":"IF(AC6351<60,(60-AC6351)/24,0)","v":0.33333333333333331},64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,22,"21:00:00",48,0.5,55.04,0.20666666666666669,47,0.54166666666666663,46.219200000000001,{"$f":"IF(AC6361<60,(60-AC6361)/24,0)","v":0.57419999999999993},51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,23,"04:00:00",46,0.58333333333333337,53.06,0.28916666666666657,46.103999999999999,0.57900000000000007,45,{"$f":"IF(AC6368<60,(60-AC6368)/24,0)","v":0.625},51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,23,"13:00:00",61,0,62.96,0,69,0,66,{"$f":"IF(AC6377<60,(60-AC6377)/24,0)","v":0},68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,23,"20:00:00",52,0.33333333333333331,60.98,0,61,0,55,{"$f":"IF(AC6384<60,(60-AC6384)/24,0)","v":0.20833333333333334},62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,24,"06:00:00",45,0.625,60.08,0,47,0.54166666666666663,46,{"$f":"IF(AC6394<60,(60-AC6394)/24,0)","v":0.58333333333333337},66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,24,"10:00:00",66,0,64.040000000000006,0,67,0,66,{"$f":"IF(AC6398<60,(60-AC6398)/24,0)","v":0},69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,24,"15:00:00",73,0,68,0,74,0,75,{"$f":"IF(AC6403<60,(60-AC6403)/24,0)","v":0},66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,24,1,55,0.20833333333333334,64.040000000000006,0,57,0.125,57,{"$f":"IF(AC6412<60,(60-AC6412)/24,0)","v":0.125},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,25,"08:00:00",52,0.33333333333333331,60.98,0,57,0.125,54.103499999999997,{"$f":"IF(AC6420<60,(60-AC6420)/24,0)","v":0.24568750000000014},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,25,"17:00:00",54,0.25,64.94,0,62,0,59,{"$f":"IF(AC6429<60,(60-AC6429)/24,0)","v":4.1666666666666664E-2},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,26,"01:00:00",34,1.0833333333333333,42.98,0.70916666666666683,43,0.70833333333333337,39.2468,{"$f":"IF(AC6437<60,(60-AC6437)/24,0)","v":0.86471666666666669},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,26,"07:00:00",34.129800000000003,1.0779249999999998,41,0.79166666666666663,41,0.79166666666666663,43.097900000000003,{"$f":"IF(AC6443<60,(60-AC6443)/24,0)","v":0.70425416666666651},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,26,"18:00:00",54,0.25,60.08,0,55,0.20833333333333334,54,{"$f":"IF(AC6454<60,(60-AC6454)/24,0)","v":0.25},51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,26,"21:00:00",39,0.875,57.92,8.66666666666666E-2,47,0.54166666666666663,46,{"$f":"IF(AC6457<60,(60-AC6457)/24,0)","v":0.58333333333333337},51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,27,"03:00:00",36.349800000000002,0.98542499999999988,57.92,8.66666666666666E-2,43,0.70833333333333337,43.097900000000003,{"$f":"IF(AC6463<60,(60-AC6463)/24,0)","v":0.70425416666666651},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,27,"11:00:00",63,0,66.02,0,64,0,55,{"$f":"IF(AC6471<60,(60-AC6471)/24,0)","v":0.20833333333333334},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,27,"20:00:00",66,0,66.92,0,50,0.41666666666666669,55,{"$f":"IF(AC6480<60,(60-AC6480)/24,0)","v":0.20833333333333334},57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,28,"04:00:00",63,0,60.08,0,41,0.79166666666666663,55,{"$f":"IF(AC6488<60,(60-AC6488)/24,0)","v":0.20833333333333334},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,28,"13:00:00",66,0,68,0,70,0,70,{"$f":"IF(AC6497<60,(60-AC6497)/24,0)","v":0},51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,28,"18:00:00",63,0,62.06,0,57,0.125,64,{"$f":"IF(AC6502<60,(60-AC6502)/24,0)","v":0},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,29,"06:00:00",52,0.33333333333333331,37.94,0.9191666666666668,61,0,63.008600000000001,{"$f":"IF(AC6514<60,(60-AC6514)/24,0)","v":0},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,29,"08:00:00",54,0.25,53.06,0.28916666666666657,65,0,64,{"$f":"IF(AC6516<60,(60-AC6516)/24,0)","v":0},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,29,"15:00:00",61,0,75.02,0,59,4.1666666666666664E-2,75,{"$f":"IF(AC6523<60,(60-AC6523)/24,0)","v":0},51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,30,"05:00:00",37.226799999999997,0.94888333333333341,46.94,0.5441666666666668,41,0.79166666666666663,64,{"$f":"IF(AC6537<60,(60-AC6537)/24,0)","v":0},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,30,"08:00:00",48,0.5,46.04,0.58166666666666667,54,0.25,64,{"$f":"IF(AC6540<60,(60-AC6540)/24,0)","v":0},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,30,"15:00:00",57,0.125,75.92,0,69,0,63,{"$f":"IF(AC6547<60,(60-AC6547)/24,0)","v":0},64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,1,"01:00:00",46,0.58333333333333337,65.84,0,44,0.66666666666666663,53,{"$f":"IF(AC6557<60,(60-AC6557)/24,0)","v":0.29166666666666669},54.86,0.2141666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,1,"05:00:00",54.027900000000002,0.24883749999999991,73.94,0,36.063899999999997,0.9973375000000001,63,{"$f":"IF(AC6561<60,(60-AC6561)/24,0)","v":0},57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,1,"18:00:00",41,0.79166666666666663,62.96,0,45,0.625,48,{"$f":"IF(AC6574<60,(60-AC6574)/24,0)","v":0.5},73.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,2,"02:00:00",39,0.875,53.06,0.28916666666666657,37.133800000000001,0.95275833333333326,36,{"$f":"IF(AC6582<60,(60-AC6582)/24,0)","v":1},68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,2,"03:00:00",39,0.875,50,0.41666666666666669,37.133800000000001,0.95275833333333326,34,{"$f":"IF(AC6583<60,(60-AC6583)/24,0)","v":1.0833333333333333},66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,2,"16:00:00",46,0.58333333333333337,55.04,0.20666666666666669,46,0.58333333333333337,55,{"$f":"IF(AC6596<60,(60-AC6596)/24,0)","v":0.20833333333333334},80.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,2,"20:00:00",45,0.625,53.06,0.28916666666666657,37,0.95833333333333337,43,{"$f":"IF(AC6600<60,(60-AC6600)/24,0)","v":0.70833333333333337},73.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,3,"02:00:00",43,0.70833333333333337,50,0.41666666666666669,36,1,37,{"$f":"IF(AC6606<60,(60-AC6606)/24,0)","v":0.95833333333333337},69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,3,"13:00:00",48,0.5,60.08,0,54,0.25,57,{"$f":"IF(AC6617<60,(60-AC6617)/24,0)","v":0.125},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,3,"23:00:00",37,0.95833333333333337,55.04,0.20666666666666669,36,1,36,{"$f":"IF(AC6627<60,(60-AC6627)/24,0)","v":1},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,4,"06:00:00",25,1.4583333333333333,55.94,0.16916666666666677,37.133800000000001,0.95275833333333326,30.1447,{"$f":"IF(AC6634<60,(60-AC6634)/24,0)","v":1.2439708333333332},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,4,"15:00:00",57,0.125,66.02,0,52,0.33333333333333331,63,{"$f":"IF(AC6643<60,(60-AC6643)/24,0)","v":0},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,4,"22:00:00",32,1.1666666666666667,55.04,0.20666666666666669,43,0.70833333333333337,36,{"$f":"IF(AC6650<60,(60-AC6650)/24,0)","v":1},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,4,1,28,1.3333333333333333,53.06,0.28916666666666657,37.133800000000001,0.95275833333333326,34,{"$f":"IF(AC6652<60,(60-AC6652)/24,0)","v":1.0833333333333333},62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,5,"12:00:00",54,0.25,57.02,0.12416666666666654,52,0.33333333333333331,57,{"$f":"IF(AC6664<60,(60-AC6664)/24,0)","v":0.125},78.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,5,"17:00:00",46,0.58333333333333337,53.06,0.28916666666666657,50,0.41666666666666669,57,{"$f":"IF(AC6669<60,(60-AC6669)/24,0)","v":0.125},71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,6,"02:00:00",21,1.625,33.08,1.1216666666666668,30,1.25,30,{"$f":"IF(AC6678<60,(60-AC6678)/24,0)","v":1.25},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,6,"10:00:00",43,0.70833333333333337,55.04,0.20666666666666669,46,0.58333333333333337,45,{"$f":"IF(AC6686<60,(60-AC6686)/24,0)","v":0.625},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,6,"16:00:00",54,0.25,48.02,0.49916666666666654,54,0.25,55,{"$f":"IF(AC6692<60,(60-AC6692)/24,0)","v":0.20833333333333334},57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,7,"03:00:00",28,1.3333333333333333,35.96,1.0016666666666667,29,1.2916666666666667,28.3657,{"$f":"IF(AC6703<60,(60-AC6703)/24,0)","v":1.3180958333333332},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,7,"09:00:00",37,0.95833333333333337,42.98,0.70916666666666683,35,1.0416666666666667,41,{"$f":"IF(AC6709<60,(60-AC6709)/24,0)","v":0.79166666666666663},56.48,0.14666666666666681]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,7,"12:00:00",57,0.125,50,0.41666666666666669,54,0.25,52,{"$f":"IF(AC6712<60,(60-AC6712)/24,0)","v":0.33333333333333331},62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,7,"23:00:00",50,0.41666666666666669,30.02,1.2491666666666668,36.063899999999997,0.9973375000000001,54,{"$f":"IF(AC6723<60,(60-AC6723)/24,0)","v":0.25},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,8,"05:00:00",48,0.5,26.96,1.3766666666666667,30,1.25,54,{"$f":"IF(AC6729<60,(60-AC6729)/24,0)","v":0.25},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,8,"13:00:00",55,0.20833333333333334,68,0,68,0,59,{"$f":"IF(AC6737<60,(60-AC6737)/24,0)","v":4.1666666666666664E-2},57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,8,"22:00:00",55,0.20833333333333334,59,4.1666666666666664E-2,46,0.58333333333333337,57,{"$f":"IF(AC6746<60,(60-AC6746)/24,0)","v":0.125},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,9,"03:00:00",54,0.25,48.02,0.49916666666666654,41,0.79166666666666663,55,{"$f":"IF(AC6751<60,(60-AC6751)/24,0)","v":0.20833333333333334},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,9,"15:00:00",54,0.25,57.02,0.12416666666666654,75,0,55,{"$f":"IF(AC6763<60,(60-AC6763)/24,0)","v":0.20833333333333334},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,9,"20:00:00",50,0.41666666666666669,46.04,0.58166666666666667,54,0.25,54,{"$f":"IF(AC6768<60,(60-AC6768)/24,0)","v":0.25},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,9,1,50,0.41666666666666669,42.98,0.70916666666666683,51.082599999999999,0.37155833333333338,54,{"$f":"IF(AC6772<60,(60-AC6772)/24,0)","v":0.25},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,10,"10:00:00",54,0.25,42.08,0.7466666666666667,57,0.125,55,{"$f":"IF(AC6782<60,(60-AC6782)/24,0)","v":0.20833333333333334},57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,10,"17:00:00",55,{"$f":"IF(W6789<60,(60-W6789)/24,0)","v":0.20833333333333334},46.94,0.5441666666666668,66,0,57,{"$f":"IF(AC6789<60,(60-AC6789)/24,0)","v":0.125},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,10,1,54,0.25,26.06,1.4141666666666666,49.048699999999997,0.45630416666666679,57,{"$f":"IF(AC6796<60,(60-AC6796)/24,0)","v":0.125},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,11,"10:00:00",57,0.125,46.04,0.58166666666666667,52,0.33333333333333331,59,{"$f":"IF(AC6806<60,(60-AC6806)/24,0)","v":4.1666666666666664E-2},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,11,"14:00:00",59,4.1666666666666664E-2,55.04,0.20666666666666669,73,0,63,{"$f":"IF(AC6810<60,(60-AC6810)/24,0)","v":0},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,12,"03:00:00",48,0.5,26.96,1.3766666666666667,45,0.625,52,{"$f":"IF(AC6823<60,(60-AC6823)/24,0)","v":0.33333333333333331},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,12,"04:00:00",48,0.5,28.94,1.2941666666666667,45,0.625,52,{"$f":"IF(AC6824<60,(60-AC6824)/24,0)","v":0.33333333333333331},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,12,"12:00:00",55,0.20833333333333334,55.94,0.16916666666666677,59,4.1666666666666664E-2,55,{"$f":"IF(AC6832<60,(60-AC6832)/24,0)","v":0.20833333333333334},57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,12,"21:00:00",43,0.70833333333333337,46.04,0.58166666666666667,56,0.16666666666666666,52,{"$f":"IF(AC6841<60,(60-AC6841)/24,0)","v":0.33333333333333331},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,13,"05:00:00",45,0.625,51.08,0.37166666666666676,47,0.54166666666666663,50,{"$f":"IF(AC6849<60,(60-AC6849)/24,0)","v":0.41666666666666669},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,13,"11:00:00",55,0.20833333333333334,57.92,8.66666666666666E-2,63,0,52,{"$f":"IF(AC6855<60,(60-AC6855)/24,0)","v":0.33333333333333331},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,13,"22:00:00",48,0.5,57.02,0.12416666666666654,43,0.70833333333333337,52,{"$f":"IF(AC6866<60,(60-AC6866)/24,0)","v":0.33333333333333331},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,14,"01:00:00",45,0.625,57.02,0.12416666666666654,37.133800000000001,0.95275833333333326,52,{"$f":"IF(AC6869<60,(60-AC6869)/24,0)","v":0.33333333333333331},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,14,"15:00:00",48,0.5,62.06,0,64,0,48,{"$f":"IF(AC6883<60,(60-AC6883)/24,0)","v":0.5},51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,14,"22:00:00",43,0.70833333333333337,59,4.1666666666666664E-2,54,0.25,46.014699999999998,{"$f":"IF(AC6890<60,(60-AC6890)/24,0)","v":0.58272083333333347},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,14,1,43,0.70833333333333337,55.04,0.20666666666666669,55,0.20833333333333334,46.014699999999998,{"$f":"IF(AC6892<60,(60-AC6892)/24,0)","v":0.58272083333333347},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,15,"09:00:00",45,0.625,51.98,0.33416666666666678,55,0.20833333333333334,48,{"$f":"IF(AC6901<60,(60-AC6901)/24,0)","v":0.5},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,15,"21:00:00",45,0.625,39.92,0.83666666666666656,48,0.5,48,{"$f":"IF(AC6913<60,(60-AC6913)/24,0)","v":0.5},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,16,"02:00:00",43,0.70833333333333337,30.92,{"$f":"IF(Y6918<60,(60-Y6918)/24,0)","v":1.2116666666666667},45,{"$f":"IF(AA6918<60,(60-AA6918)/24,0)","v":0.625},48,{"$f":"IF(AC6918<60,(60-AC6918)/24,0)","v":0.5},44.6,{"$f":"IF(AE6918<60,(60-AE6918)/24,0)","v":0.64166666666666661}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,16,"07:00:00",45,0.625,30.02,1.2491666666666668,39,0.875,48,{"$f":"IF(AC6923<60,(60-AC6923)/24,0)","v":0.5},51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,16,"19:00:00",46,0.58333333333333337,48.92,0.46166666666666661,39,0.875,45,{"$f":"IF(AC6935<60,(60-AC6935)/24,0)","v":0.625},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,16,"21:00:00",43,0.70833333333333337,46.94,0.5441666666666668,36,1,37,{"$f":"IF(AC6937<60,(60-AC6937)/24,0)","v":0.95833333333333337},57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,17,"04:00:00",28,1.3333333333333333,41,0.79166666666666663,28,1.3333333333333333,36.314900000000002,{"$f":"IF(AC6944<60,(60-AC6944)/24,0)","v":0.98687916666666664},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,17,"18:00:00",46,0.58333333333333337,44.96,0.62666666666666659,43,0.70833333333333337,54,{"$f":"IF(AC6958<60,(60-AC6958)/24,0)","v":0.25},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,17,"21:00:00",46,0.58333333333333337,44.06,0.66416666666666657,39,0.875,52,{"$f":"IF(AC6961<60,(60-AC6961)/24,0)","v":0.33333333333333331},49.1,0.45416666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,18,"08:00:00",46,0.58333333333333337,35.96,1.0016666666666667,39,0.875,52,{"$f":"IF(AC6972<60,(60-AC6972)/24,0)","v":0.33333333333333331},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,18,"14:00:00",77,0,50,0.41666666666666669,50,0.41666666666666669,75,{"$f":"IF(AC6978<60,(60-AC6978)/24,0)","v":0},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,18,"22:00:00",68,0,26.96,1.3766666666666667,34,1.0833333333333333,64,{"$f":"IF(AC6986<60,(60-AC6986)/24,0)","v":0},37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,19,"07:00:00",57,0.125,26.06,1.4141666666666666,34,1.0833333333333333,61,{"$f":"IF(AC6995<60,(60-AC6995)/24,0)","v":0},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,19,"15:00:00",55,0.20833333333333334,64.040000000000006,0,46,0.58333333333333337,63,{"$f":"IF(AC7003<60,(60-AC7003)/24,0)","v":0},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,19,"16:00:00",55,0.20833333333333334,62.06,0,46,0.58333333333333337,61,{"$f":"IF(AC7004<60,(60-AC7004)/24,0)","v":0},59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,20,"05:00:00",37,0.95833333333333337,33.979999999999997,1.0841666666666667,25,1.4583333333333333,36,{"$f":"IF(AC7017<60,(60-AC7017)/24,0)","v":1},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,20,"09:00:00",52,0.33333333333333331,46.94,0.5441666666666668,34,1.0833333333333333,55,{"$f":"IF(AC7021<60,(60-AC7021)/24,0)","v":0.20833333333333334},51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,20,"19:00:00",39,0.875,46.94,0.5441666666666668,39,0.875,52,{"$f":"IF(AC7031<60,(60-AC7031)/24,0)","v":0.33333333333333331},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,21,"02:00:00",39,0.875,44.06,0.66416666666666657,43,0.70833333333333337,39,{"$f":"IF(AC7038<60,(60-AC7038)/24,0)","v":0.875},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,21,"09:00:00",39,{"$f":"IF(W7045<60,(60-W7045)/24,0)","v":0.875},42.08,0.7466666666666667,55,0.20833333333333334,45,{"$f":"IF(AC7045<60,(60-AC7045)/24,0)","v":0.625},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,21,"19:00:00",39,0.875,53.06,0.28916666666666657,52,0.33333333333333331,45,{"$f":"IF(AC7055<60,(60-AC7055)/24,0)","v":0.625},37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,22,"02:00:00",37,0.95833333333333337,42.98,0.70916666666666683,41,0.79166666666666663,39,{"$f":"IF(AC7062<60,(60-AC7062)/24,0)","v":0.875},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,22,"04:00:00",36,1,37.04,0.95666666666666667,39,0.875,37,{"$f":"IF(AC7064<60,(60-AC7064)/24,0)","v":0.95833333333333337},28.22,1.3241666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,22,"16:00:00",43,0.70833333333333337,68,0,36,1,46,{"$f":"IF(AC7076<60,(60-AC7076)/24,0)","v":0.58333333333333337},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,22,"21:00:00",43,0.70833333333333337,46.04,0.58166666666666667,34,1.0833333333333333,45,{"$f":"IF(AC7081<60,(60-AC7081)/24,0)","v":0.625},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,23,"06:00:00",28,1.3333333333333333,44.06,0.66416666666666657,32,1.1666666666666667,30,{"$f":"IF(AC7090<60,(60-AC7090)/24,0)","v":1.25},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,23,"14:00:00",54,0.25,71.06,0,39,0.875,55,{"$f":"IF(AC7098<60,(60-AC7098)/24,0)","v":0.20833333333333334},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,23,"20:00:00",43,0.70833333333333337,51.98,0.33416666666666678,36,1,46,{"$f":"IF(AC7104<60,(60-AC7104)/24,0)","v":0.58333333333333337},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,24,"07:00:00",30,1.25,37.94,0.9191666666666668,28,1.3333333333333333,34,{"$f":"IF(AC7115<60,(60-AC7115)/24,0)","v":1.0833333333333333},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,24,"13:00:00",64,0,51.98,0.33416666666666678,41,0.79166666666666663,70,{"$f":"IF(AC7121<60,(60-AC7121)/24,0)","v":0},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,24,"16:00:00",66,0,50,0.41666666666666669,45,0.625,66,{"$f":"IF(AC7124<60,(60-AC7124)/24,0)","v":0},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,25,"03:00:00",55,0.20833333333333334,24.08,1.4966666666666668,25,1.4583333333333333,46,{"$f":"IF(AC7135<60,(60-AC7135)/24,0)","v":0.58333333333333337},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,25,"09:00:00",48,0.5,39.92,0.83666666666666656,34,1.0833333333333333,55,{"$f":"IF(AC7141<60,(60-AC7141)/24,0)","v":0.20833333333333334},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,25,"17:00:00",46,0.58333333333333337,50,0.41666666666666669,52,0.33333333333333331,55,{"$f":"IF(AC7149<60,(60-AC7149)/24,0)","v":0.20833333333333334},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,26,"02:00:00",21,1.625,35.06,1.0391666666666666,46,0.58333333333333337,28.2209,{"$f":"IF(AC7158<60,(60-AC7158)/24,0)","v":1.3241291666666666},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,26,"07:00:00",21,1.625,33.979999999999997,1.0841666666666667,52,0.33333333333333331,30.217700000000001,{"$f":"IF(AC7163<60,(60-AC7163)/24,0)","v":1.2409291666666666},34.340000000000003,1.0691666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,26,"19:00:00",30,1.25,44.96,0.62666666666666659,63,0,34,{"$f":"IF(AC7175<60,(60-AC7175)/24,0)","v":1.0833333333333333},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,27,"04:00:00",19,1.7083333333333333,44.96,0.62666666666666659,61,0,34,{"$f":"IF(AC7184<60,(60-AC7184)/24,0)","v":1.0833333333333333},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,27,"06:00:00",19,1.7083333333333333,44.96,0.62666666666666659,61,0,36,{"$f":"IF(AC7186<60,(60-AC7186)/24,0)","v":1},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,27,"13:00:00",50,0.41666666666666669,48.02,0.49916666666666654,64,0,52,{"$f":"IF(AC7193<60,(60-AC7193)/24,0)","v":0.33333333333333331},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,27,"20:00:00",36,1,46.94,0.5441666666666668,55,0.20833333333333334,36,{"$f":"IF(AC7200<60,(60-AC7200)/24,0)","v":1},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,28,"06:00:00",25,1.4583333333333333,46.94,0.5441666666666668,41,0.79166666666666663,39.075600000000001,{"$f":"IF(AC7210<60,(60-AC7210)/24,0)","v":0.8718499999999999},37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,28,"13:00:00",48,0.5,60.98,0,55,0.20833333333333334,52,{"$f":"IF(AC7217<60,(60-AC7217)/24,0)","v":0.33333333333333331},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,28,"23:00:00",46,0.58333333333333337,39.92,0.83666666666666656,45,0.625,43,{"$f":"IF(AC7227<60,(60-AC7227)/24,0)","v":0.70833333333333337},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,29,"03:00:00",41,0.79166666666666663,33.08,1.1216666666666668,45,0.625,46,{"$f":"IF(AC7231<60,(60-AC7231)/24,0)","v":0.58333333333333337},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,29,"16:00:00",43,0.70833333333333337,66.92,0,52,0.33333333333333331,46,{"$f":"IF(AC7244<60,(60-AC7244)/24,0)","v":0.58333333333333337},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,29,"17:00:00",43,0.70833333333333337,60.98,0,51,0.375,46,{"$f":"IF(AC7245<60,(60-AC7245)/24,0)","v":0.58333333333333337},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,30,"01:00:00",39,0.875,55.04,0.20666666666666669,45,0.625,42,{"$f":"IF(AC7253<60,(60-AC7253)/24,0)","v":0.75},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,30,"14:00:00",39,0.875,53.06,0.28916666666666657,55,0.20833333333333334,48,{"$f":"IF(AC7266<60,(60-AC7266)/24,0)","v":0.5},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,30,"18:00:00",37,0.95833333333333337,39.92,0.83666666666666656,43,0.70833333333333337,46,{"$f":"IF(AC7270<60,(60-AC7270)/24,0)","v":0.58333333333333337},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,30,1,39,0.875,28.94,1.2941666666666667,34,1.0833333333333333,45,{"$f":"IF(AC7276<60,(60-AC7276)/24,0)","v":0.625},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,31,"11:00:00",45,0.625,39.92,0.83666666666666656,54,0.25,46,{"$f":"IF(AC7287<60,(60-AC7287)/24,0)","v":0.58333333333333337},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,31,"14:00:00",46,0.58333333333333337,46.94,0.5441666666666668,64,0,46,{"$f":"IF(AC7290<60,(60-AC7290)/24,0)","v":0.58333333333333337},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,1,"04:00:00",43,0.70833333333333337,57.02,0.12416666666666654,42,0.75,52,{"$f":"IF(AC7304<60,(60-AC7304)/24,0)","v":0.33333333333333331},51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,1,"11:00:00",63,0,57.02,0.12416666666666654,57,0.125,55,{"$f":"IF(AC7311<60,(60-AC7311)/24,0)","v":0.20833333333333334},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,1,"13:00:00",64,0,57.02,0.12416666666666654,64,0,58,{"$f":"IF(AC7313<60,(60-AC7313)/24,0)","v":8.3333333333333329E-2},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,2,"01:00:00",45,0.625,39.020000000000003,0.87416666666666654,36,1,58,{"$f":"IF(AC7325<60,(60-AC7325)/24,0)","v":8.3333333333333329E-2},57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,2,"06:00:00",43,0.70833333333333337,33.979999999999997,1.0841666666666667,43,0.70833333333333337,51,{"$f":"IF(AC7330<60,(60-AC7330)/24,0)","v":0.375},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,2,"11:00:00",39,0.875,50,0.41666666666666669,57,0.125,47,{"$f":"IF(AC7335<60,(60-AC7335)/24,0)","v":0.54166666666666663},62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,2,"23:00:00",37,0.95833333333333337,42.08,0.7466666666666667,64,0,45,{"$f":"IF(AC7347<60,(60-AC7347)/24,0)","v":0.625},60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,3,"08:00:00",34,1.0833333333333333,41,0.79166666666666663,63,0,36,{"$f":"IF(AC7356<60,(60-AC7356)/24,0)","v":1},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,3,"16:00:00",55,0.20833333333333334,41,0.79166666666666663,50,0.41666666666666669,58,{"$f":"IF(AC7364<60,(60-AC7364)/24,0)","v":8.3333333333333329E-2},57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,3,"22:00:00",55,0.20833333333333334,35.06,1.0391666666666666,45,0.625,44,{"$f":"IF(AC7370<60,(60-AC7370)/24,0)","v":0.66666666666666663},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,4,"01:00:00",48,0.5,32,1.1666666666666667,41,0.79166666666666663,44,{"$f":"IF(AC7373<60,(60-AC7373)/24,0)","v":0.66666666666666663},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,4,"12:00:00",50,0.41666666666666669,35.96,1.0016666666666667,46,0.58333333333333337,62,{"$f":"IF(AC7384<60,(60-AC7384)/24,0)","v":0},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,4,"18:00:00",43,0.70833333333333337,28.04,1.3316666666666668,41,0.79166666666666663,55,{"$f":"IF(AC7390<60,(60-AC7390)/24,0)","v":0.20833333333333334},51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,5,"02:00:00",34,1.0833333333333333,26.06,1.4141666666666666,34,1.0833333333333333,56,{"$f":"IF(AC7398<60,(60-AC7398)/24,0)","v":0.16666666666666666},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,5,"11:00:00",43,0.70833333333333337,42.98,0.70916666666666683,48,0.5,67,{"$f":"IF(AC7407<60,(60-AC7407)/24,0)","v":0},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,5,"19:00:00",46,0.58333333333333337,41,0.79166666666666663,54,0.25,60,{"$f":"IF(AC7415<60,(60-AC7415)/24,0)","v":0},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,6,"04:00:00",37.140599999999999,0.95247500000000007,42.08,0.7466666666666667,39,0.875,56,{"$f":"IF(AC7424<60,(60-AC7424)/24,0)","v":0.16666666666666666},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,6,"09:00:00",45,{"$f":"IF(W7429<60,(60-W7429)/24,0)","v":0.625},46.94,0.5441666666666668,54,0.25,55,{"$f":"IF(AC7429<60,(60-AC7429)/24,0)","v":0.20833333333333334},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,6,"13:00:00",48,0.5,51.08,0.37166666666666676,57,0.125,52,{"$f":"IF(AC7433<60,(60-AC7433)/24,0)","v":0.33333333333333331},53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,6,"22:00:00",48,0.5,46.94,0.5441666666666668,45,0.625,57,{"$f":"IF(AC7442<60,(60-AC7442)/24,0)","v":0.125},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,7,"08:00:00",47,0.54166666666666663,37.04,0.95666666666666667,37,0.95833333333333337,42,{"$f":"IF(AC7452<60,(60-AC7452)/24,0)","v":0.75},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,7,"15:00:00",48,0.5,53.06,0.28916666666666657,39,0.875,53,{"$f":"IF(AC7459<60,(60-AC7459)/24,0)","v":0.29166666666666669},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,7,"22:00:00",43,0.70833333333333337,46.04,0.58166666666666667,34,1.0833333333333333,30,{"$f":"IF(AC7466<60,(60-AC7466)/24,0)","v":1.25},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,8,"08:00:00",39,0.875,44.96,0.62666666666666659,28,1.3333333333333333,42,{"$f":"IF(AC7476<60,(60-AC7476)/24,0)","v":0.75},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,8,"12:00:00",43,0.70833333333333337,44.96,0.62666666666666659,37,0.95833333333333337,58,{"$f":"IF(AC7480<60,(60-AC7480)/24,0)","v":8.3333333333333329E-2},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,8,"17:00:00",39,0.875,44.06,0.66416666666666657,36,1,54,{"$f":"IF(AC7485<60,(60-AC7485)/24,0)","v":0.25},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,9,"02:00:00",27,1.375,44.06,{"$f":"IF(Y7494<60,(60-Y7494)/24,0)","v":0.66416666666666657},30,{"$f":"IF(AA7494<60,(60-AA7494)/24,0)","v":1.25},46,{"$f":"IF(AC7494<60,(60-AC7494)/24,0)","v":0.58333333333333337},42.8,{"$f":"IF(AE7494<60,(60-AE7494)/24,0)","v":0.71666666666666679}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,9,"10:00:00",34,1.0833333333333333,44.96,0.62666666666666659,43,0.70833333333333337,50,{"$f":"IF(AC7502<60,(60-AC7502)/24,0)","v":0.41666666666666669},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,9,"19:00:00",34,1.0833333333333333,51.08,0.37166666666666676,52,0.33333333333333331,50,{"$f":"IF(AC7511<60,(60-AC7511)/24,0)","v":0.41666666666666669},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,10,"03:00:00",37.213900000000002,0.94942083333333327,33.08,1.1216666666666668,57,0.125,41,{"$f":"IF(AC7519<60,(60-AC7519)/24,0)","v":0.79166666666666663},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,10,"09:00:00",39,0.875,42.08,0.7466666666666667,61,0,47,{"$f":"IF(AC7525<60,(60-AC7525)/24,0)","v":0.54166666666666663},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,10,"20:00:00",30,1.25,44.06,0.66416666666666657,55,0.20833333333333334,38,{"$f":"IF(AC7536<60,(60-AC7536)/24,0)","v":0.91666666666666663},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,10,"23:00:00",28,1.3333333333333333,33.979999999999997,1.0841666666666667,46,0.58333333333333337,35,{"$f":"IF(AC7539<60,(60-AC7539)/24,0)","v":1.0416666666666667},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,11,"05:00:00",27,1.375,33.08,1.1216666666666668,36,1,35,{"$f":"IF(AC7545<60,(60-AC7545)/24,0)","v":1.0416666666666667},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,11,"13:00:00",32,1.1666666666666667,50,0.41666666666666669,37,0.95833333333333337,42,{"$f":"IF(AC7553<60,(60-AC7553)/24,0)","v":0.75},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,11,"22:00:00",28,1.3333333333333333,48.02,0.49916666666666654,25,1.4583333333333333,31,{"$f":"IF(AC7562<60,(60-AC7562)/24,0)","v":1.2083333333333333},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,12,"06:00:00",21,1.625,42.98,0.70916666666666683,19,1.7083333333333333,24,{"$f":"IF(AC7570<60,(60-AC7570)/24,0)","v":1.5},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,12,"15:00:00",43,0.70833333333333337,42.08,0.7466666666666667,43,0.70833333333333337,52,{"$f":"IF(AC7579<60,(60-AC7579)/24,0)","v":0.33333333333333331},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,12,"20:00:00",27,1.375,33.08,1.1216666666666668,43,0.70833333333333337,34,{"$f":"IF(AC7584<60,(60-AC7584)/24,0)","v":1.0833333333333333},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,13,"08:00:00",25,1.4583333333333333,26.06,1.4141666666666666,37.133800000000001,0.95275833333333326,35,{"$f":"IF(AC7596<60,(60-AC7596)/24,0)","v":1.0416666666666667},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,13,"10:00:00",34,1.0833333333333333,32,1.1666666666666667,41,0.79166666666666663,44,{"$f":"IF(AC7598<60,(60-AC7598)/24,0)","v":0.66666666666666663},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,13,"17:00:00",37,0.95833333333333337,37.04,0.95666666666666667,45,0.625,50,{"$f":"IF(AC7605<60,(60-AC7605)/24,0)","v":0.41666666666666669},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,14,"07:00:00",39,0.875,26.96,1.3766666666666667,37,0.95833333333333337,34,{"$f":"IF(AC7619<60,(60-AC7619)/24,0)","v":1.0833333333333333},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,14,"10:00:00",52,0.33333333333333331,48.02,{"$f":"IF(Y7622<60,(60-Y7622)/24,0)","v":0.49916666666666654},48,{"$f":"IF(AA7622<60,(60-AA7622)/24,0)","v":0.5},43,{"$f":"IF(AC7622<60,(60-AC7622)/24,0)","v":0.70833333333333337},24.8,{"$f":"IF(AE7622<60,(60-AE7622)/24,0)","v":1.4666666666666668}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,14,"17:00:00",39,0.875,64.040000000000006,0,48,0.5,54,{"$f":"IF(AC7629<60,(60-AC7629)/24,0)","v":0.25},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,15,"03:00:00",25,1.4583333333333333,57.92,8.66666666666666E-2,37,0.95833333333333337,53,{"$f":"IF(AC7639<60,(60-AC7639)/24,0)","v":0.29166666666666669},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,15,"07:00:00",28,1.3333333333333333,57.02,0.12416666666666654,37,0.95833333333333337,56,{"$f":"IF(AC7643<60,(60-AC7643)/24,0)","v":0.16666666666666666},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,15,"20:00:00",34.129800000000003,1.0779249999999998,60.08,0,34,1.0833333333333333,41,{"$f":"IF(AC7656<60,(60-AC7656)/24,0)","v":0.79166666666666663},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,16,"04:00:00",36,1,62.96,0,30,1.25,35,{"$f":"IF(AC7664<60,(60-AC7664)/24,0)","v":1.0416666666666667},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,16,"05:00:00",36,1,62.06,0,30,1.25,33,{"$f":"IF(AC7665<60,(60-AC7665)/24,0)","v":1.125},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,16,"18:00:00",57,0.125,57.02,0.12416666666666654,34,1.0833333333333333,37,{"$f":"IF(AC7678<60,(60-AC7678)/24,0)","v":0.95833333333333337},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,16,"22:00:00",45,0.625,42.98,0.70916666666666683,32,1.1666666666666667,30,{"$f":"IF(AC7682<60,(60-AC7682)/24,0)","v":1.25},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,17,"04:00:00",39,0.875,37.04,0.95666666666666667,30,1.25,24,{"$f":"IF(AC7688<60,(60-AC7688)/24,0)","v":1.5},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,17,"15:00:00",37,0.95833333333333337,41,0.79166666666666663,37,0.95833333333333337,50,{"$f":"IF(AC7699<60,(60-AC7699)/24,0)","v":0.41666666666666669},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,17,1,32,1.1666666666666667,26.06,1.4141666666666666,25,1.4583333333333333,30,{"$f":"IF(AC7708<60,(60-AC7708)/24,0)","v":1.25},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,18,"07:00:00",25,1.4583333333333333,28.04,1.3316666666666668,34,1.0833333333333333,32,{"$f":"IF(AC7715<60,(60-AC7715)/24,0)","v":1.1666666666666667},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,18,"17:00:00",25,1.4583333333333333,37.94,0.9191666666666668,36,1,44,{"$f":"IF(AC7725<60,(60-AC7725)/24,0)","v":0.66666666666666663},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,18,1,14,1.9166666666666667,30.02,1.2491666666666668,30,1.25,43,{"$f":"IF(AC7732<60,(60-AC7732)/24,0)","v":0.70833333333333337},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,19,"02:00:00",14,1.9166666666666667,28.94,1.2941666666666667,30,1.25,41,{"$f":"IF(AC7734<60,(60-AC7734)/24,0)","v":0.79166666666666663},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,19,"14:00:00",36,1,35.06,1.0391666666666666,59,4.1666666666666664E-2,54,{"$f":"IF(AC7746<60,(60-AC7746)/24,0)","v":0.25},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,19,"19:00:00",21,1.625,28.94,1.2941666666666667,48,0.5,40,{"$f":"IF(AC7751<60,(60-AC7751)/24,0)","v":0.83333333333333337},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,20,"04:00:00",19,1.7083333333333333,28.04,1.3316666666666668,34,1.0833333333333333,35,{"$f":"IF(AC7760<60,(60-AC7760)/24,0)","v":1.0416666666666667},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,20,"12:00:00",43,0.70833333333333337,35.06,1.0391666666666666,63,0,46,{"$f":"IF(AC7768<60,(60-AC7768)/24,0)","v":0.58333333333333337},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,20,"18:00:00",37,0.95833333333333337,39.92,0.83666666666666656,61,0,32,{"$f":"IF(AC7774<60,(60-AC7774)/24,0)","v":1.1666666666666667},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,21,"05:00:00",37,0.95833333333333337,33.08,1.1216666666666668,37,0.95833333333333337,27,{"$f":"IF(AC7785<60,(60-AC7785)/24,0)","v":1.375},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,21,"11:00:00",52,0.33333333333333331,28.04,1.3316666666666668,50,0.41666666666666669,39,{"$f":"IF(AC7791<60,(60-AC7791)/24,0)","v":0.875},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,21,"14:00:00",54,0.25,24.98,1.4591666666666665,55,0.20833333333333334,45,{"$f":"IF(AC7794<60,(60-AC7794)/24,0)","v":0.625},51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,22,"01:00:00",34,1.0833333333333333,19.940000000000001,1.6691666666666667,43,0.70833333333333337,47,{"$f":"IF(AC7805<60,(60-AC7805)/24,0)","v":0.54166666666666663},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,22,"07:00:00",36,1,19.04,1.7066666666666668,43,0.70833333333333337,49,{"$f":"IF(AC7811<60,(60-AC7811)/24,0)","v":0.45833333333333331},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,22,"15:00:00",36,1,28.04,1.3316666666666668,66,0,45,{"$f":"IF(AC7819<60,(60-AC7819)/24,0)","v":0.625},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,22,1,27,1.375,23,1.5416666666666667,54,0.25,35,{"$f":"IF(AC7828<60,(60-AC7828)/24,0)","v":1.0416666666666667},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,23,"05:00:00",21,1.625,21.02,1.6241666666666668,54,0.25,32,{"$f":"IF(AC7833<60,(60-AC7833)/24,0)","v":1.1666666666666667},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,23,"17:00:00",18,1.75,17.96,1.7516666666666667,59,4.1666666666666664E-2,24,{"$f":"IF(AC7845<60,(60-AC7845)/24,0)","v":1.5},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,23,"22:00:00",14,1.9166666666666667,10.94,2.0441666666666669,50,0.41666666666666669,20,{"$f":"IF(AC7850<60,(60-AC7850)/24,0)","v":1.6666666666666667},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,24,"02:00:00",3,2.375,1.04,2.4566666666666666,52,0.33333333333333331,19,{"$f":"IF(AC7854<60,(60-AC7854)/24,0)","v":1.7083333333333333},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,24,"12:00:00",23,1.5416666666666667,26.06,1.4141666666666666,66,0,27,{"$f":"IF(AC7864<60,(60-AC7864)/24,0)","v":1.375},37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,24,"19:00:00",21,1.625,21.92,1.5866666666666667,63,0,26,{"$f":"IF(AC7871<60,(60-AC7871)/24,0)","v":1.4166666666666667},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,25,"02:00:00",17,1.7916666666666667,12.92,{"$f":"IF(Y7878<60,(60-Y7878)/24,0)","v":1.9616666666666667},54,{"$f":"IF(AA7878<60,(60-AA7878)/24,0)","v":0.25},28,{"$f":"IF(AC7878<60,(60-AC7878)/24,0)","v":1.3333333333333333},21.2,{"$f":"IF(AE7878<60,(60-AE7878)/24,0)","v":1.6166666666666665}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,25,"12:00:00",19,1.7083333333333333,28.94,1.2941666666666667,46,0.58333333333333337,44,{"$f":"IF(AC7888<60,(60-AC7888)/24,0)","v":0.66666666666666663},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,25,"16:00:00",21,1.625,30.92,1.2116666666666667,45,0.625,39,{"$f":"IF(AC7892<60,(60-AC7892)/24,0)","v":0.875},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,26,"05:00:00",7,2.2083333333333335,30.02,1.2491666666666668,43,0.70833333333333337,28,{"$f":"IF(AC7905<60,(60-AC7905)/24,0)","v":1.3333333333333333},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,26,"06:00:00",5,2.2916666666666665,30.02,1.2491666666666668,45,0.625,28,{"$f":"IF(AC7906<60,(60-AC7906)/24,0)","v":1.3333333333333333},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,26,"14:00:00",23,1.5416666666666667,37.04,0.95666666666666667,46,0.58333333333333337,34,{"$f":"IF(AC7914<60,(60-AC7914)/24,0)","v":1.0833333333333333},49.28,0.4466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,26,"23:00:00",21,1.625,37.94,0.9191666666666668,61,0,20,{"$f":"IF(AC7923<60,(60-AC7923)/24,0)","v":1.6666666666666667},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,27,"07:00:00",18,1.75,24.08,1.4966666666666668,55,0.20833333333333334,13.5901,{"$f":"IF(AC7931<60,(60-AC7931)/24,0)","v":1.9337458333333333},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,27,"13:00:00",30,1.25,33.979999999999997,1.0841666666666667,50,0.41666666666666669,30,{"$f":"IF(AC7937<60,(60-AC7937)/24,0)","v":1.25},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,27,1,28,1.3333333333333333,28.94,1.2941666666666667,34,1.0833333333333333,29,{"$f":"IF(AC7948<60,(60-AC7948)/24,0)","v":1.2916666666666667},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,28,"03:00:00",30,1.25,30.92,1.2116666666666667,39,0.875,31,{"$f":"IF(AC7951<60,(60-AC7951)/24,0)","v":1.2083333333333333},21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,28,"17:00:00",34,1.0833333333333333,48.92,0.46166666666666661,43,0.70833333333333337,36,{"$f":"IF(AC7965<60,(60-AC7965)/24,0)","v":1},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,28,1,30,1.25,33.08,1.1216666666666668,36,1,43,{"$f":"IF(AC7972<60,(60-AC7972)/24,0)","v":0.70833333333333337},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,29,"02:00:00",37.398499999999999,0.94172916666666673,32,1.1666666666666667,30,1.25,43,{"$f":"IF(AC7974<60,(60-AC7974)/24,0)","v":0.70833333333333337},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,29,"11:00:00",48,0.5,19.04,1.7066666666666668,39,0.875,47,{"$f":"IF(AC7983<60,(60-AC7983)/24,0)","v":0.54166666666666663},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,29,"23:00:00",50,0.41666666666666669,14,1.9166666666666667,28,1.3333333333333333,39,{"$f":"IF(AC7995<60,(60-AC7995)/24,0)","v":0.875},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,30,"04:00:00",52,0.33333333333333331,15.98,1.8341666666666665,28,1.3333333333333333,33,{"$f":"IF(AC8000<60,(60-AC8000)/24,0)","v":1.125},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,30,"09:00:00",54,{"$f":"IF(W8005<60,(60-W8005)/24,0)","v":0.25},19.04,1.7066666666666668,30,1.25,34,{"$f":"IF(AC8005<60,(60-AC8005)/24,0)","v":1.0833333333333333},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,30,"21:00:00",39,0.875,26.06,1.4141666666666666,27,1.375,34,{"$f":"IF(AC8017<60,(60-AC8017)/24,0)","v":1.0833333333333333},37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,30,"23:00:00",38,0.91666666666666663,27.68,1.3466666666666667,30,1.25,34,{"$f":"IF(AC8019<60,(60-AC8019)/24,0)","v":1.0833333333333333},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,1,"06:00:00",36,1,30.92,1.2116666666666667,32,1.1666666666666667,34,{"$f":"IF(AC8026<60,(60-AC8026)/24,0)","v":1.0833333333333333},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,1,"20:00:00",46,0.58333333333333337,35.06,1.0391666666666666,39,0.875,25,{"$f":"IF(AC8040<60,(60-AC8040)/24,0)","v":1.4583333333333333},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,1,"23:00:00",47,0.54166666666666663,35.06,1.0391666666666666,37,0.95833333333333337,24,{"$f":"IF(AC8043<60,(60-AC8043)/24,0)","v":1.5},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,2,"10:00:00",45.107900000000001,0.62050416666666663,42.08,0.7466666666666667,37,0.95833333333333337,30,{"$f":"IF(AC8054<60,(60-AC8054)/24,0)","v":1.25},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,2,"16:00:00",34,1.0833333333333333,37.04,0.95666666666666667,36,1,32,{"$f":"IF(AC8060<60,(60-AC8060)/24,0)","v":1.1666666666666667},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,2,1,30,1.25,28.04,1.3316666666666668,28,1.3333333333333333,27,{"$f":"IF(AC8068<60,(60-AC8068)/24,0)","v":1.375},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,3,"09:00:00",32,1.1666666666666667,23,1.5416666666666667,28,1.3333333333333333,28,{"$f":"IF(AC8077<60,(60-AC8077)/24,0)","v":1.3333333333333333},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,3,"17:00:00",28,1.3333333333333333,24.08,1.4966666666666668,30,1.25,37,{"$f":"IF(AC8085<60,(60-AC8085)/24,0)","v":0.95833333333333337},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,3,"18:00:00",27,1.375,23,1.5416666666666667,28,1.3333333333333333,34,{"$f":"IF(AC8086<60,(60-AC8086)/24,0)","v":1.0833333333333333},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,4,"07:00:00",28,1.3333333333333333,15.08,1.8716666666666668,25,1.4583333333333333,28,{"$f":"IF(AC8099<60,(60-AC8099)/24,0)","v":1.3333333333333333},37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,4,"11:00:00",34,1.0833333333333333,26.96,1.3766666666666667,25,1.4583333333333333,36,{"$f":"IF(AC8103<60,(60-AC8103)/24,0)","v":1},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,4,"21:00:00",32,1.1666666666666667,24.08,1.4966666666666668,18,1.75,36,{"$f":"IF(AC8113<60,(60-AC8113)/24,0)","v":1},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,5,"04:00:00",27,1.375,21.02,1.6241666666666668,16,1.8333333333333333,33,{"$f":"IF(AC8120<60,(60-AC8120)/24,0)","v":1.125},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,5,"11:00:00",32,1.1666666666666667,30.02,1.2491666666666668,30,1.25,34,{"$f":"IF(AC8127<60,(60-AC8127)/24,0)","v":1.0833333333333333},55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,5,"21:00:00",28,1.3333333333333333,28.94,1.2941666666666667,23,1.5416666666666667,28.148099999999999,{"$f":"IF(AC8137<60,(60-AC8137)/24,0)","v":1.3271625},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,6,"04:00:00",27,1.375,28.94,1.2941666666666667,23,1.5416666666666667,29,{"$f":"IF(AC8144<60,(60-AC8144)/24,0)","v":1.2916666666666667},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,6,"06:00:00",28,1.3333333333333333,28.04,1.3316666666666668,23,1.5416666666666667,30,{"$f":"IF(AC8146<60,(60-AC8146)/24,0)","v":1.25},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,6,"18:00:00",28,1.3333333333333333,30.92,1.2116666666666667,28,1.3333333333333333,32,{"$f":"IF(AC8158<60,(60-AC8158)/24,0)","v":1.1666666666666667},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,6,"23:00:00",27,1.375,28.04,1.3316666666666668,25,1.4583333333333333,31,{"$f":"IF(AC8163<60,(60-AC8163)/24,0)","v":1.2083333333333333},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,7,"08:00:00",27,1.375,15.98,1.8341666666666665,21,1.625,32,{"$f":"IF(AC8172<60,(60-AC8172)/24,0)","v":1.1666666666666667},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,7,"16:00:00",30,1.25,30.92,1.2116666666666667,25,1.4583333333333333,37,{"$f":"IF(AC8180<60,(60-AC8180)/24,0)","v":0.95833333333333337},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,7,"22:00:00",28,1.3333333333333333,19.940000000000001,1.6691666666666667,18,1.75,37,{"$f":"IF(AC8186<60,(60-AC8186)/24,0)","v":0.95833333333333337},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,8,"09:00:00",30,{"$f":"IF(W8197<60,(60-W8197)/24,0)","v":1.25},35.06,1.0391666666666666,14,1.9166666666666667,32,{"$f":"IF(AC8197<60,(60-AC8197)/24,0)","v":1.1666666666666667},37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,8,"15:00:00",34,1.0833333333333333,39.020000000000003,0.87416666666666654,30,1.25,37,{"$f":"IF(AC8203<60,(60-AC8203)/24,0)","v":0.95833333333333337},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,8,"18:00:00",30,1.25,37.04,0.95666666666666667,19,1.7083333333333333,27,{"$f":"IF(AC8206<60,(60-AC8206)/24,0)","v":1.375},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,9,"05:00:00",12,2,23,1.5416666666666667,18,1.75,14,{"$f":"IF(AC8217<60,(60-AC8217)/24,0)","v":1.9166666666666667},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,9,"11:00:00",23,1.5416666666666667,35.96,1.0016666666666667,24,1.5,27,{"$f":"IF(AC8223<60,(60-AC8223)/24,0)","v":1.375},37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,9,"19:00:00",28,1.3333333333333333,28.94,1.2941666666666667,25,1.4583333333333333,25,{"$f":"IF(AC8231<60,(60-AC8231)/24,0)","v":1.4583333333333333},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,10,"04:00:00",27,1.375,26.06,1.4141666666666666,27,1.375,17,{"$f":"IF(AC8240<60,(60-AC8240)/24,0)","v":1.7916666666666667},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,10,"13:00:00",28,1.3333333333333333,33.979999999999997,1.0841666666666667,36,1,27,{"$f":"IF(AC8249<60,(60-AC8249)/24,0)","v":1.375},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,10,"18:00:00",21,1.625,32,1.1666666666666667,30,1.25,27,{"$f":"IF(AC8254<60,(60-AC8254)/24,0)","v":1.375},50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,11,"06:00:00",21,1.625,32,1.1666666666666667,14,1.9166666666666667,12,{"$f":"IF(AC8266<60,(60-AC8266)/24,0)","v":2},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,11,"08:00:00",21,1.625,28.94,1.2941666666666667,10,2.0833333333333335,10,{"$f":"IF(AC8268<60,(60-AC8268)/24,0)","v":2.0833333333333335},37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,11,"15:00:00",30,1.25,33.08,1.1216666666666668,36,1,34,{"$f":"IF(AC8275<60,(60-AC8275)/24,0)","v":1.0833333333333333},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,11,"22:00:00",19,1.7083333333333333,32,1.1666666666666667,19,1.7083333333333333,18,{"$f":"IF(AC8282<60,(60-AC8282)/24,0)","v":1.75},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,12,"08:00:00",28,1.3333333333333333,32,1.1666666666666667,25,1.4583333333333333,19,{"$f":"IF(AC8292<60,(60-AC8292)/24,0)","v":1.7083333333333333},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,12,"15:00:00",32,1.1666666666666667,37.04,0.95666666666666667,32,1.1666666666666667,34,{"$f":"IF(AC8299<60,(60-AC8299)/24,0)","v":1.0833333333333333},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,13,"01:00:00",32,1.1666666666666667,17.96,1.7516666666666667,12,2,30,{"$f":"IF(AC8309<60,(60-AC8309)/24,0)","v":1.25},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,13,"05:00:00",30,1.25,15.98,1.8341666666666665,7,2.2083333333333335,29,{"$f":"IF(AC8313<60,(60-AC8313)/24,0)","v":1.2916666666666667},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,13,"18:00:00",31,1.2083333333333333,28.04,{"$f":"IF(Y8326<60,(60-Y8326)/24,0)","v":1.3316666666666668},10,{"$f":"IF(AA8326<60,(60-AA8326)/24,0)","v":2.0833333333333335},34,{"$f":"IF(AC8326<60,(60-AC8326)/24,0)","v":1.0833333333333333},42.8,{"$f":"IF(AE8326<60,(60-AE8326)/24,0)","v":0.71666666666666679}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,13,"19:00:00",30,1.25,28.04,1.3316666666666668,9,2.125,34,{"$f":"IF(AC8327<60,(60-AC8327)/24,0)","v":1.0833333333333333},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,14,"03:00:00",32.26,1.1558333333333335,30.02,1.2491666666666668,-9,2.875,29,{"$f":"IF(AC8335<60,(60-AC8335)/24,0)","v":1.2916666666666667},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,14,"16:00:00",34,1.0833333333333333,23,1.5416666666666667,18,1.75,21,{"$f":"IF(AC8348<60,(60-AC8348)/24,0)","v":1.625},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,14,"20:00:00",32,1.1666666666666667,17.96,1.7516666666666667,3,2.375,16,{"$f":"IF(AC8352<60,(60-AC8352)/24,0)","v":1.8333333333333333},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,15,"02:00:00",32,1.1666666666666667,15.08,1.8716666666666668,-8,2.8333333333333335,8,{"$f":"IF(AC8358<60,(60-AC8358)/24,0)","v":2.1666666666666665},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,15,"13:00:00",34,1.0833333333333333,23,1.5416666666666667,21,1.625,18,{"$f":"IF(AC8369<60,(60-AC8369)/24,0)","v":1.75},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,15,"16:00:00",36,1,24.98,1.4591666666666665,21,1.625,23,{"$f":"IF(AC8372<60,(60-AC8372)/24,0)","v":1.5416666666666667},37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,16,"06:00:00",25,1.4583333333333333,17.96,1.7516666666666667,27,1.375,8,{"$f":"IF(AC8386<60,(60-AC8386)/24,0)","v":2.1666666666666665},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,16,"13:00:00",36,1,33.08,1.1216666666666668,34,1.0833333333333333,33,{"$f":"IF(AC8393<60,(60-AC8393)/24,0)","v":1.125},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,16,"15:00:00",36,1,33.08,1.1216666666666668,30,1.25,41,{"$f":"IF(AC8395<60,(60-AC8395)/24,0)","v":0.79166666666666663},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,17,"03:00:00",30.157900000000001,1.2434208333333332,26.96,1.3766666666666667,25,1.4583333333333333,18,{"$f":"IF(AC8407<60,(60-AC8407)/24,0)","v":1.75},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,17,"08:00:00",32.093200000000003,1.1627833333333333,26.06,1.4141666666666666,21,1.625,16,{"$f":"IF(AC8412<60,(60-AC8412)/24,0)","v":1.8333333333333333},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,17,"17:00:00",34.191699999999997,1.0753458333333334,23,1.5416666666666667,32,1.1666666666666667,30,{"$f":"IF(AC8421<60,(60-AC8421)/24,0)","v":1.25},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,18,"01:00:00",43,0.70833333333333337,19.940000000000001,1.6691666666666667,23,1.5416666666666667,20,{"$f":"IF(AC8429<60,(60-AC8429)/24,0)","v":1.6666666666666667},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,18,"10:00:00",36,1,24.08,1.4966666666666668,21,1.625,28,{"$f":"IF(AC8438<60,(60-AC8438)/24,0)","v":1.3333333333333333},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,18,"18:00:00",36,1,12.02,1.9991666666666668,28,1.3333333333333333,28,{"$f":"IF(AC8446<60,(60-AC8446)/24,0)","v":1.3333333333333333},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,18,1,37,0.95833333333333337,3.92,2.3366666666666664,21,1.625,25,{"$f":"IF(AC8452<60,(60-AC8452)/24,0)","v":1.4583333333333333},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,19,"03:00:00",34,1.0833333333333333,1.94,2.4191666666666669,19,1.7083333333333333,27,{"$f":"IF(AC8455<60,(60-AC8455)/24,0)","v":1.375},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,19,"14:00:00",34,1.0833333333333333,17.059999999999999,1.7891666666666666,27,1.375,47,{"$f":"IF(AC8466<60,(60-AC8466)/24,0)","v":0.54166666666666663},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,19,"20:00:00",30,1.25,10.039999999999999,2.0816666666666666,23,1.5416666666666667,43,{"$f":"IF(AC8472<60,(60-AC8472)/24,0)","v":0.70833333333333337},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,20,"04:00:00",25,1.4583333333333333,1.04,2.4566666666666666,12,2,35,{"$f":"IF(AC8480<60,(60-AC8480)/24,0)","v":1.0416666666666667},17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,20,"13:00:00",23,1.5416666666666667,26.06,1.4141666666666666,28,1.3333333333333333,37,{"$f":"IF(AC8489<60,(60-AC8489)/24,0)","v":0.95833333333333337},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,20,"21:00:00",18,1.75,19.04,1.7066666666666668,21,1.625,25,{"$f":"IF(AC8497<60,(60-AC8497)/24,0)","v":1.4583333333333333},42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,"06:00:00",10,2.0833333333333335,10.94,2.0441666666666669,7,2.2083333333333335,13,{"$f":"IF(AC8506<60,(60-AC8506)/24,0)","v":1.9583333333333333},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,"07:00:00",3,2.375,10.039999999999999,2.0816666666666666,5,2.2916666666666665,12,{"$f":"IF(AC8507<60,(60-AC8507)/24,0)","v":2},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,"15:00:00",25,1.4583333333333333,24.98,1.4591666666666665,27,1.375,27,{"$f":"IF(AC8515<60,(60-AC8515)/24,0)","v":1.375},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,"16:00:00",19,1.7083333333333333,24.08,1.4966666666666668,25,1.4583333333333333,25,{"$f":"IF(AC8516<60,(60-AC8516)/24,0)","v":1.4583333333333333},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,"17:00:00",10,{"$f":"IF(W8517<60,(60-W8517)/24,0)","v":2.0833333333333335},24.08,1.4966666666666668,19,1.7083333333333333,19,{"$f":"IF(AC8517<60,(60-AC8517)/24,0)","v":1.7083333333333333},37.76,0.92666666666666675]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,"18:00:00",8,2.1666666666666665,23,{"$f":"IF(Y8518<60,(60-Y8518)/24,0)","v":1.5416666666666667},18,{"$f":"IF(AA8518<60,(60-AA8518)/24,0)","v":1.75},17,{"$f":"IF(AC8518<60,(60-AC8518)/24,0)","v":1.7916666666666667},37.04,{"$f":"IF(AE8518<60,(60-AE8518)/24,0)","v":0.95666666666666667}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,"19:00:00",6,2.25,21.92,1.5866666666666667,18,1.75,15,{"$f":"IF(AC8519<60,(60-AC8519)/24,0)","v":1.875},36.32,0.98666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,"20:00:00",5,2.2916666666666665,19.940000000000001,1.6691666666666667,18,1.75,14,{"$f":"IF(AC8520<60,(60-AC8520)/24,0)","v":1.9166666666666667},35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,"21:00:00",9,2.125,19.04,1.7066666666666668,19,1.7083333333333333,12,{"$f":"IF(AC8521<60,(60-AC8521)/24,0)","v":2},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,"22:00:00",7,2.2083333333333335,17.96,1.7516666666666667,18,1.75,9,{"$f":"IF(AC8522<60,(60-AC8522)/24,0)","v":2.125},34.700000000000003,1.0541666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,"23:00:00",7,2.2083333333333335,12.92,1.9616666666666667,19,1.7083333333333333,7,{"$f":"IF(AC8523<60,(60-AC8523)/24,0)","v":2.2083333333333335},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,1,7,2.2083333333333335,8.06,2.1641666666666666,18,1.75,6,{"$f":"IF(AC8524<60,(60-AC8524)/24,0)","v":2.25},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"01:00:00",7,2.2083333333333335,6.08,2.2466666666666666,16,1.8333333333333333,5,{"$f":"IF(AC8525<60,(60-AC8525)/24,0)","v":2.2916666666666665},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"02:00:00",3,2.375,3.02,2.3741666666666665,12,2,5,{"$f":"IF(AC8526<60,(60-AC8526)/24,0)","v":2.2916666666666665},32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"03:00:00",1,2.4583333333333335,1.94,2.4191666666666669,12,2,4,{"$f":"IF(AC8527<60,(60-AC8527)/24,0)","v":2.3333333333333335},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"04:00:00",3,2.375,-3.9999999999999147E-2,2.5016666666666665,10,2.0833333333333335,4,{"$f":"IF(AC8528<60,(60-AC8528)/24,0)","v":2.3333333333333335},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"05:00:00",3,2.375,-3.9999999999999147E-2,2.5016666666666665,9,2.125,3,{"$f":"IF(AC8529<60,(60-AC8529)/24,0)","v":2.375},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"06:00:00",1,2.4583333333333335,-0.94000000000000483,2.539166666666667,7,2.2083333333333335,3,{"$f":"IF(AC8530<60,(60-AC8530)/24,0)","v":2.375},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"07:00:00",3,2.375,-2.92,2.6216666666666666,7,2.2083333333333335,3,{"$f":"IF(AC8531<60,(60-AC8531)/24,0)","v":2.375},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"08:00:00",7,2.2083333333333335,-4,2.6666666666666665,7,2.2083333333333335,-2,{"$f":"IF(AC8532<60,(60-AC8532)/24,0)","v":2.5833333333333335},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"09:00:00",10,2.0833333333333335,1.94,2.4191666666666669,9,2.125,9,{"$f":"IF(AC8533<60,(60-AC8533)/24,0)","v":2.125},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"10:00:00",14,1.9166666666666667,10.94,2.0441666666666669,12,2,10,{"$f":"IF(AC8534<60,(60-AC8534)/24,0)","v":2.0833333333333335},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"11:00:00",18,1.75,19.04,1.7066666666666668,16,1.8333333333333333,16,{"$f":"IF(AC8535<60,(60-AC8535)/24,0)","v":1.8333333333333333},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"12:00:00",21,1.625,24.98,1.4591666666666665,27,1.375,18,{"$f":"IF(AC8536<60,(60-AC8536)/24,0)","v":1.75},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"13:00:00",25,1.4583333333333333,26.06,1.4141666666666666,28,1.3333333333333333,21,{"$f":"IF(AC8537<60,(60-AC8537)/24,0)","v":1.625},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"14:00:00",27,1.375,26.06,1.4141666666666666,30,1.25,27,{"$f":"IF(AC8538<60,(60-AC8538)/24,0)","v":1.375},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"15:00:00",27,1.375,26.06,1.4141666666666666,30,1.25,23,{"$f":"IF(AC8539<60,(60-AC8539)/24,0)","v":1.5416666666666667},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"16:00:00",27,1.375,24.98,1.4591666666666665,28,1.3333333333333333,23,{"$f":"IF(AC8540<60,(60-AC8540)/24,0)","v":1.5416666666666667},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"17:00:00",25,1.4583333333333333,24.08,1.4966666666666668,27,1.375,23,{"$f":"IF(AC8541<60,(60-AC8541)/24,0)","v":1.5416666666666667},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"18:00:00",25,1.4583333333333333,23,1.5416666666666667,27,1.375,16,{"$f":"IF(AC8542<60,(60-AC8542)/24,0)","v":1.8333333333333333},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"19:00:00",25,1.4583333333333333,23,1.5416666666666667,27,1.375,12,{"$f":"IF(AC8543<60,(60-AC8543)/24,0)","v":2},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"20:00:00",25,1.4583333333333333,24.08,1.4966666666666668,28,1.3333333333333333,12,{"$f":"IF(AC8544<60,(60-AC8544)/24,0)","v":2},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"21:00:00",23,1.5416666666666667,21.92,1.5866666666666667,28,1.3333333333333333,12,{"$f":"IF(AC8545<60,(60-AC8545)/24,0)","v":2},27.68,1.3466666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"22:00:00",21,1.625,21.02,1.6241666666666668,28,1.3333333333333333,14,{"$f":"IF(AC8546<60,(60-AC8546)/24,0)","v":1.9166666666666667},27.14,1.3691666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"23:00:00",23,1.5416666666666667,21.02,1.6241666666666668,28,1.3333333333333333,13,{"$f":"IF(AC8547<60,(60-AC8547)/24,0)","v":1.9583333333333333},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,1,25,1.4583333333333333,21.02,1.6241666666666668,28,1.3333333333333333,14,{"$f":"IF(AC8548<60,(60-AC8548)/24,0)","v":1.9166666666666667},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"01:00:00",25,1.4583333333333333,21.92,1.5866666666666667,28,1.3333333333333333,15,{"$f":"IF(AC8549<60,(60-AC8549)/24,0)","v":1.875},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"02:00:00",25,1.4583333333333333,21.92,1.5866666666666667,28,1.3333333333333333,16,{"$f":"IF(AC8550<60,(60-AC8550)/24,0)","v":1.8333333333333333},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"03:00:00",25,1.4583333333333333,21.92,1.5866666666666667,30,1.25,16,{"$f":"IF(AC8551<60,(60-AC8551)/24,0)","v":1.8333333333333333},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"04:00:00",25,1.4583333333333333,21.92,1.5866666666666667,30,1.25,17,{"$f":"IF(AC8552<60,(60-AC8552)/24,0)","v":1.7916666666666667},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"05:00:00",25,1.4583333333333333,21.92,1.5866666666666667,30,1.25,18,{"$f":"IF(AC8553<60,(60-AC8553)/24,0)","v":1.75},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"06:00:00",25,1.4583333333333333,23,1.5416666666666667,28,1.3333333333333333,19,{"$f":"IF(AC8554<60,(60-AC8554)/24,0)","v":1.7083333333333333},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"07:00:00",25,1.4583333333333333,23,1.5416666666666667,25,1.4583333333333333,19,{"$f":"IF(AC8555<60,(60-AC8555)/24,0)","v":1.7083333333333333},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"08:00:00",25,1.4583333333333333,24.08,1.4966666666666668,23,1.5416666666666667,19,{"$f":"IF(AC8556<60,(60-AC8556)/24,0)","v":1.7083333333333333},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"09:00:00",25,1.4583333333333333,24.08,1.4966666666666668,27,1.375,19,{"$f":"IF(AC8557<60,(60-AC8557)/24,0)","v":1.7083333333333333},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"10:00:00",27,1.375,24.98,1.4591666666666665,32,1.1666666666666667,21,{"$f":"IF(AC8558<60,(60-AC8558)/24,0)","v":1.625},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"11:00:00",28,1.3333333333333333,28.94,1.2941666666666667,36,1,24,{"$f":"IF(AC8559<60,(60-AC8559)/24,0)","v":1.5},30.38,1.2341666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"12:00:00",30,1.25,30.92,1.2116666666666667,37,0.95833333333333337,25,{"$f":"IF(AC8560<60,(60-AC8560)/24,0)","v":1.4583333333333333},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"13:00:00",30,1.25,32,1.1666666666666667,39,0.875,27,{"$f":"IF(AC8561<60,(60-AC8561)/24,0)","v":1.375},33.26,1.1141666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"14:00:00",32,1.1666666666666667,33.979999999999997,1.0841666666666667,39,0.875,28,{"$f":"IF(AC8562<60,(60-AC8562)/24,0)","v":1.3333333333333333},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"15:00:00",30,1.25,33.979999999999997,1.0841666666666667,39,0.875,28,{"$f":"IF(AC8563<60,(60-AC8563)/24,0)","v":1.3333333333333333},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"16:00:00",30,1.25,30.92,1.2116666666666667,37,0.95833333333333337,28,{"$f":"IF(AC8564<60,(60-AC8564)/24,0)","v":1.3333333333333333},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"17:00:00",30,1.25,32,1.1666666666666667,36,1,28,{"$f":"IF(AC8565<60,(60-AC8565)/24,0)","v":1.3333333333333333},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"18:00:00",30,1.25,32,1.1666666666666667,34,1.0833333333333333,28,{"$f":"IF(AC8566<60,(60-AC8566)/24,0)","v":1.3333333333333333},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"19:00:00",30,1.25,30.92,1.2116666666666667,34,1.0833333333333333,28,{"$f":"IF(AC8567<60,(60-AC8567)/24,0)","v":1.3333333333333333},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"20:00:00",30,1.25,30.92,1.2116666666666667,34,1.0833333333333333,28,{"$f":"IF(AC8568<60,(60-AC8568)/24,0)","v":1.3333333333333333},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"21:00:00",30,1.25,26.96,1.3766666666666667,34,1.0833333333333333,28,{"$f":"IF(AC8569<60,(60-AC8569)/24,0)","v":1.3333333333333333},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"22:00:00",30,1.25,26.96,1.3766666666666667,34,1.0833333333333333,28,{"$f":"IF(AC8570<60,(60-AC8570)/24,0)","v":1.3333333333333333},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"23:00:00",30,1.25,24.08,1.4966666666666668,32,1.1666666666666667,27,{"$f":"IF(AC8571<60,(60-AC8571)/24,0)","v":1.375},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,1,30,1.25,23,1.5416666666666667,32,1.1666666666666667,27,{"$f":"IF(AC8572<60,(60-AC8572)/24,0)","v":1.375},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"01:00:00",32,1.1666666666666667,24.98,1.4591666666666665,32,1.1666666666666667,27,{"$f":"IF(AC8573<60,(60-AC8573)/24,0)","v":1.375},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"02:00:00",34,1.0833333333333333,24.98,1.4591666666666665,32,1.1666666666666667,27,{"$f":"IF(AC8574<60,(60-AC8574)/24,0)","v":1.375},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"03:00:00",32,1.1666666666666667,28.04,1.3316666666666668,32,1.1666666666666667,27,{"$f":"IF(AC8575<60,(60-AC8575)/24,0)","v":1.375},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"04:00:00",34,1.0833333333333333,28.94,1.2941666666666667,32,1.1666666666666667,27,{"$f":"IF(AC8576<60,(60-AC8576)/24,0)","v":1.375},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"05:00:00",34,1.0833333333333333,28.94,1.2941666666666667,32,1.1666666666666667,27,{"$f":"IF(AC8577<60,(60-AC8577)/24,0)","v":1.375},21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"06:00:00",32.009500000000003,1.1662708333333331,30.02,1.2491666666666668,30,1.25,28,{"$f":"IF(AC8578<60,(60-AC8578)/24,0)","v":1.3333333333333333},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"07:00:00",34,1.0833333333333333,30.02,1.2491666666666668,30,1.25,25,{"$f":"IF(AC8579<60,(60-AC8579)/24,0)","v":1.4583333333333333},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"08:00:00",36,1,30.92,1.2116666666666667,30,1.25,27,{"$f":"IF(AC8580<60,(60-AC8580)/24,0)","v":1.375},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"09:00:00",36,{"$f":"IF(W8581<60,(60-W8581)/24,0)","v":1},32,1.1666666666666667,32,1.1666666666666667,27,{"$f":"IF(AC8581<60,(60-AC8581)/24,0)","v":1.375},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"10:00:00",37,0.95833333333333337,33.08,{"$f":"IF(Y8582<60,(60-Y8582)/24,0)","v":1.1216666666666668},35,{"$f":"IF(AA8582<60,(60-AA8582)/24,0)","v":1.0416666666666667},28,{"$f":"IF(AC8582<60,(60-AC8582)/24,0)","v":1.3333333333333333},24.8,{"$f":"IF(AE8582<60,(60-AE8582)/24,0)","v":1.4666666666666668}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"11:00:00",39,0.875,32,1.1666666666666667,39,0.875,36,{"$f":"IF(AC8583<60,(60-AC8583)/24,0)","v":1},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"12:00:00",37,0.95833333333333337,33.08,1.1216666666666668,45,0.625,36,{"$f":"IF(AC8584<60,(60-AC8584)/24,0)","v":1},27.14,1.3691666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"13:00:00",37.389200000000002,0.9421166666666666,33.08,1.1216666666666668,45,0.625,34,{"$f":"IF(AC8585<60,(60-AC8585)/24,0)","v":1.0833333333333333},27.32,1.3616666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"14:00:00",37.389200000000002,0.9421166666666666,33.979999999999997,1.0841666666666667,45,0.625,36,{"$f":"IF(AC8586<60,(60-AC8586)/24,0)","v":1},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"15:00:00",41,0.79166666666666663,35.06,1.0391666666666666,43,0.70833333333333337,37,{"$f":"IF(AC8587<60,(60-AC8587)/24,0)","v":0.95833333333333337},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"16:00:00",39,0.875,33.979999999999997,1.0841666666666667,43,0.70833333333333337,28,{"$f":"IF(AC8588<60,(60-AC8588)/24,0)","v":1.3333333333333333},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"17:00:00",41,0.79166666666666663,33.979999999999997,1.0841666666666667,37,0.95833333333333337,21,{"$f":"IF(AC8589<60,(60-AC8589)/24,0)","v":1.625},21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"18:00:00",37.213900000000002,0.94942083333333327,33.08,1.1216666666666668,36,1,21,{"$f":"IF(AC8590<60,(60-AC8590)/24,0)","v":1.625},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"19:00:00",37.213900000000002,0.94942083333333327,33.08,1.1216666666666668,36,1,18,{"$f":"IF(AC8591<60,(60-AC8591)/24,0)","v":1.75},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"20:00:00",37.213900000000002,0.94942083333333327,33.08,1.1216666666666668,34,1.0833333333333333,21,{"$f":"IF(AC8592<60,(60-AC8592)/24,0)","v":1.625},17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"21:00:00",37.213900000000002,0.94942083333333327,33.08,1.1216666666666668,34,1.0833333333333333,19,{"$f":"IF(AC8593<60,(60-AC8593)/24,0)","v":1.7083333333333333},15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"22:00:00",37.213900000000002,0.94942083333333327,32,1.1666666666666667,34,1.0833333333333333,21,{"$f":"IF(AC8594<60,(60-AC8594)/24,0)","v":1.625},14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"23:00:00",39,0.875,32,1.1666666666666667,34,1.0833333333333333,21,{"$f":"IF(AC8595<60,(60-AC8595)/24,0)","v":1.625},14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,1,36.188299999999998,0.99215416666666678,32,1.1666666666666667,34,1.0833333333333333,22,{"$f":"IF(AC8596<60,(60-AC8596)/24,0)","v":1.5833333333333333},12.2,1.9916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"01:00:00",34,1.0833333333333333,33.08,1.1216666666666668,34,1.0833333333333333,23,{"$f":"IF(AC8597<60,(60-AC8597)/24,0)","v":1.5416666666666667},10.4,2.0666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"02:00:00",32,1.1666666666666667,33.08,1.1216666666666668,30,1.25,24,{"$f":"IF(AC8598<60,(60-AC8598)/24,0)","v":1.5},10.4,2.0666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"03:00:00",32,1.1666666666666667,32,1.1666666666666667,30,1.25,26,{"$f":"IF(AC8599<60,(60-AC8599)/24,0)","v":1.4166666666666667},8.6,2.1416666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"04:00:00",30,1.25,32,1.1666666666666667,28,1.3333333333333333,27,{"$f":"IF(AC8600<60,(60-AC8600)/24,0)","v":1.375},8.6,2.1416666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"05:00:00",28,1.3333333333333333,32,1.1666666666666667,28,1.3333333333333333,28,{"$f":"IF(AC8601<60,(60-AC8601)/24,0)","v":1.3333333333333333},6.8,2.2166666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"06:00:00",21,1.625,32,1.1666666666666667,28,1.3333333333333333,30,{"$f":"IF(AC8602<60,(60-AC8602)/24,0)","v":1.25},6.8,2.2166666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"07:00:00",19,1.7083333333333333,32,1.1666666666666667,28,1.3333333333333333,32,{"$f":"IF(AC8603<60,(60-AC8603)/24,0)","v":1.1666666666666667},8.6,2.1416666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"08:00:00",14,1.9166666666666667,32,1.1666666666666667,27,1.375,32,{"$f":"IF(AC8604<60,(60-AC8604)/24,0)","v":1.1666666666666667},10.4,2.0666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"09:00:00",12,2,33.08,1.1216666666666668,27,1.375,32,{"$f":"IF(AC8605<60,(60-AC8605)/24,0)","v":1.1666666666666667},12.2,1.9916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"10:00:00",12,2,30.92,1.2116666666666667,28,1.3333333333333333,33,{"$f":"IF(AC8606<60,(60-AC8606)/24,0)","v":1.125},15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"11:00:00",10,2.0833333333333335,28.04,1.3316666666666668,32,1.1666666666666667,34,{"$f":"IF(AC8607<60,(60-AC8607)/24,0)","v":1.0833333333333333},17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"12:00:00",12,2,26.96,1.3766666666666667,34,1.0833333333333333,34,{"$f":"IF(AC8608<60,(60-AC8608)/24,0)","v":1.0833333333333333},21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"13:00:00",14,1.9166666666666667,26.06,1.4141666666666666,39,0.875,34,{"$f":"IF(AC8609<60,(60-AC8609)/24,0)","v":1.0833333333333333},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"14:00:00",16,1.8333333333333333,24.08,1.4966666666666668,41,0.79166666666666663,34,{"$f":"IF(AC8610<60,(60-AC8610)/24,0)","v":1.0833333333333333},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"15:00:00",15,1.875,21.92,1.5866666666666667,43,0.70833333333333337,35,{"$f":"IF(AC8611<60,(60-AC8611)/24,0)","v":1.0416666666666667},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"16:00:00",12,2,21.02,1.6241666666666668,37,0.95833333333333337,36,{"$f":"IF(AC8612<60,(60-AC8612)/24,0)","v":1},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"17:00:00",10,2.0833333333333335,19.04,1.7066666666666668,36,1,34,{"$f":"IF(AC8613<60,(60-AC8613)/24,0)","v":1.0833333333333333},21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"18:00:00",10,2.0833333333333335,17.059999999999999,1.7891666666666666,36,1,34,{"$f":"IF(AC8614<60,(60-AC8614)/24,0)","v":1.0833333333333333},21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"19:00:00",10,2.0833333333333335,15.98,1.8341666666666665,36,1,34,{"$f":"IF(AC8615<60,(60-AC8615)/24,0)","v":1.0833333333333333},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"20:00:00",3,2.375,15.08,1.8716666666666668,37.133800000000001,0.95275833333333326,34,{"$f":"IF(AC8616<60,(60-AC8616)/24,0)","v":1.0833333333333333},15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"21:00:00",3,2.375,12.92,1.9616666666666667,37,0.95833333333333337,34,{"$f":"IF(AC8617<60,(60-AC8617)/24,0)","v":1.0833333333333333},15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"22:00:00",1,2.4583333333333335,12.02,1.9991666666666668,39,0.875,34,{"$f":"IF(AC8618<60,(60-AC8618)/24,0)","v":1.0833333333333333},15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"23:00:00",0,2.5,10.94,2.0441666666666669,41,0.79166666666666663,33,{"$f":"IF(AC8619<60,(60-AC8619)/24,0)","v":1.125},15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,1,3,2.375,10.039999999999999,2.0816666666666666,43,0.70833333333333337,33,{"$f":"IF(AC8620<60,(60-AC8620)/24,0)","v":1.125},15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"01:00:00",7,2.2083333333333335,8.9600000000000009,2.1266666666666665,41,0.79166666666666663,33,{"$f":"IF(AC8621<60,(60-AC8621)/24,0)","v":1.125},15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"02:00:00",7,2.2083333333333335,6.98,2.2091666666666665,39,0.875,34,{"$f":"IF(AC8622<60,(60-AC8622)/24,0)","v":1.0833333333333333},15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"03:00:00",3,2.375,6.08,2.2466666666666666,39,0.875,35,{"$f":"IF(AC8623<60,(60-AC8623)/24,0)","v":1.0416666666666667},17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"04:00:00",3,2.375,-4,2.6666666666666665,37.133800000000001,0.95275833333333326,35,{"$f":"IF(AC8624<60,(60-AC8624)/24,0)","v":1.0416666666666667},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"05:00:00",3,2.375,3.92,2.3366666666666664,37.133800000000001,0.95275833333333326,35,{"$f":"IF(AC8625<60,(60-AC8625)/24,0)","v":1.0416666666666667},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"06:00:00",0,2.5,-5.0800000000000054,2.7116666666666673,36,1,37,{"$f":"IF(AC8626<60,(60-AC8626)/24,0)","v":0.95833333333333337},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"07:00:00",0,2.5,-7.06,2.7941666666666669,37.133800000000001,0.95275833333333326,37,{"$f":"IF(AC8627<60,(60-AC8627)/24,0)","v":0.95833333333333337},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"08:00:00",0,2.5,-5.98,2.749166666666667,37.133800000000001,0.95275833333333326,38,{"$f":"IF(AC8628<60,(60-AC8628)/24,0)","v":0.91666666666666663},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"09:00:00",1,2.4583333333333335,5,2.2916666666666665,37.133800000000001,0.95275833333333326,39,{"$f":"IF(AC8629<60,(60-AC8629)/24,0)","v":0.875},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"10:00:00",5,2.2916666666666665,12.92,1.9616666666666667,37.133800000000001,0.95275833333333326,40,{"$f":"IF(AC8630<60,(60-AC8630)/24,0)","v":0.83333333333333337},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"11:00:00",10,2.0833333333333335,15.98,1.8341666666666665,37.133800000000001,0.95275833333333326,41,{"$f":"IF(AC8631<60,(60-AC8631)/24,0)","v":0.79166666666666663},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"12:00:00",18,1.75,17.059999999999999,1.7891666666666666,37.133800000000001,0.95275833333333326,41,{"$f":"IF(AC8632<60,(60-AC8632)/24,0)","v":0.79166666666666663},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"13:00:00",20,1.6666666666666667,19.04,1.7066666666666668,37.133800000000001,0.95275833333333326,43,{"$f":"IF(AC8633<60,(60-AC8633)/24,0)","v":0.70833333333333337},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"14:00:00",21,1.625,19.940000000000001,1.6691666666666667,37.133800000000001,0.95275833333333326,41,{"$f":"IF(AC8634<60,(60-AC8634)/24,0)","v":0.79166666666666663},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"15:00:00",21,1.625,19.940000000000001,1.6691666666666667,37,0.95833333333333337,43,{"$f":"IF(AC8635<60,(60-AC8635)/24,0)","v":0.70833333333333337},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"16:00:00",21,1.625,19.04,1.7066666666666668,36,1,39,{"$f":"IF(AC8636<60,(60-AC8636)/24,0)","v":0.875},33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"17:00:00",19,1.7083333333333333,15.98,1.8341666666666665,37.133800000000001,0.95275833333333326,39,{"$f":"IF(AC8637<60,(60-AC8637)/24,0)","v":0.875},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"18:00:00",19,1.7083333333333333,14,1.9166666666666667,37,0.95833333333333337,38,{"$f":"IF(AC8638<60,(60-AC8638)/24,0)","v":0.91666666666666663},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"19:00:00",19,1.7083333333333333,12.92,1.9616666666666667,36,1,37,{"$f":"IF(AC8639<60,(60-AC8639)/24,0)","v":0.95833333333333337},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"20:00:00",19,1.7083333333333333,8.9600000000000009,2.1266666666666665,34,1.0833333333333333,37,{"$f":"IF(AC8640<60,(60-AC8640)/24,0)","v":0.95833333333333337},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"21:00:00",19,1.7083333333333333,8.06,2.1641666666666666,32,1.1666666666666667,36,{"$f":"IF(AC8641<60,(60-AC8641)/24,0)","v":1},28.22,1.3241666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"22:00:00",19,1.7083333333333333,6.08,2.2466666666666666,32,1.1666666666666667,37,{"$f":"IF(AC8642<60,(60-AC8642)/24,0)","v":0.95833333333333337},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"23:00:00",19,1.7083333333333333,5,2.2916666666666665,30,1.25,36,{"$f":"IF(AC8643<60,(60-AC8643)/24,0)","v":1},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,1,19,1.7083333333333333,3.02,2.3741666666666665,28,1.3333333333333333,36,{"$f":"IF(AC8644<60,(60-AC8644)/24,0)","v":1},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"01:00:00",19,{"$f":"IF(W8645<60,(60-W8645)/24,0)","v":1.7083333333333333},1.94,2.4191666666666669,28,1.3333333333333333,35,{"$f":"IF(AC8645<60,(60-AC8645)/24,0)","v":1.0416666666666667},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"02:00:00",19,1.7083333333333333,-3.9999999999999147E-2,{"$f":"IF(Y8646<60,(60-Y8646)/24,0)","v":2.5016666666666665},27,{"$f":"IF(AA8646<60,(60-AA8646)/24,0)","v":1.375},35,{"$f":"IF(AC8646<60,(60-AC8646)/24,0)","v":1.0416666666666667},28.4,{"$f":"IF(AE8646<60,(60-AE8646)/24,0)","v":1.3166666666666667}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"03:00:00",21,1.625,1.94,2.4191666666666669,27,1.375,35,{"$f":"IF(AC8647<60,(60-AC8647)/24,0)","v":1.0416666666666667},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"04:00:00",21,1.625,6.98,2.2091666666666665,27,1.375,35,{"$f":"IF(AC8648<60,(60-AC8648)/24,0)","v":1.0416666666666667},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"05:00:00",19,1.7083333333333333,10.94,2.0441666666666669,27,1.375,35,{"$f":"IF(AC8649<60,(60-AC8649)/24,0)","v":1.0416666666666667},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"06:00:00",21,1.625,12.92,1.9616666666666667,28,1.3333333333333333,36,{"$f":"IF(AC8650<60,(60-AC8650)/24,0)","v":1},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"07:00:00",21,1.625,12.92,1.9616666666666667,28,1.3333333333333333,36,{"$f":"IF(AC8651<60,(60-AC8651)/24,0)","v":1},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"08:00:00",21,1.625,14,1.9166666666666667,27,1.375,36,{"$f":"IF(AC8652<60,(60-AC8652)/24,0)","v":1},21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"09:00:00",27,1.375,15.98,1.8341666666666665,28,1.3333333333333333,36,{"$f":"IF(AC8653<60,(60-AC8653)/24,0)","v":1},21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"10:00:00",28,1.3333333333333333,17.96,1.7516666666666667,30,1.25,37,{"$f":"IF(AC8654<60,(60-AC8654)/24,0)","v":0.95833333333333337},21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"11:00:00",28,1.3333333333333333,19.940000000000001,1.6691666666666667,32,1.1666666666666667,38,{"$f":"IF(AC8655<60,(60-AC8655)/24,0)","v":0.91666666666666663},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"12:00:00",28,1.3333333333333333,24.08,1.4966666666666668,32,1.1666666666666667,37,{"$f":"IF(AC8656<60,(60-AC8656)/24,0)","v":0.95833333333333337},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"13:00:00",28,1.3333333333333333,26.06,1.4141666666666666,34,1.0833333333333333,37,{"$f":"IF(AC8657<60,(60-AC8657)/24,0)","v":0.95833333333333337},26.06,1.4141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"14:00:00",28,1.3333333333333333,26.06,1.4141666666666666,36,1,39,{"$f":"IF(AC8658<60,(60-AC8658)/24,0)","v":0.875},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"15:00:00",28,1.3333333333333333,26.06,1.4141666666666666,36,1,39,{"$f":"IF(AC8659<60,(60-AC8659)/24,0)","v":0.875},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"16:00:00",28,1.3333333333333333,26.06,1.4141666666666666,36,1,37,{"$f":"IF(AC8660<60,(60-AC8660)/24,0)","v":0.95833333333333337},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"17:00:00",27,1.375,26.96,1.3766666666666667,34,1.0833333333333333,36,{"$f":"IF(AC8661<60,(60-AC8661)/24,0)","v":1},21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"18:00:00",27,1.375,26.06,1.4141666666666666,30,1.25,34,{"$f":"IF(AC8662<60,(60-AC8662)/24,0)","v":1.0833333333333333},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"19:00:00",27,1.375,26.06,1.4141666666666666,27,1.375,30,{"$f":"IF(AC8663<60,(60-AC8663)/24,0)","v":1.25},17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"20:00:00",27,1.375,26.06,1.4141666666666666,25,1.4583333333333333,30,{"$f":"IF(AC8664<60,(60-AC8664)/24,0)","v":1.25},14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"21:00:00",25,1.4583333333333333,24.08,1.4966666666666668,25,1.4583333333333333,30,{"$f":"IF(AC8665<60,(60-AC8665)/24,0)","v":1.25},14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"22:00:00",25,1.4583333333333333,24.08,1.4966666666666668,23,1.5416666666666667,34,{"$f":"IF(AC8666<60,(60-AC8666)/24,0)","v":1.0833333333333333},12.2,1.9916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"23:00:00",23,1.5416666666666667,26.06,1.4141666666666666,21,1.625,31,{"$f":"IF(AC8667<60,(60-AC8667)/24,0)","v":1.2083333333333333},12.2,1.9916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,1,21,1.625,24.08,1.4966666666666668,21,1.625,30,{"$f":"IF(AC8668<60,(60-AC8668)/24,0)","v":1.25},12.2,1.9916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"01:00:00",19,1.7083333333333333,19.04,1.7066666666666668,21,1.625,28,{"$f":"IF(AC8669<60,(60-AC8669)/24,0)","v":1.3333333333333333},10.4,2.0666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"02:00:00",21,1.625,17.96,1.7516666666666667,19,1.7083333333333333,27,{"$f":"IF(AC8670<60,(60-AC8670)/24,0)","v":1.375},10.4,2.0666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"03:00:00",21,1.625,12.92,1.9616666666666667,21,1.625,26,{"$f":"IF(AC8671<60,(60-AC8671)/24,0)","v":1.4166666666666667},8.6,2.1416666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"04:00:00",23,1.5416666666666667,10.039999999999999,2.0816666666666666,19,1.7083333333333333,25,{"$f":"IF(AC8672<60,(60-AC8672)/24,0)","v":1.4583333333333333},10.4,2.0666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"05:00:00",23,1.5416666666666667,12.92,1.9616666666666667,19,1.7083333333333333,23,{"$f":"IF(AC8673<60,(60-AC8673)/24,0)","v":1.5416666666666667},8.6,2.1416666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"06:00:00",25,1.4583333333333333,12.02,1.9991666666666668,18,1.75,23,{"$f":"IF(AC8674<60,(60-AC8674)/24,0)","v":1.5416666666666667},6.8,2.2166666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"07:00:00",23,1.5416666666666667,10.039999999999999,2.0816666666666666,18,1.75,21,{"$f":"IF(AC8675<60,(60-AC8675)/24,0)","v":1.625},5,2.2916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"08:00:00",23,1.5416666666666667,10.039999999999999,2.0816666666666666,18,1.75,21,{"$f":"IF(AC8676<60,(60-AC8676)/24,0)","v":1.625},8.6,2.1416666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"09:00:00",25,1.4583333333333333,24.08,1.4966666666666668,19,1.7083333333333333,21,{"$f":"IF(AC8677<60,(60-AC8677)/24,0)","v":1.625},12.2,1.9916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"10:00:00",25,1.4583333333333333,26.06,1.4141666666666666,21,1.625,23,{"$f":"IF(AC8678<60,(60-AC8678)/24,0)","v":1.5416666666666667},15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"11:00:00",27,1.375,28.04,1.3316666666666668,25,1.4583333333333333,25,{"$f":"IF(AC8679<60,(60-AC8679)/24,0)","v":1.4583333333333333},17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"12:00:00",28,1.3333333333333333,28.04,1.3316666666666668,28,1.3333333333333333,27,{"$f":"IF(AC8680<60,(60-AC8680)/24,0)","v":1.375},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"13:00:00",28,1.3333333333333333,28.04,1.3316666666666668,30,1.25,28,{"$f":"IF(AC8681<60,(60-AC8681)/24,0)","v":1.3333333333333333},21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"14:00:00",30,1.25,28.04,1.3316666666666668,34,1.0833333333333333,28,{"$f":"IF(AC8682<60,(60-AC8682)/24,0)","v":1.3333333333333333},21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"15:00:00",34,1.0833333333333333,28.04,1.3316666666666668,34,1.0833333333333333,30,{"$f":"IF(AC8683<60,(60-AC8683)/24,0)","v":1.25},21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"16:00:00",34,1.0833333333333333,24.98,1.4591666666666665,36,1,28,{"$f":"IF(AC8684<60,(60-AC8684)/24,0)","v":1.3333333333333333},21.38,1.6091666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"17:00:00",32,1.1666666666666667,23,1.5416666666666667,36,1,24,{"$f":"IF(AC8685<60,(60-AC8685)/24,0)","v":1.5},21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"18:00:00",32,1.1666666666666667,21.02,1.6241666666666668,37,0.95833333333333337,21,{"$f":"IF(AC8686<60,(60-AC8686)/24,0)","v":1.625},17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"19:00:00",32,1.1666666666666667,21.02,1.6241666666666668,34,1.0833333333333333,18,{"$f":"IF(AC8687<60,(60-AC8687)/24,0)","v":1.75},21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"20:00:00",30.157900000000001,1.2434208333333332,15.98,1.8341666666666665,34,1.0833333333333333,15,{"$f":"IF(AC8688<60,(60-AC8688)/24,0)","v":1.875},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"21:00:00",32,1.1666666666666667,8.06,2.1641666666666666,32,1.1666666666666667,12,{"$f":"IF(AC8689<60,(60-AC8689)/24,0)","v":2},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"22:00:00",32,1.1666666666666667,6.98,2.2091666666666665,32,1.1666666666666667,10,{"$f":"IF(AC8690<60,(60-AC8690)/24,0)","v":2.0833333333333335},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"23:00:00",32,1.1666666666666667,5,2.2916666666666665,34,1.0833333333333333,9,{"$f":"IF(AC8691<60,(60-AC8691)/24,0)","v":2.125},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,1,34,1.0833333333333333,6.08,2.2466666666666666,34,1.0833333333333333,8,{"$f":"IF(AC8692<60,(60-AC8692)/24,0)","v":2.1666666666666665},17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"01:00:00",34,1.0833333333333333,3.02,2.3741666666666665,34,1.0833333333333333,8,{"$f":"IF(AC8693<60,(60-AC8693)/24,0)","v":2.1666666666666665},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"02:00:00",34,1.0833333333333333,-3.9999999999999147E-2,2.5016666666666665,34,1.0833333333333333,8,{"$f":"IF(AC8694<60,(60-AC8694)/24,0)","v":2.1666666666666665},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"03:00:00",34,1.0833333333333333,-2.02,2.5841666666666669,34,1.0833333333333333,7,{"$f":"IF(AC8695<60,(60-AC8695)/24,0)","v":2.2083333333333335},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"04:00:00",34,1.0833333333333333,-0.94000000000000483,2.539166666666667,34,1.0833333333333333,7,{"$f":"IF(AC8696<60,(60-AC8696)/24,0)","v":2.2083333333333335},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"05:00:00",34,1.0833333333333333,-4,2.6666666666666665,34,1.0833333333333333,6,{"$f":"IF(AC8697<60,(60-AC8697)/24,0)","v":2.25},17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"06:00:00",34,1.0833333333333333,-5.0800000000000054,2.7116666666666673,34,1.0833333333333333,7,{"$f":"IF(AC8698<60,(60-AC8698)/24,0)","v":2.2083333333333335},15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"07:00:00",34,1.0833333333333333,-5.98,2.749166666666667,34,1.0833333333333333,5,{"$f":"IF(AC8699<60,(60-AC8699)/24,0)","v":2.2916666666666665},17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"08:00:00",34,1.0833333333333333,-2.92,2.6216666666666666,34,1.0833333333333333,7,{"$f":"IF(AC8700<60,(60-AC8700)/24,0)","v":2.2083333333333335},17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"09:00:00",34.362499999999997,1.0682291666666668,3.02,2.3741666666666665,36,1,9,{"$f":"IF(AC8701<60,(60-AC8701)/24,0)","v":2.125},21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"10:00:00",36,1,8.06,2.1641666666666666,36,1,12,{"$f":"IF(AC8702<60,(60-AC8702)/24,0)","v":2},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"11:00:00",36,1,17.059999999999999,1.7891666666666666,37,0.95833333333333337,19,{"$f":"IF(AC8703<60,(60-AC8703)/24,0)","v":1.7083333333333333},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"12:00:00",36,1,24.08,1.4966666666666668,37.133800000000001,0.95275833333333326,21,{"$f":"IF(AC8704<60,(60-AC8704)/24,0)","v":1.625},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"13:00:00",36,1,26.06,1.4141666666666666,39,0.875,25,{"$f":"IF(AC8705<60,(60-AC8705)/24,0)","v":1.4583333333333333},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"14:00:00",36,1,28.04,1.3316666666666668,39,0.875,28,{"$f":"IF(AC8706<60,(60-AC8706)/24,0)","v":1.3333333333333333},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"15:00:00",37,0.95833333333333337,28.04,1.3316666666666668,41,0.79166666666666663,28,{"$f":"IF(AC8707<60,(60-AC8707)/24,0)","v":1.3333333333333333},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"16:00:00",36,1,28.04,1.3316666666666668,43,0.70833333333333337,30,{"$f":"IF(AC8708<60,(60-AC8708)/24,0)","v":1.25},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"17:00:00",36.362499999999997,{"$f":"IF(W8709<60,(60-W8709)/24,0)","v":0.98489583333333341},24.98,1.4591666666666665,39,0.875,30,{"$f":"IF(AC8709<60,(60-AC8709)/24,0)","v":1.25},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"18:00:00",36.362499999999997,0.98489583333333341,19.04,{"$f":"IF(Y8710<60,(60-Y8710)/24,0)","v":1.7066666666666668},43,{"$f":"IF(AA8710<60,(60-AA8710)/24,0)","v":0.70833333333333337},30,{"$f":"IF(AC8710<60,(60-AC8710)/24,0)","v":1.25},23,{"$f":"IF(AE8710<60,(60-AE8710)/24,0)","v":1.5416666666666667}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"19:00:00",37.389200000000002,0.9421166666666666,17.96,1.7516666666666667,41,0.79166666666666663,32,{"$f":"IF(AC8711<60,(60-AC8711)/24,0)","v":1.1666666666666667},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"20:00:00",43,0.70833333333333337,15.98,1.8341666666666665,39,0.875,30,{"$f":"IF(AC8712<60,(60-AC8712)/24,0)","v":1.25},21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"21:00:00",43,0.70833333333333337,17.96,1.7516666666666667,39,0.875,30,{"$f":"IF(AC8713<60,(60-AC8713)/24,0)","v":1.25},21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"22:00:00",41,0.79166666666666663,12.02,1.9991666666666668,39,0.875,30,{"$f":"IF(AC8714<60,(60-AC8714)/24,0)","v":1.25},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"23:00:00",37,0.95833333333333337,10.94,2.0441666666666669,38,0.91666666666666663,29,{"$f":"IF(AC8715<60,(60-AC8715)/24,0)","v":1.2916666666666667},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,1,37,0.95833333333333337,8.06,2.1641666666666666,37,0.95833333333333337,30,{"$f":"IF(AC8716<60,(60-AC8716)/24,0)","v":1.25},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"01:00:00",37,0.95833333333333337,10.039999999999999,2.0816666666666666,36,1,30,{"$f":"IF(AC8717<60,(60-AC8717)/24,0)","v":1.25},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"02:00:00",36,1,8.9600000000000009,2.1266666666666665,37.133800000000001,0.95275833333333326,31,{"$f":"IF(AC8718<60,(60-AC8718)/24,0)","v":1.2083333333333333},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"03:00:00",32,1.1666666666666667,10.94,2.0441666666666669,37,0.95833333333333337,31,{"$f":"IF(AC8719<60,(60-AC8719)/24,0)","v":1.2083333333333333},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"04:00:00",30,1.25,10.94,2.0441666666666669,37,0.95833333333333337,32,{"$f":"IF(AC8720<60,(60-AC8720)/24,0)","v":1.1666666666666667},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"05:00:00",27,1.375,8.06,2.1641666666666666,36,1,32,{"$f":"IF(AC8721<60,(60-AC8721)/24,0)","v":1.1666666666666667},35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"06:00:00",25,1.4583333333333333,5,2.2916666666666665,34,1.0833333333333333,34,{"$f":"IF(AC8722<60,(60-AC8722)/24,0)","v":1.0833333333333333},37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"07:00:00",21,1.625,3.92,2.3366666666666664,34,1.0833333333333333,34,{"$f":"IF(AC8723<60,(60-AC8723)/24,0)","v":1.0833333333333333},37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"08:00:00",19,1.7083333333333333,3.02,2.3741666666666665,34,1.0833333333333333,34,{"$f":"IF(AC8724<60,(60-AC8724)/24,0)","v":1.0833333333333333},37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"09:00:00",18,1.75,6.98,2.2091666666666665,34,1.0833333333333333,34,{"$f":"IF(AC8725<60,(60-AC8725)/24,0)","v":1.0833333333333333},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"10:00:00",16,1.8333333333333333,21.92,1.5866666666666667,36,1,37,{"$f":"IF(AC8726<60,(60-AC8726)/24,0)","v":0.95833333333333337},41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"11:00:00",16,1.8333333333333333,28.04,1.3316666666666668,36,1,37,{"$f":"IF(AC8727<60,(60-AC8727)/24,0)","v":0.95833333333333337},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"12:00:00",16,1.8333333333333333,30.02,1.2491666666666668,34,1.0833333333333333,36,{"$f":"IF(AC8728<60,(60-AC8728)/24,0)","v":1},46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"13:00:00",12,2,30.92,1.2116666666666667,34,1.0833333333333333,36,{"$f":"IF(AC8729<60,(60-AC8729)/24,0)","v":1},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"14:00:00",12,2,30.92,1.2116666666666667,32,1.1666666666666667,36,{"$f":"IF(AC8730<60,(60-AC8730)/24,0)","v":1},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"15:00:00",10,2.0833333333333335,32,1.1666666666666667,30,1.25,34,{"$f":"IF(AC8731<60,(60-AC8731)/24,0)","v":1.0833333333333333},48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"16:00:00",9,2.125,30.92,1.2116666666666667,30,1.25,32,{"$f":"IF(AC8732<60,(60-AC8732)/24,0)","v":1.1666666666666667},44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"17:00:00",9,2.125,28.94,1.2941666666666667,30,1.25,30,{"$f":"IF(AC8733<60,(60-AC8733)/24,0)","v":1.25},39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"18:00:00",7,2.2083333333333335,28.04,1.3316666666666668,28,1.3333333333333333,30,{"$f":"IF(AC8734<60,(60-AC8734)/24,0)","v":1.25},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"19:00:00",5,2.2916666666666665,28.04,1.3316666666666668,27,1.375,28,{"$f":"IF(AC8735<60,(60-AC8735)/24,0)","v":1.3333333333333333},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"20:00:00",5,2.2916666666666665,26.06,1.4141666666666666,27,1.375,28,{"$f":"IF(AC8736<60,(60-AC8736)/24,0)","v":1.3333333333333333},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"21:00:00",5,2.2916666666666665,24.08,1.4966666666666668,25,1.4583333333333333,28,{"$f":"IF(AC8737<60,(60-AC8737)/24,0)","v":1.3333333333333333},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"22:00:00",3,2.375,21.02,1.6241666666666668,23,1.5416666666666667,28,{"$f":"IF(AC8738<60,(60-AC8738)/24,0)","v":1.3333333333333333},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"23:00:00",3,2.375,15.08,1.8716666666666668,21,1.625,26,{"$f":"IF(AC8739<60,(60-AC8739)/24,0)","v":1.4166666666666667},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,1,3,2.375,15.98,1.8341666666666665,19,1.7083333333333333,24,{"$f":"IF(AC8740<60,(60-AC8740)/24,0)","v":1.5},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"01:00:00",1,2.4583333333333335,10.94,2.0441666666666669,19,1.7083333333333333,23,{"$f":"IF(AC8741<60,(60-AC8741)/24,0)","v":1.5416666666666667},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"02:00:00",1,2.4583333333333335,10.94,2.0441666666666669,18,1.75,23,{"$f":"IF(AC8742<60,(60-AC8742)/24,0)","v":1.5416666666666667},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"03:00:00",1,2.4583333333333335,15.98,1.8341666666666665,18,1.75,22,{"$f":"IF(AC8743<60,(60-AC8743)/24,0)","v":1.5833333333333333},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"04:00:00",1,2.4583333333333335,17.059999999999999,1.7891666666666666,18,1.75,21,{"$f":"IF(AC8744<60,(60-AC8744)/24,0)","v":1.625},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"05:00:00",1,2.4583333333333335,19.04,1.7066666666666668,18,1.75,20,{"$f":"IF(AC8745<60,(60-AC8745)/24,0)","v":1.6666666666666667},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"06:00:00",1,2.4583333333333335,19.940000000000001,1.6691666666666667,18,1.75,20,{"$f":"IF(AC8746<60,(60-AC8746)/24,0)","v":1.6666666666666667},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"07:00:00",1,2.4583333333333335,21.02,1.6241666666666668,18,1.75,19,{"$f":"IF(AC8747<60,(60-AC8747)/24,0)","v":1.7083333333333333},25.34,1.4441666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"08:00:00",0,2.5,23,1.5416666666666667,18,1.75,18,{"$f":"IF(AC8748<60,(60-AC8748)/24,0)","v":1.75},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"09:00:00",0,2.5,24.08,1.4966666666666668,18,1.75,18,{"$f":"IF(AC8749<60,(60-AC8749)/24,0)","v":1.75},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"10:00:00",0,2.5,26.96,1.3766666666666667,19,1.7083333333333333,18,{"$f":"IF(AC8750<60,(60-AC8750)/24,0)","v":1.75},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"11:00:00",0,2.5,30.02,1.2491666666666668,21,1.625,16,{"$f":"IF(AC8751<60,(60-AC8751)/24,0)","v":1.8333333333333333},30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"12:00:00",0,2.5,35.06,1.0391666666666666,25,1.4583333333333333,16,{"$f":"IF(AC8752<60,(60-AC8752)/24,0)","v":1.8333333333333333},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"13:00:00",0,2.5,37.94,0.9191666666666668,27,1.375,14,{"$f":"IF(AC8753<60,(60-AC8753)/24,0)","v":1.9166666666666667},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"14:00:00",1,2.4583333333333335,39.92,0.83666666666666656,28,1.3333333333333333,14,{"$f":"IF(AC8754<60,(60-AC8754)/24,0)","v":1.9166666666666667},33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"15:00:00",1,2.4583333333333335,39.92,0.83666666666666656,28,1.3333333333333333,14,{"$f":"IF(AC8755<60,(60-AC8755)/24,0)","v":1.9166666666666667},32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"16:00:00",0,2.5,42.08,0.7466666666666667,28,1.3333333333333333,14,{"$f":"IF(AC8756<60,(60-AC8756)/24,0)","v":1.9166666666666667},28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"17:00:00",-4,2.6666666666666665,41,0.79166666666666663,27,1.375,10,{"$f":"IF(AC8757<60,(60-AC8757)/24,0)","v":2.0833333333333335},26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"18:00:00",-8,2.8333333333333335,41,0.79166666666666663,27,1.375,9,{"$f":"IF(AC8758<60,(60-AC8758)/24,0)","v":2.125},24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"19:00:00",-8,2.8333333333333335,41,0.79166666666666663,27,1.375,7,{"$f":"IF(AC8759<60,(60-AC8759)/24,0)","v":2.2083333333333335},23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"20:00:00",-9,2.875,41,0.79166666666666663,27,1.375,7,{"$f":"IF(AC8760<60,(60-AC8760)/24,0)","v":2.2083333333333335},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"21:00:00",-9,2.875,39.020000000000003,0.87416666666666654,27,1.375,3,{"$f":"IF(AC8761<60,(60-AC8761)/24,0)","v":2.375},21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"22:00:00",-9,2.875,39.020000000000003,0.87416666666666654,27,1.375,2,{"$f":"IF(AC8762<60,(60-AC8762)/24,0)","v":2.4166666666666665},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"23:00:00",-9,2.875,35.96,1.0016666666666667,27,1.375,-1,{"$f":"IF(AC8763<60,(60-AC8763)/24,0)","v":2.5416666666666665},19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,1,-9,2.875,37.04,0.95666666666666667,25,1.4583333333333333,-2,{"$f":"IF(AC8764<60,(60-AC8764)/24,0)","v":2.5833333333333335},19.399999999999999,1.6916666666666667]

{"sheet":"BldgShell2-Insulation","index":5,"n_rows":8764,"n_cols":32,"rows_kept":2250,"cut":true,"hidden":true,"merged":[[16,1,16,2],[16,3,16,4],[16,6,19,11],[17,1,17,2],[17,3,17,4],[18,1,18,2],[18,3,18,4],[19,1,19,2],[19,3,19,4],[8,13,8,16],[10,1,11,2],[12,1,13,2],[8,1,9,2],[0,1,1,11],[3,1,3,4],[3,6,3,11],[4,6,15,11],[5,1,7,2],[15,1,15,4]],"bounds":{"rows_first":1000,"rows_last":250,"rows_between":1000,"halvings":1}}
[null,"Measure: Insulation",null,null,null,null,null,null,null,null,null,null,null,"Table 3: Insulation kW/kWh factors"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"kW/kWh Factor",null,null,null,null,"Table 6: TMY3 Weather Data - HDD60 Calculations"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Electric",7.2999999999999996E-4,null,null,null,null,"Date",null,null,"Berlin",null,"Concord",null,"Dillant Hopkins/Keene",null,"Lebanon",null,"Pease/Portsmouth"]
[null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,"Fuel Oil ",{"$f":"O6","v":7.6000000000000004E-4},null,null,null,null,"Month","Day","Hour","db","HDD60","db","HDD60","db","HDD60","db","HDD60","db","HDD60"]
[null,null,null,"Value","Unit",null,"This measure considers savings associated with insulation.\n\nDefinition:\nInsulation: The installation of  insulation in an existing structure.",null,null,null,null,null,null,"Gas",{"$f":"O6","v":7.6000000000000004E-4},null,null,null,null,1,1,"01:00:00",20,{"$f":"IF(W5<60,(60-W5)/24,0)","v":1.6666666666666667},12.02,{"$f":"IF(Y5<60,(60-Y5)/24,0)","v":1.9991666666666668},19,{"$f":"IF(AA5<60,(60-AA5)/24,0)","v":1.7083333333333333},33,{"$f":"IF(AC5<60,(60-AC5)/24,0)","v":1.125},32,{"$f":"IF(AE5<60,(60-AE5)/24,0)","v":1.1666666666666667}]
[null,"Total Savings",null,{"$f":"L36","v":0},"kW",null,null,null,null,null,null,null,null,"Propane",7.6000000000000004E-4,null,null,null,null,1,1,"02:00:00",19,1.7083333333333333,10.94,{"$f":"IF(Y6<60,(60-Y6)/24,0)","v":2.0441666666666669},21,{"$f":"IF(AA6<60,(60-AA6)/24,0)","v":1.625},31,{"$f":"IF(AC6<60,(60-AC6)/24,0)","v":1.2083333333333333},32.9,{"$f":"IF(AE6<60,(60-AE6)/24,0)","v":1.1291666666666667}]
[null,null,null,{"$f":"J36","v":0},"kWh",null,null,null,null,null,null,null,null,"Central AC in Electrically Heated Unit",5.9000000000000003E-4,null,null,null,null,1,1,"03:00:00",19,1.7083333333333333,10.039999999999999,2.0816666666666666,21,1.625,31,1.2083333333333333,32.9,1.1291666666666667]
[null,null,null,{"$f":"K36","v":0},"MMBtu",null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,1,"04:00:00",18,1.75,8.9600000000000009,2.1266666666666665,23,1.5416666666666667,30,1.25,32.9,1.1291666666666667]
[null,"Measure Life",null,null,null,null,null,null,null,null,null,null,null,"Table 4: Coincidence Factors",null,null,null,null,null,1,1,"05:00:00",17,1.7916666666666667,6.08,2.2466666666666666,23,1.5416666666666667,29,1.2916666666666667,33.979999999999997,1.0841666666666667]
[null,null,null,25,"Years",null,null,null,null,null,null,null,null,"Measure Name","Fuel","CFsp","CFwp",null,null,1,1,"06:00:00",16,1.8333333333333333,6.08,2.2466666666666666,23,1.5416666666666667,28,1.3333333333333333,32.9,1.1291666666666667]
[null,"CFsp",null,null,null,null,null,null,null,null,null,null,null,"Air Sealing","Electric",0,0.43,null,null,1,1,"07:00:00",16,1.8333333333333333,5,2.2916666666666665,23,1.5416666666666667,28,1.3333333333333333,32.9,1.1291666666666667]
[null,null,null,{"$f":"VLOOKUP('Project Info'!D24,$O$15:$Q$18,2,FALSE)*100","v":{"$error":"#N/A"}},"%",null,null,null,null,null,null,null,null,"Air Sealing","Gas",0,0,null,null,1,1,"08:00:00",14,1.9166666666666667,5,2.2916666666666665,23,1.5416666666666667,27,1.375,33.979999999999997,1.0841666666666667]
[null,"CFwp",null,null,null,null,null,null,null,null,null,null,null,"Air Sealing","Fuel Oil",0,0,null,null,1,1,"09:00:00",14,1.9166666666666667,14,1.9166666666666667,25,1.4583333333333333,27,1.375,33.979999999999997,1.0841666666666667]
[null,null,null,{"$f":"VLOOKUP('Project Info'!D24,$O$15:$Q$18,3,FALSE)*100","v":{"$error":"#N/A"}},"%",null,null,null,null,null,null,null,null,"Air Sealing","Propane",0,0,null,null,1,1,"10:00:00",16,1.8333333333333333,17.059999999999999,1.7891666666666666,32,1.1666666666666667,29,1.2916666666666667,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Insulation","Electric",0.34,0.17,null,null,1,1,"11:00:00",17,1.7916666666666667,21.92,1.5866666666666667,37,0.95833333333333337,30,1.25,34.880000000000003,1.0466666666666666]
[null,"Building Envelope - Air Sealing and Insulation",null,null,null,null,null,null,null,null,null,null,null,"Insulation","Gas",0,0,null,null,1,1,"12:00:00",17,1.7916666666666667,24.98,1.4591666666666665,39,0.875,36,1,34.880000000000003,1.0466666666666666]
[null,"Measure Code",null,"COM-BS-ASI",null,null,"NOTE: For more information on this measure refer to the NH TRM. ",null,null,null,null,null,null,"Insulation","Fuel Oil",0,0,null,null,1,1,"13:00:00",16,1.8333333333333333,26.96,1.3766666666666667,43,0.70833333333333337,39,0.875,34.880000000000003,1.0466666666666666]
[null,"Market",null,"Commercial",null,null,null,null,null,null,null,null,null,"Insulation","Propane",0,0,null,null,1,1,"14:00:00",16,1.8333333333333333,28.04,1.3316666666666668,45,0.625,43,0.70833333333333337,34.880000000000003,1.0466666666666666]
[null,"Program Type",null,"Retrofit",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,1,"15:00:00",18,1.75,28.04,1.3316666666666668,45,0.625,43,0.70833333333333337,34.880000000000003,1.0466666666666666]
[null,"Category",null,"Building Shell",null,null,null,null,null,null,null,null,null,"Table 5: Efficiency Values",null,null,null,null,null,1,1,"16:00:00",16,1.8333333333333333,28.04,1.3316666666666668,45,0.625,39,0.875,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Boiler Type","Efficiency %",null,null,null,null,1,1,"17:00:00",14,1.9166666666666667,26.96,1.3766666666666667,36,1,34,1.0833333333333333,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Gas-fired",0.8,null,null,null,null,1,1,"18:00:00",14,1.9166666666666667,26.96,1.3766666666666667,34,1.0833333333333333,36,1,33.979999999999997,1.0841666666666667]
[null,null,null,"Table 1: Calculating Primary Energy Impact (Insulation)",null,null,null,null,null,null,null,null,null,"Condensing",0.9,null,null,null,null,1,1,"19:00:00",12,2,26.06,1.4141666666666666,30,1.25,33,1.125,33.979999999999997,1.0841666666666667]
[null,null,null,"Inputs",null,null,null,null,null,"Savings",null,null,null,"Non-Condensing",0.8,null,null,null,null,1,1,"20:00:00",12,2,26.06,1.4141666666666666,28,1.3333333333333333,30,1.25,32.9,1.1291666666666667]
[null,null,"Rexisting","Rnew","Area","HDD60","Heating System",null,"kW/kWh Factor","kWh","MMBtu","kW",null,"Electric Resistance",1,null,null,null,null,1,1,"21:00:00",12,2,24.08,1.4966666666666668,28,1.3333333333333333,25,1.4583333333333333,32.9,1.1291666666666667]
[null,1,{"$f":"IF('Building Shell Inputs'!H24=\"\",\"\",'Building Shell Inputs'!H24+VLOOKUP('Building Shell Inputs'!G24,'BldgShell2-Insulation'!$N$40:$O$43,2,FALSE))","v":""},{"$f":"IF('Building Shell Inputs'!I24=\"\",\"\",'Building Shell Inputs'!I24+C26)","v":""},{"$f":"IF('Building Shell Inputs'!J24=\"\",\"\",'Building Shell Inputs'!J24)","v":""},{"$f":"IF(OR(ISBLANK('Project Info'!$D$21)),\"\",IFERROR(VLOOKUP('Project Info'!$D$21,$N$30:$O$36,2,FALSE),\"\"))","v":""},{"$f":"IF('Project Info'!$D$25=$N$22,$O$22,IF('Project Info'!$D$25=$N$25,$O$25,IF('Project Info'!$D$25=$N$26,$O$26,IF(OR('Project Info'!$D$25='Project Info'!$Y$14,'Project Info'!$D$25='Project Info'!$Y$15),IF('Project Info'!$D$26=$N$23,$O$23,$O$24)))))","v":false},null,{"$f":"VLOOKUP('Project Info'!$D$24,'BldgShell2-Insulation'!$N$3:$O$7,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"IF('Project Info'!$D$24=\"Electric\",IFERROR((((1/C26-1/D26)*F26*24*E26)/(1000000*G26)*293.1),0))","v":false},{"$f":"IF('Project Info'!$D$24='Project Info'!$Y$10,0,IFERROR((((1/C26-1/D26)*F26*24*E26)/(1000000*G26)),0))","v":0},{"$f":"IFERROR(J26*VLOOKUP(I26,N2:O7,2,FALSE),0)","v":0},null,"Heat Pump",3,null,null,null,null,1,1,"22:00:00",7,2.2083333333333335,24.98,1.4591666666666665,27,1.375,23,1.5416666666666667,33.979999999999997,1.0841666666666667]
[null,2,{"$f":"IF('Building Shell Inputs'!H25=\"\",\"\",'Building Shell Inputs'!H25+VLOOKUP('Building Shell Inputs'!G25,'BldgShell2-Insulation'!$N$40:$O$43,2,FALSE))","v":""},{"$f":"IF('Building Shell Inputs'!I25=\"\",\"\",'Building Shell Inputs'!I25+C27)","v":""},{"$f":"IF('Building Shell Inputs'!J25=\"\",\"\",'Building Shell Inputs'!J25)","v":""},{"$f":"IF(OR(ISBLANK('Project Info'!$D$21)),\"\",IFERROR(VLOOKUP('Project Info'!$D$21,$N$30:$O$36,2,FALSE),\"\"))","v":""},{"$f":"IF('Project Info'!$D$25=$N$22,$O$22,IF('Project Info'!$D$25=$N$25,$O$25,IF('Project Info'!$D$25=$N$26,$O$26,IF(OR('Project Info'!$D$25='Project Info'!$Y$14,'Project Info'!$D$25='Project Info'!$Y$15),IF('Project Info'!$D$26=$N$23,$O$23,$O$24)))))","v":false},null,{"$f":"VLOOKUP('Project Info'!$D$24,'BldgShell2-Insulation'!$N$3:$O$7,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"IF('Project Info'!$D$24=\"Electric\",IFERROR((((1/C27-1/D27)*F27*24*E27)/(1000000*G27)*293.1),0))","v":false},{"$f":"IF('Project Info'!$D$24='Project Info'!$Y$10,0,IFERROR((((1/C27-1/D27)*F27*24*E27)/(1000000*G27)),0))","v":0},{"$f":"IFERROR(J27*VLOOKUP(I27,N3:O7,2,FALSE),0)","v":0},null,null,null,null,null,null,null,1,1,"23:00:00",7,2.2083333333333335,24.08,1.4966666666666668,27,1.375,21,1.625,33.979999999999997,1.0841666666666667]
[null,3,{"$f":"IF('Building Shell Inputs'!H26=\"\",\"\",'Building Shell Inputs'!H26+VLOOKUP('Building Shell Inputs'!G26,'BldgShell2-Insulation'!$N$40:$O$43,2,FALSE))","v":""},{"$f":"IF('Building Shell Inputs'!I26=\"\",\"\",'Building Shell Inputs'!I26+C28)","v":""},{"$f":"IF('Building Shell Inputs'!J26=\"\",\"\",'Building Shell Inputs'!J26)","v":""},{"$f":"IF(OR(ISBLANK('Project Info'!$D$21)),\"\",IFERROR(VLOOKUP('Project Info'!$D$21,$N$30:$O$36,2,FALSE),\"\"))","v":""},{"$f":"IF('Project Info'!$D$25=$N$22,$O$22,IF('Project Info'!$D$25=$N$25,$O$25,IF('Project Info'!$D$25=$N$26,$O$26,IF(OR('Project Info'!$D$25='Project Info'!$Y$14,'Project Info'!$D$25='Project Info'!$Y$15),IF('Project Info'!$D$26=$N$23,$O$23,$O$24)))))","v":false},null,{"$f":"VLOOKUP('Project Info'!$D$24,'BldgShell2-Insulation'!$N$3:$O$7,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"IF('Project Info'!$D$24=\"Electric\",IFERROR((((1/C28-1/D28)*F28*24*E28)/(1000000*G28)*293.1),0))","v":false},{"$f":"IF('Project Info'!$D$24='Project Info'!$Y$10,0,IFERROR((((1/C28-1/D28)*F28*24*E28)/(1000000*G28)),0))","v":0},{"$f":"IFERROR(J28*VLOOKUP(I28,N6:O8,2,FALSE),0)","v":0},null,"Table 7: HDD60",null,null,null,null,null,1,1,1,9,2.125,24.98,1.4591666666666665,27,1.375,23,1.5416666666666667,32.9,1.1291666666666667]
[null,4,{"$f":"IF('Building Shell Inputs'!H27=\"\",\"\",'Building Shell Inputs'!H27+VLOOKUP('Building Shell Inputs'!G27,'BldgShell2-Insulation'!$N$40:$O$43,2,FALSE))","v":""},{"$f":"IF('Building Shell Inputs'!I27=\"\",\"\",'Building Shell Inputs'!I27+C29)","v":""},{"$f":"IF('Building Shell Inputs'!J27=\"\",\"\",'Building Shell Inputs'!J27)","v":""},{"$f":"IF(OR(ISBLANK('Project Info'!$D$21)),\"\",IFERROR(VLOOKUP('Project Info'!$D$21,$N$30:$O$36,2,FALSE),\"\"))","v":""},{"$f":"IF('Project Info'!$D$25=$N$22,$O$22,IF('Project Info'!$D$25=$N$25,$O$25,IF('Project Info'!$D$25=$N$26,$O$26,IF(OR('Project Info'!$D$25='Project Info'!$Y$14,'Project Info'!$D$25='Project Info'!$Y$15),IF('Project Info'!$D$26=$N$23,$O$23,$O$24)))))","v":false},null,{"$f":"VLOOKUP('Project Info'!$D$24,'BldgShell2-Insulation'!$N$3:$O$7,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"IF('Project Info'!$D$24=\"Electric\",IFERROR((((1/C29-1/D29)*F29*24*E29)/(1000000*G29)*293.1),0))","v":false},{"$f":"IF('Project Info'!$D$24='Project Info'!$Y$10,0,IFERROR((((1/C29-1/D29)*F29*24*E29)/(1000000*G29)),0))","v":0},{"$f":"IFERROR(J29*VLOOKUP(I29,N7:O9,2,FALSE),0)","v":0},null,"City","HDD60",null,null,null,null,1,2,"01:00:00",10,2.0833333333333335,24.08,1.4966666666666668,27,1.375,25.306999999999999,1.4455416666666665,32.9,1.1291666666666667]
[null,5,{"$f":"IF('Building Shell Inputs'!H28=\"\",\"\",'Building Shell Inputs'!H28+VLOOKUP('Building Shell Inputs'!G28,'BldgShell2-Insulation'!$N$40:$O$43,2,FALSE))","v":""},{"$f":"IF('Building Shell Inputs'!I28=\"\",\"\",'Building Shell Inputs'!I28+C30)","v":""},{"$f":"IF('Building Shell Inputs'!J28=\"\",\"\",'Building Shell Inputs'!J28)","v":""},{"$f":"IF(OR(ISBLANK('Project Info'!$D$21)),\"\",IFERROR(VLOOKUP('Project Info'!$D$21,$N$30:$O$36,2,FALSE),\"\"))","v":""},{"$f":"IF('Project Info'!$D$25=$N$22,$O$22,IF('Project Info'!$D$25=$N$25,$O$25,IF('Project Info'!$D$25=$N$26,$O$26,IF(OR('Project Info'!$D$25='Project Info'!$Y$14,'Project Info'!$D$25='Project Info'!$Y$15),IF('Project Info'!$D$26=$N$23,$O$23,$O$24)))))","v":false},null,{"$f":"VLOOKUP('Project Info'!$D$24,'BldgShell2-Insulation'!$N$3:$O$7,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"IF('Project Info'!$D$24=\"Electric\",IFERROR((((1/C30-1/D30)*F30*24*E30)/(1000000*G30)*293.1),0))","v":false},{"$f":"IF('Project Info'!$D$24='Project Info'!$Y$10,0,IFERROR((((1/C30-1/D30)*F30*24*E30)/(1000000*G30)),0))","v":0},{"$f":"IFERROR(J30*VLOOKUP(I30,N8:O10,2,FALSE),0)","v":0},null,"Berlin",{"$f":"SUM(X5:X8764)","v":7420.0335949997034},null,null,null,null,1,2,"02:00:00",10,2.0833333333333335,24.08,1.4966666666666668,28,1.3333333333333333,25,1.4583333333333333,32,1.1666666666666667]
[null,6,{"$f":"IF('Building Shell Inputs'!H29=\"\",\"\",'Building Shell Inputs'!H29+VLOOKUP('Building Shell Inputs'!G29,'BldgShell2-Insulation'!$N$40:$O$43,2,FALSE))","v":""},{"$f":"IF('Building Shell Inputs'!I29=\"\",\"\",'Building Shell Inputs'!I29+C31)","v":""},{"$f":"IF('Building Shell Inputs'!J29=\"\",\"\",'Building Shell Inputs'!J29)","v":""},{"$f":"IF(OR(ISBLANK('Project Info'!$D$21)),\"\",IFERROR(VLOOKUP('Project Info'!$D$21,$N$30:$O$36,2,FALSE),\"\"))","v":""},{"$f":"IF('Project Info'!$D$25=$N$22,$O$22,IF('Project Info'!$D$25=$N$25,$O$25,IF('Project Info'!$D$25=$N$26,$O$26,IF(OR('Project Info'!$D$25='Project Info'!$Y$14,'Project Info'!$D$25='Project Info'!$Y$15),IF('Project Info'!$D$26=$N$23,$O$23,$O$24)))))","v":false},null,{"$f":"VLOOKUP('Project Info'!$D$24,'BldgShell2-Insulation'!$N$3:$O$7,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"IF('Project Info'!$D$24=\"Electric\",IFERROR((((1/C31-1/D31)*F31*24*E31)/(1000000*G31)*293.1),0))","v":false},{"$f":"IF('Project Info'!$D$24='Project Info'!$Y$10,0,IFERROR((((1/C31-1/D31)*F31*24*E31)/(1000000*G31)),0))","v":0},{"$f":"IFERROR(J31*VLOOKUP(I31,N8:O11,2,FALSE),0)","v":0},null,"Concord",{"$f":"SUM(Z5:Z8764)","v":6153.5524999997742},null,null,null,null,1,2,"03:00:00",10,2.0833333333333335,23,1.5416666666666667,30,1.25,25,1.4583333333333333,32,1.1666666666666667]
[null,7,{"$f":"IF('Building Shell Inputs'!H30=\"\",\"\",'Building Shell Inputs'!H30+VLOOKUP('Building Shell Inputs'!G30,'BldgShell2-Insulation'!$N$40:$O$43,2,FALSE))","v":""},{"$f":"IF('Building Shell Inputs'!I30=\"\",\"\",'Building Shell Inputs'!I30+C32)","v":""},{"$f":"IF('Building Shell Inputs'!J30=\"\",\"\",'Building Shell Inputs'!J30)","v":""},{"$f":"IF(OR(ISBLANK('Project Info'!$D$21)),\"\",IFERROR(VLOOKUP('Project Info'!$D$21,$N$30:$O$36,2,FALSE),\"\"))","v":""},{"$f":"IF('Project Info'!$D$25=$N$22,$O$22,IF('Project Info'!$D$25=$N$25,$O$25,IF('Project Info'!$D$25=$N$26,$O$26,IF(OR('Project Info'!$D$25='Project Info'!$Y$14,'Project Info'!$D$25='Project Info'!$Y$15),IF('Project Info'!$D$26=$N$23,$O$23,$O$24)))))","v":false},null,{"$f":"VLOOKUP('Project Info'!$D$24,'BldgShell2-Insulation'!$N$3:$O$7,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"IF('Project Info'!$D$24=\"Electric\",IFERROR((((1/C32-1/D32)*F32*24*E32)/(1000000*G32)*293.1),0))","v":false},{"$f":"IF('Project Info'!$D$24='Project Info'!$Y$10,0,IFERROR((((1/C32-1/D32)*F32*24*E32)/(1000000*G32)),0))","v":0},{"$f":"IFERROR(J32*VLOOKUP(I32,N9:O12,2,FALSE),0)","v":0},null,"Keene",{"$f":"SUM(AB5:AB8764)","v":5991.4529120373672},null,null,null,null,1,2,"04:00:00",10,2.0833333333333335,24.08,1.4966666666666668,28,1.3333333333333333,25,1.4583333333333333,32.9,1.1291666666666667]
[null,8,{"$f":"IF('Building Shell Inputs'!H31=\"\",\"\",'Building Shell Inputs'!H31+VLOOKUP('Building Shell Inputs'!G31,'BldgShell2-Insulation'!$N$40:$O$43,2,FALSE))","v":""},{"$f":"IF('Building Shell Inputs'!I31=\"\",\"\",'Building Shell Inputs'!I31+C33)","v":""},{"$f":"IF('Building Shell Inputs'!J31=\"\",\"\",'Building Shell Inputs'!J31)","v":""},{"$f":"IF(OR(ISBLANK('Project Info'!$D$21)),\"\",IFERROR(VLOOKUP('Project Info'!$D$21,$N$30:$O$36,2,FALSE),\"\"))","v":""},{"$f":"IF('Project Info'!$D$25=$N$22,$O$22,IF('Project Info'!$D$25=$N$25,$O$25,IF('Project Info'!$D$25=$N$26,$O$26,IF(OR('Project Info'!$D$25='Project Info'!$Y$14,'Project Info'!$D$25='Project Info'!$Y$15),IF('Project Info'!$D$26=$N$23,$O$23,$O$24)))))","v":false},null,{"$f":"VLOOKUP('Project Info'!$D$24,'BldgShell2-Insulation'!$N$3:$O$7,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"IF('Project Info'!$D$24=\"Electric\",IFERROR((((1/C33-1/D33)*F33*24*E33)/(1000000*G33)*293.1),0))","v":false},{"$f":"IF('Project Info'!$D$24='Project Info'!$Y$10,0,IFERROR((((1/C33-1/D33)*F33*24*E33)/(1000000*G33)),0))","v":0},{"$f":"IFERROR(J33*VLOOKUP(I33,N10:O13,2,FALSE),0)","v":0},null,"Lebanon",{"$f":"SUM(AD5:AD8764)","v":6183.3099613441227},null,null,null,null,1,2,"05:00:00",10,2.0833333333333335,19.04,1.7066666666666668,30,1.25,25,1.4583333333333333,33.979999999999997,1.0841666666666667]
[null,9,{"$f":"IF('Building Shell Inputs'!H32=\"\",\"\",'Building Shell Inputs'!H32+VLOOKUP('Building Shell Inputs'!G32,'BldgShell2-Insulation'!$N$40:$O$43,2,FALSE))","v":""},{"$f":"IF('Building Shell Inputs'!I32=\"\",\"\",'Building Shell Inputs'!I32+C34)","v":""},{"$f":"IF('Building Shell Inputs'!J32=\"\",\"\",'Building Shell Inputs'!J32)","v":""},{"$f":"IF(OR(ISBLANK('Project Info'!$D$21)),\"\",IFERROR(VLOOKUP('Project Info'!$D$21,$N$30:$O$36,2,FALSE),\"\"))","v":""},{"$f":"IF('Project Info'!$D$25=$N$22,$O$22,IF('Project Info'!$D$25=$N$25,$O$25,IF('Project Info'!$D$25=$N$26,$O$26,IF(OR('Project Info'!$D$25='Project Info'!$Y$14,'Project Info'!$D$25='Project Info'!$Y$15),IF('Project Info'!$D$26=$N$23,$O$23,$O$24)))))","v":false},null,{"$f":"VLOOKUP('Project Info'!$D$24,'BldgShell2-Insulation'!$N$3:$O$7,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"IF('Project Info'!$D$24=\"Electric\",IFERROR((((1/C34-1/D34)*F34*24*E34)/(1000000*G34)*293.1),0))","v":false},{"$f":"IF('Project Info'!$D$24='Project Info'!$Y$10,0,IFERROR((((1/C34-1/D34)*F34*24*E34)/(1000000*G34)),0))","v":0},{"$f":"IFERROR(J34*VLOOKUP(I34,N11:O14,2,FALSE),0)","v":0},null,"Portsmouth",{"$f":"SUM(AF5:AF8764)","v":5516.5874999999642},null,null,null,null,1,2,"06:00:00",10,2.0833333333333335,19.940000000000001,1.6691666666666667,30,1.25,23,1.5416666666666667,33.979999999999997,1.0841666666666667]
[null,10,{"$f":"IF('Building Shell Inputs'!H33=\"\",\"\",'Building Shell Inputs'!H33+VLOOKUP('Building Shell Inputs'!G33,'BldgShell2-Insulation'!$N$40:$O$43,2,FALSE))","v":""},{"$f":"IF('Building Shell Inputs'!I33=\"\",\"\",'Building Shell Inputs'!I33+C35)","v":""},{"$f":"IF('Building Shell Inputs'!J33=\"\",\"\",'Building Shell Inputs'!J33)","v":""},{"$f":"IF(OR(ISBLANK('Project Info'!$D$21)),\"\",IFERROR(VLOOKUP('Project Info'!$D$21,$N$30:$O$36,2,FALSE),\"\"))","v":""},{"$f":"IF('Project Info'!$D$25=$N$22,$O$22,IF('Project Info'!$D$25=$N$25,$O$25,IF('Project Info'!$D$25=$N$26,$O$26,IF(OR('Project Info'!$D$25='Project Info'!$Y$14,'Project Info'!$D$25='Project Info'!$Y$15),IF('Project Info'!$D$26=$N$23,$O$23,$O$24)))))","v":false},null,{"$f":"VLOOKUP('Project Info'!$D$24,'BldgShell2-Insulation'!$N$3:$O$7,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"IF('Project Info'!$D$24=\"Electric\",IFERROR((((1/C35-1/D35)*F35*24*E35)/(1000000*G35)*293.1),0))","v":false},{"$f":"IF('Project Info'!$D$24='Project Info'!$Y$10,0,IFERROR((((1/C35-1/D35)*F35*24*E35)/(1000000*G35)),0))","v":0},{"$f":"IFERROR(J35*VLOOKUP(I35,N6:O8,2,FALSE),0)","v":0},null,"Manchester",{"$f":"+O34","v":5516.5874999999642},"same zone as Portsmouth",null,null,null,1,2,"07:00:00",10,2.0833333333333335,24.98,1.4591666666666665,30,1.25,23,1.5416666666666667,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,"Totals",{"$f":"SUM(J26:J35)","v":0},{"$f":"SUM(K26:K35)","v":0},{"$f":"SUM(L26:L35)","v":0},null,"Laconia",{"$f":"+O32","v":5991.4529120373672},"same zone as Keene",null,null,null,1,2,"08:00:00",10,2.0833333333333335,24.08,1.4966666666666668,30,1.25,25,1.4583333333333333,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2,"09:00:00",12,2,28.94,1.2941666666666667,30,1.25,27,1.375,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 8: R values",null,null,null,null,null,1,2,"10:00:00",12,2,33.08,1.1216666666666668,31,1.2083333333333333,28,1.3333333333333333,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Location","R value",null,null,null,null,1,2,"11:00:00",14,1.9166666666666667,37.94,0.9191666666666668,32,1.1666666666666667,30,1.25,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Ceiling",3.36,null,null,null,null,1,2,"12:00:00",14,1.9166666666666667,42.08,0.7466666666666667,34,1.0833333333333333,32,1.1666666666666667,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Floor",6.16,null,null,null,null,1,2,"13:00:00",14,1.9166666666666667,44.96,0.62666666666666659,34,1.0833333333333333,36,1,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Wall",6.65,null,null,null,null,1,2,"14:00:00",14,1.9166666666666667,44.96,0.62666666666666659,37,0.95833333333333337,36,1,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"n/a - no insulation",0,null,null,null,null,1,2,"15:00:00",14,1.9166666666666667,44.96,0.62666666666666659,39,0.875,37,0.95833333333333337,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2,"16:00:00",14,1.9166666666666667,41,0.79166666666666663,39,0.875,36,1,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,{"$f":"IF('Project Info'!$D$25=\"Gas-Fired\",$O$23,IF('Project Info'!$D$25=\"Electric Resistance\",IF('Project Info'!$D$25=\"Heat Pump\",$O$26,IF('Project Info'!$D$26=\"Condensing\",$O$24,$O$25))))","v":false},null,null,null,null,null,null,null,null,null,1,2,"17:00:00",12,2,37.94,0.9191666666666668,37,0.95833333333333337,36,1,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2,"18:00:00",12,2,37.04,0.95666666666666667,36,1,39,0.875,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2,"19:00:00",10,2.0833333333333335,33.979999999999997,1.0841666666666667,37,0.95833333333333337,39,0.875,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2,"20:00:00",11,2.0416666666666665,33.979999999999997,1.0841666666666667,36,1,36,1,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2,"21:00:00",12,2,32,1.1666666666666667,41,0.79166666666666663,43,0.70833333333333337,28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2,"22:00:00",13,1.9583333333333333,30.02,1.2491666666666668,39,0.875,46,0.58333333333333337,26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2,"23:00:00",14,1.9166666666666667,28.04,1.3316666666666668,39,0.875,48,0.5,26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2,1,14,1.9166666666666667,28.04,1.3316666666666668,37.133800000000001,0.95275833333333326,46,0.58333333333333337,26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"01:00:00",16,1.8333333333333333,26.96,1.3766666666666667,39,0.875,48,0.5,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"02:00:00",16,1.8333333333333333,26.96,1.3766666666666667,41,0.79166666666666663,48,0.5,26.06,1.4141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"03:00:00",16,1.8333333333333333,28.94,1.2941666666666667,43,0.70833333333333337,46,0.58333333333333337,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"04:00:00",16,1.8333333333333333,28.94,1.2941666666666667,45,0.625,50,0.41666666666666669,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"05:00:00",16,1.8333333333333333,30.02,1.2491666666666668,43,0.70833333333333337,48,0.5,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"06:00:00",16,1.8333333333333333,30.92,1.2116666666666667,43,0.70833333333333337,50,0.41666666666666669,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"07:00:00",9,2.125,30.02,1.2491666666666668,45,0.625,50,0.41666666666666669,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"08:00:00",9,2.125,28.94,1.2941666666666667,46,0.58333333333333337,54,0.25,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"09:00:00",16,1.8333333333333333,28.04,1.3316666666666668,47,0.54166666666666663,48,0.5,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"10:00:00",18,1.75,28.94,1.2941666666666667,48,0.5,55,0.20833333333333334,28.04,1.3316666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"11:00:00",19,1.7083333333333333,28.94,1.2941666666666667,50,0.41666666666666669,54,0.25,28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"12:00:00",21,1.625,30.02,1.2491666666666668,57,0.125,50,0.41666666666666669,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"13:00:00",23,1.5416666666666667,30.02,1.2491666666666668,57,0.125,50,0.41666666666666669,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"14:00:00",22,1.5833333333333333,32,1.1666666666666667,59,4.1666666666666664E-2,48,0.5,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"15:00:00",21,1.625,30.92,1.2116666666666667,55,0.20833333333333334,46,0.58333333333333337,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"16:00:00",21,1.625,30.02,1.2491666666666668,52,0.33333333333333331,43,0.70833333333333337,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"17:00:00",16,{"$f":"IF(W69<60,(60-W69)/24,0)","v":1.8333333333333333},26.06,1.4141666666666666,46,0.58333333333333337,39,0.875,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"18:00:00",12,2,26.06,{"$f":"IF(Y70<60,(60-Y70)/24,0)","v":1.4141666666666666},45,{"$f":"IF(AA70<60,(60-AA70)/24,0)","v":0.625},39,{"$f":"IF(AC70<60,(60-AC70)/24,0)","v":0.875},29.84,{"$f":"IF(AE70<60,(60-AE70)/24,0)","v":1.2566666666666666}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"19:00:00",10,2.0833333333333335,24.08,1.4966666666666668,45,0.625,37,0.95833333333333337,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"20:00:00",10,2.0833333333333335,21.92,1.5866666666666667,43,0.70833333333333337,36,1,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"21:00:00",10,2.0833333333333335,19.940000000000001,1.6691666666666667,45,0.625,34.296999999999997,1.0709583333333335,28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"22:00:00",5,2.2916666666666665,19.940000000000001,1.6691666666666667,43,0.70833333333333337,32.508400000000002,1.1454833333333332,28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,"23:00:00",1,2.4583333333333335,17.059999999999999,1.7891666666666666,39,0.875,34.296999999999997,1.0709583333333335,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,3,1,1,2.4583333333333335,14,1.9166666666666667,39,0.875,36,1,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"01:00:00",1,2.4583333333333335,12.02,1.9991666666666668,39,0.875,35,1.0416666666666667,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"02:00:00",3,2.375,12.92,1.9616666666666667,39,0.875,36,1,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"03:00:00",5,2.2916666666666665,14,1.9166666666666667,39,0.875,36,1,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"04:00:00",7,2.2083333333333335,12.92,1.9616666666666667,39,0.875,34,1.0833333333333333,26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"05:00:00",7,2.2083333333333335,10.94,2.0441666666666669,37,0.95833333333333337,36,1,26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"06:00:00",7,2.2083333333333335,8.9600000000000009,2.1266666666666665,37.133800000000001,0.95275833333333326,36,1,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"07:00:00",7,2.2083333333333335,8.06,2.1641666666666666,37,0.95833333333333337,34,1.0833333333333333,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"08:00:00",9,2.125,8.9600000000000009,2.1266666666666665,36,1,34,1.0833333333333333,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"09:00:00",9,2.125,19.04,1.7066666666666668,36,1,34.213500000000003,1.0744374999999999,26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"10:00:00",10,2.0833333333333335,26.06,1.4141666666666666,36,1,34.213500000000003,1.0744374999999999,28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"11:00:00",16,1.8333333333333333,26.96,1.3766666666666667,36,1,34.213500000000003,1.0744374999999999,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"12:00:00",18,1.75,28.04,1.3316666666666668,37,0.95833333333333337,34.129800000000003,1.0779249999999998,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"13:00:00",21,1.625,30.02,1.2491666666666668,37.133800000000001,0.95275833333333326,34.129800000000003,1.0779249999999998,28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"14:00:00",21,1.625,30.92,1.2116666666666667,37.133800000000001,0.95275833333333326,36.349800000000002,0.98542499999999988,28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"15:00:00",21,1.625,32,1.1666666666666667,37.133800000000001,0.95275833333333326,36.349800000000002,0.98542499999999988,28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"16:00:00",21,1.625,30.02,1.2491666666666668,37.133800000000001,0.95275833333333326,43,0.70833333333333337,26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"17:00:00",21,1.625,26.96,1.3766666666666667,39,0.875,43.000999999999998,0.70829166666666676,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"18:00:00",19,1.7083333333333333,26.06,1.4141666666666666,55,0.20833333333333334,45.052900000000001,0.62279583333333333,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"19:00:00",19,1.7083333333333333,26.06,1.4141666666666666,52,0.33333333333333331,45.142299999999999,0.61907083333333335,21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"20:00:00",17,1.7916666666666667,24.08,1.4966666666666668,50,0.41666666666666669,45.142299999999999,0.61907083333333335,20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"21:00:00",18,1.75,23,1.5416666666666667,46,0.58333333333333337,45,0.625,18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"22:00:00",14,1.9166666666666667,19.940000000000001,1.6691666666666667,46,0.58333333333333337,45,0.625,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,"23:00:00",14,1.9166666666666667,19.940000000000001,1.6691666666666667,43,0.70833333333333337,43,0.70833333333333337,16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,4,1,11,2.0416666666666665,21.92,1.5866666666666667,43,0.70833333333333337,39,0.875,15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"01:00:00",8,2.1666666666666665,21.92,1.5866666666666667,39,0.875,39,0.875,14.9,1.8791666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"02:00:00",5,2.2916666666666665,19.940000000000001,1.6691666666666667,39,0.875,37,0.95833333333333337,14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"03:00:00",2,2.4166666666666665,12.02,1.9991666666666668,37,0.95833333333333337,36,1,14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"04:00:00",0,2.5,10.039999999999999,2.0816666666666666,37,0.95833333333333337,32,1.1666666666666667,12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"05:00:00",-6,2.75,8.9600000000000009,2.1266666666666665,36,1,28,1.3333333333333333,12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"06:00:00",-8,2.8333333333333335,8.06,2.1641666666666666,34,1.0833333333333333,27,1.375,12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"07:00:00",-6,2.75,6.98,2.2091666666666665,30,1.25,23,1.5416666666666667,11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"08:00:00",-6,2.75,10.039999999999999,2.0816666666666666,28,1.3333333333333333,21,1.625,11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"09:00:00",-2,2.5833333333333335,17.96,1.7516666666666667,27,1.375,21,1.625,12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"10:00:00",3,2.375,26.96,1.3766666666666667,28,1.3333333333333333,21,1.625,14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"11:00:00",10,2.0833333333333335,30.02,1.2491666666666668,28,1.3333333333333333,23,1.5416666666666667,15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"12:00:00",18,1.75,32,1.1666666666666667,28,1.3333333333333333,25,1.4583333333333333,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"13:00:00",19,1.7083333333333333,32,1.1666666666666667,30,1.25,27,1.375,21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"14:00:00",21,1.625,33.979999999999997,1.0841666666666667,30,1.25,27,1.375,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"15:00:00",21,1.625,33.08,1.1216666666666668,30,1.25,25,1.4583333333333333,24.08,1.4966666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"16:00:00",19,1.7083333333333333,32,1.1666666666666667,28,1.3333333333333333,25,1.4583333333333333,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"17:00:00",19,1.7083333333333333,30.92,1.2116666666666667,28,1.3333333333333333,21,1.625,21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"18:00:00",19,1.7083333333333333,30.92,1.2116666666666667,25,1.4583333333333333,19,1.7083333333333333,21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"19:00:00",19,1.7083333333333333,30.92,1.2116666666666667,23,1.5416666666666667,17,1.7916666666666667,20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"20:00:00",19,1.7083333333333333,32,1.1666666666666667,21,1.625,16,1.8333333333333333,20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"21:00:00",20,1.6666666666666667,32,1.1666666666666667,21,1.625,16,1.8333333333333333,20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"22:00:00",19,1.7083333333333333,32,1.1666666666666667,19,1.7083333333333333,12,2,20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,"23:00:00",19,1.7083333333333333,32,1.1666666666666667,18,1.75,10,2.0833333333333335,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5,1,19,1.7083333333333333,30.92,1.2116666666666667,16,1.8333333333333333,10,2.0833333333333335,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"01:00:00",18,1.75,32,1.1666666666666667,16,1.8333333333333333,10,2.0833333333333335,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"02:00:00",18,1.75,30.92,1.2116666666666667,16,1.8333333333333333,10,2.0833333333333335,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"03:00:00",19,1.7083333333333333,30.92,1.2116666666666667,12,2,10,2.0833333333333335,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"04:00:00",19,1.7083333333333333,30.92,1.2116666666666667,12,2,12,2,18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"05:00:00",19,1.7083333333333333,30.92,1.2116666666666667,12,2,10,2.0833333333333335,18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"06:00:00",18,1.75,30.92,1.2116666666666667,12,2,10,2.0833333333333335,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"07:00:00",16.374099999999999,1.8177458333333334,30.92,1.2116666666666667,10,2.0833333333333335,12,2,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"08:00:00",15.271800000000001,1.863675,30.92,1.2116666666666667,12,2,10,2.0833333333333335,18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"09:00:00",16.374099999999999,{"$f":"IF(W133<60,(60-W133)/24,0)","v":1.8177458333333334},32,1.1666666666666667,16,1.8333333333333333,12,2,20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"10:00:00",19.388200000000001,1.6921583333333334,33.08,{"$f":"IF(Y134<60,(60-Y134)/24,0)","v":1.1216666666666668},19,{"$f":"IF(AA134<60,(60-AA134)/24,0)","v":1.7083333333333333},18,{"$f":"IF(AC134<60,(60-AC134)/24,0)","v":1.75},23,{"$f":"IF(AE134<60,(60-AE134)/24,0)","v":1.5416666666666667}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"11:00:00",22.046199999999999,1.5814083333333333,35.06,1.0391666666666666,27,1.375,23,1.5416666666666667,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"12:00:00",25,1.4583333333333333,35.06,1.0391666666666666,28,1.3333333333333333,25,1.4583333333333333,26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"13:00:00",25,1.4583333333333333,35.96,1.0016666666666667,28,1.3333333333333333,27,1.375,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"14:00:00",25,1.4583333333333333,37.04,0.95666666666666667,31,1.2083333333333333,28,1.3333333333333333,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"15:00:00",27,1.375,37.04,0.95666666666666667,34,1.0833333333333333,28,1.3333333333333333,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"16:00:00",27,1.375,35.96,1.0016666666666667,34,1.0833333333333333,30,1.25,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"17:00:00",26,1.4166666666666667,35.06,1.0391666666666666,30,1.25,30,1.25,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"18:00:00",25,1.4583333333333333,33.979999999999997,1.0841666666666667,28,1.3333333333333333,28,1.3333333333333333,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"19:00:00",25,1.4583333333333333,33.979999999999997,1.0841666666666667,28,1.3333333333333333,27,1.375,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"20:00:00",24,1.5,32,1.1666666666666667,28,1.3333333333333333,23,1.5416666666666667,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"21:00:00",25,1.4583333333333333,32,1.1666666666666667,28,1.3333333333333333,23,1.5416666666666667,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"22:00:00",21,1.625,32,1.1666666666666667,30,1.25,21,1.625,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,"23:00:00",21,1.625,30.92,1.2116666666666667,30,1.25,23,1.5416666666666667,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,6,1,21,1.625,30.92,1.2116666666666667,27,1.375,21,1.625,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"01:00:00",25,1.4583333333333333,30.02,1.2491666666666668,26,1.4166666666666667,21,1.625,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"02:00:00",25,1.4583333333333333,30.02,1.2491666666666668,25,1.4583333333333333,21,1.625,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"03:00:00",25,1.4583333333333333,28.94,1.2941666666666667,25,1.4583333333333333,23,1.5416666666666667,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"04:00:00",23,1.5416666666666667,28.04,1.3316666666666668,23,1.5416666666666667,25,1.4583333333333333,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"05:00:00",23,1.5416666666666667,26.96,1.3766666666666667,21,1.625,25,1.4583333333333333,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"06:00:00",23,1.5416666666666667,26.06,1.4141666666666666,21,1.625,25,1.4583333333333333,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"07:00:00",21,1.625,24.98,1.4591666666666665,25,1.4583333333333333,25,1.4583333333333333,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"08:00:00",21,1.625,26.06,1.4141666666666666,25,1.4583333333333333,27,1.375,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"09:00:00",22,1.5833333333333333,28.04,1.3316666666666668,27,1.375,27,1.375,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"10:00:00",23,1.5416666666666667,28.04,1.3316666666666668,27,1.375,28,1.3333333333333333,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"11:00:00",25,1.4583333333333333,28.04,1.3316666666666668,30,1.25,30,1.25,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"12:00:00",27,1.375,26.96,1.3766666666666667,34,1.0833333333333333,32,1.1666666666666667,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"13:00:00",27,1.375,26.06,1.4141666666666666,36,1,34,1.0833333333333333,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"14:00:00",27,1.375,24.98,1.4591666666666665,37,0.95833333333333337,34,1.0833333333333333,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"15:00:00",27,1.375,24.08,1.4966666666666668,37,0.95833333333333337,34,1.0833333333333333,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"16:00:00",27,1.375,21.02,1.6241666666666668,37,0.95833333333333337,36,1,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"17:00:00",25,1.4583333333333333,19.04,1.7066666666666668,37,0.95833333333333337,34,1.0833333333333333,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"18:00:00",21,1.625,17.059999999999999,1.7891666666666666,37,0.95833333333333337,34,1.0833333333333333,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"19:00:00",21,1.625,15.08,1.8716666666666668,36,1,34,1.0833333333333333,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"20:00:00",19,1.7083333333333333,14,1.9166666666666667,36,1,32,1.1666666666666667,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"21:00:00",13,1.9583333333333333,12.92,1.9616666666666667,34,1.0833333333333333,30,1.25,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"22:00:00",7,2.2083333333333335,10.94,2.0441666666666669,34,1.0833333333333333,30,1.25,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,"23:00:00",3,2.375,10.039999999999999,2.0816666666666666,32,1.1666666666666667,30,1.25,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,7,1,1,2.4583333333333335,8.06,2.1641666666666666,32,1.1666666666666667,28,1.3333333333333333,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"01:00:00",0,2.5,6.98,2.2091666666666665,30,1.25,28,1.3333333333333333,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"02:00:00",3,2.375,6.08,2.2466666666666666,28,1.3333333333333333,27,1.375,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"03:00:00",5,2.2916666666666665,3.02,2.3741666666666665,28,1.3333333333333333,27,1.375,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"04:00:00",9,2.125,-3.9999999999999147E-2,2.5016666666666665,28,1.3333333333333333,27,1.375,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"05:00:00",9,2.125,-3.9999999999999147E-2,2.5016666666666665,28,1.3333333333333333,27,1.375,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"06:00:00",9,2.125,-0.94000000000000483,2.539166666666667,27,1.375,25,1.4583333333333333,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"07:00:00",10,2.0833333333333335,-2.02,2.5841666666666669,28,1.3333333333333333,25,1.4583333333333333,28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"08:00:00",10,2.0833333333333335,-3.9999999999999147E-2,2.5016666666666665,27,1.375,25,1.4583333333333333,28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"09:00:00",10,2.0833333333333335,5,2.2916666666666665,28,1.3333333333333333,25,1.4583333333333333,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"10:00:00",14,1.9166666666666667,8.9600000000000009,2.1266666666666665,30,1.25,27,1.375,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"11:00:00",19,1.7083333333333333,10.94,2.0441666666666669,30,1.25,28,1.3333333333333333,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"12:00:00",25,1.4583333333333333,14,1.9166666666666667,34,1.0833333333333333,30,1.25,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"13:00:00",28,1.3333333333333333,15.98,1.8341666666666665,34,1.0833333333333333,30,1.25,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"14:00:00",28,1.3333333333333333,17.059999999999999,1.7891666666666666,36,1,32,1.1666666666666667,28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"15:00:00",30,1.25,17.96,1.7516666666666667,36,1,34,1.0833333333333333,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"16:00:00",29,1.2916666666666667,17.96,1.7516666666666667,36,1,32,1.1666666666666667,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"17:00:00",28,1.3333333333333333,14,1.9166666666666667,30,1.25,30,1.25,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"18:00:00",27,1.375,12.02,1.9991666666666668,30,1.25,28,1.3333333333333333,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"19:00:00",27,1.375,10.94,2.0441666666666669,30,1.25,30,1.25,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"20:00:00",25,1.4583333333333333,8.9600000000000009,2.1266666666666665,28,1.3333333333333333,30,1.25,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"21:00:00",25,1.4583333333333333,5,2.2916666666666665,28,1.3333333333333333,30,1.25,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"22:00:00",25,1.4583333333333333,5,2.2916666666666665,27,1.375,28,1.3333333333333333,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,"23:00:00",25,1.4583333333333333,8.9600000000000009,2.1266666666666665,25,1.4583333333333333,25,1.4583333333333333,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,8,1,25,1.4583333333333333,8.9600000000000009,2.1266666666666665,27,1.375,23,1.5416666666666667,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"01:00:00",25,{"$f":"IF(W197<60,(60-W197)/24,0)","v":1.4583333333333333},10.039999999999999,2.0816666666666666,27,1.375,22,1.5833333333333333,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"02:00:00",25,1.4583333333333333,10.039999999999999,{"$f":"IF(Y198<60,(60-Y198)/24,0)","v":2.0816666666666666},27,{"$f":"IF(AA198<60,(60-AA198)/24,0)","v":1.375},21,{"$f":"IF(AC198<60,(60-AC198)/24,0)","v":1.625},24.98,{"$f":"IF(AE198<60,(60-AE198)/24,0)","v":1.4591666666666665}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"03:00:00",25,1.4583333333333333,10.94,2.0441666666666669,27,1.375,21,1.625,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"04:00:00",25,1.4583333333333333,10.94,2.0441666666666669,25,1.4583333333333333,21,1.625,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"05:00:00",23,1.5416666666666667,10.94,2.0441666666666669,23,1.5416666666666667,28,1.3333333333333333,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"06:00:00",22,1.5833333333333333,12.02,1.9991666666666668,21,1.625,28,1.3333333333333333,21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"07:00:00",19,1.7083333333333333,12.02,1.9991666666666668,19,1.7083333333333333,28,1.3333333333333333,21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"08:00:00",18,1.75,12.92,1.9616666666666667,19,1.7083333333333333,28,1.3333333333333333,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"09:00:00",18,1.75,14,1.9166666666666667,23,1.5416666666666667,30,1.25,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"10:00:00",19,1.7083333333333333,15.08,1.8716666666666668,32,1.1666666666666667,32,1.1666666666666667,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"11:00:00",21,1.625,15.98,1.8341666666666665,36,1,36,1,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"12:00:00",22,1.5833333333333333,17.059999999999999,1.7891666666666666,39,0.875,39,0.875,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"13:00:00",21,1.625,17.96,1.7516666666666667,41,0.79166666666666663,39,0.875,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"14:00:00",21,1.625,17.96,1.7516666666666667,43,0.70833333333333337,39,0.875,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"15:00:00",19,1.7083333333333333,19.940000000000001,1.6691666666666667,45,0.625,39,0.875,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"16:00:00",18,1.75,19.940000000000001,1.6691666666666667,43,0.70833333333333337,39,0.875,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"17:00:00",17,1.7916666666666667,19.940000000000001,1.6691666666666667,36,1,36,1,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"18:00:00",16,1.8333333333333333,21.02,1.6241666666666668,36,1,34,1.0833333333333333,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"19:00:00",16,1.8333333333333333,21.02,1.6241666666666668,34,1.0833333333333333,32,1.1666666666666667,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"20:00:00",13,1.9583333333333333,21.92,1.5866666666666667,34,1.0833333333333333,31,1.2083333333333333,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"21:00:00",12,2,23,1.5416666666666667,34,1.0833333333333333,30,1.25,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"22:00:00",10,2.0833333333333335,24.08,1.4966666666666668,36,1,30,1.25,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,"23:00:00",10,2.0833333333333335,24.08,1.4966666666666668,34,1.0833333333333333,30,1.25,21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,9,1,9,2.125,23,1.5416666666666667,34,1.0833333333333333,28,1.3333333333333333,21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"01:00:00",8,2.1666666666666665,19.04,1.7066666666666668,34,1.0833333333333333,30,1.25,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"02:00:00",7,2.2083333333333335,14,1.9166666666666667,34,1.0833333333333333,30,1.25,18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"03:00:00",5,2.2916666666666665,12.02,1.9991666666666668,34,1.0833333333333333,30,1.25,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"04:00:00",4,2.3333333333333335,12.92,1.9616666666666667,34,1.0833333333333333,30,1.25,14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"05:00:00",3,2.375,28.04,1.3316666666666668,34,1.0833333333333333,32,1.1666666666666667,12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"06:00:00",3,2.375,30.92,1.2116666666666667,34,1.0833333333333333,32,1.1666666666666667,14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"07:00:00",1,2.4583333333333335,32,1.1666666666666667,34,1.0833333333333333,32,1.1666666666666667,12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"08:00:00",-2,2.5833333333333335,30.02,1.2491666666666668,34,1.0833333333333333,34,1.0833333333333333,14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"09:00:00",3,2.375,28.04,1.3316666666666668,36,1,37,0.95833333333333337,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"10:00:00",6,2.25,26.96,1.3766666666666667,39,0.875,37,0.95833333333333337,20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"11:00:00",9,2.125,26.96,1.3766666666666667,43,0.70833333333333337,39,0.875,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"12:00:00",10,2.0833333333333335,26.96,1.3766666666666667,43,0.70833333333333337,37,0.95833333333333337,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"13:00:00",12,2,26.96,1.3766666666666667,43,0.70833333333333337,39,0.875,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"14:00:00",14,1.9166666666666667,24.08,1.4966666666666668,43,0.70833333333333337,40,0.83333333333333337,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"15:00:00",14,1.9166666666666667,21.92,1.5866666666666667,43,0.70833333333333337,39,0.875,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"16:00:00",12,2,19.940000000000001,1.6691666666666667,41,0.79166666666666663,39,0.875,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"17:00:00",10,2.0833333333333335,17.059999999999999,1.7891666666666666,43,0.70833333333333337,36,1,20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"18:00:00",3,2.375,14,1.9166666666666667,41,0.79166666666666663,36,1,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"19:00:00",0,2.5,12.92,1.9616666666666667,41,0.79166666666666663,37,0.95833333333333337,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"20:00:00",-4,2.6666666666666665,10.039999999999999,2.0816666666666666,41,0.79166666666666663,37,0.95833333333333337,18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"21:00:00",-6,2.75,8.9600000000000009,2.1266666666666665,39,0.875,36,1,16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"22:00:00",-8,2.8333333333333335,6.98,2.2091666666666665,39,0.875,34,1.0833333333333333,14.9,1.8791666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,"23:00:00",-6,2.75,6.98,2.2091666666666665,36,1,34,1.0833333333333333,12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,10,1,-4,2.6666666666666665,6.08,2.2466666666666666,43,0.70833333333333337,36,1,11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"01:00:00",-8,2.8333333333333335,5,2.2916666666666665,41,0.79166666666666663,43,0.70833333333333337,9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"02:00:00",-8,2.8333333333333335,3.92,2.3366666666666664,39,0.875,39,0.875,7.88,2.1716666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"03:00:00",-6,2.75,3.92,2.3366666666666664,39,0.875,43,0.70833333333333337,6.98,2.2091666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"04:00:00",0,2.5,3.02,2.3741666666666665,39,0.875,43,0.70833333333333337,5.9,2.2541666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"05:00:00",1,2.4583333333333335,3.02,2.3741666666666665,37,0.95833333333333337,43,0.70833333333333337,5,2.2916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"06:00:00",3,2.375,3.02,2.3741666666666665,34,1.0833333333333333,43,0.70833333333333337,3.92,2.3366666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"07:00:00",5,2.2916666666666665,3.02,2.3741666666666665,39,0.875,43,0.70833333333333337,2.84,2.3816666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"08:00:00",7,2.2083333333333335,3.02,2.3741666666666665,37,0.95833333333333337,45,0.625,3.92,2.3366666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"09:00:00",9,2.125,3.92,2.3366666666666664,41,0.79166666666666663,45,0.625,5,2.2916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"10:00:00",12,2,5,2.2916666666666665,45,0.625,45,0.625,6.98,2.2091666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"11:00:00",16,1.8333333333333333,6.98,2.2091666666666665,46,0.58333333333333337,43,0.70833333333333337,8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"12:00:00",25,1.4583333333333333,8.9600000000000009,2.1266666666666665,46,0.58333333333333337,43,0.70833333333333337,10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"13:00:00",27,1.375,10.039999999999999,2.0816666666666666,48,0.5,39,0.875,10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"14:00:00",27,1.375,10.94,2.0441666666666669,48,0.5,39,0.875,10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"15:00:00",27,1.375,12.02,1.9991666666666668,46,0.58333333333333337,39,0.875,10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"16:00:00",26,1.4166666666666667,12.92,1.9616666666666667,41,0.79166666666666663,37,0.95833333333333337,9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"17:00:00",23,{"$f":"IF(W261<60,(60-W261)/24,0)","v":1.5416666666666667},12.92,1.9616666666666667,39,0.875,37,0.95833333333333337,8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"18:00:00",21,1.625,12.92,{"$f":"IF(Y262<60,(60-Y262)/24,0)","v":1.9616666666666667},37,{"$f":"IF(AA262<60,(60-AA262)/24,0)","v":0.95833333333333337},36,{"$f":"IF(AC262<60,(60-AC262)/24,0)","v":1},8.9600000000000009,{"$f":"IF(AE262<60,(60-AE262)/24,0)","v":2.1266666666666665}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"19:00:00",21,1.625,14,1.9166666666666667,37,0.95833333333333337,36,1,8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"20:00:00",19,1.7083333333333333,12.02,1.9991666666666668,39,0.875,36,1,8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"21:00:00",18,1.75,10.94,2.0441666666666669,39,0.875,36,1,8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"22:00:00",18,1.75,12.02,1.9991666666666668,39,0.875,36,1,7.88,2.1716666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,"23:00:00",16,1.8333333333333333,12.92,1.9616666666666667,39,0.875,37,0.95833333333333337,8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,11,1,16,1.8333333333333333,10.94,2.0441666666666669,39,0.875,37,0.95833333333333337,8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"01:00:00",16,1.8333333333333333,10.94,2.0441666666666669,39,0.875,37,0.95833333333333337,9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"02:00:00",14,1.9166666666666667,10.94,2.0441666666666669,39,0.875,36,1,9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"03:00:00",12,2,10.94,2.0441666666666669,39,0.875,36,1,10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"04:00:00",10,2.0833333333333335,10.94,2.0441666666666669,37,0.95833333333333337,34,1.0833333333333333,11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"05:00:00",9,2.125,10.94,2.0441666666666669,37,0.95833333333333337,34,1.0833333333333333,11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"06:00:00",9,2.125,10.94,2.0441666666666669,37,0.95833333333333337,34,1.0833333333333333,12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"07:00:00",9,2.125,10.94,2.0441666666666669,36,1,34,1.0833333333333333,12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"08:00:00",7,2.2083333333333335,12.02,1.9991666666666668,36,1,34,1.0833333333333333,14.9,1.8791666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"09:00:00",10,2.0833333333333335,12.92,1.9616666666666667,36,1,32,1.1666666666666667,15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"10:00:00",12,2,14,1.9166666666666667,36,1,34,1.0833333333333333,16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"11:00:00",12,2,17.059999999999999,1.7891666666666666,34,1.0833333333333333,30,1.25,18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"12:00:00",16,1.8333333333333333,19.04,1.7066666666666668,36,1,30,1.25,21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"13:00:00",18,1.75,21.92,1.5866666666666667,36,1,30,1.25,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"14:00:00",19,1.7083333333333333,23,1.5416666666666667,36,1,30,1.25,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"15:00:00",19,1.7083333333333333,24.08,1.4966666666666668,36,1,31,1.2083333333333333,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"16:00:00",18,1.75,24.98,1.4591666666666665,36,1,30,1.25,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"17:00:00",16,1.8333333333333333,24.08,1.4966666666666668,34,1.0833333333333333,28,1.3333333333333333,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"18:00:00",7,2.2083333333333335,24.08,1.4966666666666668,30,1.25,28,1.3333333333333333,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"19:00:00",3,2.375,24.98,1.4591666666666665,30,1.25,27,1.375,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"20:00:00",0,2.5,24.08,1.4966666666666668,30,1.25,25,1.4583333333333333,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"21:00:00",-2,2.5833333333333335,23,1.5416666666666667,28,1.3333333333333333,21,1.625,26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"22:00:00",-6,2.75,23,1.5416666666666667,28,1.3333333333333333,21,1.625,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,"23:00:00",-8,2.8333333333333335,23,1.5416666666666667,27,1.375,19,1.7083333333333333,26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,12,1,-9,2.875,23,1.5416666666666667,27,1.375,19,1.7083333333333333,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"01:00:00",-9,2.875,23,1.5416666666666667,27,1.375,21,1.625,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"02:00:00",-11,2.9583333333333335,23,1.5416666666666667,25,1.4583333333333333,19,1.7083333333333333,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"03:00:00",-11,2.9583333333333335,24.08,1.4966666666666668,25,1.4583333333333333,19,1.7083333333333333,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"04:00:00",-11,2.9583333333333335,23,1.5416666666666667,25,1.4583333333333333,18,1.75,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"05:00:00",-11,2.9583333333333335,26.96,1.3766666666666667,23,1.5416666666666667,19,1.7083333333333333,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"06:00:00",-9,2.875,26.06,1.4141666666666666,23,1.5416666666666667,19,1.7083333333333333,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"07:00:00",-9,2.875,21.92,1.5866666666666667,25,1.4583333333333333,19,1.7083333333333333,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"08:00:00",-9,2.875,17.96,1.7516666666666667,25,1.4583333333333333,19,1.7083333333333333,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"09:00:00",-8,2.8333333333333335,17.96,1.7516666666666667,23,1.5416666666666667,19,1.7083333333333333,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"10:00:00",1,2.4583333333333335,17.96,1.7516666666666667,23,1.5416666666666667,19,1.7083333333333333,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"11:00:00",7,2.2083333333333335,19.04,1.7066666666666668,21,1.625,19,1.7083333333333333,41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"12:00:00",14,1.9166666666666667,19.940000000000001,1.6691666666666667,21,1.625,21,1.625,44.96,0.62666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"13:00:00",21,1.625,21.02,1.6241666666666668,21,1.625,21,1.625,47.84,0.50666666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"14:00:00",23,1.5416666666666667,21.02,1.6241666666666668,19,1.7083333333333333,19,1.7083333333333333,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"15:00:00",25,1.4583333333333333,23,1.5416666666666667,21,1.625,19,1.7083333333333333,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"16:00:00",23,1.5416666666666667,23,1.5416666666666667,21,1.625,18,1.75,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"17:00:00",23,1.5416666666666667,19.940000000000001,1.6691666666666667,19,1.7083333333333333,16,1.8333333333333333,48.92,0.46166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"18:00:00",21,1.625,19.04,1.7066666666666668,18,1.75,12,2,48.92,0.46166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"19:00:00",21,1.625,17.96,1.7516666666666667,16,1.8333333333333333,10,2.0833333333333335,46.94,0.5441666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"20:00:00",18,1.75,10.039999999999999,2.0816666666666666,14,1.9166666666666667,10,2.0833333333333335,46.94,0.5441666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"21:00:00",19,1.7083333333333333,8.06,2.1641666666666666,12,2,9,2.125,41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"22:00:00",16,1.8333333333333333,3.92,2.3366666666666664,12,2,9,2.125,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,"23:00:00",19,1.7083333333333333,1.04,2.4566666666666666,10,2.0833333333333335,7,2.2083333333333335,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,13,1,19,1.7083333333333333,-3.9999999999999147E-2,2.5016666666666665,9,2.125,5,2.2916666666666665,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"01:00:00",19,1.7083333333333333,-2.02,2.5841666666666669,7,2.2083333333333335,3,2.375,39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"02:00:00",19,1.7083333333333333,-2.02,2.5841666666666669,7,2.2083333333333335,3,2.375,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"03:00:00",21,1.625,-2.92,2.6216666666666666,7,2.2083333333333335,3,2.375,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"04:00:00",21,1.625,-5.98,2.749166666666667,5,2.2916666666666665,3,2.375,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"05:00:00",21,1.625,-7.06,2.7941666666666669,3,2.375,1,2.4583333333333335,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"06:00:00",23,1.5416666666666667,-7.06,2.7941666666666669,3,2.375,1,2.4583333333333335,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"07:00:00",25,1.4583333333333333,-7.06,2.7941666666666669,3,2.375,1,2.4583333333333335,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"08:00:00",25,1.4583333333333333,-5.98,2.749166666666667,3,2.375,1,2.4583333333333335,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"09:00:00",30,{"$f":"IF(W325<60,(60-W325)/24,0)","v":1.25},1.04,2.4566666666666666,5,2.2916666666666665,1,2.4583333333333335,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"10:00:00",30,1.25,5,{"$f":"IF(Y326<60,(60-Y326)/24,0)","v":2.2916666666666665},7,{"$f":"IF(AA326<60,(60-AA326)/24,0)","v":2.2083333333333335},3,{"$f":"IF(AC326<60,(60-AC326)/24,0)","v":2.375},37.94,{"$f":"IF(AE326<60,(60-AE326)/24,0)","v":0.9191666666666668}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"11:00:00",30,1.25,10.039999999999999,2.0816666666666666,9,2.125,5,2.2916666666666665,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"12:00:00",31,1.2083333333333333,15.08,1.8716666666666668,9,2.125,7,2.2083333333333335,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"13:00:00",30,1.25,19.04,1.7066666666666668,10,2.0833333333333335,9,2.125,39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"14:00:00",30,1.25,24.08,1.4966666666666668,10,2.0833333333333335,9,2.125,39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"15:00:00",30,1.25,24.98,1.4591666666666665,10,2.0833333333333335,10,2.0833333333333335,42.98,0.70916666666666683]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"16:00:00",30,1.25,24.98,1.4591666666666665,10,2.0833333333333335,9,2.125,41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"17:00:00",30,1.25,24.98,1.4591666666666665,10,2.0833333333333335,7,2.2083333333333335,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"18:00:00",30,1.25,24.98,1.4591666666666665,9,2.125,7,2.2083333333333335,39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"19:00:00",28,1.3333333333333333,26.06,1.4141666666666666,8,2.1666666666666665,5,2.2916666666666665,39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"20:00:00",27,1.375,26.96,1.3766666666666667,7,2.2083333333333335,3,2.375,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"21:00:00",27,1.375,24.98,1.4591666666666665,7,2.2083333333333335,3,2.375,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"22:00:00",21,1.625,21.92,1.5866666666666667,5,2.2916666666666665,3,2.375,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,"23:00:00",18,1.75,19.04,1.7066666666666668,3,2.375,1,2.4583333333333335,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,14,1,10.633100000000001,2.0569541666666669,24.08,1.4966666666666668,3,2.375,1,2.4583333333333335,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"01:00:00",9,2.125,26.06,1.4141666666666666,3,2.375,3,2.375,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"02:00:00",7,2.2083333333333335,24.98,1.4591666666666665,3,2.375,1,2.4583333333333335,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"03:00:00",9,2.125,21.02,1.6241666666666668,3,2.375,1,2.4583333333333335,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"04:00:00",10,2.0833333333333335,19.04,1.7066666666666668,1,2.4583333333333335,0,2.5,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"05:00:00",10,2.0833333333333335,17.059999999999999,1.7891666666666666,1,2.4583333333333335,0,2.5,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"06:00:00",12,2,17.96,1.7516666666666667,1,2.4583333333333335,0,2.5,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"07:00:00",14,1.9166666666666667,15.98,1.8341666666666665,0,2.5,-2,2.5833333333333335,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"08:00:00",14,1.9166666666666667,15.08,1.8716666666666668,-2,2.5833333333333335,-2,2.5833333333333335,43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"09:00:00",16,1.8333333333333333,19.04,1.7066666666666668,1,2.4583333333333335,0,2.5,53.96,0.25166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"10:00:00",17,1.7916666666666667,24.98,1.4591666666666665,3,2.375,1,2.4583333333333335,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"11:00:00",19,1.7083333333333333,26.96,1.3766666666666667,7,2.2083333333333335,3,2.375,53.96,0.25166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"12:00:00",20,1.6666666666666667,28.94,1.2941666666666667,9,2.125,7,2.2083333333333335,53.96,0.25166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"13:00:00",20,1.6666666666666667,32,1.1666666666666667,12,2,9,2.125,56.84,0.13166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"14:00:00",19,1.7083333333333333,33.08,1.1216666666666668,14,1.9166666666666667,10,2.0833333333333335,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"15:00:00",20,1.6666666666666667,33.979999999999997,1.0841666666666667,12,2,11,2.0416666666666665,59.9,4.1666666666667256E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"16:00:00",19,1.7083333333333333,35.06,1.0391666666666666,16,1.8333333333333333,10,2.0833333333333335,60.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"17:00:00",18,1.75,33.08,1.1216666666666668,12,2,9,2.125,60.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"18:00:00",18,1.75,32,1.1666666666666667,9,2.125,7,2.2083333333333335,60.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"19:00:00",18,1.75,32,1.1666666666666667,7,2.2083333333333335,5,2.2916666666666665,61.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"20:00:00",17,1.7916666666666667,30.92,1.2116666666666667,3,2.375,3,2.375,61.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"21:00:00",18,1.75,30.92,1.2116666666666667,3,2.375,3,2.375,61.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"22:00:00",19,1.7083333333333333,30.92,1.2116666666666667,1,2.4583333333333335,5,2.2916666666666665,61.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,"23:00:00",19,1.7083333333333333,30.92,1.2116666666666667,3,2.375,7,2.2083333333333335,61.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,15,1,19,1.7083333333333333,30.92,1.2116666666666667,3,2.375,7,2.2083333333333335,56.84,0.13166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"01:00:00",19,1.7083333333333333,32,1.1666666666666667,5,2.2916666666666665,7,2.2083333333333335,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"02:00:00",19,1.7083333333333333,26.06,1.4141666666666666,7,2.2083333333333335,10,2.0833333333333335,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"03:00:00",19,1.7083333333333333,26.06,1.4141666666666666,12,2,12,2,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"04:00:00",19,1.7083333333333333,23,1.5416666666666667,16,1.8333333333333333,16,1.8333333333333333,57.92,8.66666666666666E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"05:00:00",19,1.7083333333333333,21.92,1.5866666666666667,16,1.8333333333333333,18,1.75,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"06:00:00",21,1.625,21.02,1.6241666666666668,16,1.8333333333333333,16,1.8333333333333333,56.84,0.13166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"07:00:00",21,1.625,19.940000000000001,1.6691666666666667,19,1.7083333333333333,16,1.8333333333333333,54.86,0.2141666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"08:00:00",20,1.6666666666666667,23,1.5416666666666667,23,1.5416666666666667,16,1.8333333333333333,54.86,0.2141666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"09:00:00",21,1.625,24.08,1.4966666666666668,19,1.7083333333333333,18,1.75,52.88,0.29666666666666658]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"10:00:00",23,1.5416666666666667,26.96,1.3766666666666667,19,1.7083333333333333,19,1.7083333333333333,52.88,0.29666666666666658]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"11:00:00",26,1.4166666666666667,28.04,1.3316666666666668,21,1.625,23,1.5416666666666667,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"12:00:00",28,1.3333333333333333,30.92,1.2116666666666667,25,1.4583333333333333,25,1.4583333333333333,55.94,0.16916666666666677]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"13:00:00",28,1.3333333333333333,33.08,1.1216666666666668,28,1.3333333333333333,27,1.375,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"14:00:00",28,1.3333333333333333,35.06,1.0391666666666666,34,1.0833333333333333,28,1.3333333333333333,53.96,0.25166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"15:00:00",30,1.25,39.92,0.83666666666666656,34,1.0833333333333333,28,1.3333333333333333,50.9,0.37916666666666671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"16:00:00",33,1.125,37.04,0.95666666666666667,36,1,28,1.3333333333333333,50.9,0.37916666666666671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"17:00:00",34,1.0833333333333333,37.04,0.95666666666666667,36,1,28,1.3333333333333333,50.9,0.37916666666666671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"18:00:00",32,1.1666666666666667,37.04,0.95666666666666667,34,1.0833333333333333,23,1.5416666666666667,51.98,0.33416666666666678]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"19:00:00",32,1.1666666666666667,39.020000000000003,0.87416666666666654,27,1.375,19,1.7083333333333333,50.9,0.37916666666666671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"20:00:00",32,1.1666666666666667,35.96,1.0016666666666667,23,1.5416666666666667,18,1.75,50.9,0.37916666666666671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"21:00:00",30,1.25,35.06,1.0391666666666666,20,1.6666666666666667,12,2,51.98,0.33416666666666678]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"22:00:00",28,1.3333333333333333,35.06,1.0391666666666666,18,1.75,9,2.125,50.9,0.37916666666666671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,"23:00:00",27,1.375,35.96,1.0016666666666667,14,1.9166666666666667,5,2.2916666666666665,50.9,0.37916666666666671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,16,1,25,1.4583333333333333,35.06,1.0391666666666666,10,2.0833333333333335,3,2.375,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"01:00:00",25,{"$f":"IF(W389<60,(60-W389)/24,0)","v":1.4583333333333333},35.96,1.0016666666666667,9,2.125,1,2.4583333333333335,50.9,0.37916666666666671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"02:00:00",24,1.5,35.06,{"$f":"IF(Y390<60,(60-Y390)/24,0)","v":1.0391666666666666},5,{"$f":"IF(AA390<60,(60-AA390)/24,0)","v":2.2916666666666665},0,{"$f":"IF(AC390<60,(60-AC390)/24,0)","v":2.5},51.98,{"$f":"IF(AE390<60,(60-AE390)/24,0)","v":0.33416666666666678}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"03:00:00",23,1.5416666666666667,33.979999999999997,1.0841666666666667,1,2.4583333333333335,-4,2.6666666666666665,50.9,0.37916666666666671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"04:00:00",21,1.625,32,1.1666666666666667,0,2.5,-6,2.75,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"05:00:00",21,1.625,33.08,1.1216666666666668,-2,2.5833333333333335,-8,2.8333333333333335,48.92,0.46166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"06:00:00",21,1.625,33.979999999999997,1.0841666666666667,-2,2.5833333333333335,-8,2.8333333333333335,48.92,0.46166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"07:00:00",21,1.625,33.979999999999997,1.0841666666666667,-4,2.6666666666666665,-9,2.875,47.84,0.50666666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"08:00:00",20,1.6666666666666667,33.979999999999997,1.0841666666666667,-4,2.6666666666666665,-9,2.875,47.84,0.50666666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"09:00:00",20,1.6666666666666667,35.06,1.0391666666666666,-4,2.6666666666666665,-9,2.875,48.92,0.46166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"10:00:00",21,1.625,37.94,0.9191666666666668,0,2.5,-8,2.8333333333333335,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"11:00:00",21,1.625,41,0.79166666666666663,0,2.5,-6,2.75,51.98,0.33416666666666678]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"12:00:00",21,1.625,41,0.79166666666666663,1,2.4583333333333335,-4,2.6666666666666665,52.88,0.29666666666666658]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"13:00:00",21,1.625,41,0.79166666666666663,3,2.375,-2,2.5833333333333335,52.88,0.29666666666666658]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"14:00:00",21,1.625,41,0.79166666666666663,5,2.2916666666666665,0,2.5,50.9,0.37916666666666671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"15:00:00",21,1.625,39.92,0.83666666666666656,7,2.2083333333333335,0,2.5,46.94,0.5441666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"16:00:00",20,1.6666666666666667,39.92,0.83666666666666656,3,2.375,0,2.5,44.96,0.62666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"17:00:00",18,1.75,37.94,0.9191666666666668,1,2.4583333333333335,-2,2.5833333333333335,44.96,0.62666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"18:00:00",16,1.8333333333333333,37.04,0.95666666666666667,1,2.4583333333333335,-4,2.6666666666666665,44.96,0.62666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"19:00:00",14,1.9166666666666667,35.96,1.0016666666666667,0,2.5,-6,2.75,43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"20:00:00",11,2.0416666666666665,35.96,1.0016666666666667,0,2.5,-6,2.75,42.98,0.70916666666666683]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"21:00:00",10,2.0833333333333335,35.96,1.0016666666666667,0,2.5,-8,2.8333333333333335,42.98,0.70916666666666683]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"22:00:00",9,2.125,33.08,1.1216666666666668,-2,2.5833333333333335,-9,2.875,41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,"23:00:00",3,2.375,32,1.1666666666666667,-2,2.5833333333333335,-9,2.875,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,17,1,-2,2.5833333333333335,32,1.1666666666666667,-2,2.5833333333333335,-9,2.875,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"01:00:00",-6,2.75,32,1.1666666666666667,-2,2.5833333333333335,-11,2.9583333333333335,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"02:00:00",-13,3.0416666666666665,32,1.1666666666666667,-2,2.5833333333333335,-9,2.875,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"03:00:00",-15,3.125,32,1.1666666666666667,-2,2.5833333333333335,-11,2.9583333333333335,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"04:00:00",-15,3.125,30.02,1.2491666666666668,-4,2.6666666666666665,-15,3.125,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"05:00:00",-15,3.125,30.92,1.2116666666666667,-4,2.6666666666666665,-9,2.875,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"06:00:00",-17,3.2083333333333335,30.92,1.2116666666666667,-4,2.6666666666666665,-13,3.0416666666666665,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"07:00:00",-17,3.2083333333333335,30.02,1.2491666666666668,-6,2.75,-11,2.9583333333333335,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"08:00:00",-17,3.2083333333333335,28.94,1.2941666666666667,-6,2.75,-11,2.9583333333333335,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"09:00:00",-11,2.9583333333333335,32,1.1666666666666667,-2,2.5833333333333335,-9,2.875,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"10:00:00",-4,2.6666666666666665,33.08,1.1216666666666668,0,2.5,-6,2.75,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"11:00:00",3,2.375,33.979999999999997,1.0841666666666667,3,2.375,-2,2.5833333333333335,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"12:00:00",10,2.0833333333333335,33.979999999999997,1.0841666666666667,7,2.2083333333333335,0,2.5,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"13:00:00",16,1.8333333333333333,35.96,1.0016666666666667,9,2.125,3,2.375,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"14:00:00",19,1.7083333333333333,35.96,1.0016666666666667,10,2.0833333333333335,5,2.2916666666666665,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"15:00:00",19,1.7083333333333333,35.06,1.0391666666666666,12,2,7,2.2083333333333335,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"16:00:00",19,1.7083333333333333,35.06,1.0391666666666666,12,2,7,2.2083333333333335,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"17:00:00",18,1.75,33.979999999999997,1.0841666666666667,10,2.0833333333333335,3,2.375,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"18:00:00",18,1.75,33.979999999999997,1.0841666666666667,10,2.0833333333333335,1,2.4583333333333335,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"19:00:00",18,1.75,33.979999999999997,1.0841666666666667,9,2.125,1,2.4583333333333335,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"20:00:00",18,1.75,33.08,1.1216666666666668,7,2.2083333333333335,-2,2.5833333333333335,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"21:00:00",18,1.75,28.04,1.3316666666666668,7,2.2083333333333335,-6,2.75,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"22:00:00",18,1.75,26.06,1.4141666666666666,5,2.2916666666666665,-6,2.75,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,"23:00:00",16,1.8333333333333333,24.08,1.4966666666666668,7,2.2083333333333335,-8,2.8333333333333335,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,18,1,7,2.2083333333333335,23,1.5416666666666667,5,2.2916666666666665,-9,2.875,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"01:00:00",0,2.5,21.92,1.5866666666666667,3,2.375,-9,2.875,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"02:00:00",0,2.5,21.92,1.5866666666666667,1,2.4583333333333335,-9,2.875,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"03:00:00",1,2.4583333333333335,19.940000000000001,1.6691666666666667,1,2.4583333333333335,-11,2.9583333333333335,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"04:00:00",1,2.4583333333333335,19.04,1.7066666666666668,-2,2.5833333333333335,-11,2.9583333333333335,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"05:00:00",1,2.4583333333333335,17.059999999999999,1.7891666666666666,-4,2.6666666666666665,-11,2.9583333333333335,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"06:00:00",3,2.375,15.98,1.8341666666666665,-4,2.6666666666666665,-13,3.0416666666666665,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"07:00:00",5,2.2916666666666665,14,1.9166666666666667,-4,2.6666666666666665,-11,2.9583333333333335,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"08:00:00",7,2.2083333333333335,14,1.9166666666666667,0,2.5,-8,2.8333333333333335,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"09:00:00",9,2.125,17.059999999999999,1.7891666666666666,3,2.375,-6,2.75,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"10:00:00",12,2,19.04,1.7066666666666668,7,2.2083333333333335,-2,2.5833333333333335,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"11:00:00",14,1.9166666666666667,23,1.5416666666666667,9,2.125,1,2.4583333333333335,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"12:00:00",16,1.8333333333333333,23,1.5416666666666667,12,2,5,2.2916666666666665,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"13:00:00",18,1.75,24.98,1.4591666666666665,16,1.8333333333333333,10,2.0833333333333335,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"14:00:00",20,1.6666666666666667,26.96,1.3766666666666667,18,1.75,10,2.0833333333333335,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"15:00:00",22,1.5833333333333333,28.04,1.3316666666666668,19,1.7083333333333333,14,1.9166666666666667,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"16:00:00",22,1.5833333333333333,28.04,1.3316666666666668,19,1.7083333333333333,14,1.9166666666666667,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"17:00:00",21,{"$f":"IF(W453<60,(60-W453)/24,0)","v":1.625},28.94,1.2941666666666667,18,1.75,9,2.125,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"18:00:00",21.414999999999999,1.6077083333333333,28.94,{"$f":"IF(Y454<60,(60-Y454)/24,0)","v":1.2941666666666667},10,{"$f":"IF(AA454<60,(60-AA454)/24,0)","v":2.0833333333333335},3,{"$f":"IF(AC454<60,(60-AC454)/24,0)","v":2.375},35.96,{"$f":"IF(AE454<60,(60-AE454)/24,0)","v":1.0016666666666667}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"19:00:00",22,1.5833333333333333,28.04,1.3316666666666668,9,2.125,0,2.5,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"20:00:00",21,1.625,21.92,1.5866666666666667,5,2.2916666666666665,0,2.5,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"21:00:00",24,1.5,23,1.5416666666666667,3,2.375,-2,2.5833333333333335,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"22:00:00",27,1.375,21.02,1.6241666666666668,1,2.4583333333333335,-4,2.6666666666666665,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,"23:00:00",27,1.375,19.940000000000001,1.6691666666666667,0,2.5,-6,2.75,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,19,1,25,1.4583333333333333,17.96,1.7516666666666667,-2,2.5833333333333335,-4,2.6666666666666665,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"01:00:00",21,1.625,17.96,1.7516666666666667,-2,2.5833333333333335,-4,2.6666666666666665,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"02:00:00",18,1.75,17.96,1.7516666666666667,-2,2.5833333333333335,-4,2.6666666666666665,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"03:00:00",16,1.8333333333333333,19.940000000000001,1.6691666666666667,0,2.5,-2,2.5833333333333335,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"04:00:00",14,1.9166666666666667,19.940000000000001,1.6691666666666667,0,2.5,-2,2.5833333333333335,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"05:00:00",12,2,21.02,1.6241666666666668,0,2.5,-2,2.5833333333333335,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"06:00:00",12,2,21.02,1.6241666666666668,-2,2.5833333333333335,-2,2.5833333333333335,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"07:00:00",10,2.0833333333333335,21.02,1.6241666666666668,-2,2.5833333333333335,-2,2.5833333333333335,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"08:00:00",10,2.0833333333333335,21.02,1.6241666666666668,0,2.5,0,2.5,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"09:00:00",10,2.0833333333333335,21.92,1.5866666666666667,3,2.375,1,2.4583333333333335,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"10:00:00",12,2,30.92,1.2116666666666667,7,2.2083333333333335,1,2.4583333333333335,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"11:00:00",14,1.9166666666666667,35.96,1.0016666666666667,9,2.125,3,2.375,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"12:00:00",16,1.8333333333333333,41,0.79166666666666663,10,2.0833333333333335,7,2.2083333333333335,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"13:00:00",18,1.75,42.98,0.70916666666666683,10,2.0833333333333335,9,2.125,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"14:00:00",19,1.7083333333333333,42.98,0.70916666666666683,14,1.9166666666666667,10,2.0833333333333335,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"15:00:00",19,1.7083333333333333,42.08,0.7466666666666667,16,1.8333333333333333,10,2.0833333333333335,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"16:00:00",16,1.8333333333333333,42.08,0.7466666666666667,18,1.75,12,2,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"17:00:00",12,2,39.92,0.83666666666666656,18,1.75,10,2.0833333333333335,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"18:00:00",9,2.125,39.020000000000003,0.87416666666666654,16,1.8333333333333333,10,2.0833333333333335,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"19:00:00",7,2.2083333333333335,37.94,0.9191666666666668,16,1.8333333333333333,10,2.0833333333333335,39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"20:00:00",3,2.375,37.94,0.9191666666666668,16,1.8333333333333333,10,2.0833333333333335,39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"21:00:00",3,2.375,35.96,1.0016666666666667,16,1.8333333333333333,10,2.0833333333333335,39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"22:00:00",3,2.375,35.06,1.0391666666666666,16,1.8333333333333333,9,2.125,39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,"23:00:00",5,2.2916666666666665,33.979999999999997,1.0841666666666667,16,1.8333333333333333,9,2.125,39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,20,1,1,2.4583333333333335,30.92,1.2116666666666667,16,1.8333333333333333,9,2.125,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"01:00:00",3,2.375,28.04,1.3316666666666668,16,1.8333333333333333,10,2.0833333333333335,39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"02:00:00",3,2.375,26.06,1.4141666666666666,16,1.8333333333333333,10,2.0833333333333335,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"03:00:00",7,2.2083333333333335,24.98,1.4591666666666665,16,1.8333333333333333,10,2.0833333333333335,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"04:00:00",7,2.2083333333333335,21.02,1.6241666666666668,16,1.8333333333333333,12,2,39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"05:00:00",9,2.125,19.04,1.7066666666666668,16,1.8333333333333333,14,1.9166666666666667,39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"06:00:00",9,2.125,17.96,1.7516666666666667,14,1.9166666666666667,12,2,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"07:00:00",9,2.125,15.98,1.8341666666666665,12,2,10,2.0833333333333335,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"08:00:00",9,2.125,15.08,1.8716666666666668,10,2.0833333333333335,9,2.125,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"09:00:00",10,2.0833333333333335,15.98,1.8341666666666665,10,2.0833333333333335,7,2.2083333333333335,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"10:00:00",10,2.0833333333333335,17.059999999999999,1.7891666666666666,12,2,7,2.2083333333333335,42.98,0.70916666666666683]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"11:00:00",14,1.9166666666666667,17.96,1.7516666666666667,12,2,7,2.2083333333333335,43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"12:00:00",14,1.9166666666666667,17.96,1.7516666666666667,12,2,7,2.2083333333333335,43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"13:00:00",14,1.9166666666666667,19.04,1.7066666666666668,12,2,7,2.2083333333333335,43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"14:00:00",12,2,19.04,1.7066666666666668,12,2,7,2.2083333333333335,43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"15:00:00",16,1.8333333333333333,19.04,1.7066666666666668,12,2,7,2.2083333333333335,43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"16:00:00",12,2,17.96,1.7516666666666667,10,2.0833333333333335,5,2.2916666666666665,43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"17:00:00",12,2,15.08,1.8716666666666668,9,2.125,3,2.375,43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"18:00:00",12,2,12.92,1.9616666666666667,7,2.2083333333333335,1,2.4583333333333335,43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"19:00:00",13,1.9583333333333333,10.94,2.0441666666666669,5,2.2916666666666665,1,2.4583333333333335,42.98,0.70916666666666683]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"20:00:00",12,2,10.039999999999999,2.0816666666666666,3,2.375,0,2.5,41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"21:00:00",12,2,8.9600000000000009,2.1266666666666665,1,2.4583333333333335,0,2.5,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"22:00:00",12,2,6.98,2.2091666666666665,0,2.5,-2,2.5833333333333335,39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,"23:00:00",12,2,6.08,2.2466666666666666,0,2.5,-2,2.5833333333333335,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,21,1,12,2,5,2.2916666666666665,0,2.5,-2,2.5833333333333335,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"01:00:00",7,2.2083333333333335,3.92,2.3366666666666664,0,2.5,-2,2.5833333333333335,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"02:00:00",9,2.125,3.02,2.3741666666666665,0,2.5,-2,2.5833333333333335,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"03:00:00",12,2,1.94,2.4191666666666669,0,2.5,-2,2.5833333333333335,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"04:00:00",7,2.2083333333333335,1.04,2.4566666666666666,-2,2.5833333333333335,-2,2.5833333333333335,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"05:00:00",0,2.5,-3.9999999999999147E-2,2.5016666666666665,-2,2.5833333333333335,-4,2.6666666666666665,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"06:00:00",-2,2.5833333333333335,-0.94000000000000483,2.539166666666667,-2,2.5833333333333335,-4,2.6666666666666665,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"07:00:00",-2,2.5833333333333335,-2.02,2.5841666666666669,-2,2.5833333333333335,-6,2.75,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"08:00:00",-2,2.5833333333333335,-2.02,2.5841666666666669,-2,2.5833333333333335,-4,2.6666666666666665,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"09:00:00",2.1229200000000001,{"$f":"IF(W517<60,(60-W517)/24,0)","v":2.4115449999999998},-3.9999999999999147E-2,2.5016666666666665,0,2.5,-2,2.5833333333333335,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"10:00:00",10,2.0833333333333335,1.94,{"$f":"IF(Y518<60,(60-Y518)/24,0)","v":2.4191666666666669},1,{"$f":"IF(AA518<60,(60-AA518)/24,0)","v":2.4583333333333335},0,{"$f":"IF(AC518<60,(60-AC518)/24,0)","v":2.5},33.979999999999997,{"$f":"IF(AE518<60,(60-AE518)/24,0)","v":1.0841666666666667}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"11:00:00",19,1.7083333333333333,5,2.2916666666666665,3,2.375,1,2.4583333333333335,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"12:00:00",19,1.7083333333333333,6.98,2.2091666666666665,7,2.2083333333333335,3,2.375,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"13:00:00",21,1.625,8.06,2.1641666666666666,9,2.125,5,2.2916666666666665,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"14:00:00",23,1.5416666666666667,10.039999999999999,2.0816666666666666,10,2.0833333333333335,7,2.2083333333333335,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"15:00:00",23,1.5416666666666667,10.039999999999999,2.0816666666666666,10,2.0833333333333335,7,2.2083333333333335,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"16:00:00",21,1.625,10.039999999999999,2.0816666666666666,10,2.0833333333333335,7,2.2083333333333335,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"17:00:00",18,1.75,8.9600000000000009,2.1266666666666665,9,2.125,7,2.2083333333333335,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"18:00:00",7,2.2083333333333335,8.06,2.1641666666666666,7,2.2083333333333335,3,2.375,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"19:00:00",3,2.375,6.98,2.2091666666666665,5,2.2916666666666665,3,2.375,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"20:00:00",-2,2.5833333333333335,3.02,2.3741666666666665,0,2.5,1,2.4583333333333335,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"21:00:00",-4,2.6666666666666665,1.04,2.4566666666666666,0,2.5,1,2.4583333333333335,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"22:00:00",-4,2.6666666666666665,-2.02,2.5841666666666669,-2,2.5833333333333335,-4,2.6666666666666665,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,"23:00:00",-6,2.75,-7.06,2.7941666666666669,0,2.5,-8,2.8333333333333335,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,22,1,-8,2.8333333333333335,-5.98,2.749166666666667,-8,2.8333333333333335,-8,2.8333333333333335,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"01:00:00",-9,2.875,-9.0399999999999991,2.8766666666666665,-9,2.875,-11,2.9583333333333335,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"02:00:00",-8,2.8333333333333335,-7.96,2.8316666666666666,-11,2.9583333333333335,-13,3.0416666666666665,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"03:00:00",-9,2.875,-7.96,2.8316666666666666,-9,2.875,-15,3.125,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"04:00:00",-11,2.9583333333333335,-9.0399999999999991,2.8766666666666665,-9,2.875,-13,3.0416666666666665,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"05:00:00",-11,2.9583333333333335,-9.0399999999999991,2.8766666666666665,-11,2.9583333333333335,-13,3.0416666666666665,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"06:00:00",-13,3.0416666666666665,-9.0399999999999991,2.8766666666666665,-11,2.9583333333333335,-13,3.0416666666666665,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"07:00:00",-13,3.0416666666666665,-5.98,2.749166666666667,-10,2.9166666666666665,-15,3.125,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"08:00:00",-13,3.0416666666666665,-5.0800000000000054,2.7116666666666673,-9,2.875,-11,2.9583333333333335,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"09:00:00",-8,2.8333333333333335,-0.94000000000000483,2.539166666666667,-8,2.8333333333333335,-9,2.875,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"10:00:00",0,2.5,3.92,2.3366666666666664,-2,2.5833333333333335,-6,2.75,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"11:00:00",9,2.125,8.9600000000000009,2.1266666666666665,5,2.2916666666666665,0,2.5,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"12:00:00",19,1.7083333333333333,12.02,1.9991666666666668,9,2.125,3,2.375,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"13:00:00",27,1.375,15.98,1.8341666666666665,12,2,7,2.2083333333333335,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"14:00:00",28,1.3333333333333333,19.04,1.7066666666666668,16,1.8333333333333333,10,2.0833333333333335,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"15:00:00",27,1.375,21.92,1.5866666666666667,18,1.75,12,2,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"16:00:00",25,1.4583333333333333,24.08,1.4966666666666668,19,1.7083333333333333,14,1.9166666666666667,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"17:00:00",19,1.7083333333333333,26.06,1.4141666666666666,19,1.7083333333333333,16,1.8333333333333333,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"18:00:00",16,1.8333333333333333,24.98,1.4591666666666665,18,1.75,16,1.8333333333333333,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"19:00:00",12,2,24.98,1.4591666666666665,16,1.8333333333333333,10,2.0833333333333335,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"20:00:00",9,2.125,24.98,1.4591666666666665,16,1.8333333333333333,14,1.9166666666666667,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"21:00:00",9,2.125,26.06,1.4141666666666666,16,1.8333333333333333,14,1.9166666666666667,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"22:00:00",10,2.0833333333333335,24.98,1.4591666666666665,18,1.75,16,1.8333333333333333,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,"23:00:00",16,1.8333333333333333,26.06,1.4141666666666666,18,1.75,16,1.8333333333333333,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,23,1,16,1.8333333333333333,24.98,1.4591666666666665,18,1.75,16,1.8333333333333333,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"01:00:00",18,1.75,21.92,1.5866666666666667,18,1.75,16,1.8333333333333333,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"02:00:00",18,1.75,23,1.5416666666666667,14,1.9166666666666667,16,1.8333333333333333,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"03:00:00",18,1.75,26.96,1.3766666666666667,16,1.8333333333333333,18,1.75,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"04:00:00",18,1.75,26.96,1.3766666666666667,16,1.8333333333333333,18,1.75,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"05:00:00",19,1.7083333333333333,24.08,1.4966666666666668,18,1.75,16,1.8333333333333333,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"06:00:00",19,1.7083333333333333,17.059999999999999,1.7891666666666666,18,1.75,18,1.75,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"07:00:00",19,1.7083333333333333,23,1.5416666666666667,18,1.75,18,1.75,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"08:00:00",19,1.7083333333333333,24.08,1.4966666666666668,18,1.75,18,1.75,26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"09:00:00",21,1.625,26.96,1.3766666666666667,19,1.7083333333333333,18,1.75,28.04,1.3316666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"10:00:00",23,1.5416666666666667,28.94,1.2941666666666667,21,1.625,19,1.7083333333333333,28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"11:00:00",27,1.375,30.02,1.2491666666666668,25,1.4583333333333333,21,1.625,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"12:00:00",30,1.25,28.94,1.2941666666666667,27,1.375,23,1.5416666666666667,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"13:00:00",30,1.25,30.02,1.2491666666666668,28,1.3333333333333333,25,1.4583333333333333,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"14:00:00",30,1.25,30.02,1.2491666666666668,30,1.25,28,1.3333333333333333,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"15:00:00",30,1.25,30.02,1.2491666666666668,32,1.1666666666666667,28,1.3333333333333333,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"16:00:00",30,1.25,28.94,1.2941666666666667,34,1.0833333333333333,30,1.25,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"17:00:00",28,1.3333333333333333,26.96,1.3766666666666667,28,1.3333333333333333,25,1.4583333333333333,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"18:00:00",28,1.3333333333333333,26.06,1.4141666666666666,25,1.4583333333333333,23,1.5416666666666667,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"19:00:00",27,1.375,24.98,1.4591666666666665,21,1.625,19,1.7083333333333333,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"20:00:00",25,1.4583333333333333,23,1.5416666666666667,19,1.7083333333333333,16,1.8333333333333333,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"21:00:00",28,1.3333333333333333,23,1.5416666666666667,16,1.8333333333333333,16,1.8333333333333333,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"22:00:00",27,1.375,21.92,1.5866666666666667,14,1.9166666666666667,10,2.0833333333333335,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,"23:00:00",25,1.4583333333333333,17.96,1.7516666666666667,12,2,10,2.0833333333333335,26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,24,1,21,1.625,15.08,1.8716666666666668,10,2.0833333333333335,10,2.0833333333333335,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"01:00:00",18,{"$f":"IF(W581<60,(60-W581)/24,0)","v":1.75},12.92,1.9616666666666667,10,2.0833333333333335,7,2.2083333333333335,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"02:00:00",15,1.875,10.94,{"$f":"IF(Y582<60,(60-Y582)/24,0)","v":2.0441666666666669},9,{"$f":"IF(AA582<60,(60-AA582)/24,0)","v":2.125},7,{"$f":"IF(AC582<60,(60-AC582)/24,0)","v":2.2083333333333335},25.88,{"$f":"IF(AE582<60,(60-AE582)/24,0)","v":1.4216666666666669}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"03:00:00",11,2.0416666666666665,8.9600000000000009,2.1266666666666665,9,2.125,7,2.2083333333333335,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"04:00:00",9,2.125,6.98,2.2091666666666665,10,2.0833333333333335,9,2.125,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"05:00:00",7,2.2083333333333335,6.08,2.2466666666666666,14,1.9166666666666667,9,2.125,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"06:00:00",7,2.2083333333333335,3.92,2.3366666666666664,21,1.625,12,2,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"07:00:00",7,2.2083333333333335,1.94,2.4191666666666669,25,1.4583333333333333,14,1.9166666666666667,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"08:00:00",10,2.0833333333333335,1.04,2.4566666666666666,25,1.4583333333333333,16,1.8333333333333333,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"09:00:00",12,2,1.94,2.4191666666666669,23,1.5416666666666667,18,1.75,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"10:00:00",17,1.7916666666666667,3.02,2.3741666666666665,23,1.5416666666666667,18,1.75,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"11:00:00",22,1.5833333333333333,5,2.2916666666666665,23,1.5416666666666667,18,1.75,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"12:00:00",27,1.375,6.08,2.2466666666666666,25,1.4583333333333333,18,1.75,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"13:00:00",28,1.3333333333333333,8.9600000000000009,2.1266666666666665,27,1.375,18,1.75,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"14:00:00",28,1.3333333333333333,10.94,2.0441666666666669,27,1.375,19,1.7083333333333333,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"15:00:00",27,1.375,12.02,1.9991666666666668,27,1.375,19,1.7083333333333333,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"16:00:00",25,1.4583333333333333,12.92,1.9616666666666667,27,1.375,21,1.625,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"17:00:00",21,1.625,12.02,1.9991666666666668,27,1.375,23,1.5416666666666667,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"18:00:00",14,1.9166666666666667,10.039999999999999,2.0816666666666666,25,1.4583333333333333,23,1.5416666666666667,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"19:00:00",7,2.2083333333333335,6.08,2.2466666666666666,25,1.4583333333333333,21,1.625,28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"20:00:00",10,2.0833333333333335,-0.94000000000000483,2.539166666666667,25,1.4583333333333333,21,1.625,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"21:00:00",3,2.375,-3.9999999999999147E-2,2.5016666666666665,23,1.5416666666666667,19.075900000000001,1.7051708333333331,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"22:00:00",1,2.4583333333333335,-0.94000000000000483,2.539166666666667,23,1.5416666666666667,21,1.625,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,"23:00:00",0,2.5,-0.94000000000000483,2.539166666666667,23,1.5416666666666667,19,1.7083333333333333,26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,25,1,-4,2.6666666666666665,-5.0800000000000054,2.7116666666666673,23,1.5416666666666667,19,1.7083333333333333,26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"01:00:00",0,2.5,-5.98,2.749166666666667,21,1.625,19,1.7083333333333333,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"02:00:00",-4,2.6666666666666665,-5.98,2.749166666666667,21,1.625,19,1.7083333333333333,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"03:00:00",-9,2.875,-9.0399999999999991,2.8766666666666665,21,1.625,19,1.7083333333333333,21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"04:00:00",-8,2.8333333333333335,-7.06,2.7941666666666669,21,1.625,19,1.7083333333333333,20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"05:00:00",-8,2.8333333333333335,-7.96,2.8316666666666666,21,1.625,19,1.7083333333333333,20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"06:00:00",-8,2.8333333333333335,-9.94,2.9141666666666666,21,1.625,19,1.7083333333333333,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"07:00:00",-9,2.875,-9.94,2.9141666666666666,21,1.625,19,1.7083333333333333,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"08:00:00",-9,2.875,-9.0399999999999991,2.8766666666666665,21,1.625,19,1.7083333333333333,20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"09:00:00",-2,2.5833333333333335,-2.92,2.6216666666666666,23,1.5416666666666667,19,1.7083333333333333,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"10:00:00",5,2.2916666666666665,5,2.2916666666666665,25,1.4583333333333333,21,1.625,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"11:00:00",16,1.8333333333333333,12.92,1.9616666666666667,25,1.4583333333333333,23,1.5416666666666667,26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"12:00:00",21,1.625,19.940000000000001,1.6691666666666667,25,1.4583333333333333,25,1.4583333333333333,28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"13:00:00",25,1.4583333333333333,21.02,1.6241666666666668,25,1.4583333333333333,25,1.4583333333333333,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"14:00:00",27,1.375,21.92,1.5866666666666667,25,1.4583333333333333,21,1.625,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"15:00:00",27,1.375,21.92,1.5866666666666667,27,1.375,23,1.5416666666666667,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"16:00:00",27,1.375,21.92,1.5866666666666667,25,1.4583333333333333,21,1.625,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"17:00:00",19,1.7083333333333333,19.940000000000001,1.6691666666666667,25,1.4583333333333333,19,1.7083333333333333,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"18:00:00",14,1.9166666666666667,17.059999999999999,1.7891666666666666,21,1.625,16,1.8333333333333333,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"19:00:00",7,2.2083333333333335,17.96,1.7516666666666667,19,1.7083333333333333,18,1.75,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"20:00:00",7,2.2083333333333335,19.04,1.7066666666666668,18,1.75,16,1.8333333333333333,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"21:00:00",3,2.375,19.04,1.7066666666666668,16,1.8333333333333333,16,1.8333333333333333,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"22:00:00",5,2.2916666666666665,17.96,1.7516666666666667,16,1.8333333333333333,12,2,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,"23:00:00",1,2.4583333333333335,17.059999999999999,1.7891666666666666,16.050999999999998,1.8312083333333333,12,2,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,26,1,0,2.5,17.059999999999999,1.7891666666666666,14,1.9166666666666667,11,2.0416666666666665,21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"01:00:00",3,2.375,15.08,1.8716666666666668,12,2,10,2.0833333333333335,21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"02:00:00",5,2.2916666666666665,15.08,1.8716666666666668,10,2.0833333333333335,9,2.125,21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"03:00:00",7,2.2083333333333335,10.94,2.0441666666666669,9,2.125,9,2.125,21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"04:00:00",7,2.2083333333333335,8.06,2.1641666666666666,9,2.125,7,2.2083333333333335,20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"05:00:00",7,2.2083333333333335,6.08,2.2466666666666666,9,2.125,5,2.2916666666666665,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"06:00:00",9,2.125,3.92,2.3366666666666664,9,2.125,5,2.2916666666666665,18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"07:00:00",7,2.2083333333333335,1.94,2.4191666666666669,7,2.2083333333333335,3,2.375,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"08:00:00",9,2.125,3.02,2.3741666666666665,7,2.2083333333333335,3,2.375,18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"09:00:00",10,2.0833333333333335,8.9600000000000009,2.1266666666666665,9,2.125,7,2.2083333333333335,18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"10:00:00",14,1.9166666666666667,19.940000000000001,1.6691666666666667,10,2.0833333333333335,7,2.2083333333333335,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"11:00:00",18,1.75,30.02,1.2491666666666668,12,2,9,2.125,20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"12:00:00",21,1.625,30.92,1.2116666666666667,12,2,9,2.125,21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"13:00:00",25,1.4583333333333333,32,1.1666666666666667,16,1.8333333333333333,10,2.0833333333333335,21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"14:00:00",27,1.375,33.08,1.1216666666666668,14,1.9166666666666667,10,2.0833333333333335,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"15:00:00",28,1.3333333333333333,33.08,1.1216666666666668,14,1.9166666666666667,10,2.0833333333333335,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"16:00:00",28,1.3333333333333333,32,1.1666666666666667,12,2,9,2.125,20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"17:00:00",27,{"$f":"IF(W645<60,(60-W645)/24,0)","v":1.375},30.02,1.2491666666666668,10,2.0833333333333335,7,2.2083333333333335,16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"18:00:00",27,1.375,26.06,{"$f":"IF(Y646<60,(60-Y646)/24,0)","v":1.4141666666666666},9,{"$f":"IF(AA646<60,(60-AA646)/24,0)","v":2.125},3,{"$f":"IF(AC646<60,(60-AC646)/24,0)","v":2.375},15.98,{"$f":"IF(AE646<60,(60-AE646)/24,0)","v":1.8341666666666665}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"19:00:00",25,1.4583333333333333,23,1.5416666666666667,9,2.125,1,2.4583333333333335,14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"20:00:00",25,1.4583333333333333,24.08,1.4966666666666668,7,2.2083333333333335,1,2.4583333333333335,12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"21:00:00",23,1.5416666666666667,26.06,1.4141666666666666,5,2.2916666666666665,-8,2.8333333333333335,11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"22:00:00",22,1.5833333333333333,26.06,1.4141666666666666,3,2.375,-8,2.8333333333333335,11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,"23:00:00",21,1.625,24.98,1.4591666666666665,3,2.375,-4,2.6666666666666665,10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,27,1,20,1.6666666666666667,26.06,1.4141666666666666,3,2.375,-2,2.5833333333333335,9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"01:00:00",19,1.7083333333333333,26.96,1.3766666666666667,3,2.375,0,2.5,9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"02:00:00",19,1.7083333333333333,26.96,1.3766666666666667,3,2.375,1,2.4583333333333335,9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"03:00:00",19,1.7083333333333333,28.94,1.2941666666666667,3,2.375,1,2.4583333333333335,9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"04:00:00",19,1.7083333333333333,30.92,1.2116666666666667,3,2.375,1,2.4583333333333335,10.039999999999999,2.0816666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"05:00:00",19,1.7083333333333333,32,1.1666666666666667,1,2.4583333333333335,-4,2.6666666666666665,10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"06:00:00",19,1.7083333333333333,37.04,0.95666666666666667,1,2.4583333333333335,-2,2.5833333333333335,9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"07:00:00",18,1.75,37.04,0.95666666666666667,1,2.4583333333333335,-8,2.8333333333333335,10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"08:00:00",18,1.75,37.04,0.95666666666666667,1,2.4583333333333335,-8,2.8333333333333335,11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"09:00:00",18,1.75,37.04,0.95666666666666667,1,2.4583333333333335,0,2.5,14.9,1.8791666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"10:00:00",19,1.7083333333333333,37.94,0.9191666666666668,7,2.2083333333333335,1,2.4583333333333335,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"11:00:00",19,1.7083333333333333,39.020000000000003,0.87416666666666654,9,2.125,3,2.375,20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"12:00:00",19,1.7083333333333333,39.92,0.83666666666666656,9,2.125,7,2.2083333333333335,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"13:00:00",19,1.7083333333333333,41,0.79166666666666663,10,2.0833333333333335,7,2.2083333333333335,26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"14:00:00",21,1.625,42.08,0.7466666666666667,12,2,9,2.125,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"15:00:00",21,1.625,42.08,0.7466666666666667,12,2,9,2.125,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"16:00:00",19,1.7083333333333333,41,0.79166666666666663,12,2,7,2.2083333333333335,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"17:00:00",18,1.75,39.020000000000003,0.87416666666666654,10,2.0833333333333335,7,2.2083333333333335,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"18:00:00",16,1.8333333333333333,30.02,1.2491666666666668,10,2.0833333333333335,3,2.375,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"19:00:00",9,2.125,28.04,1.3316666666666668,10,2.0833333333333335,3,2.375,21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"20:00:00",1,2.4583333333333335,24.98,1.4591666666666665,10,2.0833333333333335,-2,2.5833333333333335,20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"21:00:00",-4,2.6666666666666665,21.92,1.5866666666666667,9,2.125,-8,2.8333333333333335,18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"22:00:00",-6,2.75,21.02,1.6241666666666668,9,2.125,-9,2.875,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,"23:00:00",-8,2.8333333333333335,19.940000000000001,1.6691666666666667,9,2.125,-8,2.8333333333333335,15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,28,1,-6,2.75,19.04,1.7066666666666668,9,2.125,-9,2.875,15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"01:00:00",-8,2.8333333333333335,15.98,1.8341666666666665,1,2.4583333333333335,-9,2.875,12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"02:00:00",-9,2.875,17.059999999999999,1.7891666666666666,0,2.5,-8,2.8333333333333335,14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"03:00:00",-11,2.9583333333333335,17.059999999999999,1.7891666666666666,-2,2.5833333333333335,-13,3.0416666666666665,11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"04:00:00",-11,2.9583333333333335,15.98,1.8341666666666665,-8,2.8333333333333335,-15,3.125,10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"05:00:00",-11,2.9583333333333335,15.08,1.8716666666666668,-6,2.75,-15,3.125,9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"06:00:00",-11,2.9583333333333335,15.08,1.8716666666666668,-8,2.8333333333333335,-17,3.2083333333333335,9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"07:00:00",-13,3.0416666666666665,12.02,1.9991666666666668,-11,2.9583333333333335,-18,3.25,7.88,2.1716666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"08:00:00",-11,2.9583333333333335,12.92,1.9616666666666667,-9,2.875,-18,3.25,12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"09:00:00",-8,2.8333333333333335,19.04,1.7066666666666668,-4,2.6666666666666665,-9,2.875,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"10:00:00",1,2.4583333333333335,32,1.1666666666666667,12,2,-2,2.5833333333333335,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"11:00:00",10,2.0833333333333335,39.020000000000003,0.87416666666666654,19,1.7083333333333333,7,2.2083333333333335,26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"12:00:00",19,1.7083333333333333,39.92,0.83666666666666656,23,1.5416666666666667,12,2,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"13:00:00",23,1.5416666666666667,41,0.79166666666666663,25,1.4583333333333333,18,1.75,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"14:00:00",25,1.4583333333333333,42.98,0.70916666666666683,28,1.3333333333333333,21,1.625,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"15:00:00",25,1.4583333333333333,44.96,0.62666666666666659,30,1.25,23,1.5416666666666667,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"16:00:00",25,1.4583333333333333,42.08,0.7466666666666667,30,1.25,21,1.625,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"17:00:00",21,1.625,39.92,0.83666666666666656,28,1.3333333333333333,18,1.75,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"18:00:00",18,1.75,35.96,1.0016666666666667,21,1.625,9,2.125,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"19:00:00",10,2.0833333333333335,30.92,1.2116666666666667,19,1.7083333333333333,1,2.4583333333333335,26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"20:00:00",7,2.2083333333333335,26.06,1.4141666666666666,16,1.8333333333333333,7,2.2083333333333335,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"21:00:00",7,2.2083333333333335,24.98,1.4591666666666665,10,2.0833333333333335,1,2.4583333333333335,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"22:00:00",3,2.375,24.98,1.4591666666666665,9,2.125,-2,2.5833333333333335,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,"23:00:00",0,2.5,30.02,1.2491666666666668,9,2.125,-2,2.5833333333333335,20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,29,1,0,2.5,32,1.1666666666666667,5,2.2916666666666665,-6,2.75,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"01:00:00",-2,2.5833333333333335,32,1.1666666666666667,3,2.375,-6,2.75,20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"02:00:00",-4,2.6666666666666665,32,1.1666666666666667,1,2.4583333333333335,-6,2.75,20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"03:00:00",-6,2.75,33.08,1.1216666666666668,0,2.5,-8,2.8333333333333335,18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"04:00:00",-4,2.6666666666666665,33.979999999999997,1.0841666666666667,0,2.5,-8,2.8333333333333335,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"05:00:00",-4,2.6666666666666665,33.979999999999997,1.0841666666666667,-2,2.5833333333333335,-8,2.8333333333333335,16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"06:00:00",-6,2.75,33.979999999999997,1.0841666666666667,-4,2.6666666666666665,-9,2.875,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"07:00:00",-4,2.6666666666666665,35.06,1.0391666666666666,-4,2.6666666666666665,-11,2.9583333333333335,18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"08:00:00",0,2.5,35.06,1.0391666666666666,-5.3227099999999998,2.7217795833333334,-11,2.9583333333333335,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"09:00:00",7,{"$f":"IF(W709<60,(60-W709)/24,0)","v":2.2083333333333335},35.06,1.0391666666666666,1,2.4583333333333335,-6,2.75,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"10:00:00",10,2.0833333333333335,35.06,{"$f":"IF(Y710<60,(60-Y710)/24,0)","v":1.0391666666666666},9,{"$f":"IF(AA710<60,(60-AA710)/24,0)","v":2.125},3,{"$f":"IF(AC710<60,(60-AC710)/24,0)","v":2.375},28.94,{"$f":"IF(AE710<60,(60-AE710)/24,0)","v":1.2941666666666667}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"11:00:00",14,1.9166666666666667,37.94,0.9191666666666668,18,1.75,10,2.0833333333333335,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"12:00:00",16,1.8333333333333333,37.94,0.9191666666666668,25,1.4583333333333333,16,1.8333333333333333,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"13:00:00",18,1.75,35.96,1.0016666666666667,30,1.25,21,1.625,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"14:00:00",20,1.6666666666666667,35.96,1.0016666666666667,32,1.1666666666666667,27,1.375,41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"15:00:00",21,1.625,37.04,0.95666666666666667,34,1.0833333333333333,28,1.3333333333333333,41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"16:00:00",21,1.625,37.04,0.95666666666666667,36,1,30,1.25,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"17:00:00",22,1.5833333333333333,35.96,1.0016666666666667,28,1.3333333333333333,23,1.5416666666666667,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"18:00:00",22,1.5833333333333333,35.96,1.0016666666666667,28,1.3333333333333333,25,1.4583333333333333,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"19:00:00",23,1.5416666666666667,35.06,1.0391666666666666,28,1.3333333333333333,25,1.4583333333333333,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"20:00:00",22,1.5833333333333333,33.979999999999997,1.0841666666666667,27,1.375,23,1.5416666666666667,28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"21:00:00",23,1.5416666666666667,33.979999999999997,1.0841666666666667,27,1.375,19,1.7083333333333333,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"22:00:00",25,1.4583333333333333,33.979999999999997,1.0841666666666667,28,1.3333333333333333,21,1.625,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,"23:00:00",25,1.4583333333333333,35.96,1.0016666666666667,28,1.3333333333333333,23,1.5416666666666667,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,30,1,25,1.4583333333333333,35.06,1.0391666666666666,27,1.375,21,1.625,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"01:00:00",25,1.4583333333333333,35.06,1.0391666666666666,27,1.375,23,1.5416666666666667,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"02:00:00",24,1.5,33.979999999999997,1.0841666666666667,27,1.375,23,1.5416666666666667,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"03:00:00",24,1.5,33.979999999999997,1.0841666666666667,27,1.375,21,1.625,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"04:00:00",25,1.4583333333333333,33.08,1.1216666666666668,28,1.3333333333333333,21.2469,1.6147125000000002,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"05:00:00",25,1.4583333333333333,33.08,1.1216666666666668,30,1.25,21.2469,1.6147125000000002,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"06:00:00",25,1.4583333333333333,35.06,1.0391666666666666,30,1.25,25,1.4583333333333333,18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"07:00:00",25,1.4583333333333333,30.92,1.2116666666666667,28,1.3333333333333333,27,1.375,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"08:00:00",25,1.4583333333333333,26.96,1.3766666666666667,30,1.25,27,1.375,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"09:00:00",25,1.4583333333333333,26.06,1.4141666666666666,30,1.25,25,1.4583333333333333,26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"10:00:00",27,1.375,26.96,1.3766666666666667,34,1.0833333333333333,27,1.375,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"11:00:00",27,1.375,28.04,1.3316666666666668,32,1.1666666666666667,28,1.3333333333333333,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"12:00:00",28,1.3333333333333333,28.94,1.2941666666666667,32,1.1666666666666667,30,1.25,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"13:00:00",28,1.3333333333333333,28.94,1.2941666666666667,36,1,30,1.25,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"14:00:00",27,1.375,28.04,1.3316666666666668,36,1,32,1.1666666666666667,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"15:00:00",27,1.375,26.96,1.3766666666666667,36,1,34,1.0833333333333333,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"16:00:00",26,1.4166666666666667,26.96,1.3766666666666667,36,1,34,1.0833333333333333,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"17:00:00",25,1.4583333333333333,24.98,1.4591666666666665,32,1.1666666666666667,32,1.1666666666666667,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"18:00:00",25,1.4583333333333333,24.98,1.4591666666666665,30,1.25,30,1.25,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"19:00:00",25,1.4583333333333333,23,1.5416666666666667,28,1.3333333333333333,30,1.25,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"20:00:00",23,1.5416666666666667,21.02,1.6241666666666668,28,1.3333333333333333,30,1.25,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"21:00:00",22,1.5833333333333333,19.940000000000001,1.6691666666666667,28,1.3333333333333333,28,1.3333333333333333,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"22:00:00",18,1.75,18.5,1.7291666666666667,29,1.2916666666666667,24,1.5,31.28,1.1966666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,"23:00:00",14,1.9166666666666667,17.059999999999999,1.7891666666666666,29,1.2916666666666667,20,1.6666666666666667,27.32,1.3616666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,31,1,10,2.0833333333333335,15.44,1.8566666666666667,29,1.2916666666666667,16,1.8333333333333333,23.54,1.5191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"01:00:00",5,2.2916666666666665,13.82,1.9241666666666666,29,1.2916666666666667,12,2,19.579999999999998,1.6841666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"02:00:00",1,2.4583333333333335,12.2,1.9916666666666665,29,1.2916666666666667,8,2.1666666666666665,15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"03:00:00",-3,2.625,10.76,2.0516666666666667,29,1.2916666666666667,3,2.375,11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"04:00:00",-8,2.8333333333333335,8.9600000000000009,2.1266666666666665,29,1.2916666666666667,-1,2.5416666666666665,7.88,2.1716666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"05:00:00",-4,2.6666666666666665,8.9600000000000009,2.1266666666666665,29,1.2916666666666667,-3,2.625,5.9,2.2541666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"06:00:00",-6,2.75,8.9600000000000009,2.1266666666666665,29,1.2916666666666667,-2,2.5833333333333335,5.9,2.2541666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"07:00:00",-8,2.8333333333333335,3.02,2.3741666666666665,30,1.25,-3,2.625,6.98,2.2091666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"08:00:00",-6,2.75,8.06,2.1641666666666666,30,1.25,-2,2.5833333333333335,6.98,2.2091666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"09:00:00",0,2.5,10.039999999999999,2.0816666666666666,30,1.25,4,2.3333333333333335,8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"10:00:00",16,1.8333333333333333,14,1.9166666666666667,30,1.25,8,2.1666666666666665,14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"11:00:00",25,1.4583333333333333,17.96,1.7516666666666667,32,1.1666666666666667,14,1.9166666666666667,14.9,1.8791666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"12:00:00",32,1.1666666666666667,21.92,1.5866666666666667,32,1.1666666666666667,12,2,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"13:00:00",34,1.0833333333333333,23,1.5416666666666667,34,1.0833333333333333,16,1.8333333333333333,18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"14:00:00",36,1,24.98,1.4591666666666665,35,1.0416666666666667,17,1.7916666666666667,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"15:00:00",37,0.95833333333333337,24.98,1.4591666666666665,37,0.95833333333333337,19,1.7083333333333333,18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"16:00:00",36,1,24.98,1.4591666666666665,37.133800000000001,0.95275833333333326,19,1.7083333333333333,20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"17:00:00",28,1.3333333333333333,24.08,1.4966666666666668,35,1.0416666666666667,17,1.7916666666666667,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"18:00:00",18,1.75,24.08,1.4966666666666668,35,1.0416666666666667,15,1.875,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"19:00:00",18,1.75,24.08,1.4966666666666668,35,1.0416666666666667,15,1.875,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"20:00:00",16,1.8333333333333333,24.98,1.4591666666666665,35,1.0416666666666667,13,1.9583333333333333,15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"21:00:00",9,2.125,21.92,1.5866666666666667,36,1,11,2.0416666666666665,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"22:00:00",3,2.375,21.92,1.5866666666666667,31.1968,1.2001333333333333,12,2,16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,"23:00:00",7,2.2083333333333335,21.92,1.5866666666666667,27,1.375,11,2.0416666666666665,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,1,1,1,2.4583333333333335,23,1.5416666666666667,27,1.375,11,2.0416666666666665,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"01:00:00",0,{"$f":"IF(W773<60,(60-W773)/24,0)","v":2.5},23,1.5416666666666667,23,1.5416666666666667,12,2,15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"02:00:00",0,2.5,24.08,{"$f":"IF(Y774<60,(60-Y774)/24,0)","v":1.4966666666666668},22,{"$f":"IF(AA774<60,(60-AA774)/24,0)","v":1.5833333333333333},11,{"$f":"IF(AC774<60,(60-AC774)/24,0)","v":2.0416666666666665},16.88,{"$f":"IF(AE774<60,(60-AE774)/24,0)","v":1.7966666666666669}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"03:00:00",0,2.5,24.98,1.4591666666666665,20.181000000000001,1.6591250000000002,12,2,16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"04:00:00",-2,2.5833333333333335,26.06,1.4141666666666666,16,1.8333333333333333,12,2,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"05:00:00",1,2.4583333333333335,24.98,1.4591666666666665,15,1.875,13,1.9583333333333333,18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"06:00:00",7,2.2083333333333335,24.98,1.4591666666666665,11,2.0416666666666665,15,1.875,16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"07:00:00",12,2,24.98,1.4591666666666665,10,2.0833333333333335,16,1.8333333333333333,15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"08:00:00",16,1.8333333333333333,24.08,1.4966666666666668,12.358599999999999,1.9850583333333336,17,1.7916666666666667,16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"09:00:00",28,1.3333333333333333,24.98,1.4591666666666665,17,1.7916666666666667,18,1.75,16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"10:00:00",28,1.3333333333333333,24.98,1.4591666666666665,23,1.5416666666666667,21,1.625,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"11:00:00",28,1.3333333333333333,26.06,1.4141666666666666,32,1.1666666666666667,23,1.5416666666666667,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"12:00:00",28,1.3333333333333333,28.04,1.3316666666666668,37,0.95833333333333337,24,1.5,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"13:00:00",28,1.3333333333333333,28.94,1.2941666666666667,45,0.625,24,1.5,26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"14:00:00",28,1.3333333333333333,28.94,1.2941666666666667,46,0.58333333333333337,23,1.5416666666666667,26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"15:00:00",30,1.25,30.02,1.2491666666666668,49,0.45833333333333331,23,1.5416666666666667,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"16:00:00",30,1.25,30.92,1.2116666666666667,49,0.45833333333333331,23,1.5416666666666667,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"17:00:00",30,1.25,33.08,1.1216666666666668,43,0.70833333333333337,20,1.6666666666666667,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"18:00:00",30,1.25,33.08,1.1216666666666668,35,1.0416666666666667,18,1.75,26.96,1.3766666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"19:00:00",30,1.25,30.02,1.2491666666666668,33,1.125,17,1.7916666666666667,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"20:00:00",32,1.1666666666666667,28.04,1.3316666666666668,28,1.3333333333333333,17,1.7916666666666667,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"21:00:00",32,1.1666666666666667,24.98,1.4591666666666665,22,1.5833333333333333,16,1.8333333333333333,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"22:00:00",34,1.0833333333333333,24.98,1.4591666666666665,18.210899999999999,1.7412125000000003,15,1.875,21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,"23:00:00",34,1.0833333333333333,23,1.5416666666666667,16.050999999999998,1.8312083333333333,13,1.9583333333333333,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,2,1,34,1.0833333333333333,21.92,1.5866666666666667,15,1.875,11,2.0416666666666665,16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"01:00:00",36,1,23,1.5416666666666667,11,2.0416666666666665,11,2.0416666666666665,16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"02:00:00",34.191699999999997,1.0753458333333334,23,1.5416666666666667,7,2.2083333333333335,9,2.125,15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"03:00:00",34.191699999999997,1.0753458333333334,23,1.5416666666666667,7,2.2083333333333335,8,2.1666666666666665,14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"04:00:00",34.191699999999997,1.0753458333333334,23,1.5416666666666667,4.3533299999999997,2.31861125,7,2.2083333333333335,14.9,1.8791666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"05:00:00",34.191699999999997,1.0753458333333334,21.02,1.6241666666666668,2.3201000000000001,2.403329166666667,6,2.25,11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"06:00:00",34.191699999999997,1.0753458333333334,21.02,1.6241666666666668,1,2.4583333333333335,7,2.2083333333333335,9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"07:00:00",30,1.25,21.02,1.6241666666666668,7.0163699999999996E-2,2.4970765125000001,7,2.2083333333333335,9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"08:00:00",32,1.1666666666666667,21.02,1.6241666666666668,7.0163699999999996E-2,2.4970765125000001,7,2.2083333333333335,10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"09:00:00",34.191699999999997,1.0753458333333334,24.98,1.4591666666666665,7,2.2083333333333335,8,2.1666666666666665,10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"10:00:00",34.191699999999997,1.0753458333333334,26.06,1.4141666666666666,15,1.875,7,2.2083333333333335,10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"11:00:00",37,0.95833333333333337,28.04,1.3316666666666668,19,1.7083333333333333,10,2.0833333333333335,14.9,1.8791666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"12:00:00",41,0.79166666666666663,28.94,1.2941666666666667,23,1.5416666666666667,11,2.0416666666666665,16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"13:00:00",39,0.875,30.92,1.2116666666666667,32,1.1666666666666667,12,2,15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"14:00:00",41,0.79166666666666663,32,1.1666666666666667,33,1.125,12,2,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"15:00:00",41,0.79166666666666663,32,1.1666666666666667,34,1.0833333333333333,14,1.9166666666666667,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"16:00:00",41,0.79166666666666663,32,1.1666666666666667,34,1.0833333333333333,12,2,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"17:00:00",37,0.95833333333333337,30.02,1.2491666666666668,34,1.0833333333333333,9,2.125,16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"18:00:00",28,1.3333333333333333,28.04,1.3316666666666668,32,1.1666666666666667,7,2.2083333333333335,12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"19:00:00",27,1.375,24.08,1.4966666666666668,31,1.2083333333333333,5,2.2916666666666665,11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"20:00:00",25,1.4583333333333333,24.08,1.4966666666666668,30,1.25,4,2.3333333333333335,12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"21:00:00",21,1.625,23,1.5416666666666667,28,1.3333333333333333,3,2.375,11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"22:00:00",18,1.75,21.02,1.6241666666666668,25,1.4583333333333333,1,2.4583333333333335,8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,"23:00:00",19,1.7083333333333333,19.04,1.7066666666666668,23,1.5416666666666667,-1,2.5416666666666665,8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,3,1,16,1.8333333333333333,17.059999999999999,1.7891666666666666,21,1.625,-2,2.5833333333333335,7.88,2.1716666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"01:00:00",18,1.75,8.06,2.1641666666666666,20,1.6666666666666667,-2,2.5833333333333335,5,2.2916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"02:00:00",16,1.8333333333333333,5,2.2916666666666665,20,1.6666666666666667,-3,2.625,3.92,2.3366666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"03:00:00",14,1.9166666666666667,3.02,2.3741666666666665,19,1.7083333333333333,-4,2.6666666666666665,1.94,2.4191666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"04:00:00",10,2.0833333333333335,-3.9999999999999147E-2,2.5016666666666665,18,1.75,-5,2.7083333333333335,0.85999999999999943,2.4641666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"05:00:00",12,2,-2.02,2.5841666666666669,20,1.6666666666666667,-5,2.7083333333333335,-3.9999999999999147E-2,2.5016666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"06:00:00",12,2,-0.94000000000000483,2.539166666666667,21,1.625,-4,2.6666666666666665,-1.1200000000000001,2.5466666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"07:00:00",12,2,-2.02,2.5841666666666669,27,1.375,-4,2.6666666666666665,-1.1200000000000001,2.5466666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"08:00:00",16,1.8333333333333333,-3.9999999999999147E-2,2.5016666666666665,30,1.25,-3,2.625,-3.9999999999999147E-2,2.5016666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"09:00:00",18,1.75,5,2.2916666666666665,31,1.2083333333333333,0,2.5,0.85999999999999943,2.4641666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"10:00:00",25,1.4583333333333333,10.039999999999999,2.0816666666666666,31,1.2083333333333333,4,2.3333333333333335,3.92,2.3366666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"11:00:00",30,1.25,15.98,1.8341666666666665,32,1.1666666666666667,4,2.3333333333333335,5.9,2.2541666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"12:00:00",39,0.875,21.02,1.6241666666666668,33,1.125,8,2.1666666666666665,6.98,2.2091666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"13:00:00",39,0.875,23,1.5416666666666667,36,1,9,2.125,8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"14:00:00",39,0.875,24.98,1.4591666666666665,35,1.0416666666666667,11,2.0416666666666665,10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"15:00:00",39,0.875,26.06,1.4141666666666666,35,1.0416666666666667,12,2,10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"16:00:00",39,0.875,26.06,1.4141666666666666,35,1.0416666666666667,13,1.9583333333333333,10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"17:00:00",39,{"$f":"IF(W837<60,(60-W837)/24,0)","v":0.875},26.06,1.4141666666666666,33,1.125,11,2.0416666666666665,10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"18:00:00",37,0.95833333333333337,24.98,{"$f":"IF(Y838<60,(60-Y838)/24,0)","v":1.4591666666666665},31,{"$f":"IF(AA838<60,(60-AA838)/24,0)","v":1.2083333333333333},8,{"$f":"IF(AC838<60,(60-AC838)/24,0)","v":2.1666666666666665},8.9600000000000009,{"$f":"IF(AE838<60,(60-AE838)/24,0)","v":2.1266666666666665}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"19:00:00",36,1,24.98,1.4591666666666665,30,1.25,7,2.2083333333333335,5,2.2916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"20:00:00",34,1.0833333333333333,24.08,1.4966666666666668,29,1.2916666666666667,4,2.3333333333333335,5,2.2916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"21:00:00",33,1.125,24.08,1.4966666666666668,29,1.2916666666666667,1,2.4583333333333335,3.92,2.3366666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"22:00:00",32.447400000000002,1.1480249999999999,23,1.5416666666666667,30,1.25,1,2.4583333333333335,-3.9999999999999147E-2,2.5016666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,"23:00:00",32,1.1666666666666667,24.08,1.4966666666666668,31,1.2083333333333333,-2,2.5833333333333335,1.94,2.4191666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,1,32.447400000000002,1.1480249999999999,24.08,1.4966666666666668,34,1.0833333333333333,-3,2.625,-3.9999999999999147E-2,2.5016666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"01:00:00",32,1.1666666666666667,24.08,1.4966666666666668,34,1.0833333333333333,-4,2.6666666666666665,-4,2.6666666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"02:00:00",32,1.1666666666666667,24.08,1.4966666666666668,35,1.0416666666666667,-5,2.7083333333333335,-4,2.6666666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"03:00:00",32,1.1666666666666667,24.08,1.4966666666666668,34,1.0833333333333333,-7,2.7916666666666665,-5.0800000000000054,2.7116666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"04:00:00",36,1,24.98,1.4591666666666665,35,1.0416666666666667,-8,2.8333333333333335,-9.0399999999999991,2.8766666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"05:00:00",36,1,23,1.5416666666666667,34,1.0833333333333333,-9,2.875,-8.14,2.8391666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"06:00:00",34,1.0833333333333333,24.08,1.4966666666666668,33,1.125,-8,2.8333333333333335,-8.14,2.8391666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"07:00:00",34,1.0833333333333333,24.08,1.4966666666666668,34,1.0833333333333333,-7,2.7916666666666665,-10.119999999999999,2.9216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"08:00:00",30,1.25,24.98,1.4591666666666665,35,1.0416666666666667,-6,2.75,-6.16,2.7566666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"09:00:00",30,1.25,26.06,1.4141666666666666,37,0.95833333333333337,0,2.5,-2.02,2.5841666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"10:00:00",27,1.375,26.96,1.3766666666666667,37,0.95833333333333337,6,2.25,5,2.2916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"11:00:00",25,1.4583333333333333,30.02,1.2491666666666668,41,0.79166666666666663,9,2.125,10.039999999999999,2.0816666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"12:00:00",25,1.4583333333333333,30.92,1.2116666666666667,40,0.83333333333333337,15,1.875,14.9,1.8791666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"13:00:00",24,1.5,33.979999999999997,1.0841666666666667,42,0.75,14,1.9166666666666667,14.9,1.8791666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"14:00:00",23,1.5416666666666667,35.06,1.0391666666666666,42,0.75,17,1.7916666666666667,15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"15:00:00",23,1.5416666666666667,37.04,0.95666666666666667,42,0.75,18,1.75,16.88,1.7966666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"16:00:00",21,1.625,37.04,0.95666666666666667,42,0.75,16,1.8333333333333333,14.9,1.8791666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"17:00:00",19,1.7083333333333333,35.06,1.0391666666666666,40,0.83333333333333337,15,1.875,15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"18:00:00",18,1.75,33.08,1.1216666666666668,40,0.83333333333333337,15,1.875,14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"19:00:00",16,1.8333333333333333,32,1.1666666666666667,40,0.83333333333333337,15,1.875,10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"20:00:00",16,1.8333333333333333,33.08,1.1216666666666668,38,0.91666666666666663,14,1.9166666666666667,11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"21:00:00",14,1.9166666666666667,32,1.1666666666666667,38,0.91666666666666663,14,1.9166666666666667,12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"22:00:00",12,2,35.96,1.0016666666666667,36,1,14,1.9166666666666667,14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,"23:00:00",10,2.0833333333333335,35.06,1.0391666666666666,36,1,12,2,12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,5,1,7,2.2083333333333335,33.08,1.1216666666666668,36,1,11,2.0416666666666665,14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"01:00:00",7,2.2083333333333335,32,1.1666666666666667,36,1,10,2.0833333333333335,12.92,1.9616666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"02:00:00",3,2.375,30.92,1.2116666666666667,36,1,8,2.1666666666666665,11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"03:00:00",1,2.4583333333333335,28.94,1.2941666666666667,36,1,7,2.2083333333333335,10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"04:00:00",1,2.4583333333333335,28.04,1.3316666666666668,36,1,6,2.25,9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"05:00:00",0,2.5,28.04,1.3316666666666668,36,1,5,2.2916666666666665,8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"06:00:00",0,2.5,24.08,1.4966666666666668,36,1,6,2.25,6.98,2.2091666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"07:00:00",1,2.4583333333333335,19.04,1.7066666666666668,37,0.95833333333333337,5,2.2916666666666665,6.98,2.2091666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"08:00:00",3,2.375,15.98,1.8341666666666665,35,1.0416666666666667,7,2.2083333333333335,8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"09:00:00",7,2.2083333333333335,14,1.9166666666666667,35,1.0416666666666667,12,2,9.86,2.0891666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"10:00:00",12,2,15.08,1.8716666666666668,35,1.0416666666666667,15,1.875,14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"11:00:00",16,1.8333333333333333,17.059999999999999,1.7891666666666666,38,0.91666666666666663,17,1.7916666666666667,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"12:00:00",18,1.75,17.96,1.7516666666666667,39,0.875,18,1.75,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"13:00:00",19,1.7083333333333333,19.940000000000001,1.6691666666666667,39,0.875,20,1.6666666666666667,21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"14:00:00",21,1.625,19.940000000000001,1.6691666666666667,40,0.83333333333333337,20,1.6666666666666667,21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"15:00:00",21,1.625,19.940000000000001,1.6691666666666667,40,0.83333333333333337,21,1.625,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"16:00:00",21,1.625,19.04,1.7066666666666668,40,0.83333333333333337,21,1.625,21.92,1.5866666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"17:00:00",21,1.625,17.96,1.7516666666666667,39,0.875,20,1.6666666666666667,18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"18:00:00",21,1.625,15.98,1.8341666666666665,38,0.91666666666666663,15,1.875,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"19:00:00",21,1.625,14,1.9166666666666667,38,0.91666666666666663,11,2.0416666666666665,14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"20:00:00",25,1.4583333333333333,12.02,1.9991666666666668,38,0.91666666666666663,11,2.0416666666666665,8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"21:00:00",25,1.4583333333333333,8.9600000000000009,2.1266666666666665,37,0.95833333333333337,8,2.1666666666666665,6.98,2.2091666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"22:00:00",23,1.5416666666666667,6.98,2.2091666666666665,35,1.0416666666666667,8,2.1666666666666665,10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,"23:00:00",23,1.5416666666666667,8.06,2.1641666666666666,36,1,7,2.2083333333333335,5.9,2.2541666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,6,1,21,1.625,5,2.2916666666666665,36,1,6,2.25,7.88,2.1716666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"01:00:00",21,1.625,1.04,2.4566666666666666,35,1.0416666666666667,7,2.2083333333333335,7.88,2.1716666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"02:00:00",19,1.7083333333333333,-2.02,2.5841666666666669,35,1.0416666666666667,6,2.25,6.98,2.2091666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"03:00:00",19,1.7083333333333333,1.04,2.4566666666666666,34,1.0833333333333333,6,2.25,3.92,2.3366666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"04:00:00",19,1.7083333333333333,1.04,2.4566666666666666,34,1.0833333333333333,6,2.25,3.92,2.3366666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"05:00:00",19,1.7083333333333333,-3.9999999999999147E-2,2.5016666666666665,35,1.0416666666666667,6,2.25,6.98,2.2091666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"06:00:00",18,1.75,-0.94000000000000483,2.539166666666667,35,1.0416666666666667,8,2.1666666666666665,5.9,2.2541666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"07:00:00",18,1.75,-0.94000000000000483,2.539166666666667,34,1.0833333333333333,7,2.2083333333333335,5.9,2.2541666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"08:00:00",18,1.75,1.94,2.4191666666666669,33,1.125,10,2.0833333333333335,5.9,2.2541666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"09:00:00",19,{"$f":"IF(W901<60,(60-W901)/24,0)","v":1.7083333333333333},8.06,2.1641666666666666,33,1.125,15,1.875,10.94,2.0441666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"10:00:00",19,1.7083333333333333,10.039999999999999,{"$f":"IF(Y902<60,(60-Y902)/24,0)","v":2.0816666666666666},33,{"$f":"IF(AA902<60,(60-AA902)/24,0)","v":1.125},21,{"$f":"IF(AC902<60,(60-AC902)/24,0)","v":1.625},17.96,{"$f":"IF(AE902<60,(60-AE902)/24,0)","v":1.7516666666666667}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"11:00:00",21,1.625,14,1.9166666666666667,34,1.0833333333333333,24,1.5,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"12:00:00",23,1.5416666666666667,15.98,1.8341666666666665,32,1.1666666666666667,27,1.375,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"13:00:00",23,1.5416666666666667,21.92,1.5866666666666667,32,1.1666666666666667,29,1.2916666666666667,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"14:00:00",25,1.4583333333333333,23,1.5416666666666667,29,1.2916666666666667,29,1.2916666666666667,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"15:00:00",25,1.4583333333333333,23,1.5416666666666667,26,1.4166666666666667,29,1.2916666666666667,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"16:00:00",25,1.4583333333333333,23,1.5416666666666667,24,1.5,31,1.2083333333333333,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"17:00:00",21,1.625,23,1.5416666666666667,21,1.625,31,1.2083333333333333,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"18:00:00",19,1.7083333333333333,21.92,1.5866666666666667,20,1.6666666666666667,30,1.25,28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"19:00:00",18,1.75,21.92,1.5866666666666667,19,1.7083333333333333,30,1.25,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"20:00:00",14,1.9166666666666667,21.92,1.5866666666666667,16,1.8333333333333333,29,1.2916666666666667,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"21:00:00",9,2.125,21.02,1.6241666666666668,14,1.9166666666666667,30,1.25,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"22:00:00",7,2.2083333333333335,19.940000000000001,1.6691666666666667,12,2,29,1.2916666666666667,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,"23:00:00",5,2.2916666666666665,19.940000000000001,1.6691666666666667,11,2.0416666666666665,28,1.3333333333333333,29.84,1.2566666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,7,1,1,2.4583333333333335,21.02,1.6241666666666668,10,2.0833333333333335,28,1.3333333333333333,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"01:00:00",0,2.5,19.940000000000001,1.6691666666666667,3,2.375,28,1.3333333333333333,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"02:00:00",-2,2.5833333333333335,19.940000000000001,1.6691666666666667,0,2.5,27,1.375,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"03:00:00",-6,2.75,17.96,1.7516666666666667,-1,2.5416666666666665,27,1.375,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"04:00:00",-8,2.8333333333333335,17.059999999999999,1.7891666666666666,-3,2.625,27,1.375,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"05:00:00",-8,2.8333333333333335,17.059999999999999,1.7891666666666666,-2,2.5833333333333335,27,1.375,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"06:00:00",-9,2.875,15.98,1.8341666666666665,0,2.5,29,1.2916666666666667,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"07:00:00",-9,2.875,15.98,1.8341666666666665,3,2.375,29,1.2916666666666667,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"08:00:00",-9,2.875,15.98,1.8341666666666665,3,2.375,29,1.2916666666666667,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"09:00:00",-2,2.5833333333333335,19.940000000000001,1.6691666666666667,2,2.4166666666666665,30,1.25,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"10:00:00",9,2.125,21.92,1.5866666666666667,2,2.4166666666666665,31,1.2083333333333333,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"11:00:00",16,1.8333333333333333,26.06,1.4141666666666666,3,2.375,33,1.125,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"12:00:00",21,1.625,28.04,1.3316666666666668,4,2.3333333333333335,37,0.95833333333333337,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"13:00:00",27,1.375,28.94,1.2941666666666667,5,2.2916666666666665,37,0.95833333333333337,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"14:00:00",27,1.375,30.02,1.2491666666666668,8,2.1666666666666665,37,0.95833333333333337,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"15:00:00",27,1.375,30.92,1.2116666666666667,8,2.1666666666666665,37,0.95833333333333337,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"16:00:00",28,1.3333333333333333,30.02,1.2491666666666668,8,2.1666666666666665,37,0.95833333333333337,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"17:00:00",25,1.4583333333333333,28.04,1.3316666666666668,7,2.2083333333333335,37,0.95833333333333337,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"18:00:00",19,1.7083333333333333,24.98,1.4591666666666665,7,2.2083333333333335,36,1,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"19:00:00",14,1.9166666666666667,24.08,1.4966666666666668,7,2.2083333333333335,36,1,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"20:00:00",12,2,17.96,1.7516666666666667,7,2.2083333333333335,36,1,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"21:00:00",12,2,17.059999999999999,1.7891666666666666,7,2.2083333333333335,35,1.0416666666666667,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"22:00:00",7,2.2083333333333335,19.04,1.7066666666666668,6,2.25,34,1.0833333333333333,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,"23:00:00",3,2.375,17.059999999999999,1.7891666666666666,6,2.25,33,1.125,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,8,1,0,2.5,12.02,1.9991666666666668,6,2.25,32,1.1666666666666667,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"01:00:00",0,2.5,8.9600000000000009,2.1266666666666665,6,2.25,32.049900000000001,1.1645874999999999,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"02:00:00",-2,2.5833333333333335,6.08,2.2466666666666666,6,2.25,32,1.1666666666666667,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"03:00:00",0,2.5,3.92,2.3366666666666664,6,2.25,32,1.1666666666666667,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"04:00:00",0,2.5,1.94,2.4191666666666669,5,2.2916666666666665,32.131399999999999,1.1611916666666666,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"05:00:00",-2,2.5833333333333335,1.94,2.4191666666666669,5,2.2916666666666665,33,1.125,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"06:00:00",0,2.5,3.02,2.3741666666666665,6,2.25,35.201900000000002,1.0332541666666666,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"07:00:00",1,2.4583333333333335,-3.9999999999999147E-2,2.5016666666666665,6,2.25,35,1.0416666666666667,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"08:00:00",1,2.4583333333333335,-3.9999999999999147E-2,2.5016666666666665,5,2.2916666666666665,35,1.0416666666666667,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"09:00:00",7,2.2083333333333335,12.02,1.9991666666666668,6,2.25,36,1,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"10:00:00",10,2.0833333333333335,17.96,1.7516666666666667,7,2.2083333333333335,39,0.875,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"11:00:00",19,1.7083333333333333,24.98,1.4591666666666665,8,2.1666666666666665,40,0.83333333333333337,43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"12:00:00",21,1.625,30.02,1.2491666666666668,8,2.1666666666666665,40,0.83333333333333337,44.96,0.62666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"13:00:00",25,1.4583333333333333,33.979999999999997,1.0841666666666667,9,2.125,39,0.875,42.98,0.70916666666666683]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"14:00:00",28,1.3333333333333333,35.06,1.0391666666666666,9,2.125,39,0.875,42.98,0.70916666666666683]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"15:00:00",28,1.3333333333333333,35.06,1.0391666666666666,9,2.125,29,1.2916666666666667,41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"16:00:00",31,1.2083333333333333,33.08,1.1216666666666668,9,2.125,39,0.875,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"17:00:00",32,1.1666666666666667,30.92,1.2116666666666667,9,2.125,38,0.91666666666666663,39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"18:00:00",25,1.4583333333333333,28.94,1.2941666666666667,9,2.125,38,0.91666666666666663,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"19:00:00",25,1.4583333333333333,26.96,1.3766666666666667,9,2.125,37,0.95833333333333337,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"20:00:00",25,1.4583333333333333,21.02,1.6241666666666668,9,2.125,37,0.95833333333333337,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"21:00:00",27,1.375,24.98,1.4591666666666665,9,2.125,36,1,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"22:00:00",36,1,19.940000000000001,1.6691666666666667,9,2.125,35,1.0416666666666667,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,"23:00:00",37,0.95833333333333337,14,1.9166666666666667,7,2.2083333333333335,34,1.0833333333333333,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,9,1,37,0.95833333333333337,17.059999999999999,1.7891666666666666,6,2.25,33,1.125,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"01:00:00",36,{"$f":"IF(W965<60,(60-W965)/24,0)","v":1},12.92,1.9616666666666667,4,2.3333333333333335,32,1.1666666666666667,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"02:00:00",36,1,10.94,{"$f":"IF(Y966<60,(60-Y966)/24,0)","v":2.0441666666666669},2,{"$f":"IF(AA966<60,(60-AA966)/24,0)","v":2.4166666666666665},30,{"$f":"IF(AC966<60,(60-AC966)/24,0)","v":1.25},35.96,{"$f":"IF(AE966<60,(60-AE966)/24,0)","v":1.0016666666666667}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"03:00:00",34,1.0833333333333333,8.06,2.1641666666666666,-2,2.5833333333333335,29,1.2916666666666667,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"04:00:00",34,1.0833333333333333,8.9600000000000009,2.1266666666666665,-3,2.625,28,1.3333333333333333,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"05:00:00",36,1,12.92,1.9616666666666667,-6,2.75,27,1.375,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"06:00:00",34,1.0833333333333333,10.039999999999999,2.0816666666666666,-5,2.7083333333333335,28,1.3333333333333333,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"07:00:00",34,1.0833333333333333,8.9600000000000009,2.1266666666666665,-5,2.7083333333333335,27,1.375,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"08:00:00",32,1.1666666666666667,6.08,2.2466666666666666,-7,2.7916666666666665,28,1.3333333333333333,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"09:00:00",30,1.25,17.96,1.7516666666666667,-3,2.625,30,1.25,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"10:00:00",30,1.25,23,1.5416666666666667,-1,2.5416666666666665,31,1.2083333333333333,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"11:00:00",28,1.3333333333333333,28.04,1.3316666666666668,3,2.375,33,1.125,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"12:00:00",27,1.375,32,1.1666666666666667,6,2.25,35,1.0416666666666667,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"13:00:00",27,1.375,33.08,1.1216666666666668,9,2.125,38,0.91666666666666663,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"14:00:00",28,1.3333333333333333,35.06,1.0391666666666666,11,2.0416666666666665,38,0.91666666666666663,39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"15:00:00",28,1.3333333333333333,35.06,1.0391666666666666,12,2,38,0.91666666666666663,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"16:00:00",28,1.3333333333333333,35.06,1.0391666666666666,13,1.9583333333333333,39,0.875,39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"17:00:00",27,1.375,32,1.1666666666666667,10,2.0833333333333335,37,0.95833333333333337,37.94,0.9191666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"18:00:00",27,1.375,30.92,1.2116666666666667,4,2.3333333333333335,33,1.125,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"19:00:00",27,1.375,30.02,1.2491666666666668,-2,2.5833333333333335,31,1.2083333333333333,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"20:00:00",27,1.375,28.94,1.2941666666666667,-5,2.7083333333333335,26,1.4166666666666667,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"21:00:00",25,1.4583333333333333,24.08,1.4966666666666668,-5,2.7083333333333335,26,1.4166666666666667,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"22:00:00",25,1.4583333333333333,19.940000000000001,1.6691666666666667,-6,2.75,25,1.4583333333333333,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,"23:00:00",21,1.625,21.92,1.5866666666666667,-8,2.8333333333333335,24,1.5,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,10,1,19,1.7083333333333333,21.02,1.6241666666666668,-8,2.8333333333333335,24,1.5,28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"01:00:00",19,1.7083333333333333,19.940000000000001,1.6691666666666667,-8,2.8333333333333335,24,1.5,28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"02:00:00",18,1.75,17.96,1.7516666666666667,-8,2.8333333333333335,24,1.5,28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"03:00:00",16,1.8333333333333333,19.940000000000001,1.6691666666666667,-6,2.75,24,1.5,30.92,1.2116666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"04:00:00",14,1.9166666666666667,17.059999999999999,1.7891666666666666,-5,2.7083333333333335,24,1.5,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"05:00:00",14,1.9166666666666667,15.08,1.8716666666666668,-3,2.625,25,1.4583333333333333,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"06:00:00",14,1.9166666666666667,10.94,2.0441666666666669,-1,2.5416666666666665,27,1.375,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"07:00:00",12,2,8.9600000000000009,2.1266666666666665,1,2.4583333333333335,28,1.3333333333333333,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"08:00:00",14,1.9166666666666667,12.92,1.9616666666666667,3,2.375,29,1.2916666666666667,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"09:00:00",18,1.75,15.98,1.8341666666666665,8,2.1666666666666665,30,1.25,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"10:00:00",23,1.5416666666666667,19.04,1.7066666666666668,15,1.875,31,1.2083333333333333,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"11:00:00",27,1.375,21.02,1.6241666666666668,17,1.7916666666666667,32,1.1666666666666667,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"12:00:00",28,1.3333333333333333,23,1.5416666666666667,25,1.4583333333333333,32,1.1666666666666667,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"17:00:00",30,1.25,28.04,1.3316666666666668,33,1.125,34,1.0833333333333333,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,11,"22:00:00",25,1.4583333333333333,21.92,1.5866666666666667,32,1.1666666666666667,34,1.0833333333333333,34.880000000000003,1.0466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,12,"07:00:00",27,1.375,12.02,1.9991666666666668,28,1.3333333333333333,16,1.8333333333333333,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,12,"15:00:00",48,0.5,26.06,1.4141666666666666,37,0.95833333333333337,14,1.9166666666666667,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,12,"21:00:00",39,0.875,17.059999999999999,1.7891666666666666,28,1.3333333333333333,3,2.375,7.88,2.1716666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,13,"08:00:00",28,1.3333333333333333,5,2.2916666666666665,16,1.8333333333333333,-2,2.5833333333333335,1.94,2.4191666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,13,"11:00:00",30,1.25,23,1.5416666666666667,19,1.7083333333333333,3,2.375,7.88,2.1716666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,13,"17:00:00",25,1.4583333333333333,26.06,1.4141666666666666,22,1.5833333333333333,10,2.0833333333333335,11.84,2.0066666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,14,"01:00:00",9,2.125,12.92,1.9616666666666667,18,1.75,-1,2.5416666666666665,7.88,2.1716666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,14,"10:00:00",12,2,19.940000000000001,1.6691666666666667,18,1.75,5,2.2916666666666665,17.96,1.7516666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,14,"18:00:00",10,2.0833333333333335,26.06,1.4141666666666666,22,1.5833333333333333,19,1.7083333333333333,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,15,"03:00:00",-8,2.8333333333333335,17.96,1.7516666666666667,8,2.1666666666666665,11,2.0416666666666665,20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,15,"08:00:00",-8,2.8333333333333335,10.94,2.0441666666666669,11,2.0416666666666665,15,1.875,19.940000000000001,1.6691666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,15,"20:00:00",14,1.9166666666666667,23,1.5416666666666667,28,1.3333333333333333,14,1.9166666666666667,20.84,1.6316666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,15,"22:00:00",10,2.0833333333333335,21.02,1.6241666666666668,28,1.3333333333333333,11,2.0416666666666665,15.98,1.8341666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,16,"05:00:00",5,2.2916666666666665,12.02,1.9991666666666668,32,1.1666666666666667,5,2.2916666666666665,8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,16,"19:00:00",27,1.375,21.02,1.6241666666666668,28,1.3333333333333333,20,1.6666666666666667,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,16,"22:00:00",18,1.75,12.92,1.9616666666666667,25,1.4583333333333333,20,1.6666666666666667,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,17,"05:00:00",18,1.75,15.98,1.8341666666666665,14,1.9166666666666667,17,1.7916666666666667,24.98,1.4591666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,17,"15:00:00",32,1.1666666666666667,26.06,1.4141666666666666,28,1.3333333333333333,26,1.4166666666666667,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,17,"19:00:00",30,1.25,26.96,1.3766666666666667,25,1.4583333333333333,21,1.625,23.9,1.5041666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,18,"08:00:00",28,1.3333333333333333,28.04,1.3316666666666668,22,1.5833333333333333,7,2.2083333333333335,18.86,1.7141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,18,"16:00:00",30,1.25,30.92,1.2116666666666667,48,0.5,21,1.625,28.94,1.2941666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,18,"17:00:00",32,1.1666666666666667,30.92,1.2116666666666667,47,0.54166666666666663,19,1.7083333333333333,25.88,1.4216666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,19,"06:00:00",16,1.8333333333333333,28.94,1.2941666666666667,34,1.0833333333333333,0,2.5,8.9600000000000009,2.1266666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,19,"10:00:00",28,1.3333333333333333,28.94,1.2941666666666667,38,0.91666666666666663,9,2.125,14.9,1.8791666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,19,"16:00:00",34,1.0833333333333333,32,1.1666666666666667,58,8.3333333333333329E-2,27,1.375,27.86,1.3391666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,20,"03:00:00",9,2.125,30.02,1.2491666666666668,37,0.95833333333333337,23,1.5416666666666667,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,20,"13:00:00",28,1.3333333333333333,37.04,0.95666666666666667,45,0.625,33,1.125,41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,20,"20:00:00",16,1.8333333333333333,33.979999999999997,1.0841666666666667,39,0.875,37,0.95833333333333337,39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,21,"03:00:00",7,2.2083333333333335,33.979999999999997,1.0841666666666667,38,0.91666666666666663,36,1,38.840000000000003,0.88166666666666649]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,21,"05:00:00",9,2.125,33.979999999999997,1.0841666666666667,37,0.95833333333333337,35,1.0416666666666667,40.28,0.82166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,21,"17:00:00",19,1.7083333333333333,35.06,1.0391666666666666,54,0.25,38,0.91666666666666663,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,21,"22:00:00",7,2.2083333333333335,33.979999999999997,1.0841666666666667,53,0.29166666666666669,36.349800000000002,0.98542499999999988,39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,22,"10:00:00",1,2.4583333333333335,26.06,1.4141666666666666,50,0.41666666666666669,38,0.91666666666666663,42.98,0.70916666666666683]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,22,"15:00:00",9,2.125,35.06,1.0391666666666666,49,0.45833333333333331,47,0.54166666666666663,45.86,0.58916666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,22,1,-9,2.875,19.940000000000001,1.6691666666666667,34,1.0833333333333333,35.4298,1.0237583333333333,42.98,0.70916666666666683]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,23,"06:00:00",-15,3.125,19.940000000000001,1.6691666666666667,30,1.25,35,1.0416666666666667,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,23,"17:00:00",16,1.8333333333333333,30.02,1.2491666666666668,34,1.0833333333333333,43,0.70833333333333337,44.96,0.62666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,23,"23:00:00",-8,2.8333333333333335,19.04,1.7066666666666668,29,1.2916666666666667,34.463299999999997,1.0640291666666668,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,24,"02:00:00",-9,2.875,19.04,1.7066666666666668,29,1.2916666666666667,36.147799999999997,0.99384166666666685,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,24,"13:00:00",25,1.4583333333333333,33.08,1.1216666666666668,30,1.25,43,0.70833333333333337,39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,24,"19:00:00",18,1.75,30.02,1.2491666666666668,20,1.6666666666666667,39,0.875,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,25,"03:00:00",-2,2.5833333333333335,24.98,1.4591666666666665,11,2.0416666666666665,34,1.0833333333333333,39.92,0.83666666666666656]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,25,"12:00:00",21,1.625,30.92,1.2116666666666667,20,1.6666666666666667,38,0.91666666666666663,41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,25,"17:00:00",28,1.3333333333333333,26.96,1.3766666666666667,25,1.4583333333333333,42,0.75,43.88,0.67166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,26,"05:00:00",23,1.5416666666666667,10.039999999999999,2.0816666666666666,17,1.7916666666666667,31,1.2083333333333333,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,26,"10:00:00",27,1.375,10.94,2.0441666666666669,37,0.95833333333333337,35,1.0416666666666667,36.86,0.96416666666666673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,26,"14:00:00",30,1.25,21.02,1.6241666666666668,49,0.45833333333333331,40,0.83333333333333337,41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,26,1,21,1.625,15.98,1.8341666666666665,37,0.95833333333333337,29,1.2916666666666667,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,27,"07:00:00",21,1.625,8.06,2.1641666666666666,30,1.25,23,1.5416666666666667,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,27,"14:00:00",39,0.875,32,1.1666666666666667,43,0.70833333333333337,45,0.625,53.96,0.25166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,27,1,10,2.0833333333333335,19.04,1.7066666666666668,43,0.70833333333333337,36,1,41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,28,"04:00:00",7,2.2083333333333335,14,1.9166666666666667,38,0.91666666666666663,38,0.91666666666666663,42.98,0.70916666666666683]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,28,"17:00:00",34,{"$f":"IF(W1413<60,(60-W1413)/24,0)","v":1.0833333333333333},32,1.1666666666666667,34,1.0833333333333333,43,0.70833333333333337,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,28,"18:00:00",34,1.0833333333333333,30.02,{"$f":"IF(Y1414<60,(60-Y1414)/24,0)","v":1.2491666666666668},30,{"$f":"IF(AA1414<60,(60-AA1414)/24,0)","v":1.25},40,{"$f":"IF(AC1414<60,(60-AC1414)/24,0)","v":0.83333333333333337},45.86,{"$f":"IF(AE1414<60,(60-AE1414)/24,0)","v":0.58916666666666673}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,1,"02:00:00",11,2.0416666666666665,31.64,1.1816666666666666,30,1.25,35,1.0416666666666667,23.18,1.5341666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,1,"11:00:00",22,1.5833333333333333,41,0.79166666666666663,35,1.0416666666666667,39,0.875,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,1,"19:00:00",21,1.625,37.94,0.9191666666666668,38,0.91666666666666663,37,0.95833333333333337,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,2,"01:00:00",6,2.25,35.96,1.0016666666666667,38,0.91666666666666663,35,1.0416666666666667,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,2,"12:00:00",24,1.5,39.020000000000003,0.87416666666666654,45,0.625,39,0.875,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,2,"15:00:00",25,1.4583333333333333,39.92,0.83666666666666656,47,0.54166666666666663,46,0.58333333333333337,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,3,"05:00:00",5,2.2916666666666665,26.06,1.4141666666666666,37,0.95833333333333337,33,1.125,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,3,"12:00:00",26,1.4166666666666667,28.04,1.3316666666666668,37,0.95833333333333337,37,0.95833333333333337,6.8,2.2166666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,3,"14:00:00",24,1.5,28.04,1.3316666666666668,39,0.875,39,0.875,10.4,2.0666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,3,"22:00:00",16,1.8333333333333333,17.96,1.7516666666666667,33,1.125,37,0.95833333333333337,5,2.2916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,4,"07:00:00",9,2.125,14,1.9166666666666667,28,1.3333333333333333,30,1.25,1.4,2.4416666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,4,"12:00:00",16,1.8333333333333333,30.02,1.2491666666666668,31,1.2083333333333333,43,0.70833333333333337,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,4,1,6,2.25,24.08,1.4966666666666668,34,1.0833333333333333,33,1.125,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,5,"09:00:00",13,1.9583333333333333,26.06,1.4141666666666666,38,0.91666666666666663,36,1,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,5,"17:00:00",24,1.5,37.94,0.9191666666666668,48,0.5,36,1,34.520000000000003,1.0616666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,5,"18:00:00",23,1.5416666666666667,35.06,1.0391666666666666,46,0.58333333333333337,36,1,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,6,"08:00:00",21,1.625,30.02,1.2491666666666668,33,1.125,34,1.0833333333333333,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,6,"11:00:00",25,1.4583333333333333,30.92,1.2116666666666667,32,1.1666666666666667,36,1,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,6,"22:00:00",19,1.7083333333333333,33.979999999999997,1.0841666666666667,30,1.25,30,1.25,15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,7,"04:00:00",15,1.875,33.979999999999997,1.0841666666666667,28,1.3333333333333333,29,1.2916666666666667,5,2.2916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,7,"12:00:00",19,1.7083333333333333,35.96,1.0016666666666667,28,1.3333333333333333,37,0.95833333333333337,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,7,"21:00:00",17,1.7916666666666667,33.979999999999997,1.0841666666666667,20,1.6666666666666667,30,1.25,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,8,"05:00:00",14,1.9166666666666667,33.08,1.1216666666666668,18,1.75,26,1.4166666666666667,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,8,"06:00:00",14,1.9166666666666667,33.08,1.1216666666666668,18,1.75,25,1.4583333333333333,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,8,"19:00:00",12,2,35.06,1.0391666666666666,28,1.3333333333333333,36,1,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,8,"23:00:00",9,2.125,33.979999999999997,1.0841666666666667,21,1.625,35,1.0416666666666667,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,9,"09:00:00",6,2.25,33.979999999999997,1.0841666666666667,18,1.75,36,1,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,9,"16:00:00",11,2.0416666666666665,41,0.79166666666666663,30,1.25,41,0.79166666666666663,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,9,"23:00:00",8,2.1666666666666665,35.06,1.0391666666666666,27,1.375,38,0.91666666666666663,17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,10,"09:00:00",7,2.2083333333333335,37.04,0.95666666666666667,28,1.3333333333333333,45,0.625,15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,10,"16:00:00",27,1.375,41,0.79166666666666663,43,0.70833333333333337,36,1,21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,10,"18:00:00",25,1.4583333333333333,37.04,0.95666666666666667,40,0.83333333333333337,28,1.3333333333333333,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,11,"06:00:00",-8,2.8333333333333335,24.08,1.4966666666666668,26,1.4166666666666667,12.289899999999999,1.9879208333333331,12.2,1.9916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,11,"11:00:00",30,1.25,37.04,0.95666666666666667,34,1.0833333333333333,18,1.75,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,11,"20:00:00",20,1.6666666666666667,30.92,1.2116666666666667,33,1.125,18,1.75,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,12,"04:00:00",4,2.3333333333333335,21.92,1.5866666666666667,16.050999999999998,1.8312083333333333,10,2.0833333333333335,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,12,"10:00:00",27,1.375,33.08,1.1216666666666668,23,1.5416666666666667,16,1.8333333333333333,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,12,"21:00:00",23,1.5416666666666667,28.04,1.3316666666666668,16,1.8333333333333333,8,2.1666666666666665,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,13,"03:00:00",14,1.9166666666666667,30.92,1.2116666666666667,15,1.875,-2,2.5833333333333335,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,13,"06:00:00",10,2.0833333333333335,24.98,1.4591666666666665,11,2.0416666666666665,-5.3857699999999999,2.7244070833333329,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,13,"17:00:00",50,0.41666666666666669,39.92,0.83666666666666656,15,1.875,23,1.5416666666666667,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,13,"23:00:00",25,1.4583333333333333,32,1.1666666666666667,10,2.0833333333333335,31,1.2083333333333333,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,14,"07:00:00",27,1.375,28.04,1.3316666666666668,1,2.4583333333333335,36,1,10.4,2.0666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,14,"16:00:00",53,0.29166666666666669,26.06,1.4141666666666666,25,1.4583333333333333,36,1,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,14,"21:00:00",46,0.58333333333333337,19.940000000000001,1.6691666666666667,18,1.75,36,1,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,15,"09:00:00",43,0.70833333333333337,33.08,1.1216666666666668,36,1,37,0.95833333333333337,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,15,"14:00:00",46,0.58333333333333337,50,0.41666666666666669,43,0.70833333333333337,46,0.58333333333333337,30.38,1.2341666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,15,"18:00:00",39,0.875,46.94,0.5441666666666668,37,0.95833333333333337,41,0.79166666666666663,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,16,"04:00:00",23,1.5416666666666667,32,1.1666666666666667,9,2.125,19,1.7083333333333333,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,16,"11:00:00",23,1.5416666666666667,41,0.79166666666666663,25,1.4583333333333333,36,1,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,16,"18:00:00",25,1.4583333333333333,28.94,{"$f":"IF(Y1798<60,(60-Y1798)/24,0)","v":1.2941666666666667},26,{"$f":"IF(AA1798<60,(60-AA1798)/24,0)","v":1.4166666666666667},37,{"$f":"IF(AC1798<60,(60-AC1798)/24,0)","v":0.95833333333333337},37.4,{"$f":"IF(AE1798<60,(60-AE1798)/24,0)","v":0.94166666666666676}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,17,"04:00:00",19,1.7083333333333333,17.059999999999999,1.7891666666666666,28,1.3333333333333333,25.162400000000002,1.4515666666666664,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,17,"13:00:00",35,1.0416666666666667,33.979999999999997,1.0841666666666667,50,0.41666666666666669,39,0.875,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,17,"17:00:00",38,0.91666666666666663,33.979999999999997,1.0841666666666667,56,0.16666666666666666,41,0.79166666666666663,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,18,"06:00:00",13,1.9583333333333333,17.96,1.7516666666666667,29,1.2916666666666667,28.001899999999999,1.3332541666666666,29.3,1.2791666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,18,"07:00:00",17,1.7916666666666667,19.04,1.7066666666666668,28,1.3333333333333333,28.001899999999999,1.3332541666666666,30.38,1.2341666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,18,"15:00:00",46,0.58333333333333337,33.08,1.1216666666666668,43,0.70833333333333337,37,0.95833333333333337,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,19,"04:00:00",16,1.8333333333333333,8.9600000000000009,2.1266666666666665,23,1.5416666666666667,28,1.3333333333333333,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,19,"08:00:00",24,1.5,19.940000000000001,1.6691666666666667,27,1.375,29,1.2916666666666667,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,19,"14:00:00",51,0.375,33.979999999999997,1.0841666666666667,50,0.41666666666666669,33,1.125,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,20,"01:00:00",40,0.83333333333333337,24.08,1.4966666666666668,27,1.375,8,2.1666666666666665,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,20,"04:00:00",39,0.875,19.940000000000001,1.6691666666666667,25,1.4583333333333333,10,2.0833333333333335,21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,20,"18:00:00",33,1.125,30.02,1.2491666666666668,31.1968,1.2001333333333333,36,1,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,21,"01:00:00",33,1.125,28.94,1.2941666666666667,32,1.1666666666666667,25,1.4583333333333333,37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,21,"03:00:00",33,1.125,28.94,1.2941666666666667,31,1.2083333333333333,23,1.5416666666666667,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,21,"15:00:00",38,0.91666666666666663,37.94,0.9191666666666668,41,0.79166666666666663,46,0.58333333333333337,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,21,"20:00:00",32,1.1666666666666667,37.04,0.95666666666666667,33,1.125,34,1.0833333333333333,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,22,"01:00:00",31,{"$f":"IF(W1925<60,(60-W1925)/24,0)","v":1.2083333333333333},35.06,1.0391666666666666,35,1.0416666666666667,27.324100000000001,1.3614958333333333,40.1,0.82916666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,22,"13:00:00",37,0.95833333333333337,42.98,0.70916666666666683,33,1.125,48,0.5,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,22,"22:00:00",31,1.2083333333333333,26.96,1.3766666666666667,28,1.3333333333333333,36,1,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,23,"06:00:00",24,1.5,21.02,1.6241666666666668,16,1.8333333333333333,28,1.3333333333333333,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,23,"12:00:00",28,1.3333333333333333,44.06,0.66416666666666657,37,0.95833333333333337,36,1,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,23,"15:00:00",29,1.2916666666666667,46.94,0.5441666666666668,40,0.83333333333333337,39,0.875,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,24,"02:00:00",20,1.6666666666666667,24.98,1.4591666666666665,25,1.4583333333333333,34,1.0833333333333333,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,24,"08:00:00",21,1.625,32,1.1666666666666667,25,1.4583333333333333,32,1.1666666666666667,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,24,"16:00:00",34,1.0833333333333333,48.02,0.49916666666666654,54,0.25,43,0.70833333333333337,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,25,"01:00:00",29,1.2916666666666667,28.04,1.3316666666666668,34,1.0833333333333333,27,1.375,33.26,1.1141666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,25,"09:00:00",35,1.0416666666666667,35.06,1.0391666666666666,45,0.625,37,0.95833333333333337,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,25,"18:00:00",45,0.625,35.06,1.0391666666666666,46,0.58333333333333337,39,0.875,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,25,"23:00:00",37,0.95833333333333337,24.08,1.4966666666666668,38,0.91666666666666663,27,1.375,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,26,"03:00:00",37,0.95833333333333337,21.02,1.6241666666666668,36,1,19.146799999999999,1.7022166666666667,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,26,"13:00:00",45,0.625,51.08,0.37166666666666676,71,0,41,0.79166666666666663,62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,26,"20:00:00",32,1.1666666666666667,35.96,1.0016666666666667,45,0.625,28,1.3333333333333333,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,27,"03:00:00",19,1.7083333333333333,35.06,1.0391666666666666,32,1.1666666666666667,19.146799999999999,1.7022166666666667,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,27,"13:00:00",20,1.6666666666666667,37.94,0.9191666666666668,59,4.1666666666666664E-2,50,0.41666666666666669,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,27,"20:00:00",17,1.7916666666666667,39.92,0.83666666666666656,55,0.20833333333333334,39,0.875,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,28,"06:00:00",9,2.125,21.92,1.5866666666666667,48,0.5,34,1.0833333333333333,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,28,"07:00:00",13,1.9583333333333333,26.96,1.3766666666666667,48,0.5,34,1.0833333333333333,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,28,"16:00:00",36,1,55.94,0.16916666666666677,46,0.58333333333333337,37.049100000000003,0.95628749999999985,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,28,1,20,1.6666666666666667,44.06,0.66416666666666657,36,1,37.049100000000003,0.95628749999999985,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,29,"09:00:00",29,1.2916666666666667,53.96,0.25166666666666665,46,0.58333333333333337,39.075600000000001,0.8718499999999999,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,29,"17:00:00",46,0.58333333333333337,75.02,0,46,0.58333333333333337,45,0.625,60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,29,"23:00:00",32,1.1666666666666667,64.94,0,42,0.75,30,1.25,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,30,"10:00:00",33,1.125,68,0,51,0.375,46,0.58333333333333337,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,30,"13:00:00",37,0.95833333333333337,69.98,0,56,0.16666666666666666,55,0.20833333333333334,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,30,"19:00:00",31,1.2083333333333333,55.94,0.16916666666666677,48,0.5,37,0.95833333333333337,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,31,"03:00:00",26,1.4166666666666667,53.06,0.28916666666666657,40,0.83333333333333337,30,1.25,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,31,"12:00:00",41,0.79166666666666663,60.98,0,36,1,54,0.25,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,31,"20:00:00",29,1.2916666666666667,50,0.41666666666666669,24,1.5,48,0.5,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,1,"05:00:00",36.0077,0.99967916666666667,32,1.1666666666666667,27,1.375,37,0.95833333333333337,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,1,"10:00:00",41,0.79166666666666663,33.979999999999997,1.0841666666666667,48,0.5,41,0.79166666666666663,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,1,"22:00:00",43,0.70833333333333337,33.979999999999997,1.0841666666666667,37,0.95833333333333337,36,1,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,1,1,39,0.875,33.979999999999997,1.0841666666666667,36,1,37,0.95833333333333337,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,2,"07:00:00",36,1,32,1.1666666666666667,39,0.875,37.049100000000003,0.95628749999999985,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,2,"21:00:00",34.277200000000001,1.0717833333333333,37.94,0.9191666666666668,54,0.25,50,0.41666666666666669,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,2,1,34.191699999999997,1.0753458333333334,35.06,1.0391666666666666,48,0.5,52,0.33333333333333331,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,3,"07:00:00",34.191699999999997,1.0753458333333334,30.92,1.2116666666666667,50,0.41666666666666669,48,0.5,37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,3,"17:00:00",43,0.70833333333333337,37.04,0.95666666666666667,50,0.41666666666666669,46,0.58333333333333337,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,3,"21:00:00",36.188299999999998,0.99215416666666678,33.979999999999997,1.0841666666666667,48,0.5,39,0.875,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,4,"10:00:00",43,0.70833333333333337,42.98,{"$f":"IF(Y2246<60,(60-Y2246)/24,0)","v":0.70916666666666683},52,{"$f":"IF(AA2246<60,(60-AA2246)/24,0)","v":0.33333333333333331},39,{"$f":"IF(AC2246<60,(60-AC2246)/24,0)","v":0.875},28.4,{"$f":"IF(AE2246<60,(60-AE2246)/24,0)","v":1.3166666666666667}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,4,"18:00:00",39,0.875,44.96,0.62666666666666659,55,0.20833333333333334,45,0.625,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,4,"19:00:00",37.037500000000001,0.95677083333333324,37.94,0.9191666666666668,54,0.25,43,0.70833333333333337,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,5,"08:00:00",21,1.625,39.92,0.83666666666666656,37,0.95833333333333337,43,0.70833333333333337,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,5,"12:00:00",23,1.5416666666666667,42.98,0.70916666666666683,39,0.875,54,0.25,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,5,"18:00:00",21,1.625,39.020000000000003,0.87416666666666654,37,0.95833333333333337,54,0.25,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,6,"05:00:00",21,1.625,37.94,0.9191666666666668,32,1.1666666666666667,36,1,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,6,"15:00:00",28,1.3333333333333333,51.98,0.33416666666666678,48,0.5,66,0,37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,6,"22:00:00",34,1.0833333333333333,53.96,0.25166666666666665,39,0.875,41,0.79166666666666663,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,7,"05:00:00",22,1.5833333333333333,44.96,0.62666666666666659,46,0.58333333333333337,39,0.875,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,7,"07:00:00",27,1.375,44.06,0.66416666666666657,46,0.58333333333333337,43,0.70833333333333337,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,7,"19:00:00",39,0.875,48.02,0.49916666666666654,52,0.33333333333333331,52,0.33333333333333331,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,7,1,21,1.625,35.96,1.0016666666666667,46,0.58333333333333337,46,0.58333333333333337,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,8,"09:00:00",41,0.79166666666666663,42.08,0.7466666666666667,48,0.5,46,0.58333333333333337,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,8,"18:00:00",46,0.58333333333333337,46.94,0.5441666666666668,66,0,54,0.25,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,9,"02:00:00",28,1.3333333333333333,33.08,1.1216666666666668,54,0.25,28,1.3333333333333333,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,9,"08:00:00",41,0.79166666666666663,35.06,1.0391666666666666,37.133800000000001,0.95275833333333326,37,0.95833333333333337,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,9,"19:00:00",37,0.95833333333333337,32,1.1666666666666667,32,1.1666666666666667,43,0.70833333333333337,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,10,"01:00:00",27,1.375,26.06,1.4141666666666666,34,1.0833333333333333,28,1.3333333333333333,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,10,"04:00:00",32,1.1666666666666667,23,1.5416666666666667,34,1.0833333333333333,27,1.375,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,10,"15:00:00",37,0.95833333333333337,42.98,0.70916666666666683,45,0.625,66,0,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,10,"21:00:00",30,1.25,37.04,0.95666666666666667,34,1.0833333333333333,46,0.58333333333333337,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,11,"05:00:00",19,1.7083333333333333,39.020000000000003,0.87416666666666654,27,1.375,27,1.375,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,11,"14:00:00",43,0.70833333333333337,59,4.1666666666666664E-2,45,0.625,48,0.5,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,11,"19:00:00",36,1,44.96,0.62666666666666659,37,0.95833333333333337,39,0.875,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,12,"07:00:00",27,1.375,32,1.1666666666666667,37.133800000000001,0.95275833333333326,36,1,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,12,"12:00:00",46,0.58333333333333337,46.04,0.58166666666666667,37,0.95833333333333337,46,0.58333333333333337,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,12,"16:00:00",52,0.33333333333333331,51.08,0.37166666666666676,39,0.875,46,0.58333333333333337,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,13,"02:00:00",39,0.875,21.92,1.5866666666666667,27,1.375,36,1,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,13,"09:00:00",34,1.0833333333333333,44.06,0.66416666666666657,37,0.95833333333333337,39,0.875,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,13,"16:00:00",39,0.875,48.92,0.46166666666666661,46,0.58333333333333337,54,0.25,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,14,"02:00:00",46,0.58333333333333337,37.94,0.9191666666666668,28,1.3333333333333333,36,1,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,14,"06:00:00",45,0.625,37.04,0.95666666666666667,25,1.4583333333333333,28,1.3333333333333333,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,14,"19:00:00",39,0.875,41,0.79166666666666663,52,0.33333333333333331,46,0.58333333333333337,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,14,"20:00:00",39,0.875,41,0.79166666666666663,50,0.41666666666666669,43,0.70833333333333337,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,15,"04:00:00",36,1,41,0.79166666666666663,34,1.0833333333333333,21,1.625,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,15,"13:00:00",46,0.58333333333333337,66.02,0,75,0,57,0.125,80.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,15,"21:00:00",34,1.0833333333333333,59,4.1666666666666664E-2,61,0,34,1.0833333333333333,71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,16,"03:00:00",25,1.4583333333333333,53.06,0.28916666666666657,52,0.33333333333333331,25,1.4583333333333333,64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,16,"14:00:00",52,0.33333333333333331,73.040000000000006,0,72,0,66,0,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,16,"17:00:00",52,0.33333333333333331,73.040000000000006,0,54,0.25,68,0,50.36,0.40166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,17,"07:00:00",30,1.25,30.92,1.2116666666666667,37,0.95833333333333337,34,1.0833333333333333,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,17,"14:00:00",68,0,46.94,0.5441666666666668,52,0.33333333333333331,73,0,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,17,"16:00:00",57,0.125,46.04,0.58166666666666667,48,0.5,72,0,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,17,1,50,0.41666666666666669,32,1.1666666666666667,41,0.79166666666666663,37,0.95833333333333337,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,18,"09:00:00",52,0.33333333333333331,37.94,0.9191666666666668,37,0.95833333333333337,55,0.20833333333333334,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,18,"14:00:00",59,4.1666666666666664E-2,35.06,1.0391666666666666,45,0.625,68,0,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,19,"02:00:00",46,0.58333333333333337,37.04,0.95666666666666667,39,0.875,30,1.25,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,19,"11:00:00",72,0,51.08,0.37166666666666676,43,0.70833333333333337,70,0,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,19,"19:00:00",75,0,48.92,0.46166666666666661,45,0.625,63,0,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,19,"20:00:00",73,0,48.02,0.49916666666666654,45,0.625,55,0.20833333333333334,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,20,"10:00:00",41,0.79166666666666663,53.96,{"$f":"IF(Y2630<60,(60-Y2630)/24,0)","v":0.25166666666666665},52,{"$f":"IF(AA2630<60,(60-AA2630)/24,0)","v":0.33333333333333331},75,{"$f":"IF(AC2630<60,(60-AC2630)/24,0)","v":0},53.6,{"$f":"IF(AE2630<60,(60-AE2630)/24,0)","v":0.26666666666666661}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,20,"13:00:00",46,0.58333333333333337,60.98,0,57,0.125,81,0,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,20,1,27,1.375,42.98,0.70916666666666683,50,0.41666666666666669,45,0.625,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,21,"06:00:00",28,1.3333333333333333,42.98,0.70916666666666683,46,0.58333333333333337,37,0.95833333333333337,37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,21,"14:00:00",50,0.41666666666666669,69.98,0,43,0.70833333333333337,54,0.25,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,21,"23:00:00",46,0.58333333333333337,48.92,0.46166666666666661,39,0.875,30,1.25,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,22,"07:00:00",46,0.58333333333333337,44.96,0.62666666666666659,41,0.79166666666666663,32,1.1666666666666667,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,22,"08:00:00",50,0.41666666666666669,50,0.41666666666666669,42,0.75,37,0.95833333333333337,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,22,"21:00:00",48,0.5,46.94,0.5441666666666668,41,0.79166666666666663,54,0.25,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,23,"01:00:00",45,{"$f":"IF(W2693<60,(60-W2693)/24,0)","v":0.625},39.020000000000003,0.87416666666666654,39,0.875,45,0.625,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,23,"11:00:00",46,0.58333333333333337,53.96,0.25166666666666665,45,0.625,45,0.625,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,23,"18:00:00",52,0.33333333333333331,50,0.41666666666666669,45,0.625,46,0.58333333333333337,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,24,"01:00:00",34,1.0833333333333333,35.06,1.0391666666666666,41,0.79166666666666663,50,0.41666666666666669,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,24,"11:00:00",46,0.58333333333333337,48.92,0.46166666666666661,46,0.58333333333333337,57,0.125,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,24,"18:00:00",43,0.70833333333333337,55.94,0.16916666666666677,46,0.58333333333333337,61,0,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,24,"20:00:00",37,0.95833333333333337,48.02,0.49916666666666654,46,0.58333333333333337,54,0.25,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,25,"08:00:00",30,1.25,48.92,0.46166666666666661,41,0.79166666666666663,43,0.70833333333333337,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,25,"13:00:00",46,0.58333333333333337,71.06,0,55,0.20833333333333334,46,0.58333333333333337,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,25,"22:00:00",37,0.95833333333333337,64.94,0,39,0.875,43,0.70833333333333337,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,26,"06:00:00",37.054099999999998,0.9560791666666667,60.08,0,39,0.875,37,0.95833333333333337,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,26,"12:00:00",45,0.625,73.040000000000006,0,36,1,63,0,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,26,"23:00:00",41,0.79166666666666663,55.94,0.16916666666666677,34,1.0833333333333333,55,0.20833333333333334,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,27,"05:00:00",41.1663,0.78473749999999998,51.98,0.33416666666666678,34,1.0833333333333333,52,0.33333333333333331,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,27,"08:00:00",45,0.625,53.96,0.25166666666666665,36,1,50,0.41666666666666669,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,27,"19:00:00",46,0.58333333333333337,53.96,0.25166666666666665,45,0.625,48,0.5,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,28,"01:00:00",36,1,37.04,0.95666666666666667,43,0.70833333333333337,46,0.58333333333333337,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,28,"09:00:00",37,{"$f":"IF(W2821<60,(60-W2821)/24,0)","v":0.95833333333333337},55.94,0.16916666666666677,43,0.70833333333333337,48,0.5,64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,28,"18:00:00",43,0.70833333333333337,51.98,0.33416666666666678,52,0.33333333333333331,52,0.33333333333333331,77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,28,"23:00:00",23,1.5416666666666667,48.92,0.46166666666666661,36,1,39,0.875,64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,29,"11:00:00",61,0,57.92,8.66666666666666E-2,61,0,54,0.25,77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,29,"16:00:00",73,0,64.040000000000006,0,66,0,59,4.1666666666666664E-2,75.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,29,"20:00:00",57,0.125,55.94,0.16916666666666677,54,0.25,45,0.625,62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,30,"06:00:00",46,0.58333333333333337,37.04,0.95666666666666667,45,0.625,39,0.875,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,30,"13:00:00",79,0,80.06,0,55,0.20833333333333334,48,0.5,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,30,"22:00:00",46,0.58333333333333337,67.64,0,36,1,49,0.45833333333333331,45.14,0.61916666666666664]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,1,"05:00:00",37.301699999999997,0.94576250000000017,51.98,0.33416666666666678,30,1.25,52,0.33333333333333331,37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,1,"15:00:00",45,0.625,80.959999999999994,0,52,0.33333333333333331,57,0.125,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,1,"19:00:00",39,0.875,75.02,0,46,0.58333333333333337,61,0,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,2,"08:00:00",30,1.25,66.92,0,41,0.79166666666666663,45,0.625,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,2,"09:00:00",36,1,71.599999999999994,0,43,0.70833333333333337,45,0.625,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,2,"17:00:00",37.213900000000002,0.94942083333333327,68,0,46,0.58333333333333337,59,4.1666666666666664E-2,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,3,"06:00:00",41,0.79166666666666663,64.040000000000006,0,45,0.625,37,0.95833333333333337,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,3,"10:00:00",43,0.70833333333333337,66.92,0,46,0.58333333333333337,42,0.75,51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,3,"16:00:00",37.301699999999997,0.94576250000000017,57.02,0.12416666666666654,48,0.5,43,0.70833333333333337,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,4,"03:00:00",39,0.875,42.08,0.7466666666666667,34,1.0833333333333333,43,0.70833333333333337,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,4,"06:00:00",37,0.95833333333333337,39.92,0.83666666666666656,32,1.1666666666666667,45,0.625,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,4,"20:00:00",43,0.70833333333333337,46.04,0.58166666666666667,48,0.5,44,0.66666666666666663,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,5,"03:00:00",27,1.375,30.02,1.2491666666666668,34.380299999999998,1.0674875000000001,32,1.1666666666666667,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,5,"05:00:00",25,1.4583333333333333,30.02,1.2491666666666668,34,1.0833333333333333,30,1.25,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,5,"17:00:00",66,0,53.96,0.25166666666666665,72,0,63,0,64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,5,"22:00:00",36,1,50,0.41666666666666669,46,0.58333333333333337,46,0.58333333333333337,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,6,"03:00:00",28,1.3333333333333333,42.8,0.71666666666666679,37.133800000000001,0.95275833333333326,45,0.625,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,6,"15:00:00",73,0,69.98,0,79,0,55,0.20833333333333334,77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,6,1,50,0.41666666666666669,62.06,0,59,4.1666666666666664E-2,40,0.83333333333333337,62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,7,"08:00:00",57,0.125,69.98,0,59,4.1666666666666664E-2,37,0.95833333333333337,57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,7,"14:00:00",70,0,78.08,0,73,0,46,0.58333333333333337,75.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,7,"17:00:00",70,0,69.98,0,73,0,46,0.58333333333333337,75.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,8,"04:00:00",41,0.79166666666666663,37.94,0.9191666666666668,50,0.41666666666666669,39,0.875,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,8,"10:00:00",46,0.58333333333333337,51.98,0.33416666666666678,55,0.20833333333333334,48,0.5,60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,8,"18:00:00",54,0.25,55.94,0.16916666666666677,63,0,61,0,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,9,"03:00:00",36,1,50,0.41666666666666669,52,0.33333333333333331,35,1.0416666666666667,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,9,"11:00:00",54,0.25,53.96,0.25166666666666665,50,0.41666666666666669,43,0.70833333333333337,51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,9,"20:00:00",46,0.58333333333333337,57.92,8.66666666666666E-2,52,0.33333333333333331,43,0.70833333333333337,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,10,"01:00:00",46.143500000000003,0.5773541666666665,46.94,0.5441666666666668,48,0.5,40,0.83333333333333337,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,10,"05:00:00",45,0.625,42.08,0.7466666666666667,48,0.5,41,0.79166666666666663,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,10,"15:00:00",66,0,62.96,0,72,0,46,0.58333333333333337,73.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,10,"22:00:00",46,0.58333333333333337,48.92,0.46166666666666661,55,0.20833333333333334,42,0.75,57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,11,"05:00:00",36,1,48.92,0.46166666666666661,45,0.625,37.302399999999999,0.94573333333333343,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,11,"15:00:00",54,0.25,84.02,0,63,0,64,0,64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,11,1,30,1.25,57.02,0.12416666666666654,45,0.625,51,0.375,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,12,"04:00:00",34,1.0833333333333333,48.02,0.49916666666666654,40,0.83333333333333337,50,0.41666666666666669,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,12,"09:00:00",50,0.41666666666666669,71.959999999999994,0,44.104399999999998,0.66231666666666678,55,0.20833333333333334,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,12,"18:00:00",41,0.79166666666666663,84.02,0,45,0.625,63,0,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,13,"02:00:00",39.127099999999999,0.86970416666666672,57.02,0.12416666666666654,43,0.70833333333333337,46,0.58333333333333337,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,13,"11:00:00",39,0.875,66.92,0,46,0.58333333333333337,61,0,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,13,"19:00:00",32,1.1666666666666667,55.04,0.20666666666666669,42,0.75,55,0.20833333333333334,41.9,0.75416666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,14,"01:00:00",36,1,46.04,0.58166666666666667,43,0.70833333333333337,41.143000000000001,0.78570833333333334,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,14,"12:00:00",41,0.79166666666666663,68,0,54,0.25,63,0,51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,14,"15:00:00",45,0.625,78.98,0,55,0.20833333333333334,64,0,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,14,"21:00:00",37.125799999999998,0.95309166666666678,64.94,0,41,0.79166666666666663,50,0.41666666666666669,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,15,"05:00:00",34,1.0833333333333333,60.98,0,41,0.79166666666666663,43,0.70833333333333337,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,15,"14:00:00",41,0.79166666666666663,89.06,0,55,0.20833333333333334,66,0,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,15,"22:00:00",45,0.625,56.48,0.14666666666666681,52,0.33333333333333331,48,0.5,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,16,"07:00:00",45,0.625,52.7,0.30416666666666653,46,0.58333333333333337,46,0.58333333333333337,51.98,0.33416666666666678]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,16,"12:00:00",61,0,64.94,0,72,0,52,0.33333333333333331,66.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,16,1,61,0,53.96,0.25166666666666665,61,0,41.229300000000002,0.78211249999999988,66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,17,"02:00:00",55,0.20833333333333334,53.96,{"$f":"IF(Y3270<60,(60-Y3270)/24,0)","v":0.25166666666666665},61,{"$f":"IF(AA3270<60,(60-AA3270)/24,0)","v":0},43,{"$f":"IF(AC3270<60,(60-AC3270)/24,0)","v":0.70833333333333337},66.2,{"$f":"IF(AE3270<60,(60-AE3270)/24,0)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,17,"09:00:00",52,0.33333333333333331,60.98,0,57,0.125,46,0.58333333333333337,66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,17,"23:00:00",43,0.70833333333333337,55.94,0.16916666666666677,52,0.33333333333333331,47,0.54166666666666663,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,18,"02:00:00",36,1,57.92,8.66666666666666E-2,45,0.625,40.296100000000003,0.82099583333333326,51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,18,"09:00:00",34.277200000000001,1.0717833333333333,60.98,0,36,1,54,0.25,37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,18,"19:00:00",37,0.95833333333333337,71.959999999999994,0,40,0.83333333333333337,61,0,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,18,"23:00:00",32,1.1666666666666667,62.96,0,36,1,49,0.45833333333333331,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,19,"12:00:00",43,0.70833333333333337,68,0,42,0.75,50,0.41666666666666669,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,19,"20:00:00",37,0.95833333333333337,55.94,0.16916666666666677,36,1,48,0.5,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,19,"21:00:00",28,1.3333333333333333,51.08,0.37166666666666676,35,1.0416666666666667,48,0.5,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,20,"10:00:00",45,0.625,69.98,0,35,1.0416666666666667,61,0,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,20,"14:00:00",45,0.625,73.040000000000006,0,40,0.83333333333333337,61,0,57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,20,"20:00:00",39,0.875,64.94,0,37,0.95833333333333337,55,0.20833333333333334,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,21,"07:00:00",39,0.875,57.02,0.12416666666666654,35,1.0416666666666667,50,0.41666666666666669,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,21,"17:00:00",48,0.5,77,0,54,0.25,57,0.125,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,21,1,28,1.3333333333333333,55.94,0.16916666666666677,37.133800000000001,0.95275833333333326,40,0.83333333333333337,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,22,"07:00:00",39,0.875,48.92,0.46166666666666661,37.133800000000001,0.95275833333333326,43,0.70833333333333337,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,22,"09:00:00",52,{"$f":"IF(W3397<60,(60-W3397)/24,0)","v":0.33333333333333331},44.06,0.66416666666666657,50,0.41666666666666669,48,0.5,60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,22,"21:00:00",43,0.70833333333333337,48.02,0.49916666666666654,45,0.625,46,0.58333333333333337,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,23,"02:00:00",28.29,1.32125,46.4,0.56666666666666676,36,1,48,0.5,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,23,"11:00:00",66,0,75.2,0,61,0,55,0.20833333333333334,71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,23,"20:00:00",61,0,57.38,0.10916666666666656,55,0.20833333333333334,50,0.41666666666666669,62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,24,"04:00:00",37,0.95833333333333337,27.68,1.3466666666666667,43,0.70833333333333337,43,0.70833333333333337,51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,24,"10:00:00",70,0,53.96,0.25166666666666665,60,0,61,0,75.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,24,"21:00:00",52,0.33333333333333331,50,0.41666666666666669,62,0,54,0.25,68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,25,"03:00:00",36,1,48.38,0.48416666666666658,59,4.1666666666666664E-2,49,0.45833333333333331,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,25,"06:00:00",37,0.95833333333333337,48.92,0.46166666666666661,60,0,52,0.33333333333333331,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,25,"17:00:00",63,0,51.08,0.37166666666666676,77,0,64,0,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,25,"23:00:00",43,0.70833333333333337,46.94,0.5441666666666668,60,0,63,0,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,26,"07:00:00",46,0.58333333333333337,44.96,0.62666666666666659,56,0.16666666666666666,52,0.33333333333333331,51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,26,"16:00:00",70,0,50,0.41666666666666669,67,0,54,0.25,68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,26,"21:00:00",54,0.25,48.92,0.46166666666666661,57,0.125,50,0.41666666666666669,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,27,"09:00:00",61,0,53.06,0.28916666666666657,69,0,54,0.25,68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,27,"14:00:00",77,0,71.06,0,78,0,65,0,71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,27,"18:00:00",73,0,66.92,{"$f":"IF(Y3526<60,(60-Y3526)/24,0)","v":0},77,{"$f":"IF(AA3526<60,(60-AA3526)/24,0)","v":0},66,{"$f":"IF(AC3526<60,(60-AC3526)/24,0)","v":0},60.8,{"$f":"IF(AE3526<60,(60-AE3526)/24,0)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,28,"04:00:00",43,0.70833333333333337,48.92,0.46166666666666661,61,0,39,0.875,57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,28,"11:00:00",72,0,55.04,0.20666666666666669,70,0,72,0,66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,28,"18:00:00",70,0,55.4,0.19166666666666674,68,0,75,0,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,29,"04:00:00",46.038600000000002,0.58172499999999994,44.06,0.66416666666666657,59,4.1666666666666664E-2,42,0.75,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,29,"08:00:00",66,0,48.92,0.46166666666666661,64,0,59,4.1666666666666664E-2,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,29,"21:00:00",59,4.1666666666666664E-2,44.96,0.62666666666666659,64,0,68,0,60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,29,"22:00:00",57,0.125,44.06,0.66416666666666657,64,0,65,0,60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,30,"06:00:00",61,0,46.94,0.5441666666666668,61,0,54,0.25,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,30,"15:00:00",70,0,68,0,81,0,63,0,82.4,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,30,"23:00:00",57,0.125,42.08,0.7466666666666667,64,0,58,8.3333333333333329E-2,69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,31,"05:00:00",54,0.25,37.04,0.95666666666666667,63,0,54,0.25,64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,31,"16:00:00",61,0,66.92,0,63,0,70,0,78.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,31,"19:00:00",64,0,59,4.1666666666666664E-2,63,0,64,0,64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,1,"09:00:00",55,0.20833333333333334,73.040000000000006,0,73,0,73,0,64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,1,"16:00:00",57,0.125,86,0,73,0,82,0,64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,1,"18:00:00",54,0.25,82.94,0,64,0,77,0,60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,2,"02:00:00",30,1.25,66.02,{"$f":"IF(Y3654<60,(60-Y3654)/24,0)","v":0},55,{"$f":"IF(AA3654<60,(60-AA3654)/24,0)","v":0.20833333333333334},64,{"$f":"IF(AC3654<60,(60-AC3654)/24,0)","v":0},55.4,{"$f":"IF(AE3654<60,(60-AE3654)/24,0)","v":0.19166666666666674}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,2,"11:00:00",64,0,66.92,0,75,0,75,0,57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,2,"16:00:00",64,0,59,4.1666666666666664E-2,76,0,82,0,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,3,"04:00:00",54,0.25,53.06,0.28916666666666657,64,0,70,0,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,3,"13:00:00",48,0.5,68,0,72,0,70,0,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,3,"15:00:00",48,0.5,69.98,0,78,0,75,0,57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,3,"22:00:00",38.2042,0.90815833333333329,53.96,0.25166666666666665,64,0,63,0,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,4,"12:00:00",52,0.33333333333333331,57.02,0.12416666666666654,68,0,72,0,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,4,"15:00:00",52,0.33333333333333331,57.92,8.66666666666666E-2,69,0,72,0,60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,5,"02:00:00",45,0.625,55.04,0.20666666666666669,45,0.625,43.011000000000003,0.70787499999999992,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,5,"08:00:00",45,0.625,57.92,8.66666666666666E-2,58,8.3333333333333329E-2,54,0.25,57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,5,"16:00:00",54,0.25,75.92,0,77,0,77,0,62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,6,"01:00:00",46,0.58333333333333337,53.96,0.25166666666666665,57,0.125,61,0,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,6,"09:00:00",48,0.5,60.98,0,68,0,66,0,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,6,"10:00:00",48,0.5,64.040000000000006,0,72,0,70,0,60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,6,"23:00:00",48,0.5,42.08,0.7466666666666667,67,0,64,0,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,7,"03:00:00",46.143500000000003,0.5773541666666665,35.96,1.0016666666666667,62,0,63.037300000000002,0,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,7,"13:00:00",55,0.20833333333333334,69.98,0,93,0,93,0,64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,7,"20:00:00",52,0.33333333333333331,60.08,0,74,0,81,0,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,8,"03:00:00",50,0.41666666666666669,53.96,0.25166666666666665,48,0.5,75,0,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,8,"13:00:00",54,0.25,68,0,72,0,84,0,64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,8,"20:00:00",52,0.33333333333333331,64.94,0,64,0,66,0,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,8,"22:00:00",48,0.5,64.94,0,60,0,64,0,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,9,"10:00:00",59,4.1666666666666664E-2,69.08,0,52,0.33333333333333331,57,0.125,71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,9,"15:00:00",73,0,69.98,0,55,0.20833333333333334,61,0,80.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,9,1,48,0.5,57.02,0.12416666666666654,55,0.20833333333333334,55,0.20833333333333334,62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,10,"08:00:00",61,0,60.08,0,64,0,59,4.1666666666666664E-2,75.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,10,"14:00:00",77,0,69.98,0,86,0,72,0,87.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,11,"01:00:00",46.038600000000002,0.58172499999999994,44.96,0.62666666666666659,58,8.3333333333333329E-2,48,0.5,69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,11,"07:00:00",52,0.33333333333333331,57.02,0.12416666666666654,62,0,54,0.25,71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,11,"10:00:00",73,0,71.959999999999994,0,77,0,68,0,82.4,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,11,"21:00:00",54,0.25,62.96,0,69,0,55,0.20833333333333334,77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,12,"03:00:00",39,0.875,57.02,0.12416666666666654,58,8.3333333333333329E-2,46,0.58333333333333337,62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,12,"11:00:00",64,0,60.08,0,81,0,77,0,73.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,12,"20:00:00",55,0.20833333333333334,66.02,0,70,0,64,0,64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,13,"01:00:00",57,0.125,60.08,0,63,0,54,0.25,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,13,"13:00:00",63,0,82.94,0,82,0,82,0,73.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,13,"18:00:00",63,0,75.92,0,80,0,79,0,71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,13,"22:00:00",61,0,64.94,0,61,0,64,0,66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,14,"07:00:00",61,0,66.02,0,59,4.1666666666666664E-2,70,0,68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,14,"14:00:00",63,0,82.04,0,73,0,77,0,77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,14,1,59,4.1666666666666664E-2,66.02,0,45,0.625,68,0,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,15,"07:00:00",61,0,75.92,0,52,0.33333333333333331,63,0,57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,15,"17:00:00",64,0,82.94,0,73,0,72,0,69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,15,"21:00:00",63,0,62.96,0,64,0,57,0.125,60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,16,"10:00:00",61,0,77,0,69,0,61,0,69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,16,"11:00:00",61,0,78.98,0,72,0,64,0,68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,16,"19:00:00",63,0,64.94,0,69,0,59,4.1666666666666664E-2,60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,17,"08:00:00",61,0,62.96,0,61,0,55,0.20833333333333334,64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,17,"12:00:00",70,0,73.040000000000006,0,72,0,72,0,69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,17,"18:00:00",70,0,73.94,0,77,0,61,0,69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,18,"05:00:00",61,0,46.04,0.58166666666666667,62,0,55,0.20833333333333334,60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,18,"08:00:00",64,0,66.02,0,69,0,55,0.20833333333333334,60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,18,"22:00:00",63.005299999999998,0,60.08,0,61,0,50,0.41666666666666669,57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,19,"05:00:00",63,0,51.98,0.33416666666666678,60,0,46,0.58333333333333337,57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,19,"07:00:00",64,0,62.96,0,69,0,48,0.5,57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,19,"19:00:00",72,0,82.04,0,72,0,63,0,77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,19,1,59,4.1666666666666664E-2,64.94,0,62,0,52.005600000000001,0.33309999999999995,62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,20,"05:00:00",61,0,59,4.1666666666666664E-2,65,0,52.005600000000001,0.33309999999999995,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,20,"17:00:00",72,{"$f":"IF(W4101<60,(60-W4101)/24,0)","v":0},82.04,0,77,0,73,0,71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,21,"02:00:00",59.0351,4.0204166666666673E-2,48.92,0.46166666666666661,62,0,54,0.25,62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,21,"10:00:00",73,0,73.94,0,76,0,66,0,82.4,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,21,"16:00:00",81,0,80.06,0,91,0,73,0,89.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,21,"19:00:00",72,0,75.92,0,89,0,63,0,84.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,22,"06:00:00",63,0,66.02,0,71,0,55,0.20833333333333334,75.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,22,"12:00:00",81,0,69.98,0,86,0,82,0,89.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,22,"20:00:00",70,0,66.02,0,75,0,66,0,78.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,23,"05:00:00",63,0,62.06,0,52,0.33333333333333331,54,0.25,64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,23,"13:00:00",81,0,60.98,0,78,0,86,0,78.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,23,"22:00:00",64,0,53.06,0.28916666666666657,61,0,63,0,66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,24,"03:00:00",63,0,48.92,0.46166666666666661,52.050600000000003,0.33122499999999988,57.023299999999999,0.1240291666666667,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,24,"07:00:00",68,0,55.04,0.20666666666666669,52.050600000000003,0.33122499999999988,64,0,66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,24,"17:00:00",75,0,86,0,72,0,84,0,78.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,24,1,63,0,64.040000000000006,0,57,0.125,57,0.125,62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,25,"07:00:00",63,0,60.08,0,62,0,64,0,64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,25,"17:00:00",79,0,60.98,0,82,0,73,0,78.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,26,"02:00:00",63,0,53.06,{"$f":"IF(Y4230<60,(60-Y4230)/24,0)","v":0.28916666666666657},67,{"$f":"IF(AA4230<60,(60-AA4230)/24,0)","v":0},55,{"$f":"IF(AC4230<60,(60-AC4230)/24,0)","v":0.20833333333333334},77,{"$f":"IF(AE4230<60,(60-AE4230)/24,0)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,26,"06:00:00",64,0,53.96,0.25166666666666665,67,0,59.016800000000003,4.0966666666666519E-2,77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,26,"11:00:00",73,0,57.92,8.66666666666666E-2,79,0,84,0,77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,26,"20:00:00",66,0,57.92,8.66666666666666E-2,69,0,70,0,71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,27,"04:00:00",64.077799999999996,0,59,4.1666666666666664E-2,50.082700000000003,0.4132208333333332,55,0.20833333333333334,66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,27,"13:00:00",64,0,62.06,0,77,0,91,0,80.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,27,"21:00:00",57,0.125,60.08,0,59,4.1666666666666664E-2,70,0,66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,28,"03:00:00",48.149099999999997,0.4937875000000001,60.08,0,58,8.3333333333333329E-2,75,0,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,28,"14:00:00",70,0,71.959999999999994,0,79,0,81,0,84.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,28,"17:00:00",72,{"$f":"IF(W4293<60,(60-W4293)/24,0)","v":0},73.040000000000006,0,85,0,77,0,82.4,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,28,"23:00:00",51,0.375,60.98,0,72,0,73,0,69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,29,"07:00:00",48.057000000000002,0.49762499999999993,64.94,0,76,0,73,0,73.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,29,"16:00:00",79,0,82.94,0,73,0,75,0,89.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,29,1,63,0,66.92,0,76,0,68,0,69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,30,"09:00:00",73,0,71.959999999999994,0,79,0,70,0,82.4,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,30,"14:00:00",68,0,84.02,0,88,0,79,0,87.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,1,"02:00:00",49,0.45833333333333331,62.42,0,61,0,60,0,57.92,8.66666666666666E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,1,"04:00:00",43,0.70833333333333337,57.92,8.66666666666666E-2,57,0.125,57.023299999999999,0.1240291666666667,51.08,0.37166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,1,"11:00:00",75,0,68,0,69,0,81,0,71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,2,"01:00:00",56,0.16666666666666666,59,4.1666666666666664E-2,74,0,66,0,55.94,0.16916666666666677]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,2,"04:00:00",50,0.41666666666666669,53.06,0.28916666666666657,75,0,58,8.3333333333333329E-2,53.96,0.25166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,2,"11:00:00",72,0,73.040000000000006,0,85,0,81,0,77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,2,"21:00:00",63,0,60.98,0,72,0,68,0,69.08,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,3,"01:00:00",52,0.33333333333333331,53.96,0.25166666666666665,69,0,62,0,68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,3,"14:00:00",73,0,82.94,0,78,0,75,0,73.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,3,"22:00:00",52,0.33333333333333331,73.94,0,58.0854,7.9774999999999999E-2,51,0.375,62.06,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,3,"23:00:00",50,0.41666666666666669,73.94,0,56,0.16666666666666666,52,0.33333333333333331,60.08,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,4,"12:00:00",77,0,86,0,76,0,72,0,75.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,4,"16:00:00",81,0,89.06,0,78,0,69,0,73.040000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,4,"22:00:00",64,0,80.959999999999994,0,57,0.125,62,0,60.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,5,"09:00:00",68,0,77,0,73,0,66,0,64.040000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,5,"19:00:00",68,0,71.959999999999994,0,69,0,69,0,62.06,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,6,"02:00:00",64.070300000000003,0,50,0.41666666666666669,64,0,60.010399999999997,0,62.06,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,6,"09:00:00",64,0,68,0,76,0,75,0,66.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,6,"11:00:00",64,0,71.959999999999994,0,79,0,75,0,69.08,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,6,"20:00:00",55,0.20833333333333334,64.040000000000006,0,72,0,64,0,64.040000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,7,"08:00:00",54,0.25,64.040000000000006,0,63,0,60,0,68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,7,"13:00:00",77,0,73.040000000000006,0,72,0,73,0,71.06,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,7,"22:00:00",66,0,51.98,0.33416666666666678,64,0,68,0,66.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,8,"06:00:00",63,0,53.06,0.28916666666666657,61,0,66,0,66.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,8,"12:00:00",66,0,78.08,0,67,0,82,0,80.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,8,"23:00:00",62,0,69.08,0,68,0,72,0,69.08,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,9,"05:00:00",62,0,60.98,0,65,0,66,0,66.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,9,"08:00:00",70,0,66.92,0,67,0,72,0,68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,9,"19:00:00",66,0,80.959999999999994,0,64,0,69,0,71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,10,"01:00:00",55.068100000000001,0.20549583333333329,69.98,0,61,0,60,0,57.92,8.66666666666666E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,10,"09:00:00",64,0,78.08,0,74,0,68,0,71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,10,"18:00:00",63,0,80.06,0,76,0,70,0,78.08,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,10,"23:00:00",57,0.125,66.02,0,59,4.1666666666666664E-2,60,0,62.96,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,11,"11:00:00",73,0,68,0,69,0,79,0,78.08,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,11,"16:00:00",73,0,73.94,0,67,0,79,0,78.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,11,"20:00:00",61,0,66.02,0,58,8.3333333333333329E-2,68,0,69.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,12,"06:00:00",52,0.33333333333333331,55.94,0.16916666666666677,52,0.33333333333333331,55,0.20833333333333334,60.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,12,"13:00:00",75,0,64.94,0,83,0,81,0,78.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,12,"20:00:00",63,0,60.98,0,72,0,72,0,66.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,13,"06:00:00",57,0.125,59,4.1666666666666664E-2,66,0,63,0,62.96,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,13,"10:00:00",63,0,71.959999999999994,0,79,0,64,0,66.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,13,"23:00:00",63,0,59,4.1666666666666664E-2,66,0,61,0,62.96,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,13,1,63,0,55.04,0.20666666666666669,65.072199999999995,0,60,0,62.96,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,14,"08:00:00",66,0,64.94,0,71,0,73,0,68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,14,"17:00:00",75,{"$f":"IF(W4677<60,(60-W4677)/24,0)","v":0},80.06,0,90,0,77,0,78.08,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,15,"01:00:00",66,0,62.06,0,73,0,65,0,62.06,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,15,"07:00:00",67,0,73.94,0,72,0,68,0,68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,15,"18:00:00",66,0,86,0,90,0,75,0,82.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,15,"21:00:00",68,0,78.08,0,82,0,73,0,71.06,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,16,"11:00:00",75,0,89.06,0,86,0,79,0,84.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,16,"18:00:00",70,0,82.04,0,80,0,72,0,84.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,16,"20:00:00",61,0,75.02,0,69,0,66.000699999999995,0,75.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,17,"04:00:00",54,0.25,60.98,0,58.0854,7.9774999999999999E-2,65,0,64.040000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,17,"13:00:00",74,0,87.08,0,84,0,81,0,87.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,17,"22:00:00",59,4.1666666666666664E-2,71.06,0,66,0,65,0,75.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,18,"03:00:00",54,0.25,62.06,0,64,0,60,0,71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,18,"15:00:00",81,0,91.04,0,86,0,86,0,91.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,18,"17:00:00",79,0,91.04,0,81,0,87,0,89.96,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,18,1,57,0.125,71.959999999999994,0,62,0,64,0,75.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,19,"14:00:00",70,0,91.04,0,66,0,73,0,89.96,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,19,"17:00:00",70,0,87.98,0,63,0,72,0,86,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,20,"04:00:00",54,0.25,60.08,0,47,0.54166666666666663,61,0,71.06,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,20,"10:00:00",54,0.25,84.92,0,74,0,61,0,89.06,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,20,"18:00:00",54,0.25,73.040000000000006,0,61,0,65,0,91.04,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,21,"03:00:00",57,0.125,66.92,0,52,0.33333333333333331,61,0,75.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,21,"11:00:00",64,0,82.04,0,63,0,70,0,91.04,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,21,"12:00:00",66,0,84.92,0,63,0,73,0,91.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,22,"01:00:00",48,0.5,62.96,0,60,0,50,0.41666666666666669,69.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,22,"05:00:00",45.085900000000002,0.6214208333333332,60.08,0,57,0.125,46,0.58333333333333337,69.08,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,22,"15:00:00",79,0,84.02,0,79,0,82,0,75.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,22,"22:00:00",57,0.125,69.08,0,57,0.125,64,0,68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,23,"05:00:00",52,0.33333333333333331,66.02,0,57,0.125,55,0.20833333333333334,69.08,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,23,"15:00:00",73,0,84.02,0,75,0,72,0,91.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,23,"22:00:00",59,4.1666666666666664E-2,71.06,0,58,8.3333333333333329E-2,64,0,78.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,23,1,54,0.25,71.06,0,55,0.20833333333333334,62,0,75.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,24,"12:00:00",74,0,77,0,68,0,73,0,84.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,24,"17:00:00",79,0,73.94,0,65,0,81,0,84.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,25,"02:00:00",55.075400000000002,0.20519166666666658,66.92,0,55,0.20833333333333334,69,0,66.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,25,"10:00:00",72,0,75.02,{"$f":"IF(Y4934<60,(60-Y4934)/24,0)","v":0},70,{"$f":"IF(AA4934<60,(60-AA4934)/24,0)","v":0},72,{"$f":"IF(AC4934<60,(60-AC4934)/24,0)","v":0},75.92,{"$f":"IF(AE4934<60,(60-AE4934)/24,0)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,25,"16:00:00",70,0,82.94,0,79,0,74,0,78.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,26,"03:00:00",62,0,64.94,0,51,0.375,65,0,66.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,26,"09:00:00",69,0,75.92,0,67,0,68,0,69.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,26,"12:00:00",69,0,82.94,0,74,0,72,0,69.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,26,"23:00:00",61,0,68,0,69,0,68,0,62.96,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,27,"05:00:00",56,0.16666666666666666,62.96,0,67,0,63,0,62.96,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,27,"13:00:00",72,0,86,0,82,0,73,0,78.08,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,27,"22:00:00",63,0,68,0,74,0,63,0,66.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,28,"03:00:00",50,0.41666666666666669,64.94,0,71,0,56,0.16666666666666666,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,28,"15:00:00",72,0,80.959999999999994,0,79,0,81,0,78.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,28,"20:00:00",55,0.20833333333333334,73.040000000000006,0,71,0,64,0,66.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,28,1,46.219200000000001,0.57419999999999993,64.94,0,65,0,58,8.3333333333333329E-2,64.040000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,29,"09:00:00",62,0,69.98,0,68,0,66,0,71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,29,"16:00:00",73,0,84.02,0,75,0,79,0,75.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,30,"02:00:00",55,0.20833333333333334,62.96,0,60,0,66,0,62.06,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,30,"09:00:00",70,0,64.94,0,70,0,72,0,69.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,30,"19:00:00",64,0,75.92,0,70,0,70,0,66.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,30,"23:00:00",61,0,62.96,0,57,0.125,62,0,64.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,31,"12:00:00",64,0,80.959999999999994,0,81,0,64,0,75.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,31,"13:00:00",61,0,82.94,0,79,0,64,0,75.02,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,31,"21:00:00",57,0.125,71.06,0,66,0,63,0,71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,1,"10:00:00",75,0,66.02,0,79,0,70,0,80.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,1,"14:00:00",82,0,73.94,0,85,0,79,0,86.9,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,1,"20:00:00",70,0,66.02,0,70,0,61,0,75.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,2,"07:00:00",61,0,57.92,8.66666666666666E-2,65,0,52.005600000000001,0.33309999999999995,72.86,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,2,"10:00:00",75,0,69.98,{"$f":"IF(Y5126<60,(60-Y5126)/24,0)","v":0},76,{"$f":"IF(AA5126<60,(60-AA5126)/24,0)","v":0},72,{"$f":"IF(AC5126<60,(60-AC5126)/24,0)","v":0},82.94,{"$f":"IF(AE5126<60,(60-AE5126)/24,0)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,2,1,54,0.25,55.04,0.20666666666666669,64,0,54,0.25,70.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,3,"07:00:00",59,4.1666666666666664E-2,55.94,0.16916666666666677,61,0,57,0.125,69.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,3,"09:00:00",75,0,69.08,0,67,0,66,0,70.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,3,"21:00:00",63,0,64.94,0,66,0,63,0,71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,4,"02:00:00",61,0,55.04,0.20666666666666669,64,0,57,0.125,70.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,4,"07:00:00",63,0,60.08,0,66,0,61,0,71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,4,"19:00:00",63,0,75.92,0,68,0,73,0,80.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,5,"04:00:00",46.051699999999997,0.5811791666666668,55.04,0.20666666666666669,64,0,61.023099999999999,0,73.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,5,"12:00:00",71,0,84.02,0,83,0,81,0,69.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,5,"18:00:00",63,0,82.04,0,82,0,81,0,63.86,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,5,"21:00:00",50,0.41666666666666669,69.98,0,70,0,64,0,56.84,0.13166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,6,"08:00:00",52,0.33333333333333331,64.040000000000006,0,70,0,68,0,61.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,6,"14:00:00",64,0,84.92,0,88,0,79,0,71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,6,"22:00:00",48.057000000000002,0.49762499999999993,64.94,0,79,0,66,0,57.92,8.66666666666666E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,7,"07:00:00",52,0.33333333333333331,62.96,0,73,0,66,0,59.9,4.1666666666667256E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,7,"15:00:00",70,0,78.98,0,85,0,73,0,74.84,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,7,1,54,0.25,69.08,0,63,0,68,0,55.94,0.16916666666666677]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,8,"05:00:00",52.026699999999998,0.33222083333333341,68,0,60,0,66,0,52.88,0.29666666666666658]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,8,"09:00:00",59,4.1666666666666664E-2,69.08,0,71,0,70,0,70.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,8,"19:00:00",57,0.125,75.02,0,73,0,73,0,64.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,9,"02:00:00",55,0.20833333333333334,60.08,0,65.072199999999995,0,57,0.125,56.84,0.13166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,9,"11:00:00",72,0,82.94,0,70,0,81,0,79.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,9,"18:00:00",72,0,82.94,0,73,0,82,0,73.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,10,"04:00:00",46,0.58333333333333337,57.02,0.12416666666666654,72,0,64,0,68.900000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,10,"08:00:00",61,0,69.08,0,75,0,73,0,73.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,10,"13:00:00",81,0,86,0,82,0,82,0,77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,10,"22:00:00",63,0,69.08,0,73,0,75,0,62.96,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,11,"06:00:00",64,0,62.06,0,72,0,70,0,56.84,0.13166666666666652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,11,"15:00:00",79,0,84.02,0,79,0,82,0,71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,11,"23:00:00",64,0,71.06,0,69,0,68,0,62.96,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,12,"05:00:00",63,0,64.040000000000006,0,67,0,63.037300000000002,0,60.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,12,"16:00:00",72,0,77,0,69,0,73,0,72.86,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,12,"19:00:00",66,0,69.08,0,66,0,61,0,68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,13,"01:00:00",66,{"$f":"IF(W5381<60,(60-W5381)/24,0)","v":0},50,0.41666666666666669,60,0,48.157499999999999,0.49343750000000003,65.84,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,13,"09:00:00",70,0,69.08,0,63,0,55,0.20833333333333334,69.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,13,"18:00:00",70,0,80.06,0,70,0,68,0,73.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,14,"02:00:00",66,0,64.94,0,56,0.16666666666666666,54,0.25,69.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,14,"11:00:00",70,0,87.08,0,76,0,70,0,77.900000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,14,"16:00:00",72,0,89.96,0,80,0,80,0,75.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,15,"04:00:00",52.088999999999999,0.32962500000000006,62.96,0,67,0,61,0,59.9,4.1666666666667256E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,15,"06:00:00",54,0.25,64.94,0,66,0,64,0,60.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,15,"13:00:00",72,0,91.04,0,70,0,79,0,66.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,16,"03:00:00",57.0077,0.12467916666666667,71.06,0,61,0,65,0,55.94,0.16916666666666677]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,16,"06:00:00",59,4.1666666666666664E-2,69.08,0,58,8.3333333333333329E-2,67,0,55.94,0.16916666666666677]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,16,"13:00:00",70,0,71.959999999999994,0,78,0,82,0,74.84,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,16,"23:00:00",59,4.1666666666666664E-2,55.94,0.16916666666666677,64,0,66,0,61.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,17,"03:00:00",57,0.125,50,0.41666666666666669,61,0,64.010499999999993,0,61.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,17,"16:00:00",75,0,80.959999999999994,0,84,0,77,0,75.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,17,1,50,0.41666666666666669,55.94,0.16916666666666677,67,0,66.000699999999995,0,68.900000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,18,"01:00:00",48.149099999999997,0.4937875000000001,57.02,0.12416666666666654,66,0,68,0,68.900000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,18,"14:00:00",79,0,80.06,0,80,0,73,0,68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,18,"18:00:00",72,0,71.959999999999994,0,78,0,64,0,66.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,18,1,54,0.25,64.040000000000006,0,62,0,54,0.25,65.84,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,19,"11:00:00",73,0,64.94,0,75,0,64,0,70.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,19,"21:00:00",63,0,62.96,0,59,4.1666666666666664E-2,52,0.33333333333333331,65.84,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,20,"04:00:00",55.075400000000002,0.20519166666666658,60.98,0,48,0.5,43.011000000000003,0.70787499999999992,64.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,20,"11:00:00",64,0,73.040000000000006,0,78,0,70,0,77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,20,"13:00:00",72,0,78.08,0,83,0,75,0,77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,20,"22:00:00",61,0,60.08,0,67,0,59,4.1666666666666664E-2,69.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,21,"10:00:00",61,0,73.040000000000006,0,73,0,63,0,74.84,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,21,"15:00:00",61,0,78.98,0,89,0,72,0,81.86,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,21,1,48,0.5,57.02,0.12416666666666654,64,0,55,0.20833333333333334,65.84,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,22,"08:00:00",52,0.33333333333333331,62.96,0,81,0,55,0.20833333333333334,65.84,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,22,"14:00:00",70,0,71.959999999999994,0,86,0,77,0,60.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,23,"01:00:00",46,0.58333333333333337,46.94,0.5441666666666668,57.023299999999999,0.1240291666666667,63,0,57.92,8.66666666666666E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,23,"07:00:00",48.057000000000002,0.49762499999999993,53.06,0.28916666666666657,54,0.25,61,0,57.92,8.66666666666666E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,23,"10:00:00",72,0,69.98,0,72,0,68,0,64.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,23,"21:00:00",57,0.125,62.06,0,58.0854,7.9774999999999999E-2,64.029899999999998,0,55.94,0.16916666666666677]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,24,"03:00:00",45,0.625,50,0.41666666666666669,53,0.29166666666666669,64,0,50.9,0.37916666666666671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,24,"11:00:00",63,0,75.92,0,74,0,73,0,71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,24,"20:00:00",48,0.5,68,0,64,0,63,0,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,25,"01:00:00",43.000999999999998,0.70829166666666676,64.94,0,55,0.20833333333333334,61,0,53.96,0.25166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,25,"13:00:00",73,0,66.02,0,82,0,79,0,77.900000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,25,"18:00:00",70,0,64.040000000000006,0,75,0,72,0,75.92,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,25,"22:00:00",52.088999999999999,0.32962500000000006,64.040000000000006,0,61,0,68,0,68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,26,"08:00:00",54,0.25,62.96,0,69,0,66.000699999999995,0,71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,26,"15:00:00",79,0,64.040000000000006,0,84,0,84,0,78.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,26,"22:00:00",55,0.20833333333333334,62.96,0,66,0,63.037300000000002,0,69.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,27,"08:00:00",61,0,64.040000000000006,0,62,0,66,0,73.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,27,"12:00:00",77,0,77,0,80,0,79,0,79.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,28,"01:00:00",63,0,64.040000000000006,0,63,0,57,0.125,64.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,28,"02:00:00",64,0,62.06,0,64,0,57,0.125,64.94,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,28,"10:00:00",81,0,75.92,0,72,0,72,0,78.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,28,"19:00:00",70,0,73.040000000000006,0,68,0,68,0,77.900000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,29,"03:00:00",66,0,64.94,0,65,0,57,0.125,71.959999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,29,"09:00:00",73,0,66.02,0,70,0,63,0,70.88,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,29,"20:00:00",66,0,60.08,0,65,0,64.029899999999998,0,65.84,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,29,"23:00:00",66,0,55.94,0.16916666666666677,58,8.3333333333333329E-2,61,0,59.9,4.1666666666667256E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,30,"13:00:00",79,0,57.92,8.66666666666666E-2,70,0,79,0,72.86,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,30,"20:00:00",72,0,55.04,0.20666666666666669,57,0.125,59,4.1666666666666664E-2,60.98,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,30,"22:00:00",68,0,53.96,0.25166666666666665,57,0.125,55,0.20833333333333334,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,31,"06:00:00",66,0,51.98,0.33416666666666678,60,0,55,0.20833333333333334,57.02,0.12416666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,31,"15:00:00",70,0,57.02,0.12416666666666654,69,0,75,0,63.86,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,31,1,49,0.45833333333333331,51.62,0.34916666666666679,55,0.20833333333333334,51,0.375,65.3,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,1,"05:00:00",39.301299999999998,0.86244583333333347,48.02,0.49916666666666654,46,0.58333333333333337,46,0.58333333333333337,69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,1,"17:00:00",82,0,71.959999999999994,0,80,0,84,0,84.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,1,"19:00:00",64,0,60.08,0,68,0,64,0,78.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,2,"02:00:00",45,0.625,55.04,0.20666666666666669,52,0.33333333333333331,54,0.25,73.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,2,"16:00:00",84,0,71.959999999999994,0,88,0,88,0,62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,2,"19:00:00",64,0,62.96,0,72,0,72,0,60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,3,"06:00:00",46.038600000000002,0.58172499999999994,51.98,0.33416666666666678,54,0.25,54,0.25,60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,3,"12:00:00",84,0,68,0,85,0,84,0,66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,3,"20:00:00",61,0,66.92,0,68,0,64,0,64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,4,"05:00:00",50,0.41666666666666669,62.06,0,59,4.1666666666666664E-2,55,0.20833333333333334,64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,4,"13:00:00",90,0,84.02,0,88,0,90,0,69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,4,"14:00:00",90,0,84.92,0,88,0,90,0,66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,5,"03:00:00",52,0.33333333333333331,60.08,0,61,0,61,0,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,5,"07:00:00",55,0.20833333333333334,64.94,0,64,0,66,0,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,5,"17:00:00",75,0,75.02,0,80,0,81,0,62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,5,1,55,0.20833333333333334,64.040000000000006,0,67,0,66,0,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,6,"07:00:00",59,4.1666666666666664E-2,62.06,0,70,0,70,0,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,6,"17:00:00",73,0,62.96,0,73,0,72,0,60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,6,1,68,0,59,4.1666666666666664E-2,71,0,70,0,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,7,"02:00:00",68,0,59,4.1666666666666664E-2,71,0,70,0,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,7,"14:00:00",81,0,69.98,0,80,0,81,0,71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,7,"19:00:00",73,0,66.02,0,70,0,75,0,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,8,"04:00:00",66,0,60.08,0,72,0,72,0,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,8,"12:00:00",79,0,82.94,0,79,0,79,0,77,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,8,"18:00:00",72,0,77,{"$f":"IF(Y6022<60,(60-Y6022)/24,0)","v":0},66,{"$f":"IF(AA6022<60,(60-AA6022)/24,0)","v":0},72,{"$f":"IF(AC6022<60,(60-AC6022)/24,0)","v":0},73.400000000000006,{"$f":"IF(AE6022<60,(60-AE6022)/24,0)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,9,"05:00:00",61,0,55.94,0.16916666666666677,69,0,64.029899999999998,0,60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,9,"11:00:00",77,0,69.98,0,79,0,79,0,78.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,9,"14:00:00",79,0,68,0,82,0,81,0,78.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,10,"01:00:00",55,0.20833333333333334,55.04,0.20666666666666669,70,0,66,0,60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,10,"07:00:00",63,0,57.02,0.12416666666666654,70,0,68.048900000000003,0,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,10,"15:00:00",64.070300000000003,0,62.06,0,70,0,70,0,71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,10,1,63,0,57.92,8.66666666666666E-2,65,0,64,0,51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,11,"05:00:00",54.028100000000002,0.24882916666666657,53.96,0.25166666666666665,59,4.1666666666666664E-2,55,0.20833333333333334,51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,11,"17:00:00",68,0,60.08,0,71,0,72,0,68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,12,"02:00:00",43.155700000000003,0.70184583333333317,35.96,1.0016666666666667,50,0.41666666666666669,48,0.5,62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,12,"04:00:00",41,0.79166666666666663,33.08,1.1216666666666668,48,0.5,45.008800000000001,0.62463333333333326,62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,12,"11:00:00",66,0,59,4.1666666666666664E-2,68,0,72,0,71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,12,"18:00:00",63,0,53.96,0.25166666666666665,67,0,64,0,71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,13,"04:00:00",45,0.625,32,1.1666666666666667,52,0.33333333333333331,50,0.41666666666666669,68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,13,"11:00:00",72,0,60.08,0,71,0,70,0,75.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,13,"21:00:00",57,0.125,41,0.79166666666666663,60,0,59,4.1666666666666664E-2,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,14,"01:00:00",50,{"$f":"IF(W6149<60,(60-W6149)/24,0)","v":0.41666666666666669},35.96,1.0016666666666667,55,0.20833333333333334,61,0,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,14,"14:00:00",73,0,66.92,0,73,0,75,0,73.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,14,"15:00:00",73,0,66.92,0,75,0,75,0,71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,14,"23:00:00",63,0,42.98,0.70916666666666683,64,0,66,0,60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,15,"12:00:00",72,0,69.08,0,73,0,73,0,64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,15,"16:00:00",70,0,71.06,0,76,0,72,0,66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,15,"22:00:00",63,0,46.94,0.5441666666666668,66,0,66,0,57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,16,"09:00:00",55,0.20833333333333334,55.94,0.16916666666666677,57,0.125,55.072200000000002,0.2053249999999999,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,16,"12:00:00",55,0.20833333333333334,69.98,0,60,0,55,0.20833333333333334,62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,17,"02:00:00",54,0.25,42.08,0.7466666666666667,54,0.25,55,0.20833333333333334,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,17,"09:00:00",52,0.33333333333333331,53.96,0.25166666666666665,54,0.25,52,0.33333333333333331,57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,17,"11:00:00",50,0.41666666666666669,69.98,0,57,0.125,52,0.33333333333333331,62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,17,"23:00:00",52,0.33333333333333331,50,0.41666666666666669,57,0.125,55,0.20833333333333334,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,18,"04:00:00",48,0.5,46.04,0.58166666666666667,55,0.20833333333333334,52,0.33333333333333331,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,18,"09:00:00",55,0.20833333333333334,55.04,0.20666666666666669,60,0,57,0.125,66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,18,"21:00:00",39,0.875,55.94,0.16916666666666677,52,0.33333333333333331,45,0.625,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,19,"06:00:00",30.233000000000001,1.2402916666666666,50,0.41666666666666669,38,0.91666666666666663,41.229300000000002,0.78211249999999988,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,19,"14:00:00",68,0,82.94,0,72,0,70,0,75.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,19,"20:00:00",45,0.625,66.92,0,54,0.25,54,0.25,66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,19,"23:00:00",37.140599999999999,0.95247500000000007,57.92,8.66666666666666E-2,51,0.375,46.103999999999999,0.57900000000000007,64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,20,"10:00:00",64,0,78.08,0,66,0,64,0,66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,20,"16:00:00",64,0,86,0,70,0,70,0,73.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,20,1,57,0.125,60.08,0,59,4.1666666666666664E-2,61,0,60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,21,"09:00:00",57,0.125,75.02,0,59,4.1666666666666664E-2,61,0,73.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,21,"17:00:00",52.026699999999998,0.33222083333333341,73.040000000000006,0,59,4.1666666666666664E-2,52,0.33333333333333331,68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,22,"02:00:00",48,0.5,55.94,{"$f":"IF(Y6342<60,(60-Y6342)/24,0)","v":0.16916666666666677},52.050600000000003,{"$f":"IF(AA6342<60,(60-AA6342)/24,0)","v":0.33122499999999988},48,{"$f":"IF(AC6342<60,(60-AC6342)/24,0)","v":0.5},51.8,{"$f":"IF(AE6342<60,(60-AE6342)/24,0)","v":0.34166666666666679}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,22,"07:00:00",48,0.5,59,4.1666666666666664E-2,47,0.54166666666666663,48,0.5,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,22,"11:00:00",54,0.25,64.94,0,52.050600000000003,0.33122499999999988,52,0.33333333333333331,64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,22,"21:00:00",48,0.5,55.04,0.20666666666666669,47,0.54166666666666663,46.219200000000001,0.57419999999999993,51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,23,"04:00:00",46,0.58333333333333337,53.06,0.28916666666666657,46.103999999999999,0.57900000000000007,45,0.625,51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,23,"13:00:00",61,0,62.96,0,69,0,66,0,68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,23,"20:00:00",52,0.33333333333333331,60.98,0,61,0,55,0.20833333333333334,62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,24,"06:00:00",45,0.625,60.08,0,47,0.54166666666666663,46,0.58333333333333337,66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,24,"10:00:00",66,0,64.040000000000006,0,67,0,66,0,69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,24,"15:00:00",73,0,68,0,74,0,75,0,66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,24,1,55,0.20833333333333334,64.040000000000006,0,57,0.125,57,0.125,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,25,"08:00:00",52,0.33333333333333331,60.98,0,57,0.125,54.103499999999997,0.24568750000000014,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,25,"17:00:00",54,0.25,64.94,0,62,0,59,4.1666666666666664E-2,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,26,"01:00:00",34,1.0833333333333333,42.98,0.70916666666666683,43,0.70833333333333337,39.2468,0.86471666666666669,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,26,"07:00:00",34.129800000000003,1.0779249999999998,41,0.79166666666666663,41,0.79166666666666663,43.097900000000003,0.70425416666666651,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,26,"18:00:00",54,0.25,60.08,0,55,0.20833333333333334,54,0.25,51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,26,"21:00:00",39,0.875,57.92,8.66666666666666E-2,47,0.54166666666666663,46,0.58333333333333337,51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,27,"03:00:00",36.349800000000002,0.98542499999999988,57.92,8.66666666666666E-2,43,0.70833333333333337,43.097900000000003,0.70425416666666651,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,27,"11:00:00",63,0,66.02,0,64,0,55,0.20833333333333334,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,27,"20:00:00",66,0,66.92,0,50,0.41666666666666669,55,0.20833333333333334,57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,28,"04:00:00",63,0,60.08,0,41,0.79166666666666663,55,0.20833333333333334,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,28,"13:00:00",66,0,68,0,70,0,70,0,51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,28,"18:00:00",63,0,62.06,0,57,0.125,64,0,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,29,"06:00:00",52,0.33333333333333331,37.94,0.9191666666666668,61,0,63.008600000000001,0,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,29,"08:00:00",54,0.25,53.06,0.28916666666666657,65,0,64,0,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,29,"15:00:00",61,0,75.02,0,59,4.1666666666666664E-2,75,0,51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,30,"05:00:00",37.226799999999997,0.94888333333333341,46.94,0.5441666666666668,41,0.79166666666666663,64,0,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,30,"08:00:00",48,0.5,46.04,0.58166666666666667,54,0.25,64,0,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,30,"15:00:00",57,0.125,75.92,0,69,0,63,0,64.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,1,"01:00:00",46,0.58333333333333337,65.84,0,44,0.66666666666666663,53,0.29166666666666669,54.86,0.2141666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,1,"05:00:00",54.027900000000002,0.24883749999999991,73.94,0,36.063899999999997,0.9973375000000001,63,0,57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,1,"18:00:00",41,0.79166666666666663,62.96,0,45,0.625,48,0.5,73.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,2,"02:00:00",39,0.875,53.06,0.28916666666666657,37.133800000000001,0.95275833333333326,36,1,68,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,2,"03:00:00",39,0.875,50,0.41666666666666669,37.133800000000001,0.95275833333333326,34,1.0833333333333333,66.2,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,2,"16:00:00",46,0.58333333333333337,55.04,0.20666666666666669,46,0.58333333333333337,55,0.20833333333333334,80.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,2,"20:00:00",45,0.625,53.06,0.28916666666666657,37,0.95833333333333337,43,0.70833333333333337,73.400000000000006,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,3,"02:00:00",43,0.70833333333333337,50,0.41666666666666669,36,1,37,0.95833333333333337,69.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,3,"13:00:00",48,0.5,60.08,0,54,0.25,57,0.125,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,3,"23:00:00",37,0.95833333333333337,55.04,0.20666666666666669,36,1,36,1,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,4,"06:00:00",25,1.4583333333333333,55.94,0.16916666666666677,37.133800000000001,0.95275833333333326,30.1447,1.2439708333333332,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,4,"15:00:00",57,0.125,66.02,0,52,0.33333333333333331,63,0,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,4,"22:00:00",32,1.1666666666666667,55.04,0.20666666666666669,43,0.70833333333333337,36,1,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,4,1,28,1.3333333333333333,53.06,0.28916666666666657,37.133800000000001,0.95275833333333326,34,1.0833333333333333,62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,5,"12:00:00",54,0.25,57.02,0.12416666666666654,52,0.33333333333333331,57,0.125,78.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,5,"17:00:00",46,0.58333333333333337,53.06,0.28916666666666657,50,0.41666666666666669,57,0.125,71.599999999999994,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,6,"02:00:00",21,1.625,33.08,1.1216666666666668,30,1.25,30,1.25,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,6,"10:00:00",43,0.70833333333333337,55.04,0.20666666666666669,46,0.58333333333333337,45,0.625,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,6,"16:00:00",54,0.25,48.02,0.49916666666666654,54,0.25,55,0.20833333333333334,57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,7,"03:00:00",28,1.3333333333333333,35.96,1.0016666666666667,29,1.2916666666666667,28.3657,1.3180958333333332,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,7,"09:00:00",37,0.95833333333333337,42.98,0.70916666666666683,35,1.0416666666666667,41,0.79166666666666663,56.48,0.14666666666666681]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,7,"12:00:00",57,0.125,50,0.41666666666666669,54,0.25,52,0.33333333333333331,62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,7,"23:00:00",50,0.41666666666666669,30.02,1.2491666666666668,36.063899999999997,0.9973375000000001,54,0.25,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,8,"05:00:00",48,0.5,26.96,1.3766666666666667,30,1.25,54,0.25,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,8,"13:00:00",55,0.20833333333333334,68,0,68,0,59,4.1666666666666664E-2,57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,8,"22:00:00",55,0.20833333333333334,59,4.1666666666666664E-2,46,0.58333333333333337,57,0.125,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,9,"03:00:00",54,0.25,48.02,0.49916666666666654,41,0.79166666666666663,55,0.20833333333333334,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,9,"15:00:00",54,0.25,57.02,0.12416666666666654,75,0,55,0.20833333333333334,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,9,"20:00:00",50,0.41666666666666669,46.04,0.58166666666666667,54,0.25,54,0.25,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,9,1,50,0.41666666666666669,42.98,0.70916666666666683,51.082599999999999,0.37155833333333338,54,0.25,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,10,"10:00:00",54,0.25,42.08,0.7466666666666667,57,0.125,55,0.20833333333333334,57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,10,"17:00:00",55,{"$f":"IF(W6789<60,(60-W6789)/24,0)","v":0.20833333333333334},46.94,0.5441666666666668,66,0,57,0.125,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,10,1,54,0.25,26.06,1.4141666666666666,49.048699999999997,0.45630416666666679,57,0.125,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,11,"10:00:00",57,0.125,46.04,0.58166666666666667,52,0.33333333333333331,59,4.1666666666666664E-2,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,11,"14:00:00",59,4.1666666666666664E-2,55.04,0.20666666666666669,73,0,63,0,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,12,"03:00:00",48,0.5,26.96,1.3766666666666667,45,0.625,52,0.33333333333333331,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,12,"04:00:00",48,0.5,28.94,1.2941666666666667,45,0.625,52,0.33333333333333331,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,12,"12:00:00",55,0.20833333333333334,55.94,0.16916666666666677,59,4.1666666666666664E-2,55,0.20833333333333334,57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,12,"21:00:00",43,0.70833333333333337,46.04,0.58166666666666667,56,0.16666666666666666,52,0.33333333333333331,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,13,"05:00:00",45,0.625,51.08,0.37166666666666676,47,0.54166666666666663,50,0.41666666666666669,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,13,"11:00:00",55,0.20833333333333334,57.92,8.66666666666666E-2,63,0,52,0.33333333333333331,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,13,"22:00:00",48,0.5,57.02,0.12416666666666654,43,0.70833333333333337,52,0.33333333333333331,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,14,"01:00:00",45,0.625,57.02,0.12416666666666654,37.133800000000001,0.95275833333333326,52,0.33333333333333331,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,14,"15:00:00",48,0.5,62.06,0,64,0,48,0.5,51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,14,"22:00:00",43,0.70833333333333337,59,4.1666666666666664E-2,54,0.25,46.014699999999998,0.58272083333333347,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,14,1,43,0.70833333333333337,55.04,0.20666666666666669,55,0.20833333333333334,46.014699999999998,0.58272083333333347,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,15,"09:00:00",45,0.625,51.98,0.33416666666666678,55,0.20833333333333334,48,0.5,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,15,"21:00:00",45,0.625,39.92,0.83666666666666656,48,0.5,48,0.5,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,16,"02:00:00",43,0.70833333333333337,30.92,{"$f":"IF(Y6918<60,(60-Y6918)/24,0)","v":1.2116666666666667},45,{"$f":"IF(AA6918<60,(60-AA6918)/24,0)","v":0.625},48,{"$f":"IF(AC6918<60,(60-AC6918)/24,0)","v":0.5},44.6,{"$f":"IF(AE6918<60,(60-AE6918)/24,0)","v":0.64166666666666661}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,16,"07:00:00",45,0.625,30.02,1.2491666666666668,39,0.875,48,0.5,51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,16,"19:00:00",46,0.58333333333333337,48.92,0.46166666666666661,39,0.875,45,0.625,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,16,"21:00:00",43,0.70833333333333337,46.94,0.5441666666666668,36,1,37,0.95833333333333337,57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,17,"04:00:00",28,1.3333333333333333,41,0.79166666666666663,28,1.3333333333333333,36.314900000000002,0.98687916666666664,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,17,"18:00:00",46,0.58333333333333337,44.96,0.62666666666666659,43,0.70833333333333337,54,0.25,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,17,"21:00:00",46,0.58333333333333337,44.06,0.66416666666666657,39,0.875,52,0.33333333333333331,49.1,0.45416666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,18,"08:00:00",46,0.58333333333333337,35.96,1.0016666666666667,39,0.875,52,0.33333333333333331,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,18,"14:00:00",77,0,50,0.41666666666666669,50,0.41666666666666669,75,0,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,18,"22:00:00",68,0,26.96,1.3766666666666667,34,1.0833333333333333,64,0,37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,19,"07:00:00",57,0.125,26.06,1.4141666666666666,34,1.0833333333333333,61,0,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,19,"15:00:00",55,0.20833333333333334,64.040000000000006,0,46,0.58333333333333337,63,0,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,19,"16:00:00",55,0.20833333333333334,62.06,0,46,0.58333333333333337,61,0,59,4.1666666666666664E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,20,"05:00:00",37,0.95833333333333337,33.979999999999997,1.0841666666666667,25,1.4583333333333333,36,1,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,20,"09:00:00",52,0.33333333333333331,46.94,0.5441666666666668,34,1.0833333333333333,55,0.20833333333333334,51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,20,"19:00:00",39,0.875,46.94,0.5441666666666668,39,0.875,52,0.33333333333333331,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,21,"02:00:00",39,0.875,44.06,0.66416666666666657,43,0.70833333333333337,39,0.875,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,21,"09:00:00",39,{"$f":"IF(W7045<60,(60-W7045)/24,0)","v":0.875},42.08,0.7466666666666667,55,0.20833333333333334,45,0.625,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,21,"19:00:00",39,0.875,53.06,0.28916666666666657,52,0.33333333333333331,45,0.625,37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,22,"02:00:00",37,0.95833333333333337,42.98,0.70916666666666683,41,0.79166666666666663,39,0.875,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,22,"04:00:00",36,1,37.04,0.95666666666666667,39,0.875,37,0.95833333333333337,28.22,1.3241666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,22,"16:00:00",43,0.70833333333333337,68,0,36,1,46,0.58333333333333337,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,22,"21:00:00",43,0.70833333333333337,46.04,0.58166666666666667,34,1.0833333333333333,45,0.625,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,23,"06:00:00",28,1.3333333333333333,44.06,0.66416666666666657,32,1.1666666666666667,30,1.25,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,23,"14:00:00",54,0.25,71.06,0,39,0.875,55,0.20833333333333334,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,23,"20:00:00",43,0.70833333333333337,51.98,0.33416666666666678,36,1,46,0.58333333333333337,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,24,"07:00:00",30,1.25,37.94,0.9191666666666668,28,1.3333333333333333,34,1.0833333333333333,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,24,"13:00:00",64,0,51.98,0.33416666666666678,41,0.79166666666666663,70,0,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,24,"16:00:00",66,0,50,0.41666666666666669,45,0.625,66,0,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,25,"03:00:00",55,0.20833333333333334,24.08,1.4966666666666668,25,1.4583333333333333,46,0.58333333333333337,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,25,"09:00:00",48,0.5,39.92,0.83666666666666656,34,1.0833333333333333,55,0.20833333333333334,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,25,"17:00:00",46,0.58333333333333337,50,0.41666666666666669,52,0.33333333333333331,55,0.20833333333333334,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,26,"02:00:00",21,1.625,35.06,1.0391666666666666,46,0.58333333333333337,28.2209,1.3241291666666666,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,26,"07:00:00",21,1.625,33.979999999999997,1.0841666666666667,52,0.33333333333333331,30.217700000000001,1.2409291666666666,34.340000000000003,1.0691666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,26,"19:00:00",30,1.25,44.96,0.62666666666666659,63,0,34,1.0833333333333333,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,27,"04:00:00",19,1.7083333333333333,44.96,0.62666666666666659,61,0,34,1.0833333333333333,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,27,"06:00:00",19,1.7083333333333333,44.96,0.62666666666666659,61,0,36,1,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,27,"13:00:00",50,0.41666666666666669,48.02,0.49916666666666654,64,0,52,0.33333333333333331,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,27,"20:00:00",36,1,46.94,0.5441666666666668,55,0.20833333333333334,36,1,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,28,"06:00:00",25,1.4583333333333333,46.94,0.5441666666666668,41,0.79166666666666663,39.075600000000001,0.8718499999999999,37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,28,"13:00:00",48,0.5,60.98,0,55,0.20833333333333334,52,0.33333333333333331,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,28,"23:00:00",46,0.58333333333333337,39.92,0.83666666666666656,45,0.625,43,0.70833333333333337,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,29,"03:00:00",41,0.79166666666666663,33.08,1.1216666666666668,45,0.625,46,0.58333333333333337,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,29,"16:00:00",43,0.70833333333333337,66.92,0,52,0.33333333333333331,46,0.58333333333333337,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,29,"17:00:00",43,0.70833333333333337,60.98,0,51,0.375,46,0.58333333333333337,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,30,"01:00:00",39,0.875,55.04,0.20666666666666669,45,0.625,42,0.75,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,30,"14:00:00",39,0.875,53.06,0.28916666666666657,55,0.20833333333333334,48,0.5,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,30,"18:00:00",37,0.95833333333333337,39.92,0.83666666666666656,43,0.70833333333333337,46,0.58333333333333337,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,30,1,39,0.875,28.94,1.2941666666666667,34,1.0833333333333333,45,0.625,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,31,"11:00:00",45,0.625,39.92,0.83666666666666656,54,0.25,46,0.58333333333333337,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,31,"14:00:00",46,0.58333333333333337,46.94,0.5441666666666668,64,0,46,0.58333333333333337,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,1,"04:00:00",43,0.70833333333333337,57.02,0.12416666666666654,42,0.75,52,0.33333333333333331,51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,1,"11:00:00",63,0,57.02,0.12416666666666654,57,0.125,55,0.20833333333333334,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,1,"13:00:00",64,0,57.02,0.12416666666666654,64,0,58,8.3333333333333329E-2,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,2,"01:00:00",45,0.625,39.020000000000003,0.87416666666666654,36,1,58,8.3333333333333329E-2,57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,2,"06:00:00",43,0.70833333333333337,33.979999999999997,1.0841666666666667,43,0.70833333333333337,51,0.375,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,2,"11:00:00",39,0.875,50,0.41666666666666669,57,0.125,47,0.54166666666666663,62.6,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,2,"23:00:00",37,0.95833333333333337,42.08,0.7466666666666667,64,0,45,0.625,60.8,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,3,"08:00:00",34,1.0833333333333333,41,0.79166666666666663,63,0,36,1,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,3,"16:00:00",55,0.20833333333333334,41,0.79166666666666663,50,0.41666666666666669,58,8.3333333333333329E-2,57.2,0.11666666666666654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,3,"22:00:00",55,0.20833333333333334,35.06,1.0391666666666666,45,0.625,44,0.66666666666666663,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,4,"01:00:00",48,0.5,32,1.1666666666666667,41,0.79166666666666663,44,0.66666666666666663,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,4,"12:00:00",50,0.41666666666666669,35.96,1.0016666666666667,46,0.58333333333333337,62,0,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,4,"18:00:00",43,0.70833333333333337,28.04,1.3316666666666668,41,0.79166666666666663,55,0.20833333333333334,51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,5,"02:00:00",34,1.0833333333333333,26.06,1.4141666666666666,34,1.0833333333333333,56,0.16666666666666666,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,5,"11:00:00",43,0.70833333333333337,42.98,0.70916666666666683,48,0.5,67,0,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,5,"19:00:00",46,0.58333333333333337,41,0.79166666666666663,54,0.25,60,0,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,6,"04:00:00",37.140599999999999,0.95247500000000007,42.08,0.7466666666666667,39,0.875,56,0.16666666666666666,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,6,"09:00:00",45,{"$f":"IF(W7429<60,(60-W7429)/24,0)","v":0.625},46.94,0.5441666666666668,54,0.25,55,0.20833333333333334,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,6,"13:00:00",48,0.5,51.08,0.37166666666666676,57,0.125,52,0.33333333333333331,53.6,0.26666666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,6,"22:00:00",48,0.5,46.94,0.5441666666666668,45,0.625,57,0.125,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,7,"08:00:00",47,0.54166666666666663,37.04,0.95666666666666667,37,0.95833333333333337,42,0.75,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,7,"15:00:00",48,0.5,53.06,0.28916666666666657,39,0.875,53,0.29166666666666669,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,7,"22:00:00",43,0.70833333333333337,46.04,0.58166666666666667,34,1.0833333333333333,30,1.25,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,8,"08:00:00",39,0.875,44.96,0.62666666666666659,28,1.3333333333333333,42,0.75,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,8,"12:00:00",43,0.70833333333333337,44.96,0.62666666666666659,37,0.95833333333333337,58,8.3333333333333329E-2,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,8,"17:00:00",39,0.875,44.06,0.66416666666666657,36,1,54,0.25,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,9,"02:00:00",27,1.375,44.06,{"$f":"IF(Y7494<60,(60-Y7494)/24,0)","v":0.66416666666666657},30,{"$f":"IF(AA7494<60,(60-AA7494)/24,0)","v":1.25},46,{"$f":"IF(AC7494<60,(60-AC7494)/24,0)","v":0.58333333333333337},42.8,{"$f":"IF(AE7494<60,(60-AE7494)/24,0)","v":0.71666666666666679}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,9,"10:00:00",34,1.0833333333333333,44.96,0.62666666666666659,43,0.70833333333333337,50,0.41666666666666669,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,9,"19:00:00",34,1.0833333333333333,51.08,0.37166666666666676,52,0.33333333333333331,50,0.41666666666666669,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,10,"03:00:00",37.213900000000002,0.94942083333333327,33.08,1.1216666666666668,57,0.125,41,0.79166666666666663,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,10,"09:00:00",39,0.875,42.08,0.7466666666666667,61,0,47,0.54166666666666663,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,10,"20:00:00",30,1.25,44.06,0.66416666666666657,55,0.20833333333333334,38,0.91666666666666663,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,10,"23:00:00",28,1.3333333333333333,33.979999999999997,1.0841666666666667,46,0.58333333333333337,35,1.0416666666666667,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,11,"05:00:00",27,1.375,33.08,1.1216666666666668,36,1,35,1.0416666666666667,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,11,"13:00:00",32,1.1666666666666667,50,0.41666666666666669,37,0.95833333333333337,42,0.75,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,11,"22:00:00",28,1.3333333333333333,48.02,0.49916666666666654,25,1.4583333333333333,31,1.2083333333333333,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,12,"06:00:00",21,1.625,42.98,0.70916666666666683,19,1.7083333333333333,24,1.5,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,12,"15:00:00",43,0.70833333333333337,42.08,0.7466666666666667,43,0.70833333333333337,52,0.33333333333333331,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,12,"20:00:00",27,1.375,33.08,1.1216666666666668,43,0.70833333333333337,34,1.0833333333333333,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,13,"08:00:00",25,1.4583333333333333,26.06,1.4141666666666666,37.133800000000001,0.95275833333333326,35,1.0416666666666667,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,13,"10:00:00",34,1.0833333333333333,32,1.1666666666666667,41,0.79166666666666663,44,0.66666666666666663,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,13,"17:00:00",37,0.95833333333333337,37.04,0.95666666666666667,45,0.625,50,0.41666666666666669,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,14,"07:00:00",39,0.875,26.96,1.3766666666666667,37,0.95833333333333337,34,1.0833333333333333,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,14,"10:00:00",52,0.33333333333333331,48.02,{"$f":"IF(Y7622<60,(60-Y7622)/24,0)","v":0.49916666666666654},48,{"$f":"IF(AA7622<60,(60-AA7622)/24,0)","v":0.5},43,{"$f":"IF(AC7622<60,(60-AC7622)/24,0)","v":0.70833333333333337},24.8,{"$f":"IF(AE7622<60,(60-AE7622)/24,0)","v":1.4666666666666668}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,14,"17:00:00",39,0.875,64.040000000000006,0,48,0.5,54,0.25,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,15,"03:00:00",25,1.4583333333333333,57.92,8.66666666666666E-2,37,0.95833333333333337,53,0.29166666666666669,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,15,"07:00:00",28,1.3333333333333333,57.02,0.12416666666666654,37,0.95833333333333337,56,0.16666666666666666,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,15,"20:00:00",34.129800000000003,1.0779249999999998,60.08,0,34,1.0833333333333333,41,0.79166666666666663,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,16,"04:00:00",36,1,62.96,0,30,1.25,35,1.0416666666666667,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,16,"05:00:00",36,1,62.06,0,30,1.25,33,1.125,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,16,"18:00:00",57,0.125,57.02,0.12416666666666654,34,1.0833333333333333,37,0.95833333333333337,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,16,"22:00:00",45,0.625,42.98,0.70916666666666683,32,1.1666666666666667,30,1.25,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,17,"04:00:00",39,0.875,37.04,0.95666666666666667,30,1.25,24,1.5,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,17,"15:00:00",37,0.95833333333333337,41,0.79166666666666663,37,0.95833333333333337,50,0.41666666666666669,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,17,1,32,1.1666666666666667,26.06,1.4141666666666666,25,1.4583333333333333,30,1.25,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,18,"07:00:00",25,1.4583333333333333,28.04,1.3316666666666668,34,1.0833333333333333,32,1.1666666666666667,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,18,"17:00:00",25,1.4583333333333333,37.94,0.9191666666666668,36,1,44,0.66666666666666663,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,18,1,14,1.9166666666666667,30.02,1.2491666666666668,30,1.25,43,0.70833333333333337,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,19,"02:00:00",14,1.9166666666666667,28.94,1.2941666666666667,30,1.25,41,0.79166666666666663,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,19,"14:00:00",36,1,35.06,1.0391666666666666,59,4.1666666666666664E-2,54,0.25,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,19,"19:00:00",21,1.625,28.94,1.2941666666666667,48,0.5,40,0.83333333333333337,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,20,"04:00:00",19,1.7083333333333333,28.04,1.3316666666666668,34,1.0833333333333333,35,1.0416666666666667,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,20,"12:00:00",43,0.70833333333333337,35.06,1.0391666666666666,63,0,46,0.58333333333333337,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,20,"18:00:00",37,0.95833333333333337,39.92,0.83666666666666656,61,0,32,1.1666666666666667,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,21,"05:00:00",37,0.95833333333333337,33.08,1.1216666666666668,37,0.95833333333333337,27,1.375,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,21,"11:00:00",52,0.33333333333333331,28.04,1.3316666666666668,50,0.41666666666666669,39,0.875,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,21,"14:00:00",54,0.25,24.98,1.4591666666666665,55,0.20833333333333334,45,0.625,51.8,0.34166666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,22,"01:00:00",34,1.0833333333333333,19.940000000000001,1.6691666666666667,43,0.70833333333333337,47,0.54166666666666663,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,22,"07:00:00",36,1,19.04,1.7066666666666668,43,0.70833333333333337,49,0.45833333333333331,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,22,"15:00:00",36,1,28.04,1.3316666666666668,66,0,45,0.625,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,22,1,27,1.375,23,1.5416666666666667,54,0.25,35,1.0416666666666667,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,23,"05:00:00",21,1.625,21.02,1.6241666666666668,54,0.25,32,1.1666666666666667,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,23,"17:00:00",18,1.75,17.96,1.7516666666666667,59,4.1666666666666664E-2,24,1.5,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,23,"22:00:00",14,1.9166666666666667,10.94,2.0441666666666669,50,0.41666666666666669,20,1.6666666666666667,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,24,"02:00:00",3,2.375,1.04,2.4566666666666666,52,0.33333333333333331,19,1.7083333333333333,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,24,"12:00:00",23,1.5416666666666667,26.06,1.4141666666666666,66,0,27,1.375,37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,24,"19:00:00",21,1.625,21.92,1.5866666666666667,63,0,26,1.4166666666666667,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,25,"02:00:00",17,1.7916666666666667,12.92,{"$f":"IF(Y7878<60,(60-Y7878)/24,0)","v":1.9616666666666667},54,{"$f":"IF(AA7878<60,(60-AA7878)/24,0)","v":0.25},28,{"$f":"IF(AC7878<60,(60-AC7878)/24,0)","v":1.3333333333333333},21.2,{"$f":"IF(AE7878<60,(60-AE7878)/24,0)","v":1.6166666666666665}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,25,"12:00:00",19,1.7083333333333333,28.94,1.2941666666666667,46,0.58333333333333337,44,0.66666666666666663,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,25,"16:00:00",21,1.625,30.92,1.2116666666666667,45,0.625,39,0.875,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,26,"05:00:00",7,2.2083333333333335,30.02,1.2491666666666668,43,0.70833333333333337,28,1.3333333333333333,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,26,"06:00:00",5,2.2916666666666665,30.02,1.2491666666666668,45,0.625,28,1.3333333333333333,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,26,"14:00:00",23,1.5416666666666667,37.04,0.95666666666666667,46,0.58333333333333337,34,1.0833333333333333,49.28,0.4466666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,26,"23:00:00",21,1.625,37.94,0.9191666666666668,61,0,20,1.6666666666666667,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,27,"07:00:00",18,1.75,24.08,1.4966666666666668,55,0.20833333333333334,13.5901,1.9337458333333333,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,27,"13:00:00",30,1.25,33.979999999999997,1.0841666666666667,50,0.41666666666666669,30,1.25,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,27,1,28,1.3333333333333333,28.94,1.2941666666666667,34,1.0833333333333333,29,1.2916666666666667,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,28,"03:00:00",30,1.25,30.92,1.2116666666666667,39,0.875,31,1.2083333333333333,21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,28,"17:00:00",34,1.0833333333333333,48.92,0.46166666666666661,43,0.70833333333333337,36,1,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,28,1,30,1.25,33.08,1.1216666666666668,36,1,43,0.70833333333333337,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,29,"02:00:00",37.398499999999999,0.94172916666666673,32,1.1666666666666667,30,1.25,43,0.70833333333333337,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,29,"11:00:00",48,0.5,19.04,1.7066666666666668,39,0.875,47,0.54166666666666663,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,29,"23:00:00",50,0.41666666666666669,14,1.9166666666666667,28,1.3333333333333333,39,0.875,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,30,"04:00:00",52,0.33333333333333331,15.98,1.8341666666666665,28,1.3333333333333333,33,1.125,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,30,"09:00:00",54,{"$f":"IF(W8005<60,(60-W8005)/24,0)","v":0.25},19.04,1.7066666666666668,30,1.25,34,1.0833333333333333,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,30,"21:00:00",39,0.875,26.06,1.4141666666666666,27,1.375,34,1.0833333333333333,37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,30,"23:00:00",38,0.91666666666666663,27.68,1.3466666666666667,30,1.25,34,1.0833333333333333,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,1,"06:00:00",36,1,30.92,1.2116666666666667,32,1.1666666666666667,34,1.0833333333333333,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,1,"20:00:00",46,0.58333333333333337,35.06,1.0391666666666666,39,0.875,25,1.4583333333333333,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,1,"23:00:00",47,0.54166666666666663,35.06,1.0391666666666666,37,0.95833333333333337,24,1.5,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,2,"10:00:00",45.107900000000001,0.62050416666666663,42.08,0.7466666666666667,37,0.95833333333333337,30,1.25,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,2,"16:00:00",34,1.0833333333333333,37.04,0.95666666666666667,36,1,32,1.1666666666666667,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,2,1,30,1.25,28.04,1.3316666666666668,28,1.3333333333333333,27,1.375,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,3,"09:00:00",32,1.1666666666666667,23,1.5416666666666667,28,1.3333333333333333,28,1.3333333333333333,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,3,"17:00:00",28,1.3333333333333333,24.08,1.4966666666666668,30,1.25,37,0.95833333333333337,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,3,"18:00:00",27,1.375,23,1.5416666666666667,28,1.3333333333333333,34,1.0833333333333333,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,4,"07:00:00",28,1.3333333333333333,15.08,1.8716666666666668,25,1.4583333333333333,28,1.3333333333333333,37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,4,"11:00:00",34,1.0833333333333333,26.96,1.3766666666666667,25,1.4583333333333333,36,1,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,4,"21:00:00",32,1.1666666666666667,24.08,1.4966666666666668,18,1.75,36,1,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,5,"04:00:00",27,1.375,21.02,1.6241666666666668,16,1.8333333333333333,33,1.125,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,5,"11:00:00",32,1.1666666666666667,30.02,1.2491666666666668,30,1.25,34,1.0833333333333333,55.4,0.19166666666666674]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,5,"21:00:00",28,1.3333333333333333,28.94,1.2941666666666667,23,1.5416666666666667,28.148099999999999,1.3271625,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,6,"04:00:00",27,1.375,28.94,1.2941666666666667,23,1.5416666666666667,29,1.2916666666666667,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,6,"06:00:00",28,1.3333333333333333,28.04,1.3316666666666668,23,1.5416666666666667,30,1.25,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,6,"18:00:00",28,1.3333333333333333,30.92,1.2116666666666667,28,1.3333333333333333,32,1.1666666666666667,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,6,"23:00:00",27,1.375,28.04,1.3316666666666668,25,1.4583333333333333,31,1.2083333333333333,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,7,"08:00:00",27,1.375,15.98,1.8341666666666665,21,1.625,32,1.1666666666666667,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,7,"16:00:00",30,1.25,30.92,1.2116666666666667,25,1.4583333333333333,37,0.95833333333333337,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,7,"22:00:00",28,1.3333333333333333,19.940000000000001,1.6691666666666667,18,1.75,37,0.95833333333333337,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,8,"09:00:00",30,{"$f":"IF(W8197<60,(60-W8197)/24,0)","v":1.25},35.06,1.0391666666666666,14,1.9166666666666667,32,1.1666666666666667,37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,8,"15:00:00",34,1.0833333333333333,39.020000000000003,0.87416666666666654,30,1.25,37,0.95833333333333337,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,8,"18:00:00",30,1.25,37.04,0.95666666666666667,19,1.7083333333333333,27,1.375,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,9,"05:00:00",12,2,23,1.5416666666666667,18,1.75,14,1.9166666666666667,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,9,"11:00:00",23,1.5416666666666667,35.96,1.0016666666666667,24,1.5,27,1.375,37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,9,"19:00:00",28,1.3333333333333333,28.94,1.2941666666666667,25,1.4583333333333333,25,1.4583333333333333,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,10,"04:00:00",27,1.375,26.06,1.4141666666666666,27,1.375,17,1.7916666666666667,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,10,"13:00:00",28,1.3333333333333333,33.979999999999997,1.0841666666666667,36,1,27,1.375,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,10,"18:00:00",21,1.625,32,1.1666666666666667,30,1.25,27,1.375,50,0.41666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,11,"06:00:00",21,1.625,32,1.1666666666666667,14,1.9166666666666667,12,2,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,11,"08:00:00",21,1.625,28.94,1.2941666666666667,10,2.0833333333333335,10,2.0833333333333335,37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,11,"15:00:00",30,1.25,33.08,1.1216666666666668,36,1,34,1.0833333333333333,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,11,"22:00:00",19,1.7083333333333333,32,1.1666666666666667,19,1.7083333333333333,18,1.75,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,12,"08:00:00",28,1.3333333333333333,32,1.1666666666666667,25,1.4583333333333333,19,1.7083333333333333,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,12,"15:00:00",32,1.1666666666666667,37.04,0.95666666666666667,32,1.1666666666666667,34,1.0833333333333333,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,13,"01:00:00",32,1.1666666666666667,17.96,1.7516666666666667,12,2,30,1.25,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,13,"05:00:00",30,1.25,15.98,1.8341666666666665,7,2.2083333333333335,29,1.2916666666666667,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,13,"18:00:00",31,1.2083333333333333,28.04,{"$f":"IF(Y8326<60,(60-Y8326)/24,0)","v":1.3316666666666668},10,{"$f":"IF(AA8326<60,(60-AA8326)/24,0)","v":2.0833333333333335},34,{"$f":"IF(AC8326<60,(60-AC8326)/24,0)","v":1.0833333333333333},42.8,{"$f":"IF(AE8326<60,(60-AE8326)/24,0)","v":0.71666666666666679}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,13,"19:00:00",30,1.25,28.04,1.3316666666666668,9,2.125,34,1.0833333333333333,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,14,"03:00:00",32.26,1.1558333333333335,30.02,1.2491666666666668,-9,2.875,29,1.2916666666666667,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,14,"16:00:00",34,1.0833333333333333,23,1.5416666666666667,18,1.75,21,1.625,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,14,"20:00:00",32,1.1666666666666667,17.96,1.7516666666666667,3,2.375,16,1.8333333333333333,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,15,"02:00:00",32,1.1666666666666667,15.08,1.8716666666666668,-8,2.8333333333333335,8,2.1666666666666665,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,15,"13:00:00",34,1.0833333333333333,23,1.5416666666666667,21,1.625,18,1.75,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,15,"16:00:00",36,1,24.98,1.4591666666666665,21,1.625,23,1.5416666666666667,37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,16,"06:00:00",25,1.4583333333333333,17.96,1.7516666666666667,27,1.375,8,2.1666666666666665,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,16,"13:00:00",36,1,33.08,1.1216666666666668,34,1.0833333333333333,33,1.125,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,16,"15:00:00",36,1,33.08,1.1216666666666668,30,1.25,41,0.79166666666666663,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,17,"03:00:00",30.157900000000001,1.2434208333333332,26.96,1.3766666666666667,25,1.4583333333333333,18,1.75,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,17,"08:00:00",32.093200000000003,1.1627833333333333,26.06,1.4141666666666666,21,1.625,16,1.8333333333333333,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,17,"17:00:00",34.191699999999997,1.0753458333333334,23,1.5416666666666667,32,1.1666666666666667,30,1.25,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,18,"01:00:00",43,0.70833333333333337,19.940000000000001,1.6691666666666667,23,1.5416666666666667,20,1.6666666666666667,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,18,"10:00:00",36,1,24.08,1.4966666666666668,21,1.625,28,1.3333333333333333,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,18,"18:00:00",36,1,12.02,1.9991666666666668,28,1.3333333333333333,28,1.3333333333333333,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,18,1,37,0.95833333333333337,3.92,2.3366666666666664,21,1.625,25,1.4583333333333333,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,19,"03:00:00",34,1.0833333333333333,1.94,2.4191666666666669,19,1.7083333333333333,27,1.375,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,19,"14:00:00",34,1.0833333333333333,17.059999999999999,1.7891666666666666,27,1.375,47,0.54166666666666663,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,19,"20:00:00",30,1.25,10.039999999999999,2.0816666666666666,23,1.5416666666666667,43,0.70833333333333337,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,20,"04:00:00",25,1.4583333333333333,1.04,2.4566666666666666,12,2,35,1.0416666666666667,17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,20,"13:00:00",23,1.5416666666666667,26.06,1.4141666666666666,28,1.3333333333333333,37,0.95833333333333337,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,20,"21:00:00",18,1.75,19.04,1.7066666666666668,21,1.625,25,1.4583333333333333,42.8,0.71666666666666679]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,"06:00:00",10,2.0833333333333335,10.94,2.0441666666666669,7,2.2083333333333335,13,1.9583333333333333,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,"07:00:00",3,2.375,10.039999999999999,2.0816666666666666,5,2.2916666666666665,12,2,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,"15:00:00",25,1.4583333333333333,24.98,1.4591666666666665,27,1.375,27,1.375,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,"16:00:00",19,1.7083333333333333,24.08,1.4966666666666668,25,1.4583333333333333,25,1.4583333333333333,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,"17:00:00",10,{"$f":"IF(W8517<60,(60-W8517)/24,0)","v":2.0833333333333335},24.08,1.4966666666666668,19,1.7083333333333333,19,1.7083333333333333,37.76,0.92666666666666675]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,"18:00:00",8,2.1666666666666665,23,{"$f":"IF(Y8518<60,(60-Y8518)/24,0)","v":1.5416666666666667},18,{"$f":"IF(AA8518<60,(60-AA8518)/24,0)","v":1.75},17,{"$f":"IF(AC8518<60,(60-AC8518)/24,0)","v":1.7916666666666667},37.04,{"$f":"IF(AE8518<60,(60-AE8518)/24,0)","v":0.95666666666666667}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,"19:00:00",6,2.25,21.92,1.5866666666666667,18,1.75,15,1.875,36.32,0.98666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,"20:00:00",5,2.2916666666666665,19.940000000000001,1.6691666666666667,18,1.75,14,1.9166666666666667,35.96,1.0016666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,"21:00:00",9,2.125,19.04,1.7066666666666668,19,1.7083333333333333,12,2,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,"22:00:00",7,2.2083333333333335,17.96,1.7516666666666667,18,1.75,9,2.125,34.700000000000003,1.0541666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,"23:00:00",7,2.2083333333333335,12.92,1.9616666666666667,19,1.7083333333333333,7,2.2083333333333335,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,21,1,7,2.2083333333333335,8.06,2.1641666666666666,18,1.75,6,2.25,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"01:00:00",7,2.2083333333333335,6.08,2.2466666666666666,16,1.8333333333333333,5,2.2916666666666665,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"02:00:00",3,2.375,3.02,2.3741666666666665,12,2,5,2.2916666666666665,32.9,1.1291666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"03:00:00",1,2.4583333333333335,1.94,2.4191666666666669,12,2,4,2.3333333333333335,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"04:00:00",3,2.375,-3.9999999999999147E-2,2.5016666666666665,10,2.0833333333333335,4,2.3333333333333335,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"05:00:00",3,2.375,-3.9999999999999147E-2,2.5016666666666665,9,2.125,3,2.375,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"06:00:00",1,2.4583333333333335,-0.94000000000000483,2.539166666666667,7,2.2083333333333335,3,2.375,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"07:00:00",3,2.375,-2.92,2.6216666666666666,7,2.2083333333333335,3,2.375,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"08:00:00",7,2.2083333333333335,-4,2.6666666666666665,7,2.2083333333333335,-2,2.5833333333333335,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"09:00:00",10,2.0833333333333335,1.94,2.4191666666666669,9,2.125,9,2.125,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"10:00:00",14,1.9166666666666667,10.94,2.0441666666666669,12,2,10,2.0833333333333335,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"11:00:00",18,1.75,19.04,1.7066666666666668,16,1.8333333333333333,16,1.8333333333333333,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"12:00:00",21,1.625,24.98,1.4591666666666665,27,1.375,18,1.75,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"13:00:00",25,1.4583333333333333,26.06,1.4141666666666666,28,1.3333333333333333,21,1.625,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"14:00:00",27,1.375,26.06,1.4141666666666666,30,1.25,27,1.375,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"15:00:00",27,1.375,26.06,1.4141666666666666,30,1.25,23,1.5416666666666667,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"16:00:00",27,1.375,24.98,1.4591666666666665,28,1.3333333333333333,23,1.5416666666666667,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"17:00:00",25,1.4583333333333333,24.08,1.4966666666666668,27,1.375,23,1.5416666666666667,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"18:00:00",25,1.4583333333333333,23,1.5416666666666667,27,1.375,16,1.8333333333333333,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"19:00:00",25,1.4583333333333333,23,1.5416666666666667,27,1.375,12,2,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"20:00:00",25,1.4583333333333333,24.08,1.4966666666666668,28,1.3333333333333333,12,2,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"21:00:00",23,1.5416666666666667,21.92,1.5866666666666667,28,1.3333333333333333,12,2,27.68,1.3466666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"22:00:00",21,1.625,21.02,1.6241666666666668,28,1.3333333333333333,14,1.9166666666666667,27.14,1.3691666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,"23:00:00",23,1.5416666666666667,21.02,1.6241666666666668,28,1.3333333333333333,13,1.9583333333333333,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,22,1,25,1.4583333333333333,21.02,1.6241666666666668,28,1.3333333333333333,14,1.9166666666666667,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"01:00:00",25,1.4583333333333333,21.92,1.5866666666666667,28,1.3333333333333333,15,1.875,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"02:00:00",25,1.4583333333333333,21.92,1.5866666666666667,28,1.3333333333333333,16,1.8333333333333333,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"03:00:00",25,1.4583333333333333,21.92,1.5866666666666667,30,1.25,16,1.8333333333333333,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"04:00:00",25,1.4583333333333333,21.92,1.5866666666666667,30,1.25,17,1.7916666666666667,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"05:00:00",25,1.4583333333333333,21.92,1.5866666666666667,30,1.25,18,1.75,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"06:00:00",25,1.4583333333333333,23,1.5416666666666667,28,1.3333333333333333,19,1.7083333333333333,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"07:00:00",25,1.4583333333333333,23,1.5416666666666667,25,1.4583333333333333,19,1.7083333333333333,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"08:00:00",25,1.4583333333333333,24.08,1.4966666666666668,23,1.5416666666666667,19,1.7083333333333333,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"09:00:00",25,1.4583333333333333,24.08,1.4966666666666668,27,1.375,19,1.7083333333333333,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"10:00:00",27,1.375,24.98,1.4591666666666665,32,1.1666666666666667,21,1.625,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"11:00:00",28,1.3333333333333333,28.94,1.2941666666666667,36,1,24,1.5,30.38,1.2341666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"12:00:00",30,1.25,30.92,1.2116666666666667,37,0.95833333333333337,25,1.4583333333333333,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"13:00:00",30,1.25,32,1.1666666666666667,39,0.875,27,1.375,33.26,1.1141666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"14:00:00",32,1.1666666666666667,33.979999999999997,1.0841666666666667,39,0.875,28,1.3333333333333333,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"15:00:00",30,1.25,33.979999999999997,1.0841666666666667,39,0.875,28,1.3333333333333333,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"16:00:00",30,1.25,30.92,1.2116666666666667,37,0.95833333333333337,28,1.3333333333333333,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"17:00:00",30,1.25,32,1.1666666666666667,36,1,28,1.3333333333333333,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"18:00:00",30,1.25,32,1.1666666666666667,34,1.0833333333333333,28,1.3333333333333333,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"19:00:00",30,1.25,30.92,1.2116666666666667,34,1.0833333333333333,28,1.3333333333333333,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"20:00:00",30,1.25,30.92,1.2116666666666667,34,1.0833333333333333,28,1.3333333333333333,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"21:00:00",30,1.25,26.96,1.3766666666666667,34,1.0833333333333333,28,1.3333333333333333,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"22:00:00",30,1.25,26.96,1.3766666666666667,34,1.0833333333333333,28,1.3333333333333333,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,"23:00:00",30,1.25,24.08,1.4966666666666668,32,1.1666666666666667,27,1.375,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,23,1,30,1.25,23,1.5416666666666667,32,1.1666666666666667,27,1.375,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"01:00:00",32,1.1666666666666667,24.98,1.4591666666666665,32,1.1666666666666667,27,1.375,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"02:00:00",34,1.0833333333333333,24.98,1.4591666666666665,32,1.1666666666666667,27,1.375,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"03:00:00",32,1.1666666666666667,28.04,1.3316666666666668,32,1.1666666666666667,27,1.375,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"04:00:00",34,1.0833333333333333,28.94,1.2941666666666667,32,1.1666666666666667,27,1.375,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"05:00:00",34,1.0833333333333333,28.94,1.2941666666666667,32,1.1666666666666667,27,1.375,21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"06:00:00",32.009500000000003,1.1662708333333331,30.02,1.2491666666666668,30,1.25,28,1.3333333333333333,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"07:00:00",34,1.0833333333333333,30.02,1.2491666666666668,30,1.25,25,1.4583333333333333,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"08:00:00",36,1,30.92,1.2116666666666667,30,1.25,27,1.375,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"09:00:00",36,{"$f":"IF(W8581<60,(60-W8581)/24,0)","v":1},32,1.1666666666666667,32,1.1666666666666667,27,1.375,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"10:00:00",37,0.95833333333333337,33.08,{"$f":"IF(Y8582<60,(60-Y8582)/24,0)","v":1.1216666666666668},35,{"$f":"IF(AA8582<60,(60-AA8582)/24,0)","v":1.0416666666666667},28,{"$f":"IF(AC8582<60,(60-AC8582)/24,0)","v":1.3333333333333333},24.8,{"$f":"IF(AE8582<60,(60-AE8582)/24,0)","v":1.4666666666666668}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"11:00:00",39,0.875,32,1.1666666666666667,39,0.875,36,1,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"12:00:00",37,0.95833333333333337,33.08,1.1216666666666668,45,0.625,36,1,27.14,1.3691666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"13:00:00",37.389200000000002,0.9421166666666666,33.08,1.1216666666666668,45,0.625,34,1.0833333333333333,27.32,1.3616666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"14:00:00",37.389200000000002,0.9421166666666666,33.979999999999997,1.0841666666666667,45,0.625,36,1,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"15:00:00",41,0.79166666666666663,35.06,1.0391666666666666,43,0.70833333333333337,37,0.95833333333333337,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"16:00:00",39,0.875,33.979999999999997,1.0841666666666667,43,0.70833333333333337,28,1.3333333333333333,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"17:00:00",41,0.79166666666666663,33.979999999999997,1.0841666666666667,37,0.95833333333333337,21,1.625,21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"18:00:00",37.213900000000002,0.94942083333333327,33.08,1.1216666666666668,36,1,21,1.625,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"19:00:00",37.213900000000002,0.94942083333333327,33.08,1.1216666666666668,36,1,18,1.75,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"20:00:00",37.213900000000002,0.94942083333333327,33.08,1.1216666666666668,34,1.0833333333333333,21,1.625,17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"21:00:00",37.213900000000002,0.94942083333333327,33.08,1.1216666666666668,34,1.0833333333333333,19,1.7083333333333333,15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"22:00:00",37.213900000000002,0.94942083333333327,32,1.1666666666666667,34,1.0833333333333333,21,1.625,14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,"23:00:00",39,0.875,32,1.1666666666666667,34,1.0833333333333333,21,1.625,14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,24,1,36.188299999999998,0.99215416666666678,32,1.1666666666666667,34,1.0833333333333333,22,1.5833333333333333,12.2,1.9916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"01:00:00",34,1.0833333333333333,33.08,1.1216666666666668,34,1.0833333333333333,23,1.5416666666666667,10.4,2.0666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"02:00:00",32,1.1666666666666667,33.08,1.1216666666666668,30,1.25,24,1.5,10.4,2.0666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"03:00:00",32,1.1666666666666667,32,1.1666666666666667,30,1.25,26,1.4166666666666667,8.6,2.1416666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"04:00:00",30,1.25,32,1.1666666666666667,28,1.3333333333333333,27,1.375,8.6,2.1416666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"05:00:00",28,1.3333333333333333,32,1.1666666666666667,28,1.3333333333333333,28,1.3333333333333333,6.8,2.2166666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"06:00:00",21,1.625,32,1.1666666666666667,28,1.3333333333333333,30,1.25,6.8,2.2166666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"07:00:00",19,1.7083333333333333,32,1.1666666666666667,28,1.3333333333333333,32,1.1666666666666667,8.6,2.1416666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"08:00:00",14,1.9166666666666667,32,1.1666666666666667,27,1.375,32,1.1666666666666667,10.4,2.0666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"09:00:00",12,2,33.08,1.1216666666666668,27,1.375,32,1.1666666666666667,12.2,1.9916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"10:00:00",12,2,30.92,1.2116666666666667,28,1.3333333333333333,33,1.125,15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"11:00:00",10,2.0833333333333335,28.04,1.3316666666666668,32,1.1666666666666667,34,1.0833333333333333,17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"12:00:00",12,2,26.96,1.3766666666666667,34,1.0833333333333333,34,1.0833333333333333,21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"13:00:00",14,1.9166666666666667,26.06,1.4141666666666666,39,0.875,34,1.0833333333333333,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"14:00:00",16,1.8333333333333333,24.08,1.4966666666666668,41,0.79166666666666663,34,1.0833333333333333,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"15:00:00",15,1.875,21.92,1.5866666666666667,43,0.70833333333333337,35,1.0416666666666667,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"16:00:00",12,2,21.02,1.6241666666666668,37,0.95833333333333337,36,1,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"17:00:00",10,2.0833333333333335,19.04,1.7066666666666668,36,1,34,1.0833333333333333,21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"18:00:00",10,2.0833333333333335,17.059999999999999,1.7891666666666666,36,1,34,1.0833333333333333,21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"19:00:00",10,2.0833333333333335,15.98,1.8341666666666665,36,1,34,1.0833333333333333,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"20:00:00",3,2.375,15.08,1.8716666666666668,37.133800000000001,0.95275833333333326,34,1.0833333333333333,15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"21:00:00",3,2.375,12.92,1.9616666666666667,37,0.95833333333333337,34,1.0833333333333333,15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"22:00:00",1,2.4583333333333335,12.02,1.9991666666666668,39,0.875,34,1.0833333333333333,15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,"23:00:00",0,2.5,10.94,2.0441666666666669,41,0.79166666666666663,33,1.125,15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,25,1,3,2.375,10.039999999999999,2.0816666666666666,43,0.70833333333333337,33,1.125,15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"01:00:00",7,2.2083333333333335,8.9600000000000009,2.1266666666666665,41,0.79166666666666663,33,1.125,15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"02:00:00",7,2.2083333333333335,6.98,2.2091666666666665,39,0.875,34,1.0833333333333333,15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"03:00:00",3,2.375,6.08,2.2466666666666666,39,0.875,35,1.0416666666666667,17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"04:00:00",3,2.375,-4,2.6666666666666665,37.133800000000001,0.95275833333333326,35,1.0416666666666667,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"05:00:00",3,2.375,3.92,2.3366666666666664,37.133800000000001,0.95275833333333326,35,1.0416666666666667,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"06:00:00",0,2.5,-5.0800000000000054,2.7116666666666673,36,1,37,0.95833333333333337,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"07:00:00",0,2.5,-7.06,2.7941666666666669,37.133800000000001,0.95275833333333326,37,0.95833333333333337,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"08:00:00",0,2.5,-5.98,2.749166666666667,37.133800000000001,0.95275833333333326,38,0.91666666666666663,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"09:00:00",1,2.4583333333333335,5,2.2916666666666665,37.133800000000001,0.95275833333333326,39,0.875,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"10:00:00",5,2.2916666666666665,12.92,1.9616666666666667,37.133800000000001,0.95275833333333326,40,0.83333333333333337,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"11:00:00",10,2.0833333333333335,15.98,1.8341666666666665,37.133800000000001,0.95275833333333326,41,0.79166666666666663,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"12:00:00",18,1.75,17.059999999999999,1.7891666666666666,37.133800000000001,0.95275833333333326,41,0.79166666666666663,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"13:00:00",20,1.6666666666666667,19.04,1.7066666666666668,37.133800000000001,0.95275833333333326,43,0.70833333333333337,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"14:00:00",21,1.625,19.940000000000001,1.6691666666666667,37.133800000000001,0.95275833333333326,41,0.79166666666666663,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"15:00:00",21,1.625,19.940000000000001,1.6691666666666667,37,0.95833333333333337,43,0.70833333333333337,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"16:00:00",21,1.625,19.04,1.7066666666666668,36,1,39,0.875,33.979999999999997,1.0841666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"17:00:00",19,1.7083333333333333,15.98,1.8341666666666665,37.133800000000001,0.95275833333333326,39,0.875,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"18:00:00",19,1.7083333333333333,14,1.9166666666666667,37,0.95833333333333337,38,0.91666666666666663,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"19:00:00",19,1.7083333333333333,12.92,1.9616666666666667,36,1,37,0.95833333333333337,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"20:00:00",19,1.7083333333333333,8.9600000000000009,2.1266666666666665,34,1.0833333333333333,37,0.95833333333333337,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"21:00:00",19,1.7083333333333333,8.06,2.1641666666666666,32,1.1666666666666667,36,1,28.22,1.3241666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"22:00:00",19,1.7083333333333333,6.08,2.2466666666666666,32,1.1666666666666667,37,0.95833333333333337,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,"23:00:00",19,1.7083333333333333,5,2.2916666666666665,30,1.25,36,1,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,26,1,19,1.7083333333333333,3.02,2.3741666666666665,28,1.3333333333333333,36,1,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"01:00:00",19,{"$f":"IF(W8645<60,(60-W8645)/24,0)","v":1.7083333333333333},1.94,2.4191666666666669,28,1.3333333333333333,35,1.0416666666666667,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"02:00:00",19,1.7083333333333333,-3.9999999999999147E-2,{"$f":"IF(Y8646<60,(60-Y8646)/24,0)","v":2.5016666666666665},27,{"$f":"IF(AA8646<60,(60-AA8646)/24,0)","v":1.375},35,{"$f":"IF(AC8646<60,(60-AC8646)/24,0)","v":1.0416666666666667},28.4,{"$f":"IF(AE8646<60,(60-AE8646)/24,0)","v":1.3166666666666667}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"03:00:00",21,1.625,1.94,2.4191666666666669,27,1.375,35,1.0416666666666667,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"04:00:00",21,1.625,6.98,2.2091666666666665,27,1.375,35,1.0416666666666667,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"05:00:00",19,1.7083333333333333,10.94,2.0441666666666669,27,1.375,35,1.0416666666666667,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"06:00:00",21,1.625,12.92,1.9616666666666667,28,1.3333333333333333,36,1,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"07:00:00",21,1.625,12.92,1.9616666666666667,28,1.3333333333333333,36,1,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"08:00:00",21,1.625,14,1.9166666666666667,27,1.375,36,1,21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"09:00:00",27,1.375,15.98,1.8341666666666665,28,1.3333333333333333,36,1,21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"10:00:00",28,1.3333333333333333,17.96,1.7516666666666667,30,1.25,37,0.95833333333333337,21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"11:00:00",28,1.3333333333333333,19.940000000000001,1.6691666666666667,32,1.1666666666666667,38,0.91666666666666663,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"12:00:00",28,1.3333333333333333,24.08,1.4966666666666668,32,1.1666666666666667,37,0.95833333333333337,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"13:00:00",28,1.3333333333333333,26.06,1.4141666666666666,34,1.0833333333333333,37,0.95833333333333337,26.06,1.4141666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"14:00:00",28,1.3333333333333333,26.06,1.4141666666666666,36,1,39,0.875,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"15:00:00",28,1.3333333333333333,26.06,1.4141666666666666,36,1,39,0.875,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"16:00:00",28,1.3333333333333333,26.06,1.4141666666666666,36,1,37,0.95833333333333337,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"17:00:00",27,1.375,26.96,1.3766666666666667,34,1.0833333333333333,36,1,21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"18:00:00",27,1.375,26.06,1.4141666666666666,30,1.25,34,1.0833333333333333,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"19:00:00",27,1.375,26.06,1.4141666666666666,27,1.375,30,1.25,17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"20:00:00",27,1.375,26.06,1.4141666666666666,25,1.4583333333333333,30,1.25,14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"21:00:00",25,1.4583333333333333,24.08,1.4966666666666668,25,1.4583333333333333,30,1.25,14,1.9166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"22:00:00",25,1.4583333333333333,24.08,1.4966666666666668,23,1.5416666666666667,34,1.0833333333333333,12.2,1.9916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,"23:00:00",23,1.5416666666666667,26.06,1.4141666666666666,21,1.625,31,1.2083333333333333,12.2,1.9916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,27,1,21,1.625,24.08,1.4966666666666668,21,1.625,30,1.25,12.2,1.9916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"01:00:00",19,1.7083333333333333,19.04,1.7066666666666668,21,1.625,28,1.3333333333333333,10.4,2.0666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"02:00:00",21,1.625,17.96,1.7516666666666667,19,1.7083333333333333,27,1.375,10.4,2.0666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"03:00:00",21,1.625,12.92,1.9616666666666667,21,1.625,26,1.4166666666666667,8.6,2.1416666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"04:00:00",23,1.5416666666666667,10.039999999999999,2.0816666666666666,19,1.7083333333333333,25,1.4583333333333333,10.4,2.0666666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"05:00:00",23,1.5416666666666667,12.92,1.9616666666666667,19,1.7083333333333333,23,1.5416666666666667,8.6,2.1416666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"06:00:00",25,1.4583333333333333,12.02,1.9991666666666668,18,1.75,23,1.5416666666666667,6.8,2.2166666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"07:00:00",23,1.5416666666666667,10.039999999999999,2.0816666666666666,18,1.75,21,1.625,5,2.2916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"08:00:00",23,1.5416666666666667,10.039999999999999,2.0816666666666666,18,1.75,21,1.625,8.6,2.1416666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"09:00:00",25,1.4583333333333333,24.08,1.4966666666666668,19,1.7083333333333333,21,1.625,12.2,1.9916666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"10:00:00",25,1.4583333333333333,26.06,1.4141666666666666,21,1.625,23,1.5416666666666667,15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"11:00:00",27,1.375,28.04,1.3316666666666668,25,1.4583333333333333,25,1.4583333333333333,17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"12:00:00",28,1.3333333333333333,28.04,1.3316666666666668,28,1.3333333333333333,27,1.375,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"13:00:00",28,1.3333333333333333,28.04,1.3316666666666668,30,1.25,28,1.3333333333333333,21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"14:00:00",30,1.25,28.04,1.3316666666666668,34,1.0833333333333333,28,1.3333333333333333,21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"15:00:00",34,1.0833333333333333,28.04,1.3316666666666668,34,1.0833333333333333,30,1.25,21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"16:00:00",34,1.0833333333333333,24.98,1.4591666666666665,36,1,28,1.3333333333333333,21.38,1.6091666666666669]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"17:00:00",32,1.1666666666666667,23,1.5416666666666667,36,1,24,1.5,21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"18:00:00",32,1.1666666666666667,21.02,1.6241666666666668,37,0.95833333333333337,21,1.625,17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"19:00:00",32,1.1666666666666667,21.02,1.6241666666666668,34,1.0833333333333333,18,1.75,21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"20:00:00",30.157900000000001,1.2434208333333332,15.98,1.8341666666666665,34,1.0833333333333333,15,1.875,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"21:00:00",32,1.1666666666666667,8.06,2.1641666666666666,32,1.1666666666666667,12,2,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"22:00:00",32,1.1666666666666667,6.98,2.2091666666666665,32,1.1666666666666667,10,2.0833333333333335,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,"23:00:00",32,1.1666666666666667,5,2.2916666666666665,34,1.0833333333333333,9,2.125,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,28,1,34,1.0833333333333333,6.08,2.2466666666666666,34,1.0833333333333333,8,2.1666666666666665,17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"01:00:00",34,1.0833333333333333,3.02,2.3741666666666665,34,1.0833333333333333,8,2.1666666666666665,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"02:00:00",34,1.0833333333333333,-3.9999999999999147E-2,2.5016666666666665,34,1.0833333333333333,8,2.1666666666666665,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"03:00:00",34,1.0833333333333333,-2.02,2.5841666666666669,34,1.0833333333333333,7,2.2083333333333335,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"04:00:00",34,1.0833333333333333,-0.94000000000000483,2.539166666666667,34,1.0833333333333333,7,2.2083333333333335,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"05:00:00",34,1.0833333333333333,-4,2.6666666666666665,34,1.0833333333333333,6,2.25,17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"06:00:00",34,1.0833333333333333,-5.0800000000000054,2.7116666666666673,34,1.0833333333333333,7,2.2083333333333335,15.8,1.8416666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"07:00:00",34,1.0833333333333333,-5.98,2.749166666666667,34,1.0833333333333333,5,2.2916666666666665,17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"08:00:00",34,1.0833333333333333,-2.92,2.6216666666666666,34,1.0833333333333333,7,2.2083333333333335,17.600000000000001,1.7666666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"09:00:00",34.362499999999997,1.0682291666666668,3.02,2.3741666666666665,36,1,9,2.125,21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"10:00:00",36,1,8.06,2.1641666666666666,36,1,12,2,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"11:00:00",36,1,17.059999999999999,1.7891666666666666,37,0.95833333333333337,19,1.7083333333333333,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"12:00:00",36,1,24.08,1.4966666666666668,37.133800000000001,0.95275833333333326,21,1.625,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"13:00:00",36,1,26.06,1.4141666666666666,39,0.875,25,1.4583333333333333,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"14:00:00",36,1,28.04,1.3316666666666668,39,0.875,28,1.3333333333333333,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"15:00:00",37,0.95833333333333337,28.04,1.3316666666666668,41,0.79166666666666663,28,1.3333333333333333,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"16:00:00",36,1,28.04,1.3316666666666668,43,0.70833333333333337,30,1.25,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"17:00:00",36.362499999999997,{"$f":"IF(W8709<60,(60-W8709)/24,0)","v":0.98489583333333341},24.98,1.4591666666666665,39,0.875,30,1.25,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"18:00:00",36.362499999999997,0.98489583333333341,19.04,{"$f":"IF(Y8710<60,(60-Y8710)/24,0)","v":1.7066666666666668},43,{"$f":"IF(AA8710<60,(60-AA8710)/24,0)","v":0.70833333333333337},30,{"$f":"IF(AC8710<60,(60-AC8710)/24,0)","v":1.25},23,{"$f":"IF(AE8710<60,(60-AE8710)/24,0)","v":1.5416666666666667}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"19:00:00",37.389200000000002,0.9421166666666666,17.96,1.7516666666666667,41,0.79166666666666663,32,1.1666666666666667,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"20:00:00",43,0.70833333333333337,15.98,1.8341666666666665,39,0.875,30,1.25,21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"21:00:00",43,0.70833333333333337,17.96,1.7516666666666667,39,0.875,30,1.25,21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"22:00:00",41,0.79166666666666663,12.02,1.9991666666666668,39,0.875,30,1.25,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,"23:00:00",37,0.95833333333333337,10.94,2.0441666666666669,38,0.91666666666666663,29,1.2916666666666667,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,29,1,37,0.95833333333333337,8.06,2.1641666666666666,37,0.95833333333333337,30,1.25,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"01:00:00",37,0.95833333333333337,10.039999999999999,2.0816666666666666,36,1,30,1.25,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"02:00:00",36,1,8.9600000000000009,2.1266666666666665,37.133800000000001,0.95275833333333326,31,1.2083333333333333,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"03:00:00",32,1.1666666666666667,10.94,2.0441666666666669,37,0.95833333333333337,31,1.2083333333333333,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"04:00:00",30,1.25,10.94,2.0441666666666669,37,0.95833333333333337,32,1.1666666666666667,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"05:00:00",27,1.375,8.06,2.1641666666666666,36,1,32,1.1666666666666667,35.6,1.0166666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"06:00:00",25,1.4583333333333333,5,2.2916666666666665,34,1.0833333333333333,34,1.0833333333333333,37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"07:00:00",21,1.625,3.92,2.3366666666666664,34,1.0833333333333333,34,1.0833333333333333,37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"08:00:00",19,1.7083333333333333,3.02,2.3741666666666665,34,1.0833333333333333,34,1.0833333333333333,37.4,0.94166666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"09:00:00",18,1.75,6.98,2.2091666666666665,34,1.0833333333333333,34,1.0833333333333333,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"10:00:00",16,1.8333333333333333,21.92,1.5866666666666667,36,1,37,0.95833333333333337,41,0.79166666666666663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"11:00:00",16,1.8333333333333333,28.04,1.3316666666666668,36,1,37,0.95833333333333337,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"12:00:00",16,1.8333333333333333,30.02,1.2491666666666668,34,1.0833333333333333,36,1,46.4,0.56666666666666676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"13:00:00",12,2,30.92,1.2116666666666667,34,1.0833333333333333,36,1,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"14:00:00",12,2,30.92,1.2116666666666667,32,1.1666666666666667,36,1,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"15:00:00",10,2.0833333333333335,32,1.1666666666666667,30,1.25,34,1.0833333333333333,48.2,0.49166666666666653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"16:00:00",9,2.125,30.92,1.2116666666666667,30,1.25,32,1.1666666666666667,44.6,0.64166666666666661]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"17:00:00",9,2.125,28.94,1.2941666666666667,30,1.25,30,1.25,39.200000000000003,0.86666666666666659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"18:00:00",7,2.2083333333333335,28.04,1.3316666666666668,28,1.3333333333333333,30,1.25,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"19:00:00",5,2.2916666666666665,28.04,1.3316666666666668,27,1.375,28,1.3333333333333333,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"20:00:00",5,2.2916666666666665,26.06,1.4141666666666666,27,1.375,28,1.3333333333333333,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"21:00:00",5,2.2916666666666665,24.08,1.4966666666666668,25,1.4583333333333333,28,1.3333333333333333,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"22:00:00",3,2.375,21.02,1.6241666666666668,23,1.5416666666666667,28,1.3333333333333333,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,"23:00:00",3,2.375,15.08,1.8716666666666668,21,1.625,26,1.4166666666666667,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,30,1,3,2.375,15.98,1.8341666666666665,19,1.7083333333333333,24,1.5,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"01:00:00",1,2.4583333333333335,10.94,2.0441666666666669,19,1.7083333333333333,23,1.5416666666666667,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"02:00:00",1,2.4583333333333335,10.94,2.0441666666666669,18,1.75,23,1.5416666666666667,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"03:00:00",1,2.4583333333333335,15.98,1.8341666666666665,18,1.75,22,1.5833333333333333,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"04:00:00",1,2.4583333333333335,17.059999999999999,1.7891666666666666,18,1.75,21,1.625,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"05:00:00",1,2.4583333333333335,19.04,1.7066666666666668,18,1.75,20,1.6666666666666667,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"06:00:00",1,2.4583333333333335,19.940000000000001,1.6691666666666667,18,1.75,20,1.6666666666666667,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"07:00:00",1,2.4583333333333335,21.02,1.6241666666666668,18,1.75,19,1.7083333333333333,25.34,1.4441666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"08:00:00",0,2.5,23,1.5416666666666667,18,1.75,18,1.75,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"09:00:00",0,2.5,24.08,1.4966666666666668,18,1.75,18,1.75,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"10:00:00",0,2.5,26.96,1.3766666666666667,19,1.7083333333333333,18,1.75,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"11:00:00",0,2.5,30.02,1.2491666666666668,21,1.625,16,1.8333333333333333,30.2,1.2416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"12:00:00",0,2.5,35.06,1.0391666666666666,25,1.4583333333333333,16,1.8333333333333333,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"13:00:00",0,2.5,37.94,0.9191666666666668,27,1.375,14,1.9166666666666667,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"14:00:00",1,2.4583333333333335,39.92,0.83666666666666656,28,1.3333333333333333,14,1.9166666666666667,33.799999999999997,1.0916666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"15:00:00",1,2.4583333333333335,39.92,0.83666666666666656,28,1.3333333333333333,14,1.9166666666666667,32,1.1666666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"16:00:00",0,2.5,42.08,0.7466666666666667,28,1.3333333333333333,14,1.9166666666666667,28.4,1.3166666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"17:00:00",-4,2.6666666666666665,41,0.79166666666666663,27,1.375,10,2.0833333333333335,26.6,1.3916666666666666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"18:00:00",-8,2.8333333333333335,41,0.79166666666666663,27,1.375,9,2.125,24.8,1.4666666666666668]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"19:00:00",-8,2.8333333333333335,41,0.79166666666666663,27,1.375,7,2.2083333333333335,23,1.5416666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"20:00:00",-9,2.875,41,0.79166666666666663,27,1.375,7,2.2083333333333335,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"21:00:00",-9,2.875,39.020000000000003,0.87416666666666654,27,1.375,3,2.375,21.2,1.6166666666666665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"22:00:00",-9,2.875,39.020000000000003,0.87416666666666654,27,1.375,2,2.4166666666666665,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,"23:00:00",-9,2.875,35.96,1.0016666666666667,27,1.375,-1,2.5416666666666665,19.399999999999999,1.6916666666666667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,31,1,-9,2.875,37.04,0.95666666666666667,25,1.4583333333333333,-2,2.5833333333333335,19.399999999999999,1.6916666666666667]

{"sheet":"Compressed Air Inputs","index":6,"n_rows":63,"n_cols":22,"rows_kept":63,"cut":false,"hidden":false,"merged":[[29,8,29,9],[30,8,30,9],[31,8,31,9],[32,8,32,9],[24,8,24,9],[25,8,25,9],[26,8,26,9],[27,8,27,9],[28,8,28,9],[0,1,1,19],[30,11,30,12],[31,11,31,12],[32,11,32,12],[25,11,25,12],[26,11,26,12],[27,11,27,12],[28,11,28,12],[29,11,29,12],[25,17,26,17],[25,18,26,18],[27,17,28,17],[27,18,28,18],[3,1,3,2],[23,11,23,12],[24,11,24,12],[4,7,7,10],[3,4,3,5],[36,13,36,15],[36,16,37,16],[19,16,19,18],[27,16,28,16],[21,16,22,16],[23,16,24,16],[25,16,26,16],[21,18,22,18],[23,17,24,17],[23,18,24,18],[21,17,22,17],[21,8,21,9],[22,8,22,9],[23,8,23,9]]}
[null,"Compressed Air Systems: Input Sheet"]
[]
[]
[null,"Input Tables for Compressed Air Measures",null,null,"Key",null,null,"Instructions"]
[null,1,"Compressor System & Storage",null,null,"Input Cells",null,"Please fill out this Input Sheet with the facility's compressed air systems information (fill in all ORANGE cells) and as applicable to the measure selection on the \"Measure Summary\" tab. Include copy of the CAGI data sheet for reference, photos of compressor nameplate and setpoints and documentation of run hours or load profile if available. All compressed air measures will refer back to this sheet."]
[null,2,"Air Nozzle",null,null,"Calculation Cells"]
[null,3,"Zero Loss Condensate Drain",null,null,"Guidance/ Information Cells"]
[null,4,"Low Pressure Drop Filter & Added Storage"]
[null,5,"Compressed Air Leak Detection"]
[null,6,"New Air Compressor"]
[null,7,"New Refrigerate Air Dryer"]
[]
[null,"Table 1: Existing Compressed Air System Inputs",null,null,null,null,null,null,null,null,"Existing Case Operating Inputs",null,null,null,null,null,null,null,null,null,null,"Compressor Type Options"]
[null,null,"Compressor",null,"CAGI ",null,null,"Air Compressor","Baseload","Control","Annual Run","Load Profile - % time at each load",null,null,null,"Pressure","Storage",null,null,null,null,"Load / No Load"]
[null,"No.","Manufacturer","Model","hp","cfm","kW","Type","or Trim","Type","Hours",0.25,0.5,0.75,1,"(psi)","(gallons)",null,null,null,null,"Modulating"]
[null,1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Turn Valve"]
[null,2,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Variable Speed"]
[null,3]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Annual Run Hour Estimation ",null,null,null,null,"Pipe Diameter Options"]
[null,"Table 2: Air Nozzle ECM Inputs",null,null,null,null,null,null,null,null,null,"Table 3: Zero Loss Condensate Drain ECM Inputs",null,null,null,null,"Shift:","Hours:","Notes:",null,null,0.5]
[null,"Nozzle",null,null,null,"Existing","Proposed",null,"End Use",null,null,"Drain",null,"Pipe","Drain",null,"Single shift (8/5)",1976,"7 AM – 3 PM, weekdays, minus some holidays and scheduled down time",null,null,0.75]
[null,"ID","Manufacturer","Model","Qty","cfm","cfm","hrs/yr","Description",null,null,"Location",null,"Diameter","Hours",null,null,null,null,null,null,1]
[null,1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"2-shift (16/5)",3952,"7AM – 11 PM, weekdays, minus some holidays and scheduled down time",null,null,1.25]
[null,2,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.5]
[null,3,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3-shift (24/5)",5928,"24 hours per day, weekdays, minus some holidays and scheduled down time",null,null,1.75]
[null,4,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2]
[null,5,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"4-shift (24/7)",8320,"24 hours per day, 7 days a week minus some holidays and scheduled down time",null,null,2.5]
[null,6,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3]
[null,7,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.5]
[null,8,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4]
[null,9]
[null,10]
[]
[]
[null,"Table 4: Additional Storage and Low Pressure Drop Filter ECM Inputs",null,null,null,null,null,"Table 5: Compressed Air Leak Detection ECM Inputs",null,null,null,null,null,"Table 6: New Air Compressor Inputs"]
[null,"Total Storage (if new storage added)",null,null,"gallons",null,null,"ID","# Of Leaks","Leakage CFM known?","CFM Leak","dB reading",null,"Compressor",null,null,"Is it an oil flooded, rotary screw compressor with Variable Speed Drive or Variable Displacement capacity control?"]
[null,"Pressure (if pressure reduced w/new storage)",null,null,"psi",null,null,1,null,null,null,null,null,"No.","Manufacturer","Model",null,"CAGI hp","Annual Run Hours"]
[null,"# of Low Pressure Drop Filters Installed",null,null,null,null,null,2,null,null,null,null,null,1]
[null,"Baseline System Pressure drop",null,null,null,null,null,3,null,null,null,null,null,2]
[null,"System Pressure drop w/low pressure drop filters",null,null,"psi",null,null,4,null,null,null,null,null,3]
[null,null,null,null,null,null,null,5]
[null,null,null,null,null,null,null,6,null,null,null,null,null,"Table 7: New Refrigerated Air Dryer Inputs"]
[null,null,null,null,null,null,null,7,null,null,null,null,null,"Compressor",null,null,"CAGI ","Annual ","VFD-Equipped?"]
[null,null,null,null,null,null,null,8,null,null,null,null,null,"No.","Manufacturer","Model","CFM","Run Hours"]
[null,null,null,null,null,null,null,9,null,null,null,null,null,1]
[null,null,null,null,null,null,null,10,null,null,null,null,null,2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"`"]

{"sheet":"CompAir1-Storage","index":7,"n_rows":30,"n_cols":30,"rows_kept":30,"cut":false,"hidden":true,"merged":[[9,27,9,29],[21,1,21,13],[5,1,7,2],[1,21,1,25],[2,16,2,19],[11,21,11,25],[21,21,21,25],[0,1,1,13],[3,1,3,4],[3,6,3,13],[8,1,8,2],[9,1,9,2],[10,1,10,2],[14,6,17,13],[4,6,13,13]]}
[null,"Measure: Adding Compressor Storage"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 4: kW base calculations for Comp 1"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 2: % kW values",null,null,null,null,"gal/cfm",{"$f":"+'Compressed Air Inputs'!Q16/'Compressed Air Inputs'!F16","v":{"$error":"#DIV/0!"}},null,{"$f":"+'Compressed Air Inputs'!D37/'Compressed Air Inputs'!F16","v":{"$error":"#DIV/0!"}}]
[null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,null,null,null,"Helper","%","Tank plus Distribution Storage","%",null,"%","Baseline",null,"Proposed"]
[null,null,null,"Value","Unit",null,"Adding storage capacity to compressed air systems with previously insufficient storage results in less system pressure fluctuations and allows lower average system pressures, leading to air compressor energy savings when operated at lower system pressures. It also reduces cycling losses in compressor systems that use a compressor with load-unload controls for part-load modulation.\n\nResults: \nkWpr: Average kW savings from the system pressure reduction\nkWhpr: Gross annual kWh savings from system pressure reduction\nkWcl: Average kW savings from the reduction in cycling losses for load/unload compressors\nkWhcl: Gross annual kWh savings from the reduction in cycling losses for load/unload compressors",null,null,null,null,null,null,null,null,null,"Column","Load","gal/cfm","kW",null,"Load","% kW","kW","% kW","kW"]
[null,"Total Savings",null,{"$f":"SUM(K29,M29)","v":0},"kW",null,null,null,null,null,null,null,null,null,null,null,{"$f":"R6&S6","v":"0.251"},0.25,1,0.7,null,0.25,{"$f":"MIN($T$6,IF(W$3<$S$7,TREND($T$6:$T$7,$S$6:$S$7,W$3),IF(W$3<$S$8,TREND($T$7:$T$8,$S$7:$S$8,W$3),IF(W$3<$S$9,TREND($T$8:$T$9,$S$8:$S$9,W$3),$T$9))))","v":{"$error":"#DIV/0!"}},{"$f":"+W6*'Compressed Air Inputs'!$G$16","v":{"$error":"#DIV/0!"}},{"$f":"MIN($T$6,IF(Y$3<$S$7,TREND($T$6:$T$7,$S$6:$S$7,Y$3),IF(Y$3<$S$8,TREND($T$7:$T$8,$S$7:$S$8,Y$3),IF(Y$3<$S$9,TREND($T$8:$T$9,$S$8:$S$9,Y$3),$T$9))))","v":{"$error":"#DIV/0!"}},{"$f":"+Y6*'Compressed Air Inputs'!$G$16","v":{"$error":"#DIV/0!"}}]
[null,null,null,{"$f":"SUM(L29,N29)","v":0},"kWh",null,null,null,null,null,null,null,null,null,null,null,{"$f":"R7&S7","v":"0.253"},0.25,3,0.55000000000000004,null,0.5,{"$f":"MIN($T$10,IF($W$3<$S$11,TREND($T$10:$T$11,$S$10:$S$11,$W$3),IF($W$3<$S$12,TREND($T$11:$T$12,$S$11:$S$12,$W$3),IF($W$3<$S$13,TREND($T$12:$T$13,$S$12:$S$13,$W$3),$T$13))))","v":{"$error":"#DIV/0!"}},{"$f":"+W7*'Compressed Air Inputs'!$G$16","v":{"$error":"#DIV/0!"}},{"$f":"MIN($T$10,IF($Y$3<$S$11,TREND($T$10:$T$11,$S$10:$S$11,$Y$3),IF($Y$3<$S$12,TREND($T$11:$T$12,$S$11:$S$12,$Y$3),IF($Y$3<$S$13,TREND($T$12:$T$13,$S$12:$S$13,$Y$3),$T$13))))","v":{"$error":"#DIV/0!"}},{"$f":"+Y7*'Compressed Air Inputs'!$G$16","v":{"$error":"#DIV/0!"}}]
[null,null,null,0,"MMBtu",null,null,null,null,null,null,null,null,null,null,null,"0.255",0.25,5,0.5,null,0.75,{"$f":"MIN($T$14,IF($W$3<$S$15,TREND($T$14:$T$15,$S$14:$S$15,$W$3),IF($W$3<$S$16,TREND($T$15:$T$16,$S$15:$S$16,$W$3),IF($W$3<$S$17,TREND($T$16:$T$17,$S$16:$S$17,$W$3),$T$17))))","v":{"$error":"#DIV/0!"}},{"$f":"+W8*'Compressed Air Inputs'!$G$16","v":{"$error":"#DIV/0!"}},{"$f":"MIN($T$14,IF($Y$3<$S$15,TREND($T$14:$T$15,$S$14:$S$15,$Y$3),IF($Y$3<$S$16,TREND($T$15:$T$16,$S$15:$S$16,$Y$3),IF($Y$3<$S$17,TREND($T$16:$T$17,$S$16:$S$17,$Y$3),$T$17))))","v":{"$error":"#DIV/0!"}},{"$f":"+Y8*'Compressed Air Inputs'!$G$16","v":{"$error":"#DIV/0!"}}]
[null,"Measure Life",null,17,"Years",null,null,null,null,null,null,null,null,null,null,null,"0.2510",0.25,10,0.48,null,1,1,{"$f":"+W9*'Compressed Air Inputs'!$G$16","v":0},1,{"$f":"+Y9*'Compressed Air Inputs'!$G$16","v":0}]
[null,"CFsp",null,{"$f":"S21*100","v":117},"%",null,null,null,null,null,null,null,null,null,null,null,"0.51",0.5,1,0.88,null,"Avg kW",null,{"$f":"(X6*'Compressed Air Inputs'!L16+'CompAir1-Storage'!X7*'Compressed Air Inputs'!M16+'CompAir1-Storage'!X8*'Compressed Air Inputs'!N16+'CompAir1-Storage'!X9*'Compressed Air Inputs'!O16)","v":{"$error":"#DIV/0!"}},null,{"$f":"(Z6*'Compressed Air Inputs'!L16+'CompAir1-Storage'!Z7*'Compressed Air Inputs'!M16+'CompAir1-Storage'!Z8*'Compressed Air Inputs'!N16+'CompAir1-Storage'!Z9*'Compressed Air Inputs'!O16)","v":{"$error":"#DIV/0!"}},null,"Table 7: Summary Table kW base"]
[null,"CFwp",null,{"$f":"T21*100","v":98},"%",null,null,null,null,null,null,null,null,null,null,null,"0.53",0.5,3,0.76,null,null,null,null,null,null,null,"Comp","kW base","kW proposed"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"0.55",0.5,5,0.71,null,"Table 5: kW base calculations for Comp 2",null,null,null,null,null,1,{"$f":"X10","v":{"$error":"#DIV/0!"}},{"$f":"Z10","v":{"$error":"#DIV/0!"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"0.510",0.5,10,0.68,null,"gal/cfm",{"$f":"IFERROR('Compressed Air Inputs'!Q17/'Compressed Air Inputs'!F17,\"-\")","v":"-"},null,{"$f":"IFERROR('Compressed Air Inputs'!S17/'Compressed Air Inputs'!F17,\"-\")","v":"-"},null,null,2,{"$f":"X20","v":0},{"$f":"Z20","v":0}]
[null,"Compressed Air - Adding Compressor Storage",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"0.751",0.75,1,0.96,null,"%","Baseline",null,"Proposed",null,null,3,{"$f":"X30","v":0},{"$f":"Z30","v":0}]
[null,"Measure Code",null,"COM-CA-CS",null,null,"NOTE: For more information on this measure refer to the NH TRM. ",null,null,null,null,null,null,null,null,null,"0.753",0.75,3,0.92,null,"Load","% kW","kW","% kW","kW"]
[null,"Market",null,"Commercial",null,null,null,null,null,null,null,null,null,null,null,null,"0.755",0.75,5,0.89,null,0.25,{"$f":"MIN($T$6,IF(W$13<$S$7,TREND($T$6:$T$7,$S$6:$S$7,W$13),IF(W$13<$S$8,TREND($T$7:$T$8,$S$7:$S$8,W$13),IF(W$13<$S$9,TREND($T$8:$T$9,$S$8:$S$9,W$13),$T$9))))","v":0.48},{"$f":"+W16*'Compressed Air Inputs'!$G$17","v":0},{"$f":"MIN($T$6,IF(Y$13<$S$7,TREND($T$6:$T$7,$S$6:$S$7,Y$13),IF(Y$13<$S$8,TREND($T$7:$T$8,$S$7:$S$8,Y$13),IF(Y$13<$S$9,TREND($T$8:$T$9,$S$8:$S$9,Y$13),$T$9))))","v":0.48},{"$f":"+Y16*'Compressed Air Inputs'!$G$17","v":0}]
[null,"Program Type",null,"Retrofit",null,null,null,null,null,null,null,null,null,null,null,null,"0.7510",0.75,10,0.86,null,0.5,{"$f":"MIN($T$10,IF($W$13<$S$11,TREND($T$10:$T$11,$S$10:$S$11,$W$13),IF($W$13<$S$12,TREND($T$11:$T$12,$S$11:$S$12,$W$13),IF($W$13<$S$13,TREND($T$12:$T$13,$S$12:$S$13,$W$13),$T$13))))","v":0.68},{"$f":"+W17*'Compressed Air Inputs'!$G$17","v":0},{"$f":"MIN($T$10,IF($Y$13<$S$11,TREND($T$10:$T$11,$S$10:$S$11,$Y$13),IF($Y$13<$S$12,TREND($T$11:$T$12,$S$11:$S$12,$Y$13),IF($Y$13<$S$13,TREND($T$12:$T$13,$S$12:$S$13,$Y$13),$T$13))))","v":0.68},{"$f":"+Y17*'Compressed Air Inputs'!$G$17","v":0}]
[null,"Category",null,"Compressed Air",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.75,{"$f":"MIN($T$14,IF($W$13<$S$15,TREND($T$14:$T$15,$S$14:$S$15,$W$13),IF($W$13<$S$16,TREND($T$15:$T$16,$S$15:$S$16,$W$13),IF($W$13<$S$17,TREND($T$16:$T$17,$S$16:$S$17,$W$13),$T$17))))","v":0.86},{"$f":"+W18*'Compressed Air Inputs'!$G$17","v":0},{"$f":"MIN($T$14,IF($Y$13<$S$15,TREND($T$14:$T$15,$S$14:$S$15,$Y$13),IF($Y$13<$S$16,TREND($T$15:$T$16,$S$15:$S$16,$Y$13),IF($Y$13<$S$17,TREND($T$16:$T$17,$S$16:$S$17,$Y$13),$T$17))))","v":0.86},{"$f":"+Y18*'Compressed Air Inputs'!$G$17","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 3: Coincidence Factors",null,null,null,1,1,{"$f":"+W19*'Compressed Air Inputs'!$G$17","v":0},1,{"$f":"+Y19*'Compressed Air Inputs'!$G$17","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Program","CFsp","CFwp",null,"Avg kW",null,{"$f":"(X16*'Compressed Air Inputs'!L17+'CompAir1-Storage'!X17*'Compressed Air Inputs'!M17+'CompAir1-Storage'!X18*'Compressed Air Inputs'!N17+'CompAir1-Storage'!X19*'Compressed Air Inputs'!O17)","v":0},null,{"$f":"(Z16*'Compressed Air Inputs'!L17+'CompAir1-Storage'!Z17*'Compressed Air Inputs'!M17+'CompAir1-Storage'!Z18*'Compressed Air Inputs'!N17+'CompAir1-Storage'!Z19*'Compressed Air Inputs'!O17)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"LBES, SBES, Muni",1.17,0.98]
[null,"Table 1: Calculating Primary Energy Impact ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 6: kW base calculations for Comp 3"]
[null,null,"Inputs",null,null,null,null,null,null,null,"Savings",null,null,null,null,null,null,null,null,null,null,"gal/cfm",{"$f":"IFERROR(+'Compressed Air Inputs'!Q18/'Compressed Air Inputs'!F18,\"-\")","v":"-"},null,{"$f":"IFERROR('Compressed Air Inputs'!S18/'Compressed Air Inputs'!F18,\"-\")","v":"-"}]
[null,null,"Model","Base case",null,"Proposed",null,null,"Annual",null,"Pressure Reduction",null,"Cycling Savings",null,null,null,null,null,null,null,null,"%","Baseline",null,"Proposed"]
[null,null,"No.","kWbase","psibase","psiEE","kWpsi, ee","kWcycling","Hours",null,"kW","kWh","kW","kWh",null,null,null,null,null,null,null,"Load","% kW","kW","% kW","kW"]
[null,1,{"$f":"'Compressed Air Inputs'!D16","v":0},{"$f":"IFERROR(AC12,\"\")","v":""},{"$f":"'Compressed Air Inputs'!$P$16","v":0},{"$f":"'Compressed Air Inputs'!$D$38","v":0},{"$f":"IF(F26>0,D26-(D26*(E26-F26)*0.004),D26)","v":""},{"$f":"IF(F26>0,IFERROR(AD12-AD12*(E26-F26)*0.004,\"\"),AD12)","v":{"$error":"#DIV/0!"}},{"$f":"'Compressed Air Inputs'!K16","v":0},null,{"$f":"IFERROR((D26*(E26-F26)*0.004),\"\")","v":""},{"$f":"IFERROR(K26*I26,\"\")","v":""},{"$f":"IFERROR(IF('Compressed Air Inputs'!I16=\"Baseload\",0,(G26-H26)),\"\")","v":""},{"$f":"IFERROR(M26*I26,\"\")","v":""},null,null,null,null,null,null,null,0.25,{"$f":"MIN($T$6,IF(W$23<$S$7,TREND($T$6:$T$7,$S$6:$S$7,W$23),IF(W$23<$S$8,TREND($T$7:$T$8,$S$7:$S$8,W$23),IF(W$23<$S$9,TREND($T$8:$T$9,$S$8:$S$9,W$23),$T$9))))","v":0.48},{"$f":"+W26*'Compressed Air Inputs'!$G$18","v":0},{"$f":"MIN($T$6,IF(Y$23<$S$7,TREND($T$6:$T$7,$S$6:$S$7,Y$23),IF(Y$23<$S$8,TREND($T$7:$T$8,$S$7:$S$8,Y$23),IF(Y$23<$S$9,TREND($T$8:$T$9,$S$8:$S$9,Y$23),$T$9))))","v":0.48},{"$f":"+Y26*'Compressed Air Inputs'!$G$18","v":0}]
[null,2,{"$f":"'Compressed Air Inputs'!D17","v":0},0,{"$f":"'Compressed Air Inputs'!$P$16","v":0},{"$f":"'Compressed Air Inputs'!$D$38","v":0},{"$f":"IF(F27>0,D27-(D27*(E27-F27)*0.004),D27)","v":0},{"$f":"IF(F27>0,IFERROR(AD13-AD13*(E27-F27)*0.004,\"\"),AD13)","v":0},{"$f":"'Compressed Air Inputs'!K17","v":0},null,{"$f":"IFERROR((D27*(E27-F27)*0.004),\"\")","v":0},{"$f":"IFERROR(K27*I27,\"\")","v":0},{"$f":"IFERROR(IF('Compressed Air Inputs'!I17=\"Baseload\",0,(G27-H27)),\"\")","v":0},{"$f":"IFERROR(M27*I27,\"\")","v":0},null,null,null,null,null,null,null,0.5,{"$f":"MIN($T$10,IF($W$23<$S$11,TREND($T$10:$T$11,$S$10:$S$11,$W$23),IF($W$23<$S$12,TREND($T$11:$T$12,$S$11:$S$12,$W$23),IF($W$23<$S$13,TREND($T$12:$T$13,$S$12:$S$13,$W$23),$T$13))))","v":0.68},{"$f":"+W27*'Compressed Air Inputs'!$G$18","v":0},{"$f":"MIN($T$10,IF($Y$23<$S$11,TREND($T$10:$T$11,$S$10:$S$11,$Y$23),IF($Y$23<$S$12,TREND($T$11:$T$12,$S$11:$S$12,$Y$23),IF($Y$23<$S$13,TREND($T$12:$T$13,$S$12:$S$13,$Y$23),$T$13))))","v":0.68},{"$f":"+Y27*'Compressed Air Inputs'!$G$18","v":0}]
[null,3,{"$f":"'Compressed Air Inputs'!D18","v":0},0,{"$f":"'Compressed Air Inputs'!$P$16","v":0},{"$f":"'Compressed Air Inputs'!$D$38","v":0},0,0,{"$f":"'Compressed Air Inputs'!K18","v":0},null,{"$f":"IFERROR((D28*(E28-F28)*0.004),\"\")","v":0},{"$f":"IFERROR(K28*I28,\"\")","v":0},{"$f":"IFERROR(IF('Compressed Air Inputs'!I18=\"Baseload\",0,(G28-H28)),\"\")","v":0},{"$f":"IFERROR(M28*I28,\"\")","v":0},null,null,null,null,null,null,null,0.75,{"$f":"MIN($T$14,IF($W$23<$S$15,TREND($T$14:$T$15,$S$14:$S$15,$W$23),IF($W$23<$S$16,TREND($T$15:$T$16,$S$15:$S$16,$W$23),IF($W$23<$S$17,TREND($T$16:$T$17,$S$16:$S$17,$W$23),$T$17))))","v":0.86},{"$f":"+W28*'Compressed Air Inputs'!$G$18","v":0},{"$f":"MIN($T$14,IF($Y$23<$S$15,TREND($T$14:$T$15,$S$14:$S$15,$Y$23),IF($Y$23<$S$16,TREND($T$15:$T$16,$S$15:$S$16,$Y$23),IF($Y$23<$S$17,TREND($T$16:$T$17,$S$16:$S$17,$Y$23),$T$17))))","v":0.86},{"$f":"+Y28*'Compressed Air Inputs'!$G$18","v":0}]
[null,null,"Totals",null,null,null,null,null,null,null,{"$f":"SUM(K26:K28)","v":0},{"$f":"SUM(L26:L28)","v":0},0,0,null,null,null,null,null,null,null,1,1,{"$f":"+W29*'Compressed Air Inputs'!$G$18","v":0},1,{"$f":"+Y29*'Compressed Air Inputs'!$G$18","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Avg kW",null,{"$f":"(X26*'Compressed Air Inputs'!L18+'CompAir1-Storage'!X27*'Compressed Air Inputs'!M18+'CompAir1-Storage'!X28*'Compressed Air Inputs'!N18+'CompAir1-Storage'!X29*'Compressed Air Inputs'!O18)","v":0},null,{"$f":"(Z26*'Compressed Air Inputs'!L18+'CompAir1-Storage'!Z27*'Compressed Air Inputs'!M18+'CompAir1-Storage'!Z28*'Compressed Air Inputs'!N18+'CompAir1-Storage'!Z29*'Compressed Air Inputs'!O18)","v":0}]

{"sheet":"CompAir2-Nozzle","index":8,"n_rows":34,"n_cols":17,"rows_kept":34,"cut":false,"hidden":true,"merged":[[23,14,23,16],[2,14,2,16],[6,14,6,16],[20,1,20,11],[21,10,21,11],[13,1,13,2],[13,3,13,4],[13,6,16,11],[14,1,14,2],[14,3,14,4],[15,1,15,2],[15,3,15,4],[16,1,16,2],[16,3,16,4],[13,14,13,15],[0,1,1,11],[3,1,3,4],[3,6,3,11],[4,6,12,11],[5,1,7,2],[8,1,8,2],[9,1,9,2],[10,1,10,2],[12,1,12,4]]}
[null,"Measure: Air Nozzles"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 2: Coincidence Factors"]
[null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,null,"Program","CFsp","CFwp"]
[null,null,null,"Value","Unit",null,"This measure covers the installation of engineered air nozzles which provide effective air nozzle action while reducing compressed air system air flow.",null,null,null,null,null,null,null,"LBES, SBES, Muni",0.8,0.54]
[null,"Total Savings",null,{"$f":"SUM(K34)","v":0},"kW"]
[null,null,null,{"$f":"L34","v":0},"kWh",null,null,null,null,null,null,null,null,null,"Table 3: kW/cfm"]
[null,null,null,0,"MMBtu",null,null,null,null,null,null,null,null,null,"No.","Compressor Type","kW/cfm"]
[null,"Measure Life",null,13,"Years",null,null,null,null,null,null,null,null,null,1,{"$f":"'Compressed Air Inputs'!I16","v":0},{"$f":"'Compressed Air Inputs'!G16/'Compressed Air Inputs'!F16","v":{"$error":"#DIV/0!"}}]
[null,"CFsp",null,{"$f":"P5*100","v":80},"%",null,null,null,null,null,null,null,null,null,2,{"$f":"'Compressed Air Inputs'!I17","v":0},{"$f":"'Compressed Air Inputs'!G17/'Compressed Air Inputs'!F17","v":{"$error":"#DIV/0!"}}]
[null,"CFwp",null,{"$f":"Q5*100","v":54},"%",null,null,null,null,null,null,null,null,null,3,{"$f":"'Compressed Air Inputs'!I18","v":0},{"$f":"'Compressed Air Inputs'!G18/'Compressed Air Inputs'!F18","v":{"$error":"#DIV/0!"}}]
[]
[null,"Compressed Air - Air Nozzles"]
[null,"Measure Code",null,"COM-CA-AN",null,null,"NOTE: For more information on this measure refer to the NH TRM.",null,null,null,null,null,null,null,"Table 4: kW/CFM Default Values"]
[null,"Market",null,"Commercial",null,null,null,null,null,null,null,null,null,null,"Air Compressor Type","SAVE ( kW/CFM)"]
[null,"Program Type",null,"Retrofit",null,null,null,null,null,null,null,null,null,null,"Single-acting Reciprocating",0.23]
[null,"Category",null,"Compressed Air",null,null,null,null,null,null,null,null,null,null,"Double-acting Reciprocating",0.155]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Lubricant-injected Rotary Screw (Single Stage)",0.185]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Lubricant-injected Rotary Screw (Double Stage)",0.16500000000000001]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Lubricant-free Rotary Screw",0.2]
[null,"Table 1: Calculating Primary Energy Impact ",null,null,null,null,null,null,null,null,null,null,null,null,"Centrifugal ",0.18]
[null,null,"Inputs",null,null,null,null,null,null,null,"Savings",null,null,null,"Other",0.19]
[null,null,"Quantity","Air Nozzle Model No. ","FLOWbase (CFM)","FLOWEE (CFM)","kW/cfm","hours/year",null,null,"kW","kWh"]
[null,1,{"$f":"+'Compressed Air Inputs'!E24","v":0},{"$f":"IF('Compressed Air Inputs'!I24=\"\",\"\",'Compressed Air Inputs'!I24)","v":""},{"$f":"IFERROR(IF(OR(ISBLANK(D24)),\"\",'Compressed Air Inputs'!F24),\"Error: fill in Input Sheet\")","v":0},{"$f":"IFERROR(IF(OR(ISBLANK(D24)),\"\",'Compressed Air Inputs'!G24),\"Error: fill in Input Sheet\")","v":0},{"$f":"IFERROR(IFERROR(VLOOKUP(\"Trim\",$P$9:$Q$11,2,FALSE),VLOOKUP(\"Trim\",$P$26:$Q$28,2,FALSE)),IFERROR(Q9,Q26))","v":""},{"$f":"IFERROR(IF(OR(ISBLANK(D24)),\"\",'Compressed Air Inputs'!H24),\"Error: fill in Input Sheet\")","v":0},null,null,{"$f":"IFERROR((E24-F24)*G24*C24,\"\")","v":""},{"$f":"IFERROR(K24*H24,\"\")","v":""},null,null,"Table 5: kW/cfm Backup"]
[null,2,{"$f":"+'Compressed Air Inputs'!E25","v":0},{"$f":"IF('Compressed Air Inputs'!I25=\"\",\"\",'Compressed Air Inputs'!I25)","v":""},{"$f":"IFERROR(IF(OR(ISBLANK(D25)),\"\",'Compressed Air Inputs'!F25),\"Error: fill in Input Sheet\")","v":0},{"$f":"IFERROR(IF(OR(ISBLANK(D25)),\"\",'Compressed Air Inputs'!G25),\"Error: fill in Input Sheet\")","v":0},{"$f":"IFERROR(IFERROR(VLOOKUP(\"Trim\",$P$9:$Q$11,2,FALSE),VLOOKUP(\"Trim\",$P$26:$Q$28,2,FALSE)),IFERROR(Q10,Q27))","v":""},{"$f":"IFERROR(IF(OR(ISBLANK(D25)),\"\",'Compressed Air Inputs'!H25),\"Error: fill in Input Sheet\")","v":0},null,null,"","",null,null,"No.","Compressor Type","kW/cfm"]
[null,3,{"$f":"+'Compressed Air Inputs'!E26","v":0},{"$f":"IF('Compressed Air Inputs'!I26=\"\",\"\",'Compressed Air Inputs'!I26)","v":""},{"$f":"IFERROR(IF(OR(ISBLANK(D26)),\"\",'Compressed Air Inputs'!F26),\"Error: fill in Input Sheet\")","v":0},{"$f":"IFERROR(IF(OR(ISBLANK(D26)),\"\",'Compressed Air Inputs'!G26),\"Error: fill in Input Sheet\")","v":0},"",{"$f":"IFERROR(IF(OR(ISBLANK(D26)),\"\",'Compressed Air Inputs'!H26),\"Error: fill in Input Sheet\")","v":0},null,null,"","",null,null,1,{"$f":"'Compressed Air Inputs'!I16","v":0},{"$f":"IFERROR(VLOOKUP('Compressed Air Inputs'!H16,$O$16:$P$22,2,FALSE),\"\")","v":""}]
[null,4,{"$f":"+'Compressed Air Inputs'!E27","v":0},{"$f":"IF('Compressed Air Inputs'!I27=\"\",\"\",'Compressed Air Inputs'!I27)","v":""},{"$f":"IFERROR(IF(OR(ISBLANK(D27)),\"\",'Compressed Air Inputs'!F27),\"Error: fill in Input Sheet\")","v":0},{"$f":"IFERROR(IF(OR(ISBLANK(D27)),\"\",'Compressed Air Inputs'!G27),\"Error: fill in Input Sheet\")","v":0},0,{"$f":"IFERROR(IF(OR(ISBLANK(D27)),\"\",'Compressed Air Inputs'!H27),\"Error: fill in Input Sheet\")","v":0},null,null,0,0,null,null,2,{"$f":"'Compressed Air Inputs'!I17","v":0},{"$f":"IFERROR(VLOOKUP('Compressed Air Inputs'!H17,$O$16:$P$22,2,FALSE),\"\")","v":""}]
[null,5,{"$f":"+'Compressed Air Inputs'!E28","v":0},{"$f":"IF('Compressed Air Inputs'!I28=\"\",\"\",'Compressed Air Inputs'!I28)","v":""},{"$f":"IFERROR(IF(OR(ISBLANK(D28)),\"\",'Compressed Air Inputs'!F28),\"Error: fill in Input Sheet\")","v":0},{"$f":"IFERROR(IF(OR(ISBLANK(D28)),\"\",'Compressed Air Inputs'!G28),\"Error: fill in Input Sheet\")","v":0},0,{"$f":"IFERROR(IF(OR(ISBLANK(D28)),\"\",'Compressed Air Inputs'!H28),\"Error: fill in Input Sheet\")","v":0},null,null,0,0,null,null,3,{"$f":"'Compressed Air Inputs'!I18","v":0},{"$f":"IFERROR(VLOOKUP('Compressed Air Inputs'!H18,$O$16:$P$22,2,FALSE),\"\")","v":""}]
[null,6,{"$f":"+'Compressed Air Inputs'!E29","v":0},{"$f":"IF('Compressed Air Inputs'!I29=\"\",\"\",'Compressed Air Inputs'!I29)","v":""},{"$f":"IFERROR(IF(OR(ISBLANK(D29)),\"\",'Compressed Air Inputs'!F29),\"Error: fill in Input Sheet\")","v":0},{"$f":"IFERROR(IF(OR(ISBLANK(D29)),\"\",'Compressed Air Inputs'!G29),\"Error: fill in Input Sheet\")","v":0},0,{"$f":"IFERROR(IF(OR(ISBLANK(D29)),\"\",'Compressed Air Inputs'!H29),\"Error: fill in Input Sheet\")","v":0},null,null,0,0]
[null,7,{"$f":"+'Compressed Air Inputs'!E30","v":0},{"$f":"IF('Compressed Air Inputs'!I30=\"\",\"\",'Compressed Air Inputs'!I30)","v":""},{"$f":"IFERROR(IF(OR(ISBLANK(D30)),\"\",'Compressed Air Inputs'!F30),\"Error: fill in Input Sheet\")","v":0},{"$f":"IFERROR(IF(OR(ISBLANK(D30)),\"\",'Compressed Air Inputs'!G30),\"Error: fill in Input Sheet\")","v":0},0,{"$f":"IFERROR(IF(OR(ISBLANK(D30)),\"\",'Compressed Air Inputs'!H30),\"Error: fill in Input Sheet\")","v":0},null,null,0,0]
[null,8,{"$f":"+'Compressed Air Inputs'!E31","v":0},{"$f":"IF('Compressed Air Inputs'!I31=\"\",\"\",'Compressed Air Inputs'!I31)","v":""},{"$f":"IFERROR(IF(OR(ISBLANK(D31)),\"\",'Compressed Air Inputs'!F31),\"Error: fill in Input Sheet\")","v":0},{"$f":"IFERROR(IF(OR(ISBLANK(D31)),\"\",'Compressed Air Inputs'!G31),\"Error: fill in Input Sheet\")","v":0},0,{"$f":"IFERROR(IF(OR(ISBLANK(D31)),\"\",'Compressed Air Inputs'!H31),\"Error: fill in Input Sheet\")","v":0},null,null,0,0]
[null,9,{"$f":"+'Compressed Air Inputs'!E32","v":0},{"$f":"IF('Compressed Air Inputs'!I32=\"\",\"\",'Compressed Air Inputs'!I32)","v":""},{"$f":"IFERROR(IF(OR(ISBLANK(D32)),\"\",'Compressed Air Inputs'!F32),\"Error: fill in Input Sheet\")","v":0},{"$f":"IFERROR(IF(OR(ISBLANK(D32)),\"\",'Compressed Air Inputs'!G32),\"Error: fill in Input Sheet\")","v":0},0,{"$f":"IFERROR(IF(OR(ISBLANK(D32)),\"\",'Compressed Air Inputs'!H32),\"Error: fill in Input Sheet\")","v":0},null,null,0,0]
[null,10,{"$f":"+'Compressed Air Inputs'!E33","v":0},{"$f":"IF('Compressed Air Inputs'!I33=\"\",\"\",'Compressed Air Inputs'!I33)","v":""},{"$f":"IFERROR(IF(OR(ISBLANK(D33)),\"\",'Compressed Air Inputs'!F33),\"Error: fill in Input Sheet\")","v":0},{"$f":"IFERROR(IF(OR(ISBLANK(D33)),\"\",'Compressed Air Inputs'!G33),\"Error: fill in Input Sheet\")","v":0},0,{"$f":"IFERROR(IF(OR(ISBLANK(D33)),\"\",'Compressed Air Inputs'!H33),\"Error: fill in Input Sheet\")","v":0},null,null,0,0]
[null,"Totals",{"$f":"SUM(C24:C33)","v":0},null,{"$f":"SUMPRODUCT(E24:E33,$H$24:$H$33)/SUM($H$24:$H$33)","v":{"$error":"#DIV/0!"}},{"$f":"SUMPRODUCT(F24:F33,$H$24:$H$33)/SUM($H$24:$H$33)","v":{"$error":"#DIV/0!"}},null,null,null,null,{"$f":"SUM(K24:K33)","v":0},{"$f":"SUM(L24:L33)","v":0}]

{"sheet":"CompAir3-LPFilter","index":9,"n_rows":26,"n_cols":16,"rows_kept":26,"cut":false,"hidden":true,"merged":[[14,3,14,4],[15,1,15,2],[15,3,15,4],[16,1,16,2],[16,3,16,4],[1,13,1,15],[20,1,20,10],[21,9,21,10],[3,1,3,4],[3,6,3,10],[4,6,12,10],[5,1,7,2],[8,1,8,2],[9,1,9,2],[10,1,10,2],[12,1,12,4],[13,1,13,2],[13,3,13,4],[13,6,16,10],[14,1,14,2],[0,1,1,10]]}
[null,"Measure: Low Pressure Drop Filter"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 2: Coincidence Factors"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Program","CFsp","CFwp"]
[null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,"LBES, SBES, Muni",0.8,0.54]
[null,null,null,"Value","Unit",null,"Filters remove solids and aerosols from compressed air systems. Low pressure drop filters have longer lives and lower pressure drops than traditional coalescing filters, resulting in low air compressor energy use."]
[null,"Total Savings",null,{"$f":"IF(O26=\"No - No savings result\", 0, J26)","v":0},"kW"]
[null,null,null,{"$f":"IF(O26=\"No - No savings result\", 0, K26)","v":0},"kWh"]
[null,null,null,0,"MMBtu"]
[null,"Measure Life",null,5,"Years"]
[null,"CFsp",null,{"$f":"O4*100","v":80},"%"]
[null,"CFwp",null,{"$f":"P4*100","v":54},"%"]
[]
[null,"Compressed Air - Low Pressue Drop Filter"]
[null,"Measure Code",null,"COM-CA-LPDF",null,null,"NOTE: For more information on this measure refer to the NH TRM. "]
[null,"Market",null,"Commercial"]
[null,"Program Type",null,"Retrofit"]
[null,"Category",null,"Compressed Air"]
[]
[]
[]
[null,"Table 1: Calculating Primary Energy Impact "]
[null,null,"Inputs",null,null,null,null,null,null,"Savings"]
[null,null,"Base case",null,"Proposed","Annual",null,null,null,"Demand","Energy"]
[null,null,"kW","psi drop","psi drop","Hours",null,null,null,"kW","kWh",null,null,"Savings Check"]
[null,1,{"$f":"IFERROR('CompAir1-Storage'!AC12,\"\")","v":""},{"$f":"'Compressed Air Inputs'!D40","v":0},0.5,{"$f":"'Compressed Air Inputs'!K16","v":0},null,null,null,{"$f":"IFERROR(IF(O26=\"No - No savings result\",\"\",C25*(D25-E25)*0.004),\"\")","v":""},{"$f":"IFERROR(IF(O26=\"No - No savings result\",\"\",J25*F25),\"\")","v":""},null,null,"Current compressor HP",{"$f":"'Compressed Air Inputs'!E16","v":0}]
[null,null,"Totals",null,null,null,null,null,null,{"$f":"SUM(J25:J25)","v":0},{"$f":"SUM(K25:K25)","v":0},null,null,"Compresser 15 - 75 HP?",{"$f":"IF(AND(O25<=75, O25>=15),\"Yes - Savings result\", \"No - No savings result\")","v":"No - No savings result"}]

{"sheet":"CompAir4-ZeroLossDrain","index":10,"n_rows":31,"n_cols":16,"rows_kept":31,"cut":false,"hidden":true,"merged":[[1,13,1,15],[5,13,5,15],[20,1,20,10],[21,9,21,10],[13,1,13,2],[13,3,13,4],[13,6,16,10],[14,1,14,2],[14,3,14,4],[15,1,15,2],[15,3,15,4],[16,1,16,2],[16,3,16,4],[0,1,1,10],[3,1,3,4],[3,6,3,10],[4,6,12,10],[5,1,7,2],[8,1,8,2],[9,1,9,2],[10,1,10,2],[12,1,12,4]]}
[null,"Measure: Zero Loss Condensate Drain"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 2: Coincidence Factors"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Program","CFsp","CFwp"]
[null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,"LBES, SBES, Muni",0.8,0.54]
[null,null,null,"Value","Unit",null,"Drains remove water from a compressed air system. Zero loss condensate drains remove water from a compressed air system without venting any air, resulting in less air demand and consequently less air compressor energy use. Savings result only if compressor is rated ≤ 75 HP."]
[null,"Total Savings",null,{"$f":"IF(O23=\"Yes - Savings result\", J31, 0)","v":0},"kW",null,null,null,null,null,null,null,null,"Table 3: CFM calculations based on pipe size"]
[null,null,null,{"$f":"IF(O23=\"Yes - Savings result\", K31, 0)","v":0},"kWh",null,null,null,null,null,null,null,null,"Size (inches)","psi/1000 ft","cfm"]
[null,null,null,0,"MMBtu",null,null,null,null,null,null,null,null,0.5,2,5.533199470812491]
[null,"Measure Life",null,15,"Years",null,null,null,null,null,null,null,null,0.75,2,14.038852124372049]
[null,"CFsp",null,{"$f":"O4*100","v":80},"%",null,null,null,null,null,null,null,null,1,2,26.687665950381156]
[null,"CFwp",null,{"$f":"P4*100","v":54},"%",null,null,null,null,null,null,null,null,1.25,2,55.371514803104347]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1.5,2,83.225364367085476]
[null,"Compressed Air - Zero Loss Condensate Drain",null,null,null,null,null,null,null,null,null,null,null,1.75,2,115.23028845136395]
[null,"Measure Code",null,"COM-CA-ZLCD",null,null,"NOTE: For more information on this measure refer to the NH TRM. ",null,null,null,null,null,null,2,2,161.04603253278987]
[null,"Market",null,"Commercial",null,null,null,null,null,null,null,null,null,2.5,2,258.66333994412815]
[null,"Program Type",null,"Retrofit",null,null,null,null,null,null,null,null,null,3,2,459.09900086324757]
[null,"Category",null,"Compressed Air",null,null,null,null,null,null,null,null,null,3.5,2,672.64248049177422]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,2,943.81859410430843]
[]
[]
[null,"Table 1: Calculating Primary Energy Impact ",null,null,null,null,null,null,null,null,null,null,"Savings Check"]
[null,null,"Inputs",null,null,null,null,null,null,"Savings",null,null,"Current compressor HP:",null,{"$f":"IF('Compressed Air Inputs'!I16=\"trim\",'Compressed Air Inputs'!E16,IF('Compressed Air Inputs'!I17=\"trim\",'Compressed Air Inputs'!E17,IF('Compressed Air Inputs'!I18=\"trim\",'Compressed Air Inputs'!E18,\"\")))","v":""}]
[null,null,"Pipe Size","CFMpipe","kW/cfm","CFMsaved","Hours",null,null,"kW","kWh",null,"Compresser ≤ 75 HP?",null,{"$f":"IF(O22<=75,\"Yes - Savings result\", \"No - No savings result\")","v":"No - No savings result"}]
[null,1,{"$f":"IF(ISBLANK('Compressed Air Inputs'!N24),\"\",'Compressed Air Inputs'!N24)","v":""},{"$f":"IF(C24=\"\",\"\",VLOOKUP(C24,$N$8:$P$18,3,FALSE))","v":""},{"$f":"IF(C24=\"\",\"\",LOOKUP(\"trim\",'Compressed Air Inputs'!$I$16:$I$18,'Compressed Air Inputs'!$G$16:$G$18)/LOOKUP(\"trim\",'Compressed Air Inputs'!$I$16:$I$18,'Compressed Air Inputs'!$F$16:$F$18))","v":""},{"$f":"IF(G24=\"\",\"\",0.049)","v":""},{"$f":"IF(ISBLANK('Compressed Air Inputs'!O24),\"\",'Compressed Air Inputs'!O24)","v":""},null,null,{"$f":"IFERROR(IF(O23=\"No - No savings result\",\"\",D24*F24*E24),\"\")","v":""},{"$f":"IFERROR(J24*G24,\"\")","v":""}]
[null,2,{"$f":"IF(ISBLANK('Compressed Air Inputs'!N25),\"\",'Compressed Air Inputs'!N25)","v":""},{"$f":"IF(C25=\"\",\"\",VLOOKUP(C25,$N$8:$P$18,3,FALSE))","v":""},{"$f":"IF(C25=\"\",\"\",LOOKUP(\"trim\",'Compressed Air Inputs'!$I$16:$I$18,'Compressed Air Inputs'!$G$16:$G$18)/LOOKUP(\"trim\",'Compressed Air Inputs'!$I$16:$I$18,'Compressed Air Inputs'!$F$16:$F$18))","v":""},"",{"$f":"IF(ISBLANK('Compressed Air Inputs'!O25),\"\",'Compressed Air Inputs'!O25)","v":""},null,null,{"$f":"IFERROR(D25*F25*E25,\"\")","v":""},{"$f":"IFERROR(J25*G25,\"\")","v":""}]
[null,3,{"$f":"IF(ISBLANK('Compressed Air Inputs'!N26),\"\",'Compressed Air Inputs'!N26)","v":""},"",{"$f":"IF(C26=\"\",\"\",LOOKUP(\"trim\",'Compressed Air Inputs'!$I$16:$I$18,'Compressed Air Inputs'!$G$16:$G$18)/LOOKUP(\"trim\",'Compressed Air Inputs'!$I$16:$I$18,'Compressed Air Inputs'!$F$16:$F$18))","v":""},"",{"$f":"IF(ISBLANK('Compressed Air Inputs'!O26),\"\",'Compressed Air Inputs'!O26)","v":""},null,null,"",""]
[null,4,{"$f":"IF(ISBLANK('Compressed Air Inputs'!N27),\"\",'Compressed Air Inputs'!N27)","v":""},"",{"$f":"IF(C27=\"\",\"\",LOOKUP(\"trim\",'Compressed Air Inputs'!$I$16:$I$18,'Compressed Air Inputs'!$G$16:$G$18)/LOOKUP(\"trim\",'Compressed Air Inputs'!$I$16:$I$18,'Compressed Air Inputs'!$F$16:$F$18))","v":""},"",{"$f":"IF(ISBLANK('Compressed Air Inputs'!O27),\"\",'Compressed Air Inputs'!O27)","v":""},null,null,"",""]
[null,5,{"$f":"IF(ISBLANK('Compressed Air Inputs'!N28),\"\",'Compressed Air Inputs'!N28)","v":""},"",{"$f":"IF(C28=\"\",\"\",LOOKUP(\"trim\",'Compressed Air Inputs'!$I$16:$I$18,'Compressed Air Inputs'!$G$16:$G$18)/LOOKUP(\"trim\",'Compressed Air Inputs'!$I$16:$I$18,'Compressed Air Inputs'!$F$16:$F$18))","v":""},"",{"$f":"IF(ISBLANK('Compressed Air Inputs'!O28),\"\",'Compressed Air Inputs'!O28)","v":""},null,null,"",""]
[null,6,{"$f":"IF(ISBLANK('Compressed Air Inputs'!N29),\"\",'Compressed Air Inputs'!N29)","v":""},"",{"$f":"IF(C29=\"\",\"\",LOOKUP(\"trim\",'Compressed Air Inputs'!$I$16:$I$18,'Compressed Air Inputs'!$G$16:$G$18)/LOOKUP(\"trim\",'Compressed Air Inputs'!$I$16:$I$18,'Compressed Air Inputs'!$F$16:$F$18))","v":""},"",{"$f":"IF(ISBLANK('Compressed Air Inputs'!O29),\"\",'Compressed Air Inputs'!O29)","v":""},null,null,"",""]
[null,7,{"$f":"IF(ISBLANK('Compressed Air Inputs'!N30),\"\",'Compressed Air Inputs'!N30)","v":""},"",{"$f":"IF(C30=\"\",\"\",LOOKUP(\"trim\",'Compressed Air Inputs'!$I$16:$I$18,'Compressed Air Inputs'!$G$16:$G$18)/LOOKUP(\"trim\",'Compressed Air Inputs'!$I$16:$I$18,'Compressed Air Inputs'!$F$16:$F$18))","v":""},"",{"$f":"IF(ISBLANK('Compressed Air Inputs'!O30),\"\",'Compressed Air Inputs'!O30)","v":""},null,null,"",""]
[null,null,null,null,null,null,null,null,"Totals:",{"$f":"SUM(J24:J30)","v":0},{"$f":"SUM(K24:K30)","v":0}]

{"sheet":"CompAir5-LeakRepair","index":11,"n_rows":124,"n_cols":34,"rows_kept":124,"cut":false,"hidden":true,"merged":[[27,13,27,15],[8,1,8,2],[9,1,9,2],[10,1,10,2],[20,1,20,10],[1,18,1,33],[0,1,1,10],[1,13,1,15],[3,1,3,4],[3,6,3,10],[5,13,5,14],[15,13,15,14],[21,8,21,10],[12,1,12,4],[13,1,13,2],[13,3,13,4],[13,6,16,10],[14,1,14,2],[14,3,14,4],[15,1,15,2],[15,3,15,4],[16,1,16,2],[16,3,16,4],[4,6,12,10],[5,1,7,2],[21,13,21,15]]}
[null,"Measure: Compressed Air Leak Detection & Repair"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 2: Coincidence Factors",null,null,null,null,"Table 5: FLOW RATE CHART - CFM"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Program","CFsp","CFwp",null,null,"PSI:",150,140,130,120,110,100,90,80,70,60,50,40,30,20,10]
[null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,"LBES, SBES, Muni",0.8,0.54,null,null,"dB Reading","Leak Rate","Leak Rate","Leak Rate","Leak Rate","Leak Rate","Leak Rate","Leak Rate","Leak Rate","Leak Rate","Leak Rate","Leak Rate","Leak Rate","Leak Rate","Leak Rate","Leak Rate"]
[null,null,null,"Value","Unit",null,"This measure covers the repair of compressed air losses identified through ultrasonic leak detection. Air leaks are common in compressed air systems, often wasting 20%-30% of the compressor’s output. Air leak loss rate depend on the supply pressure in an uncontrolled system, as well as leak size quantity and time. This measure is applicable for general plant compressed air systems in manufacturing environments (70 to 125 psig).",null,null,null,null,null,null,null,null,null,null,null,1,2.9700000000000001E-2,2.5820000000000003E-2,2.1940000000000001E-2,1.8800000000000001E-2,1.6400000000000001E-2,1.4E-2,1.1679999999999999E-2,9.3600000000000003E-3,7.1800000000000006E-3,5.1400000000000005E-3,3.0999999999999999E-3,2.2599999999999999E-3,1.42E-3,8.0000000000000004E-4,4.0000000000000002E-4]
[null,"Total Savings",null,{"$f":"J34","v":0},"kW",null,null,null,null,null,null,null,null,"Table 3: kW/CFM Efficiencies",null,null,null,null,2,7.1684585736322193E-2,6.3261453224984582E-2,5.4838320713646964E-2,4.7892696884293054E-2,4.2424581736922852E-2,3.695646658955265E-2,3.1436984618505415E-2,2.5917502647458176E-2,2.0521833600315349E-2,1.5249977477076935E-2,9.978121353838517E-3,7.4989920476886893E-3,5.0198627415388606E-3,3.0826146716488672E-3,1.687247838018708E-3]
[null,null,null,{"$f":"K34","v":0},"kWh",null,null,null,null,null,null,null,null,"Air Compressor Type","SAVE ( kW/CFM)",null,null,null,3,0.12002535200342099,0.10687981676235792,9.3734281521294843E-2,8.2770443585774178E-2,7.3988302955795934E-2,6.520616232581769E-2,5.6125934135842812E-2,4.704570594586794E-2,3.7958655760934441E-2,2.8864783581042323E-2,1.9770911401150205E-2,1.5154223125016944E-2,1.0537534848883683E-2,6.7914824325181391E-3,3.9160658759203101E-3]
[null,null,null,0,"MMBtu",null,null,null,null,null,null,null,null,"Single-acting Reciprocating",0.23,null,null,null,4,0.17301952296929715,0.15507307912054652,0.13712663527179589,0.12203387957486106,0.10979481202974202,9.7555744484622967E-2,8.4693540602528233E-2,7.1831336720433486E-2,5.8743601097826836E-2,4.5430333734708291E-2,3.2117066371589738E-2,2.4986501278011511E-2,1.785593618443328E-2,1.1899440147511781E-2,7.1170131672470124E-3]
[null,"Measure Life",null,5,"Years",null,null,null,null,null,null,null,null,"Double-acting Reciprocating",0.155,null,null,null,5,0.22976671695602091,0.20698578645417554,0.18420485595233013,0.16491983057887036,0.14913071033379618,0.13334159008872201,0.116546853330844,9.9752116572965982E-2,8.2442263153396006E-2,6.4617293072134069E-2,4.6792322990872132E-2,3.6846087500425319E-2,2.6899852009978506E-2,1.8388504320789138E-2,1.1312044432857221E-2]
[null,"CFsp",null,{"$f":"O4*100","v":80},"%",null,null,null,null,null,null,null,null,"Lubricant-injected Rotary Screw (Single Stage)",0.185,null,null,null,6,0.28969588000745722,0.26207161925326616,0.23444735849907516,0.2109337447751127,0.19153077808137878,0.17212781138764485,0.15129299733903367,0.13045818329042247,0.10876014057654937,8.6198869197414402E-2,6.3637597818279434E-2,5.062607625645045E-2,3.7614554694621459E-2,2.6245340678042461E-2,1.651843420671345E-2]
[null,"CFwp",null,{"$f":"P4*100","v":54},"%",null,null,null,null,null,null,null,null,"Lubricant-injected Rotary Screw (Double Stage)",0.16500000000000001,null,null,null,7,0.35240744742744601,0.31994624542092981,0.28748504341441361,0.25972375878319098,0.23666239152726207,0.21360102427133312,0.18864756482656952,0.1636941053818059,0.13748019292184149,0.11000582744667631,8.2531461971511122E-2,6.624443385158596E-2,4.9957405731660805E-2,3.5459421414609754E-2,2.2750480900432815E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Lubricant-free Rotary Screw",0.2,null,null,null,8,0.41760379893434829,0.38032210717044179,0.34304041540653529,0.31102416435773572,0.28427335402404302,0.25752254369035033,0.22839269936814127,0.19926285504593222,0.16843370022947562,0.13590523491877143,0.10337676960806728,8.363523401655501E-2,6.3893698425042722E-2,4.6022091319181217E-2,3.0020412698970496E-2]
[null,"Compressed Air - Zero Loss Condensate Drain",null,null,null,null,null,null,null,null,null,null,null,"Centrifugal ",0.18,null,null,null,9,0.48505337116313507,0.44297461280734013,0.40089585445154519,0.36462580315121651,0.33416445890635421,0.30370311466149191,0.27035481214292634,0.23700650962436073,0.2014845278296192,0.16378886675870172,0.12609320568778423,0.10274375531466962,7.9394304941554986E-2,5.7926029790454706E-2,3.8338929861368755E-2]
[null,"COM-CA-AN",null,"COM-CA-AN",null,null,"NOTE: For more information on this measure refer to the NH TRM. ",null,null,null,null,null,null,"Other",0.19,null,null,null,10,0.55457009834973625,0.50772269350674692,0.46087528866375771,0.42035889783826308,0.38617352103026309,0.35198814422226316,0.3143914955754713,0.27679484692867945,0.23651976500235133,0.19356624979648704,0.15061273459062274,0.12352347740529793,9.643422021997311E-2,7.1164913178965422E-2,4.7715556282274842E-2]
[null,"Market",null,"Commercial",null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,0.6260007170770534,0.5744167570644344,0.5228327970518154,0.47808233857628635,0.44016538163784719,0.40224842469940802,0.36038326853404712,0.31851811236868621,0.27344375361144069,0.2251601922623106,0.17687663091318048,0.14593411596029809,0.11499160100741568,8.5733189326963916E-2,5.8158880918942765E-2]
[null,"Program Type",null,"Retrofit",null,null,null,null,null,null,null,null,null,"Table 4: Marginal Efficiency Factors",null,null,null,null,12,0.6992164696247094,0.64293079215305493,0.58664511468140057,0.53767661662332045,0.49602529797881451,0.45437397933430862,0.40822807962421181,0.36208217991411495,0.31217407267290237,0.258503757900574,0.20483344312824564,0.16994027154350949,0.13504709995877337,0.10162591977987984,6.967673100682889E-2]
[null,"Category",null,"Compressed Air",null,null,null,null,null,null,null,null,null,"Control Type","% kW/ % Load",null,null,null,13,0.77410743511377977,0.7131569591293011,0.65220648314482244,0.59903895620833525,0.55365437831983966,0.50826980043134407,0.4578374880901902,0.40740517574903629,0.35263872386845002,0.29353813244843135,0.23443754102841266,0.19551046359541746,0.15658338616242229,0.11883866519589789,8.2276300695844268E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Inlet Valve Modulated",0.31,null,null,null,14,0.85057851445222898,0.78500174970304415,0.71942498495385931,0.66207984087738136,0.6129663174736103,0.56385279406983912,0.50913391764503357,0.45441504122022813,0.394774091636031,0.33021106889244234,0.26564804614885368,0.2226164175924159,0.17958478903597816,0.13736739959945715,9.5964249282852937E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Variable Displacement",0.69,null,null,null,15,0.92854650105443792,0.85838317898011596,0.7882198569057941,0.72672046195359019,0.67388499412350411,0.62104952629341803,0.56204862506264952,0.50304772383188101,0.43852342322523197,0.3684757232427025,0.29842802326017304,0.25123252512813449,0.20403702699609591,0.15720844461205649,0.11074677797601619]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Variable Speed Drive",0.85,null,null,null,16,1.0079378898492644,0.93322868096145539,0.85851947207364632,0.79289079813163688,0.73634265913542707,0.67979452013921726,0.61652016131274123,0.5532458024862652,0.4838356695756541,0.40828976258090777,0.33274385558616143,0.28133542590814187,0.22992699623012225,0.17835841794638108,0.12662969105691835]
[null,"Table 1: Calculating Primary Energy Impact ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,17,1.0886872033710575,1.0094734976884245,0.93025979200579179,0.86052813978891274,0.80027854103778728,0.74002894228666183,0.67249318193515273,0.60495742158364352,0.53066458369395764,0.44961466826609509,0.36856475283823248,0.31290367802749575,0.25724260321675907,0.20081419234892728,0.1436184454240004]
[null,null,"Inputs",null,null,null,null,null,"Savings",null,null,null,null,"Table 5: kW/cfm",null,null,null,null,18,1.1707356892874023,1.0870594236314817,1.003383157975561,0.92957593454851617,0.86563775335034743,0.80169957215217869,0.72991751116596215,0.65813545017974573,0.57896800724913144,0.49241518237411924,0.4058623574991071,0.34591749365922397,0.2859726298193408,0.22457286236672058,0.16171819130136328]
[null,null,"# Leaks","CFMleak","kW/cfm","MEF","Hours","psi",null,"kW","kWh",null,null,"No.","Compressor Type","kW/cfm",null,null,19,1.2540302906507708,1.1659338113545172,1.0778373320582639,0.9999828699565837,0.93237042504947687,0.86475798014236993,0.78874739437540831,0.71273680860844668,0.6287072976294954,0.53665886143855446,0.44461042524761341,0.38035852417843063,0.31610662310924792,0.24963171708556164,0.18093380610737192]
[null,1,{"$f":"IF(ISBLANK('Compressed Air Inputs'!I38),\"\",'Compressed Air Inputs'!I38)","v":""},{"$f":"IFERROR(IF('Compressed Air Inputs'!J38=\"Yes\",'Compressed Air Inputs'!K38,INDEX($T$5:$AH$124,MATCH(ROUND('Compressed Air Inputs'!L38,0),$S$5:$S$124,0),MATCH(MROUND(H24,10),$T$3:$AH$3,0))),\"\")","v":""},{"$f":"IFERROR(IFERROR(VLOOKUP(\"Trim\",$O$24:$P$26,2,FALSE),VLOOKUP(\"Trim\",$O$30:$P$32,2,FALSE)),IFERROR($P$24,$P$30))","v":""},{"$f":"VLOOKUP(IFERROR(VLOOKUP(\"Trim\",'Compressed Air Inputs'!$I$16:$J$18,2,FALSE),'Compressed Air Inputs'!$J$16),$N$18:$O$20,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"8760","v":8760},{"$f":"IFERROR(VLOOKUP(\"Trim\",'Compressed Air Inputs'!$I$16:$P$18,8,FALSE),'Compressed Air Inputs'!$P$16)","v":0},null,{"$f":"IFERROR(K24/G24,\"\")","v":""},{"$f":"IFERROR(C24*D24*E24*F24*G24,\"\")","v":""},null,null,1,{"$f":"'Compressed Air Inputs'!I16","v":0},{"$f":"'Compressed Air Inputs'!G16/'Compressed Air Inputs'!F16","v":{"$error":"#DIV/0!"}},null,null,20,1.338522820267753,1.2460487730394538,1.1535747258111546,1.0717021344985855,1.0004309991017464,0.92915986370490733,0.84894089286202057,0.76872192201913381,0.67984686174129472,0.58231571202850307,0.48478456231571143,0.41620968330233865,0.34763480428896582,0.27598821750245972,0.20126992294282031]
[null,2,{"$f":"IF(ISBLANK('Compressed Air Inputs'!I39),\"\",'Compressed Air Inputs'!I39)","v":""},{"$f":"IFERROR(IF('Compressed Air Inputs'!J39=\"Yes\",'Compressed Air Inputs'!K39,INDEX($T$5:$AH$124,MATCH(ROUND('Compressed Air Inputs'!L39,0),$S$5:$S$124,0),MATCH(MROUND(H25,10),$T$3:$AH$3,0))),\"\")","v":""},{"$f":"IFERROR(IFERROR(VLOOKUP(\"Trim\",$O$24:$P$26,2,FALSE),VLOOKUP(\"Trim\",$O$30:$P$32,2,FALSE)),IFERROR($P$24,$P$30))","v":""},{"$f":"VLOOKUP(IFERROR(VLOOKUP(\"Trim\",'Compressed Air Inputs'!$I$16:$J$18,2,FALSE),'Compressed Air Inputs'!$J$16),$N$18:$O$20,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"8760","v":8760},{"$f":"IFERROR(VLOOKUP(\"Trim\",'Compressed Air Inputs'!$I$16:$P$18,8,FALSE),'Compressed Air Inputs'!$P$16)","v":0},null,{"$f":"IFERROR(K25/G25,\"\")","v":""},{"$f":"IFERROR(C25*D25*E25*F25*G25,\"\")","v":""},null,null,2,{"$f":"'Compressed Air Inputs'!I17","v":0},{"$f":"'Compressed Air Inputs'!G17/'Compressed Air Inputs'!F17","v":{"$error":"#DIV/0!"}},null,null,21,1.4241692904412888,1.3273605313220478,1.2305517722028068,1.144690814994513,1.0697776596971662,0.99486450439981966,0.91045938803212367,0.82605427166442758,0.73235377223260201,0.62935788973664675,0.5263620072406916,0.45345499991555471,0.38054799259041783,0.30363997754770106,0.22273095478740434]
[null,3,{"$f":"IF(ISBLANK('Compressed Air Inputs'!I40),\"\",'Compressed Air Inputs'!I40)","v":""},{"$f":"IFERROR(IF('Compressed Air Inputs'!J40=\"Yes\",'Compressed Air Inputs'!K40,INDEX($T$5:$AH$124,MATCH(ROUND('Compressed Air Inputs'!L40,0),$S$5:$S$124,0),MATCH(MROUND(H26,10),$T$3:$AH$3,0))),\"\")","v":""},"",{"$f":"VLOOKUP(IFERROR(VLOOKUP(\"Trim\",'Compressed Air Inputs'!$I$16:$J$18,2,FALSE),'Compressed Air Inputs'!$J$16),$N$18:$O$20,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"8760","v":8760},{"$f":"IFERROR(VLOOKUP(\"Trim\",'Compressed Air Inputs'!$I$16:$P$18,8,FALSE),'Compressed Air Inputs'!$P$16)","v":0},null,"","",null,null,3,{"$f":"'Compressed Air Inputs'!I18","v":0},{"$f":"'Compressed Air Inputs'!G18/'Compressed Air Inputs'!F18","v":{"$error":"#DIV/0!"}},null,null,22,1.5109293627713536,1.4098288856659256,1.3087284085604978,1.2189093998362823,1.140371859493279,1.0618343191502759,0.97326717085771564,0.88470002256515545,0.78619744827766935,0.67775944799525734,0.56932144771284532,0.49207949439307441,0.41483754107330351,0.33258474801900684,0.24532111523018441]
[null,4,{"$f":"IF(ISBLANK('Compressed Air Inputs'!I41),\"\",'Compressed Air Inputs'!I41)","v":""},{"$f":"IFERROR(IF('Compressed Air Inputs'!J41=\"Yes\",'Compressed Air Inputs'!K41,INDEX($T$5:$AH$124,MATCH(ROUND('Compressed Air Inputs'!L41,0),$S$5:$S$124,0),MATCH(MROUND(H27,10),$T$3:$AH$3,0))),\"\")","v":""},"",{"$f":"VLOOKUP(IFERROR(VLOOKUP(\"Trim\",'Compressed Air Inputs'!$I$16:$J$18,2,FALSE),'Compressed Air Inputs'!$J$16),$N$18:$O$20,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"8760","v":8760},{"$f":"IFERROR(VLOOKUP(\"Trim\",'Compressed Air Inputs'!$I$16:$P$18,8,FALSE),'Compressed Air Inputs'!$P$16)","v":0},null,"","",null,null,null,null,null,null,null,23,1.5987658919813077,1.4934167693441447,1.3880676467069819,1.2943213654604713,1.2121779256046128,1.1300344857487545,1.0373310986868414,0.94462771162492798,0.84134938757688438,0.72749612654271034,0.61364286550853631,0.53206907375119616,0.45049528199385608,0.36282040286665262,0.26904443636958597]
[null,5,{"$f":"IF(ISBLANK('Compressed Air Inputs'!I42),\"\",'Compressed Air Inputs'!I42)","v":""},{"$f":"IFERROR(IF('Compressed Air Inputs'!J42=\"Yes\",'Compressed Air Inputs'!K42,INDEX($T$5:$AH$124,MATCH(ROUND('Compressed Air Inputs'!L42,0),$S$5:$S$124,0),MATCH(MROUND(H28,10),$T$3:$AH$3,0))),\"\")","v":""},"",{"$f":"VLOOKUP(IFERROR(VLOOKUP(\"Trim\",'Compressed Air Inputs'!$I$16:$J$18,2,FALSE),'Compressed Air Inputs'!$J$16),$N$18:$O$20,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"8760","v":8760},{"$f":"IFERROR(VLOOKUP(\"Trim\",'Compressed Air Inputs'!$I$16:$P$18,8,FALSE),'Compressed Air Inputs'!$P$16)","v":0},null,"","",null,null,"Table 5: kW/cfm Backup",null,null,null,null,24,1.6876445442781478,1.5780898783372588,1.46853521239637,1.3708928290611755,1.2851627283316756,1.1994326276021756,1.1026203058736863,1.005807984145197,0.89778293945432408,0.77854517180106786,0.65930740414781153,0.5734104420509426,0.48751347995407363,0.39434492739666205,0.29390478437870787]
[null,6,{"$f":"IF(ISBLANK('Compressed Air Inputs'!I43),\"\",'Compressed Air Inputs'!I43)","v":""},{"$f":"IFERROR(IF('Compressed Air Inputs'!J43=\"Yes\",'Compressed Air Inputs'!K43,INDEX($T$5:$AH$124,MATCH(ROUND('Compressed Air Inputs'!L43,0),$S$5:$S$124,0),MATCH(MROUND(H29,10),$T$3:$AH$3,0))),\"\")","v":""},"",{"$f":"VLOOKUP(IFERROR(VLOOKUP(\"Trim\",'Compressed Air Inputs'!$I$16:$J$18,2,FALSE),'Compressed Air Inputs'!$J$16),$N$18:$O$20,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"8760","v":8760},{"$f":"IFERROR(VLOOKUP(\"Trim\",'Compressed Air Inputs'!$I$16:$P$18,8,FALSE),'Compressed Air Inputs'!$P$16)","v":0},null,"","",null,null,"No.","Compressor Type","kW/cfm",null,null,25,1.7775334754460681,1.6638163579376148,1.5500992404291616,1.4485922545883592,1.3592954004152071,1.2699985462420553,1.1691059578717735,1.0682133695014915,0.95547311127773216,0.8308851832004952,0.70629725512325825,0.61609102328082899,0.52588479143839983,0.42715640805390354,0.31990587312734009]
[null,7,{"$f":"IF(ISBLANK('Compressed Air Inputs'!I44),\"\",'Compressed Air Inputs'!I44)","v":""},{"$f":"IFERROR(IF('Compressed Air Inputs'!J44=\"Yes\",'Compressed Air Inputs'!K44,INDEX($T$5:$AH$124,MATCH(ROUND('Compressed Air Inputs'!L44,0),$S$5:$S$124,0),MATCH(MROUND(H30,10),$T$3:$AH$3,0))),\"\")","v":""},"",{"$f":"VLOOKUP(IFERROR(VLOOKUP(\"Trim\",'Compressed Air Inputs'!$I$16:$J$18,2,FALSE),'Compressed Air Inputs'!$J$16),$N$18:$O$20,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"8760","v":8760},{"$f":"IFERROR(VLOOKUP(\"Trim\",'Compressed Air Inputs'!$I$16:$P$18,8,FALSE),'Compressed Air Inputs'!$P$16)","v":0},null,"","",null,null,1,{"$f":"'Compressed Air Inputs'!I16","v":0},{"$f":"IFERROR(VLOOKUP('Compressed Air Inputs'!H16,$N$8:$O$14,2,FALSE),\"\")","v":""},null,null,26,1.8684030572908492,1.7505665361183667,1.6327300149458841,1.5273902020322794,1.4345470973775527,1.341703992722826,1.2367610407657152,1.1318180888086045,1.0143964021528777,0.88449598079853542,0.75459555944419299,0.6600988945426346,0.5656022296410762,0.46125302351789832,0.34705127617310094]
[null,8,{"$f":"IF(ISBLANK('Compressed Air Inputs'!I45),\"\",'Compressed Air Inputs'!I45)","v":""},{"$f":"IFERROR(IF('Compressed Air Inputs'!J45=\"Yes\",'Compressed Air Inputs'!K45,INDEX($T$5:$AH$124,MATCH(ROUND('Compressed Air Inputs'!L45,0),$S$5:$S$124,0),MATCH(MROUND(H31,10),$T$3:$AH$3,0))),\"\")","v":""},"",{"$f":"VLOOKUP(IFERROR(VLOOKUP(\"Trim\",'Compressed Air Inputs'!$I$16:$J$18,2,FALSE),'Compressed Air Inputs'!$J$16),$N$18:$O$20,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"8760","v":8760},{"$f":"IFERROR(VLOOKUP(\"Trim\",'Compressed Air Inputs'!$I$16:$P$18,8,FALSE),'Compressed Air Inputs'!$P$16)","v":0},null,"","",null,null,2,{"$f":"'Compressed Air Inputs'!I17","v":0},{"$f":"IFERROR(VLOOKUP('Compressed Air Inputs'!H17,$N$8:$O$14,2,FALSE),\"\")","v":""},null,null,27,1.9602256435791674,1.8383126951446798,1.7163997467101924,1.6072591121868398,1.5108907915746219,1.414522470962404,1.3055601799534393,1.1965978889444746,1.0745306591352317,0.93935849052571097,0.80418632191619022,0.70542272781381843,0.60665913371144664,0.49663303689801408,0.37534443737352069]
[null,9,{"$f":"IF(ISBLANK('Compressed Air Inputs'!I46),\"\",'Compressed Air Inputs'!I46)","v":""},{"$f":"IFERROR(IF('Compressed Air Inputs'!J46=\"Yes\",'Compressed Air Inputs'!K46,INDEX($T$5:$AH$124,MATCH(ROUND('Compressed Air Inputs'!L46,0),$S$5:$S$124,0),MATCH(MROUND(H32,10),$T$3:$AH$3,0))),\"\")","v":""},"",{"$f":"VLOOKUP(IFERROR(VLOOKUP(\"Trim\",'Compressed Air Inputs'!$I$16:$J$18,2,FALSE),'Compressed Air Inputs'!$J$16),$N$18:$O$20,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"8760","v":8760},{"$f":"IFERROR(VLOOKUP(\"Trim\",'Compressed Air Inputs'!$I$16:$P$18,8,FALSE),'Compressed Air Inputs'!$P$16)","v":0},null,"","",null,null,3,{"$f":"'Compressed Air Inputs'!I18","v":0},{"$f":"IFERROR(VLOOKUP('Compressed Air Inputs'!H18,$N$8:$O$14,2,FALSE),\"\")","v":""},null,null,28,2.0529753685092378,1.9270288747183608,1.8010823809274839,1.688173120732321,1.5883010941328721,1.4884290675334233,1.3754794830004911,1.2625298984675588,1.1358549521791552,0.9954546441352804,0.85505433609140558,0.75205173890372856,0.64904914171605155,0.53329478885612702,0.40478868032395499]
[null,10,{"$f":"IF(ISBLANK('Compressed Air Inputs'!I47),\"\",'Compressed Air Inputs'!I47)","v":""},{"$f":"IFERROR(IF('Compressed Air Inputs'!J47=\"Yes\",'Compressed Air Inputs'!K47,INDEX($T$5:$AH$124,MATCH(ROUND('Compressed Air Inputs'!L47,0),$S$5:$S$124,0),MATCH(MROUND(H33,10),$T$3:$AH$3,0))),\"\")","v":""},"",{"$f":"VLOOKUP(IFERROR(VLOOKUP(\"Trim\",'Compressed Air Inputs'!$I$16:$J$18,2,FALSE),'Compressed Air Inputs'!$J$16),$N$18:$O$20,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"8760","v":8760},{"$f":"IFERROR(VLOOKUP(\"Trim\",'Compressed Air Inputs'!$I$16:$P$18,8,FALSE),'Compressed Air Inputs'!$P$16)","v":0},null,"","",null,null,null,null,null,null,null,29,2.1466279721834711,2.0166907013233213,1.8867534304631712,1.7701078967308308,1.6667541001262995,1.5634003035217685,1.4464964026873788,1.3295925018529888,1.1983494647931492,1.0527672915078596,0.90718511822257031,0.79997564248584652,0.69276616674912272,0.57123669151696366,0.43538721678936931]
[null,null,null,null,null,null,null,null,"Totals: ",{"$f":"SUM(J24:J33)","v":0},{"$f":"SUM(K24:K33)","v":0},null,null,null,null,null,null,null,30,2.241160648653159,2.1072752394952143,1.9733898303372699,1.8530405015912126,1.7462272532570429,1.6394140049228731,1.5185896170418525,1.3977652291608318,1.261995397948912,1.1112801234060932,0.96056484886327442,0.84918461229511799,0.73780437572696156,0.61045722305156502,0.46714315426892838]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,31,2.3365519129563439,2.1987608615568659,2.0609698101573883,1.9369492653082252,1.8266992270093767,1.7164491887105284,1.5917389237486004,1.4670286587866723,1.3267748852447216,1.1709776031227483,1.015180321000775,0.89966924574222773,0.78415817048368031,0.65095492283929024,0.50005950280905742]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,32,2.4327814842352606,2.2911271330013379,2.1494727817674151,2.0218136773673052,1.9081498198010087,1.794485962234712,1.6659251468010727,1.5373643313674334,1.392670917680674,1.2318449057407947,1.0710188938009155,0.95142053232599433,0.83182217085107324,0.69272838712971052,0.53413918116190651]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,33,2.5298301825443512,2.3843547112097832,2.2388792398752151,2.1076142901699741,1.9905598620940603,1.8735054340181465,1.7411300536346521,1.6087546732511577,1.4596672766874275,1.2938678639434615,1.1280684511994956,1.0044298253286641,0.88079119945783269,0.7357762651385984,0.56938502237096122]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,34,2.627679837376748,2.4784252555931778,2.3291706738096076,2.1943326332045299,2.0739111337779437,1.9534896343513577,1.8173362812797702,1.6811829282081825,1.5277484742777421,1.3570329194884492,1.1863173646991561,1.0586888163624399,0.93106026802572406,0.78009725552262121,0.6057997788531313]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,35,2.726313206271239,2.5733213475694199,2.4203294888676008,2.2819511364836282,2.1581862904175027,2.0344214443513766,1.8945272703146441,1.7546330962779118,1.5968996993740772,1.4213270796031403,1.2457544598322035,1.1141895124035555,0.98262456497490758,0.82569010318586045,0.64338612703641418]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,36,2.8257139021311466,2.669026419047448,2.5123389359637494,2.3704530620103865,2.243368797187359,2.1162845323643316,1.9726872055928393,1.829089878821347,1.6671067695150021,1.4867378776738049,1.3063689858326075,1.170924215005761,1.0354794441789146,0.8725535963782618,0.6821466716038026]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,37,2.9258663281053425,2.765524688301543,2.6051830484977434,2.459822442230168,2.3294428694988176,2.1990632967674668,2.0518009628804248,1.904538628993383,1.7383560872656008,1.5532533376970785,1.3681505881285563,1.2288855014308662,1.0896204147331758,0.92068656405189797,0.72208394938703246]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,38,3.0267556190606122,2.8628011022920501,2.698846585523488,2.550044024585373,2.4163934194777053,2.2827428143700375,2.1318540606685894,1.9809653069671413,1.8106346007578071,1.6208619420405868,1.4310892833233664,1.2880662074718918,1.145043131620417,0.97008787344575265,0.76320043294789852]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,39,3.1283675888214391,2.9608412846309777,2.7933149804405168,2.6411032214224748,2.5042060075768511,2.3673087937312274,2.2128326165358176,2.0583564393404084,1.8839297678700506,1.6895526021247442,1.4951754363794381,1.3484594117759245,1.2017433871724112,1.0207564278737313,0.80549853387988501]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,40,3.2306886824750003,3.0596314885087907,2.8885742945425812,2.7329860646099196,2.5928667987108063,2.4527475328116926,2.2947233075236366,2.1366990822355807,1.9582295236250913,1.7593146316921682,1.5603997397592453,1.4100584215002139,1.2597171032411825,1.0726911646939992,0.84898060585866386]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,41,3.3337059331400325,3.1591585539965292,2.984611174853026,2.8256791643165338,2.6823625223870535,2.5390458804575733,2.3775133340650152,2.2159807876724575,2.0335222504430019,1.8301377223766493,1.6267531943102964,1.4728567591572428,1.3189603240041892,1.1258910534405959,0.89364894746646284]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,42,3.4374069226826829,3.2594098692193239,3.0814128157559648,2.91916967147634,2.7726804363804494,2.6261912012845583,2.4611903870674321,2.2961895728503059,2.1097967509351778,1.9020119213220485,1.6942270917089193,1.5368481505233229,1.3794692093377265,1.1803550941006944,0.93950580481222645]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,43,3.5417797459332259,3.3603733349660381,3.1789669239988498,3.0134452435297354,2.8638082935586944,2.7141713435876533,2.5457426178057085,2.3773138920237638,2.187042222966499,1.974927610633914,1.7628129983013288,1.6020265135011744,1.4412400287010201,1.2360823155229417,0.98655337396693932]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,44,3.6468129780171608,3.4620373323577431,3.2772616866983255,3.1084940130851439,2.9557343115181989,2.8029746099512534,2.6311586103245972,2.459342610697941,2.2652482367478068,2.0488754884741938,1.8325027402005811,1.6683859478405556,1.5042691554805299,1.2930717739440669,1.0347938032311665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,45,3.752495644464775,3.5643906932468585,3.3762857420289416,3.2043045591911405,3.0484471447334553,2.8925897302757702,2.7174273560892575,2.5422649819027443,2.3444047137506399,2.1238465516329446,1.903288389515249,1.7359207256326386,1.5685530617500278,1.3513225516224814,1.0842291952499994]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,46,3.8588171938061184,3.6674226730604795,3.4760281523148406,3.3008658809481335,3.1419358589603581,2.9830058369725827,2.8045382306543689,2.6260706243361551,2.4245019072617278,2.1998320794310873,1.9751622516004466,1.8046252825038223,1.634088313407198,1.4108337555688788,1.1348616089888646]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,47,3.9657674723950271,3.7711229258371581,3.5764783792792887,3.3981673732221607,3.2361899076657745,3.0742124421093884,2.8924809721504632,2.710749502191538,2.5055303844165646,2.2768236188255426,2.0481168532345211,1.8744942094432608,1.7008715656520006,1.4716045163649831,1.1866930615822084]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,48,4.0733367012371486,3.8754814812368528,3.6776262612365573,3.4961988042519732,3.3311991102831002,3.1661994163142277,2.9812456614100915,2.7962919065059553,2.5874810095702792,2.3548129706030623,2.1221449316358454,1.9455222452058933,1.7688995587759413,1.533633987062585,1.2397255300658245]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,49,4.1815154546238418,3.9804887233300423,3.7794619920362424,3.5949502949652263,3.4269536321169931,3.2589569692687603,3.070822703577031,2.8826884378853017,2.6703449288802585,2.4337921765619011,2.1972394242435436,2.0177042692391316,1.8381691142347198,1.5969213421558077,1.2939609530023957]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,50,4.2902946403971871,4.0861353709947306,3.8819761015922731,3.69441229984105,3.5234439657410608,3.3524756316410711,3.1612028110597765,2.9699299904784819,2.7541135559891652,2.5137535075918271,2.2733934591944887,2.0910352950871371,1.9086771309797854,1.6614657766203995,1.3494012320089792]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,51,4.3996654816912821,4.1924124597695718,3.985159437847861,3.7945755891745652,3.6206609137496835,3.4467462383248022,3.2523769877058726,3.058007737086943,2.8387785587091772,2.5946894525725752,2.3506003464359733,2.1655104642313625,1.9804205820267518,1.7272665050143403,1.4060482331941278]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,52,4.5096195000125388,4.2993113250284338,4.089003150044328,3.8954312326151133,3.7185955727407891,3.541759912866465,3.3443365140874231,3.1469131153083811,2.9243318466190766,2.6765927080195104,2.4288535694199438,2.2411250403304934,2.0533965112410431,1.7943227606347938,1.4639037885117452]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,53,4.6201484995368531,4.4068235863565155,4.1934986731761779,3.9969705838638538,3.8172393184195439,3.6375080529752339,3.4370729337996879,3.2366378146241419,3.0107655594951379,2.7594561684126759,2.5081467773302144,2.3178744038266159,2.1276020303230174,1.8626337947268123,1.5229696970380002]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,54,4.7312445525147542,4.5149411330211002,4.2986377135274463,4.0991852664286892,3.9165837917248298,3.7339823170209705,3.5305780406851781,3.3271737643493857,3.0980720565049849,2.8432729171519755,2.5884737777989661,2.3957540468878054,2.2030343159766446,1.9321988757397268,1.5832477261770528]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,55,4.8428999856871897,4.6236561104412912,4.4044122351953927,4.2020671603451367,4.0166208858905215,3.8311746114359058,3.6248438669046186,3.4185131223733309,3.1862439061007839,2.928036218086977,2.6698285300731701,2.4747595686602288,2.279690607247288,2.0030172886274893,1.6447396128008336]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,56,4.9551073676248567,4.732960907571103,4.5108144475173484,4.3056083897812059,4.1173427343626745,3.9290770789441436,3.7198626717842478,3.5106482646243524,3.2752738765546128,3.0137395075750288,2.7522051385954449,2.5548866708055309,2.3575682030156169,2.0750883341896396,1.707447064327599]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,57,5.0678594969128303,4.842848145118972,4.6178367933251137,4.4098013114526848,4.2187416995016864,4.027682087550688,3.8156269313758457,3.6035717752010035,3.3651549270843035,3.1003763870257464,2.8355978469671892,2.6361311533014899,2.4366644596357907,2.1484113284498454,1.7713717597436547]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,58,5.1811493911102158,4.9533106645345013,4.7254719379587868,4.5146385037824395,4.3208103620054592,4.1269822202284789,3.9121293286722176,3.6972764371159568,3.455880199523238,3.1879406158940613,2.9200010322648846,2.7184889104860606,2.5169767887072365,2.222985602069254,1.836515350572113]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,59,5.2949702764214193,5.0643415177000453,4.8337127589786704,4.6201127567439642,4.4235415109959257,4.2269702652478873,4.0093627444263262,3.7917552236047642,3.5474430104918158,3.2764261050874803,3.0054091996831449,2.8019559273266816,2.5985026549702184,2.2988104997921255,1.902879461792403]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,60,5.4093155780218476,5.1759339572707788,4.9425523365197099,4.7262170623350084,4.5269281347166759,4.3276392070983434,4.1073202485271505,3.8870012899559585,3.6398368440323741,3.3658269107563981,3.0918169774804221,2.8865282758983875,2.6812395743163528,2.3758853799214643,1.9704656927137214]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,61,5.5241789109864312,5.2880814276124122,5.0519839442383931,4.8329446056324343,4.6309634117945366,4.428982217956638,4.2059950918898501,3.9830079658230613,3.7330553446728527,3.456137228439224,3.1792191122055953,2.9722021120557796,2.7651851119059638,2.4542096138225706,2.0392756178055995]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,62,5.6395540717739623,5.4007775562901772,5.1620010408063921,4.9402887563836773,4.7356407030220335,4.5309926496603889,4.3053806988214403,4.0797687479824916,3.827092310887477,3.5473513875363958,3.2676104641853145,3.0589736722850658,2.8503368803848175,2.5337825854525398,2.1093107874882326]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63,5.7554350302248425,5.5140161460673074,5.2725972619097732,5.0482430610946443,4.8409535436219215,4.6336640261491988,4.4054706598270226,4.1772772935048472,3.9219416889258003,3.6394638460898814,3.3569860032539629,3.1468392707237371,2.9366925381935114,2.6146036909140187,2.1805727288852594]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64,5.8718159220336563,5.6277911673748759,5.3837664127160956,5.1568012355771984,4.9468956359581835,4.7369900363391686,4.5062587248243942,4.2755274133096197,4.0175975669836843,3.7324691858465879,3.4473408047094916,3.235795296336379,3.0242497879632659,2.696672338031564,2.2530629465412724]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,65,5.9886910416612515,5.7420967512181713,5.4955024607750911,5.2659571579227391,5.0534608426611136,4.8409645273994881,4.6077387967378467,4.3745130660762062,4.1140541696922641,3.8263621075860215,3.5386700454797788,3.3258382102360873,3.1130063749923962,2.7799879459491259,2.3267829231062764]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,66,6.1060548356544171,5.8569271824880564,5.6077995293216958,5.3757048618713412,5.160643180136991,4.9455814984026407,4.7099049254444738,4.4742283524863069,4.2113058529028891,3.9211374266942221,3.630969000485555,3.4169645431418934,3.2029600857982321,2.8645499447472993,2.4017341199890949]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,67,6.2239018963438362,5.9722768936483792,5.7206518909529231,5.4860385305485604,5.2684368124352909,5.0508350943220224,4.812751302048448,4.5746675097748737,4.3093470987478435,4.0167900689673575,3.7242330391868719,3.5091708929632741,3.2941087467396764,2.9503577750791115,2.4779179779815799]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,68,6.3422269558935538,6.0881404587729335,5.8340539616523142,5.5969524905442229,5.3768360454486599,5.1567196003530968,4.9162722534609227,4.6758249065687485,4.4081725109583934,4.1133150666298555,3.818457622301318,3.6024539225035972,3.3864502227058764,3.0374108878231416,2.5553359178553934]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,69,6.4610248806774369,6.2045125879077485,5.9480002951380593,5.7084412063097902,5.4858353214229396,5.263229436536089,5.0204622372648959,4.7776950379937029,4.5077768104230787,4.2107075545530233,3.913638298682967,3.6968103572749538,3.4799824158669401,3.1257087437529134,2.6339893409328727]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,70,6.5802906659602121,6.3213881217365397,6.0624855775128674,5.8204992748528417,5.5954292137564625,5.3703591526600825,5.125315836846208,4.8802725210323334,4.6081548309707232,4.3089627666613755,4.0097707023520286,3.7922369834174852,3.5747032644829422,3.2152508132216306,2.7138796296335514]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,71,6.7000194308624437,6.4387620265288632,6.1775046221952836,5.933121420708793,5.7056124220693913,5.4781034234299906,5.2308277567731896,4.9835520901163886,4.7093015153635429,4.4080760325146517,4.1068505496657615,3.8887306457166737,3.6706107417675864,3.3060365758612518,2.7950081479976707]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,72,6.8202064135904976,6.5566293893522261,6.2930523651139554,6.0463024911717067,5.81637976752548,5.5864570438792533,5.336992818408965,5.0875285929386767,4.8112119114872582,4.5080427740547115,4.2048736366221648,3.9862882457127702,3.7677028548033751,3.3980655202950967,2.8773762421879341]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,73,6.9408469669140187,6.6749854135308535,6.4091238601476892,6.1600374517674013,5.9277261883899888,5.6954149250125763,5.4438059557415919,5.1921969864706083,4.9138811687257498,4.6088585025070161,4.3038358362882834,4.0849067398967476,3.8659776435052113,3.4913371438632224,2.9609852409707806]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,74,7.0619365538749452,6.7938254143352479,6.5257142747955506,6.2743213819533965,6.0396467358087857,5.804972089664175,5.55126221141842,5.2975523331726651,5.0173045345090106,4.7105188154274549,4.4037330963458992,4.1845831379877785,3.9654331796296574,3.5858509523597997,3.0458364561782041]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,75,7.1834707437130811,6.9131448148877492,6.6428188860624182,6.3891494710314021,6.1521365697946999,5.9151236685579986,5.6593567329719274,5.4035897973858571,5.121477351023775,4.8130193938856802,4.5045614367475864,4.2853145012873828,4.0660675658271792,3.6816064597817766,3.1319311831511731]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,76,7.3054452079947962,7.0329391422706991,6.7604330765466019,6.5045170142591804,6.2651909554084355,6.0258648965576906,5.768084769225533,5.5103046418933763,5.2263950520772156,4.9163559997770507,4.6063169474768859,4.3870979411059929,4.1678789347351,3.7786031880883391,3.2192707011657093]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,77,7.4278557169318278,7.1532040238243741,6.8785523307169205,6.6204194091494664,6.3788052591220135,6.1371911090945606,5.8774416668683145,5.6176922246420693,5.3320531601044578,5.0205244732554819,4.708995786406506,4.4899306172576487,4.2708654481087915,3.876840666970371,3.3078562738423871]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,78,7.5506981358788554,7.2739351836233661,6.9971722313678768,6.7368521519447091,6.4929749453538648,6.2490977387630204,5.9874228671887586,5.7257479956144959,5.4384472833117297,5.1255207302804608,4.812594177249192,4.5938097366191997,4.3750252959892082,3.9763184336295385,3.3976891495401906]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,79,7.67396842199879,7.3951284391204819,7.1162884562421747,6.8538108342571471,6.607695573165401,6.361580312073654,6.0980239029581931,5.8344674938427321,5.5455731129472072,5.2313407602716175,4.9171084075960287,4.6987325517503553,4.480356695904681,4.0770360325664052,3.4887705617355271]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,80,7.7976626210856832,7.516779697948123,7.2358967748105627,6.9712911398643262,6.7229627931094136,6.4746344463545009,6.2092403954551152,5.9438463445557304,5.6534264206923002,5.3379806238648237,5.0225348270373482,4.8046963595712473,4.5868578921051473,4.1789930153771015,3.5811017293871092]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,81,7.9217768645360991,7.6388849548680451,7.355993045199992,7.0892888416512188,6.8387723442217272,6.5882558467922356,6.3210680516225182,6.0538802564528007,5.7620030561667326,5.445436450764312,5.1288698453618915,4.9116985000945315,4.6945271548271714,4.2821889405581217,3.6746838572873814]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,82,8.0463073664600238,7.7614402888606353,7.476573211261246,7.2077997986902638,6.9551200511476887,6.7024403036051137,6.4335026613505146,6.1645650190959147,5.8712989445408654,5.5537044376853668,5.2361099308298682,5.0197363552089493,4.8033627795880305,4.3866233733187832,3.7695181364012083]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,83,8.1712504209235792,7.8844418603459765,7.5976332997683729,7.3268199534517384,7.0720018213960731,6.8171836893404079,6.5465400948774954,6.275896500414583,5.9813100842497429,5.662780846382975,5.3442516085162071,5.1288073475118834,4.9133630865075597,4.4922958854010648,3.8656057441923988]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,84,8.2966023993156242,8.0078859085289285,7.7191694177422336,7.446345329136963,7.1894136427131183,6.9324819562892728,6.660176300303025,6.3878706443167781,6.0920325448029544,5.7726620017615558,5.4532914587201562,5.2389089391881267,5.0245264196560981,4.5992060549062677,3.9629478449386348]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,85,8.4223597478316421,8.1317687488615178,7.8411777498913926,7.566372027127616,7.3073515805701881,7.0483311340127601,6.7744073012066508,6.5004834684005424,6.2034624646855745,5.8833442900617463,5.5632261154379181,5.3500386309327013,5.1368511464274835,4.707353466128394,4.0615455900354336]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,86,8.5485189850680001,8.2560867706158874,7.9636545561637728,7.6868962245447197,7.4258117757587252,7.1647273269727316,6.8892291943666404,6.61373106176055,6.3155960493450092,5.9948241571200169,5.6740522648950256,5.4621939609153163,5.250335656935607,4.8167377093936521,4.1614001182894507]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,87,8.6750766997209041,8.3808364345620703,8.0865961694032347,7.8079141719115261,7.5447904420869438,7.2816667122623606,7.0046381475736599,6.72760958288496,6.4284295692596105,6.1070981066976131,5.7857666441356148,5.5753725037846129,5.364978363433611,4.9273583809060453,4.2625125562019157]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,88,8.8020295483839686,8.5060142707445578,8.2099989931051471,7.9294221909144662,7.6642838641725177,7.3991455374305684,7.1206303975340628,6.8421152576375572,6.5419593580845419,6.2201626988750158,5.8983660396654898,5.6895718697099387,5.4807776997543867,5.0392150825985285,4.3648840182423632]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,89,8.9293742534393452,8.6316168763526342,8.3338594992659232,8.0514166722572078,7.7842883953264908,7.5171601183957728,7.2372022478583684,6.9572443773209631,6.6561818108711304,6.3340145485088692,6.011847286146609,5.8047897034590843,5.5977321207715605,5.1523074219896099,4.4685156071132326]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,90,9.0571076010373943,8.7576409136794808,8.4581742263215656,8.1738940736029395,7.9048004555236018,7.6357068374442632,7.3543500671305182,7.0729932968167724,6.7710933823559865,6.4486503237481596,6.1262072651403328,5.9210236835101373,5.7158401018799418,5.2666350120451684,4.5734084140058169]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,91,9.1852264391600809,8.8840831081651928,8.5829397771703064,8.2968509176000218,8.0258165294543389,7.7547821413086551,7.4720702870536257,7.1893584327985964,6.8866905853162859,6.5640667446066931,6.2414429038971004,6.038271521195731,5.8351001384943615,5.3821974710450107,4.6795635188476794]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,92,9.3137276757639373,9.0109402465197022,8.7081528172754652,8.4202837899872165,8.1473331646549578,7.8743825393226992,7.5903594006686355,7.3063362620145718,7.0029699889881085,6.6802605815892449,6.3575511741903812,6.1565309598783511,5.955510745566321,5.4989944224542837,4.7869819905422393]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,93,9.4426082769983726,9.1382091749211938,8.8338100728440168,8.5441893377740126,8.2693469697111794,7.9945046016483463,7.7092139606420576,7.4239233196357688,7.1199282175446506,6.7972286543687037,6.4745290911927569,6.2757997741550682,6.0770704571173804,5.617025494799214,4.8956648872005708]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,94,9.5718652654955942,9.2658867972864645,8.9599083290773347,8.6685642674925401,8.3918546125320823,8.1151449575716246,7.8286305776194878,7.542116197667351,7.2375619486314733,6.9149678305118529,6.5923737123922335,6.3960757690904853,6.199777825788737,5.7362903215472274,5.0056132563659572]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,95,9.7014957187283635,9.3939700736093954,9.0864444284904273,8.7934053435175432,8.5148528186907413,8.2363002938639411,7.9486059186417037,7.6609115434194655,7.3558679119560546,7.0334750242514712,6.7110821365468878,6.5173567794765015,6.3236314224061152,5.8567885409910856,5.1168281352314136]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,96,9.8314967674323892,9.5224560183643021,9.2134152692962132,8.9187093864508462,8.6383383698281992,8.3579673532055541,8.0691367056202381,7.780306058034923,7.4748428879290243,7.1527471953025437,6.830651502676063,6.6396406691176981,6.4486298355593332,5.9785197961368981,5.2293105508503936]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,97,9.9618655940901011,9.6513416989709508,9.3408178038518006,9.044473271567453,8.7623081021179097,8.4801429326683646,8.1902197138697463,7.9002964950711281,7.594483706354775,7.272781347720688,6.9510789890866,6.7629253301412771,6.5747716711959532,6.1014837345959068,5.343061520341136]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,98,10.092599431472699,9.780624234318207,9.4686490371637149,9.1706939273201868,8.8867589047876212,8.6028238822550573,8.3118517706943145,8.0208796591335716,7.7147872451690356,7.3935745288007073,7.0723618124323799,6.8872086823303693,6.7020555522283578,6.2256800084798387,5.458082051084812]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,99,10.223695561237864,9.9103007933435148,9.5969060254491652,9.2973683339000033,9.0116877186960291,8.7260071034920532,8.4340297540253477,8.1420524045586422,7.83575042922139,7.5151238280135901,7.1944972268057912,7.0124886724797069,6.8304801181536234,6.351108274299591,5.5743731409176105]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,100,10.35515131258034,10.040368593665647,9.7255858747509532,9.4244935218496391,9.1370915349617032,8.8496895480737674,8.5567505911085799,8.2638116341433925,7.9573702291005981,7.6374263759801977,7.3174825228597964,7.1387632737728124,6.9600440246858284,6.4777681928673383,5.6919357783173439]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,101,10.486964060932822,10.170824900267995,9.8546857396031662,9.5520665707277317,9.2629673936416896,8.9738682165556476,8.68001125723789,8.3861542979201307,8.0796436600008086,7.7604793434799211,7.4413150269590336,7.2660304851794884,7.0907459433999431,6.6056594292015447,5.8107709425842931]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,102,10.619131226715011,10.301667024230319,9.9842028217456278,9.6800846078214366,9.3893123824577458,9.0985401570940567,8.803808774534005,8.5090773919739515,8.2025677806269464,7.884279940492986,7.5659921003590256,7.3942883308731453,7.222584561387265,6.7347816524352284,5.9308796040170355]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,103,10.751650274128382,10.432892321506529,10.114134368884676,9.8085448069051182,9.51612363556786,9.2237024642306018,8.928140210765882,8.6325779573011623,8.3261396921374562,8.0088254152747638,7.6915111384120705,7.523534859666805,7.3555585809215405,6.865134535726968,6.0522627240830866]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,104,10.884518709994582,10.564498191746356,10.244477673498132,9.9374443870430209,9.6433983323810253,9.3493522777190297,9.0530026782128985,8.7566530787067673,8.4503565371227047,8.1341130534607107,7.8178695697987184,7.6537681444670493,7.4896667191353794,6.9967177561745597,6.1749212555845894]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,105,11.017734082635711,10.696482077159217,10.375230071682724,10.066780611434158,9.7711336964135231,9.4754867813928865,9.1783933325662144,8.8812998837395423,8.5752154986177516,8.260140177200844,7.9450648557839347,7.7849862817454296,7.6249077077069245,7.1295309947316392,6.2988561428195737]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,106,11.151293980794264,10.828841461418003,10.506388942041742,10.196550786297287,9.8993269941846407,9.6021032020719943,9.3043093718674026,9.0065155416628109,8.7007137991477581,8.3869041443222461,8.073094489496734,7.917187391026256,7.761280292555778,7.2635739361265008,6.4240683217384262]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,107,11.285196032591179,10.961573868601263,10.637951704611348,10.326752259794352,10.027975534150279,9.7291988085062062,9.4307480354828748,9.1322972624595415,8.8268486998047777,8.5144023475185833,8.2019559952323888,8.0503696143903554,7.898783233548321,7.3988462687836032,6.5505587200962001]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,108,11.419437904520237,11.094676862172054,10.76991581982387,10.457382420990765,10.157076665672735,9.8567709103547045,9.5577066031125,9.2586422958702972,8.9536174993546407,8.642632213565534,8.3316469277764273,8.1845311159941012,8.0374153042117751,7.5353476847472995,6.6783282576006755]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,109,11.554017300477247,11.228148043991778,10.90227878750631,10.588438698850736,10.286627778025057,9.9848168571993767,9.6851823938309707,9.3855479304625629,9.0810175333725454,8.7715912025609146,8.4621648717492839,8.3196700816030109,8.1771752914567379,7.6730778796078649,6.807377846056391]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,110,11.688931960822455,11.361985053367611,11.03503814591277,10.71991856126647,10.416626299428714,10.113334037590956,9.8131727651606635,9.5130114927303708,9.2090461734063975,8.9012768071887471,8.5935074409710968,8.4557847181395172,8.3180619953079376,7.8120365524297073,6.9377083895048273]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,111,11.824179661474773,11.49618556613194,11.168191470789107,10.851819514119398,10.547069696122813,10.242319878126226,9.941675112174412,9.6410303462225979,9.3377008261664649,9.0316865520060094,8.7256722778455558,8.5928732532441252,8.4600742286426946,7.9522234056815906,7.0693207843608112]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,112,11.959758213036542,11.630747293752639,11.301736374468737,10.984139100372518,10.677955471463981,10.371771842555445,10.070686866627362,9.7696018906992794,9.4669789327406573,9.1628179927514992,8.8586570527623412,8.7309339348497552,8.6032108169371693,8.0936381451690256,7.2022159195453224]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,113,12.095665459947403,11.765667982472724,11.435670504998043,11.116874899192226,10.809281165055269,10.501687430918315,10.200205496116263,9.8987235613142115,9.5968779678339846,9.2946687156755843,8.9924594635171839,8.8699650307683733,8.7474705980195608,8.2362804799683786,7.336394676614824]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,114,12.231899279666077,11.90094541247815,11.569991545290222,11.25002452509853,10.941044351903074,10.632064178707619,10.330228503265477,10.028392827823337,9.7273954390316089,9.4272363368902941,9.1270772347489793,9.0099648282897427,8.8928524218305061,8.380150122362986,7.4718579298871823]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,115,12.368457581879106,12.036577397092843,11.704697212306581,11.383585627142621,11.073242641600963,10.762899656059307,10.46075342493841,10.158607193817513,9.8585288860843452,9.5605185017389047,9.2625081173934642,9.1509316337918243,9.0393551501901843,8.5252467877810627,7.6086065465644559]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,116,12.505338307735144,12.17256178199953,11.839785256263918,11.517555888110483,11.205873677539227,10.894191466967971,10.591777831473426,10.28936419597888,9.9902758802157869,9.6945128841841459,9.3987498881525049,9.2928637723621801,9.1869776565718553,8.6715701947352706,7.7466413868524269]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,117,12.64253942910393,12.308896444485486,11.975253459867041,11.651933023751599,11.338935136139161,11.025937248526725,10.723299325943296,10.420661403359867,10.122634023450265,9.829217186214489,9.5358003489787126,9.4357595874301943,9.3357188258816741,8.8191200647639896,7.8859633040771389]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,118,12.780058947858885,12.445579292712164,12.111099637565443,11.786714782031753,11.472424726111091,11.15813467019043,10.855315543437156,10.552496416683882,10.255600947960707,9.9646291372676323,9.6736573265745562,9.5796174404095247,9.4855775542444913,8.9678961223741815,8.0265731447985917]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,119,12.917894895182464,12.58260826500781,12.247321634833156,11.921898942408982,11.606340187735288,11.290781433061595,10.987824150364318,10.684866867667044,10.389174315435884,10.100746493670838,9.8123186719057944,9.7244357103506793,9.6365527487955642,9.117898094985815,8.1684717489214336]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,120,13.056045330893269,12.719981329182062,12.383917327470852,12.057483315131744,11.740679292164735,11.423875269197726,11.120822843778814,10.817770418359903,10.523351816466027,10.237567038097186,9.9517822597283452,9.870212793603045,9.7886433274777449,9.2691257128777842,8.3116599498031629]

{"sheet":"CompAir6-NewCompressor","index":12,"n_rows":27,"n_cols":16,"rows_kept":27,"cut":false,"hidden":true,"merged":[[7,13,7,14],[0,1,1,10],[3,1,3,4],[3,6,3,10],[5,1,7,2],[8,1,8,2],[9,1,9,2],[10,1,10,2],[12,1,12,4],[4,6,13,10],[13,1,13,2],[13,3,13,4],[14,6,16,10],[14,1,14,2],[14,3,14,4],[15,1,15,2],[15,3,15,4],[16,1,16,2],[16,3,16,4]]}
[null,"Measure: Air Compressor"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 2: Coincidence Factors"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Program","CFsp","CFwp"]
[null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,"LBES new, SBES new, Muni new",1.17,0.98]
[null,null,null,"Value","Unit",null,"Covers the installation of oil flooded, rotary screw compressors with Variable Speed Drive or Variable Displacement capacity control with properly sized air receiver. Efficient air compressors use various  control schemes to improve compression efficiencies at partial loads."]
[null,"Total Savings",null,{"$f":"I27","v":0},"kW"]
[null,null,null,{"$f":"J27","v":0},"kWh",null,null,null,null,null,null,null,null,"Lookup Table (2026 TRM)"]
[null,null,null,0,"MMBtu",null,null,null,null,null,null,null,null,"Horsepower",null,"Savings"]
[null,"Measure Life",null,15,"Years",null,null,null,null,null,null,null,null,"Min","Max","(kW/HP)"]
[null,"CFsp",null,{"$f":"O4*100","v":117},"%",null,null,null,null,null,null,null,null,15,24,0.124]
[null,"CFwp",null,{"$f":"P4*100","v":98},"%",null,null,null,null,null,null,null,null,25,74,0.188]
[null,null,null,null,null,null,null,null,null,null,null,null,null,75,"None",0.215]
[null,"Compressed Air - Low Pressue Drop Filter"]
[null,"Measure Code",null,"COM-CA-AC"]
[null,"Market",null,"Commercial",null,null,"NOTE: For more information on this measure refer to the NH TRM. "]
[null,"Program Type",null,"Lost Opportunity"]
[null,"Category",null,"Compressed Air"]
[]
[]
[]
[null,"Table 1: Calculating Primary Energy Impact "]
[null,null,"HP","Save","Annual",null,null,null,"Savings"]
[null,null,"Compressor","kW/HP","Hours",null,null,null,"kW","kWh"]
[null,1,{"$f":"'Compressed Air Inputs'!R39","v":0},{"$f":"IF(C24<15,0,OFFSET($O$10,MATCH(C24,$N$10:$N$12,1)-1,1))","v":0},{"$f":"'Compressed Air Inputs'!S39","v":0},null,null,null,{"$f":"C24*D24","v":0},{"$f":"I24*E24","v":0}]
[null,2,{"$f":"'Compressed Air Inputs'!R40","v":0},{"$f":"IF(C25<15,0,OFFSET($O$10,MATCH(C25,$N$10:$N$12,1)-1,1))","v":0},{"$f":"'Compressed Air Inputs'!S40","v":0},null,null,null,{"$f":"C25*D25","v":0},{"$f":"I25*E25","v":0}]
[null,3,{"$f":"'Compressed Air Inputs'!R41","v":0},{"$f":"IF(C26<15,0,OFFSET($O$10,MATCH(C26,$N$10:$N$12,1)-1,1))","v":0},{"$f":"'Compressed Air Inputs'!S41","v":0},null,null,null,{"$f":"C26*D26","v":0},0]
[null,null,null,null,null,null,null,"Totals: ",{"$f":"SUM(I24:I26)","v":0},{"$f":"SUM(J24:J26)","v":0}]

{"sheet":"CompAir7-NewAirDryer","index":13,"n_rows":27,"n_cols":16,"rows_kept":27,"cut":false,"hidden":true,"merged":[[14,6,16,10],[4,6,13,10],[13,3,13,4],[14,1,14,2],[14,3,14,4],[15,1,15,2],[15,3,15,4],[16,1,16,2],[16,3,16,4],[8,1,8,2],[9,1,9,2],[10,1,10,2],[12,1,12,4],[13,1,13,2],[0,1,1,10],[1,13,1,15],[3,1,3,4],[3,6,3,10],[5,1,7,2]]}
[null,"Measure: New Refrigerated Air Dryer"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 2: Coincidence Factors"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Program","CFsp","CFwp"]
[null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,"LBES new, SBES new, Muni new",1.17,0.98]
[null,null,null,"Value","Unit",null,"The installation of cycling or variable frequency drive (VFD)-equipped refrigerated compressed air dryers. Refrigerated air dryers remove the moisture from a compressed air system to enhance overall system performance. An efficient refrigerated dryer cycles on and off or uses a variable speed drive as required by the demand for compressed air instead of running continuously. Only properly sized refrigerated air dryers used in a single-compressor system are eligible."]
[null,"Total Savings",null,{"$f":"I27","v":0},"kW"]
[null,null,null,{"$f":"J27","v":0},"kWh"]
[null,null,null,0,"MMBtu"]
[null,"Measure Life",null,15,"Years"]
[null,"CFsp",null,{"$f":"O4*100","v":117},"%"]
[null,"CFwp",null,{"$f":"P4*100","v":98},"%"]
[]
[null,"Compressed Air - Low Pressue Drop Filter"]
[null,"Measure Code",null,"COM-CA-RAD"]
[null,"Market",null,"Commercial",null,null,"NOTE: For more information on this measure refer to the NH TRM. "]
[null,"Program Type",null,"Lost Opportunity"]
[null,"Category",null,"Compressed Air"]
[]
[]
[]
[null,"Table 1: Calculating Primary Energy Impact "]
[null,null,"Dryer","Save","Annual",null,null,null,"Savings"]
[null,null,"CFM","kW/CFM","Hours",null,null,null,"kW","kWh"]
[null,1,{"$f":"'Compressed Air Inputs'!Q46","v":0},{"$f":"IF('Compressed Air Inputs'!S46=\"Yes\",0.00554,0)","v":0},{"$f":"'Compressed Air Inputs'!R46","v":0},null,null,null,{"$f":"C24*D24","v":0},{"$f":"I24*E24","v":0}]
[null,2,{"$f":"'Compressed Air Inputs'!Q47","v":0},{"$f":"IF('Compressed Air Inputs'!S47=\"Yes\",0.00554,0)","v":0},{"$f":"'Compressed Air Inputs'!R47","v":0},null,null,null,{"$f":"C25*D25","v":0},{"$f":"I25*E25","v":0}]
[null,3,{"$f":"'Compressed Air Inputs'!Q48","v":0},{"$f":"IF('Compressed Air Inputs'!S48=\"Yes\",0.00554,0)","v":0},{"$f":"'Compressed Air Inputs'!R48","v":0},null,null,null,0,0]
[null,null,null,null,null,null,null,"Totals: ",{"$f":"SUM(I24:I26)","v":0},{"$f":"SUM(J24:J26)","v":0}]

{"sheet":"Hot Water Inputs","index":14,"n_rows":24,"n_cols":19,"rows_kept":24,"cut":false,"hidden":false,"merged":[[9,18,11,18],[16,15,18,15],[16,16,18,16],[8,15,8,18],[9,15,11,15],[9,16,11,16],[0,1,0,4],[2,1,2,8],[3,1,6,8],[8,1,9,10],[9,17,11,17],[3,11,3,12],[4,11,4,12],[5,11,5,12],[2,10,2,12]]}
[null,"Hot Water Measures: Input Sheet"]
[]
[null,"Instructions",null,null,null,null,null,null,null,null,"Key"]
[null,"Please fill out all ORANGE cells in this Input Sheet with the facility's hot water system information as it relates to the selected measures on the \"Measure Summary\" tab. Measures referenced by this sheet include showerheads, steam traps and water heaters.",null,null,null,null,null,null,null,null,null,"Input Cells"]
[null,null,null,null,null,null,null,null,null,null,null,"Guidance/ Information Cells"]
[null,null,null,null,null,null,null,null,null,null,null,"Calculation Cells"]
[]
[]
[null,"Table 1: ECM Questions",null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 2: Showerheads"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Quantity of\nthermostatic shut off\nvalves to be installed","Quantity of low\nflow showerheads\nto be installed","Quantity of low flow\nshowerhead with integrated \nthermostatic valve to be installed","Proposed low \nflow showerhead \nflow rate (gpm)"]
[null,"Hot Water ECM1 - Showerheads"]
[null,"Has Table 2 been completed?"]
[null,"Inventory & location of shut off valve & showerhead locations submitted to NHSaves?",null,null,null,null,null,null,null,null,null,{"$f":"IF(K13=\"No\",\"Please submit this\",\"\")","v":""}]
[null,"Cut sheets for installed equipment submitted to NHSaves?",null,null,null,null,null,null,null,null,null,{"$f":"IF(K14=\"No\",\"Please submit this\",\"\")","v":""},null,null,null,null,null,null,{"$f":"IF(S13>1.5,\"Flow rate must be 1.5 GPM or less\",\"\")","v":""}]
[null,"Hot Water ECM2 - Steam Traps"]
[null,"Table 3 has been completed?",null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 3: Steam Traps"]
[null,"Inventory & location of steam traps to be replaced/repaired provided to NHSaves?",null,null,null,null,null,null,null,null,null,{"$f":"IF(K17=\"No\",\"Please submit this\",\"\")","v":""},null,null,null,"Quantity of low pressure\n(≤ 10 psig) traps to be\nreplaced/repaired","Quantity of high\npressure (> 10 psig) traps\nto be replaced/repaired"]
[null,"Hot Water ECM3 - Water Heaters"]
[null,"Table 4 completed?"]
[null,"Inventory of Water Heaters provided to NHSaves?",null,null,null,null,null,null,null,null,null,{"$f":"IF(K20=\"No\",\"Please submit this\",\"\")","v":""}]
[null,"Cutsheet provided to NHSaves?",null,null,null,null,null,null,null,null,null,{"$f":"IF(K21=\"No\",\"Please submit this\",\"\")","v":""}]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 4: Water Heaters"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Water Heater type","Quantity","Capacity (MBtuh)","Building hours"]

{"sheet":"HW1-Showerheads","index":15,"n_rows":38,"n_cols":19,"rows_kept":38,"cut":false,"hidden":true,"merged":[[23,2,23,4],[1,14,1,18],[17,1,17,2],[17,3,17,4],[26,14,26,17],[3,1,3,4],[3,6,3,10],[5,1,7,2],[8,1,8,2],[4,6,13,10],[16,1,16,2],[16,3,16,4],[13,1,13,4],[14,1,14,2],[14,3,14,4],[17,14,17,15],[15,1,15,2],[0,1,1,10],[9,1,9,2],[10,1,10,2],[11,1,11,2],[15,3,15,4],[14,6,17,10]]}
[null,"Measure: Showerheads",null,null,null,null,null,null,null,null,null,null,null,null,"Additional information"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 2: Savings Values"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Measure Name","Fuel Type","ΔkWh","ΔkW","ΔMMBtu"]
[null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,null,"Thermostatic Shut-Off Valve","Gas",0,0,0.33]
[null,null,null,"Value","Unit",null,"This measure considers savings associated with showerheads.\n\nDefinitions:\nThermostatic Shut-Off Valve: Installation of a stand-alone thermostatic shut-off valve on standard flow showerhead.\nLow-Flow Showerhead, Electric, Gas, Oil, Propane: Installation of a low-flow showerhead with a flow rate of 1.5 GPM or less.",null,null,null,null,null,null,null,"Thermostatic Shut-Off Valve","Electric",69,0.02,0]
[null,"Total Savings",null,{"$f":"IF('Hot Water Inputs'!S13 > 1.5,0,I29)","v":0},"kW",null,null,null,null,null,null,null,null,null,"Thermostatic Shut-Off Valve","Fuel Oil",0,0,0.33]
[null,null,null,{"$f":"IF('Hot Water Inputs'!S13>1.5,0,J29)","v":0},"kWh",null,null,null,null,null,null,null,null,null,"Thermostatic Shut-Off Valve","Propane",0,0,0.33]
[null,null,null,{"$f":"IF('Hot Water Inputs'!S13>1.5,0,K29)","v":0},"MMBtu",null,null,null,null,null,null,null,null,null,"Low Flow Showerhead","Electric",507,0.09,0]
[null,"Annual water savings",null,{"$f":"IFERROR(VLOOKUP(D26,$O$20:$P$22,2,FALSE)*C26,0)+IFERROR(VLOOKUP(D27,$O$20:$P$22,2,FALSE)*C27,0) + IFERROR(VLOOKUP(D28,$O$20:$P$22,2,FALSE)*C28,0)","v":0},"gallons",null,null,null,null,null,null,null,null,null,"Low Flow Showerhead","Gas",0,0,2.65]
[null,"Measure Life",null,{"$f":"IFERROR(SUMPRODUCT(C26:C28,E26:E28)/SUM(C26:C28),12)","v":12},"Years",null,null,null,null,null,null,null,null,null,"Low Flow Showerhead","Fuel Oil",0,0,2.65]
[null,"CFsp",null,{"$f":"IF($D$26=$O$29,VLOOKUP('Project Info'!$D$27,$P$29:$R$32,2,FALSE),IF($D$26=$O$33,VLOOKUP('Project Info'!$D$27,$P$33:$R$36,2,FALSE),IF($D26=$O$37,VLOOKUP('Project Info'!$D$27,$P$37:$R$38,2,FALSE),0)))*100","v":{"$error":"#N/A"}},"%",null,null,null,null,null,null,null,null,null,"Low Flow Showerhead","Propane",0,0,2.65]
[null,"CFwp",null,{"$f":"IF($D$26=$O$29,VLOOKUP('Project Info'!$D$27,$P$29:$R$32,3,FALSE),IF($D$26=$O$33,VLOOKUP('Project Info'!$D$27,$P$33:$R$36,3,FALSE),IF($D26=O37,VLOOKUP('Project Info'!$D$27,$P$37:$R$38,3,FALSE),0)))*100","v":{"$error":"#N/A"}},"%",null,null,null,null,null,null,null,null,null,"OMP Low-Flow Shower Head  with Integrated Thermostatic Valve","Gas",0,0,1.41]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"OMP Low-Flow Shower Head with Integrated Thermostatic Valve","Electric",183,0.04,0]
[null,"Hot Water - Showerheads"]
[null,"Measure Code",null,"COM-HW-SH",null,null,"NOTE: For more information on this measure refer to the NH TRM. "]
[null,"Market",null,"Commercial"]
[null,"Program Type",null,"Retrofit"]
[null,"Category",null,"Hot Water",null,null,null,null,null,null,null,null,null,null,"Table 3: Annual Water Savings"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Measure Name","Gallons saved per unit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Thermostatic Shut-Off Valve",558]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Low Flow Showerhead",7300]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"OMP Low-Flow Shower Head  with Integrated Thermostatic Valve",558]
[null,"Table 1: Calculating Primary Energy Impact "]
[null,null,"Inputs",null,null,null,null,null,"Savings"]
[null,null,"Quantity","Measure Name","Measure Life",null,null,null,"kW","kWh","MMBtu"]
[null,1,{"$f":"'Hot Water Inputs'!P13","v":0},"Thermostatic Shut-Off Valve",15,null,null,null,{"$f":"IFERROR(IF($D26=$O$4,VLOOKUP('Project Info'!$D$27,$P$4:$S$7,3,FALSE),IF($D26=$O$8,VLOOKUP('Project Info'!$D$27,$P$8:$S$11,3,FALSE),IF($D26=$O$12,VLOOKUP('Project Info'!$D$27,$P$12:$S$13,3,FALSE),0)))*$C26,0)","v":0},{"$f":"IFERROR(IF($D26=$O$4,VLOOKUP('Project Info'!$D$27,$P$4:$S$7,2,FALSE),IF($D26=$O$8,VLOOKUP('Project Info'!$D$27,$P$8:$S$11,2,FALSE),IF($D26=$O$12,VLOOKUP('Project Info'!$D$27,$P$12:$S$13,2,FALSE),0)))*$C26,0)","v":0},{"$f":"IFERROR(IF($D26=$O$4,VLOOKUP('Project Info'!$D$27,$P$4:$S$7,4,FALSE),IF($D26=$O$8,VLOOKUP('Project Info'!$D$27,$P$8:$S$11,4,FALSE),IF($D26=O12,VLOOKUP('Project Info'!$D$27,$P$12:$S$13,4,FALSE),0)))*$C26,0)","v":0}]
[null,2,{"$f":"'Hot Water Inputs'!Q13","v":0},"Low Flow Showerhead",10,null,null,null,{"$f":"IFERROR(IF($D27=$O$4,VLOOKUP('Project Info'!$D$27,$P$4:$S$7,3,FALSE),IF($D27=$O$8,VLOOKUP('Project Info'!$D$27,$P$8:$S$11,3,FALSE),IF($D27=$O$12,VLOOKUP('Project Info'!$D$27,$P$12:$S$13,3,FALSE),0)))*$C27,0)","v":0},{"$f":"IFERROR(IF($D27=$O$4,VLOOKUP('Project Info'!$D$27,$P$4:$S$7,2,FALSE),IF($D27=$O$8,VLOOKUP('Project Info'!$D$27,$P$8:$S$11,2,FALSE),IF($D27=$O$12,VLOOKUP('Project Info'!$D$27,$P$12:$S$13,2,FALSE),0)))*$C27,0)","v":0},{"$f":"IFERROR(IF($D27=$O$4,VLOOKUP('Project Info'!$D$27,$P$4:$S$7,4,FALSE),IF($D27=$O$8,VLOOKUP('Project Info'!$D$27,$P$8:$S$11,4,FALSE),IF($D27=O12,VLOOKUP('Project Info'!$D$27,$P$12:$S$13,4,FALSE),0)))*$C27,0)","v":0},null,null,null,"Table 4: Coincidence Factors - Summer/Winter Peak"]
[null,3,{"$f":"'Hot Water Inputs'!R13","v":0},"OMP Low-Flow Shower Head  with Integrated Thermostatic Valve",10,null,null,null,{"$f":"IFERROR(IF($D28=$O$4,VLOOKUP('Project Info'!$D$27,$P$4:$S$7,3,FALSE),IF($D28=$O$8,VLOOKUP('Project Info'!$D$27,$P$8:$S$11,3,FALSE),IF($D28=$O$12,VLOOKUP('Project Info'!$D$27,$P$12:$S$13,3,FALSE),0)))*$C28,0)","v":0},{"$f":"IFERROR(IF($D28=$O$4,VLOOKUP('Project Info'!$D$27,$P$4:$S$7,2,FALSE),IF($D28=$O$8,VLOOKUP('Project Info'!$D$27,$P$8:$S$11,2,FALSE),IF($D28=$O$12,VLOOKUP('Project Info'!$D$27,$P$12:$S$13,2,FALSE),0)))*$C28,0)","v":0},null,null,null,null,"Measure Name","Fuel Type","CFsp","CFwp"]
[null,null,null,null,null,null,null,"Totals:",{"$f":"SUM(I26:I27)","v":0},{"$f":"SUM(J26:J27)","v":0},{"$f":"SUM(K26:K27)","v":0},null,null,null,"Thermostatic Shut-Off Valve","Gas",0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Thermostatic Shut-Off Valve","Electric",0.31,0.81]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Thermostatic Shut-Off Valve","Fuel Oil",0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Thermostatic Shut-Off Valve","Propane",0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Low Flow Showerhead","Electric",0.31,0.81]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Low Flow Showerhead","Gas",0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Low Flow Showerhead","Fuel Oil",0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Low Flow Showerhead","Propane",0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"OMP Low-Flow Shower Head  with Integrated Thermostatic Valve","Gas",0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"OMP Low-Flow Shower Head  with Integrated Thermostatic Valve","Electric",0.31,0.81]

{"sheet":"HW2-SteamTraps","index":16,"n_rows":27,"n_cols":21,"rows_kept":27,"cut":false,"hidden":true,"merged":[[8,1,8,2],[9,1,9,2],[10,1,10,2],[4,6,12,10],[1,14,1,20],[0,1,1,10],[3,1,3,4],[3,6,3,10],[5,1,7,2],[12,1,12,4],[13,1,13,2],[13,6,16,10],[14,1,14,2],[16,1,16,2],[15,1,15,2]]}
[null,"Measure: Steam Traps"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 2: Savings Values"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Fuel Type","Pressure","ΔkWh","ΔkW","ΔMMBtu","CFsp","CFwp"]
[null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,null,"Gas","Low Pressure (≤= 10 psig)",0,0,8.4,0,0]
[null,null,null,"Value","Unit",null,"This measure considers the repair or replacement of malfunctioning steam traps.",null,null,null,null,null,null,null,"Gas","High Pressure (> 10 psig)",0,0,35.6,0,0]
[null,"Total Savings",null,{"$f":"I27","v":0},"kW",null,null,null,null,null,null,null,null,null,"Oil","Low Pressure (≤= 10 psig)",0,0,8.4,0,0]
[null,null,null,{"$f":"J27","v":0},"kWh",null,null,null,null,null,null,null,null,null,"Oil","High Pressure (> 10 psig)",0,0,35.6,0,0]
[null,null,null,{"$f":"K27","v":0},"MMBtu",null,null,null,null,null,null,null,null,null,"Propane","Low Pressure (≤= 10 psig)",0,0,8.4,0,0]
[null,"Measure Life",null,6,"Years",null,null,null,null,null,null,null,null,null,"Propane","High Pressure (> 10 psig)",0,0,35.6,0,0]
[null,"CFsp",null,0,"%"]
[null,"CFwp",null,0,"%"]
[]
[null,"Hot Water - Steam Traps"]
[null,"Measure Code",null,"COM-HVAC-ST",null,null,"NOTE: For more information on this measure refer to the NH TRM. "]
[null,"Market",null,"Commercial"]
[null,"Program Type",null,"Retrofit"]
[null,"Category",null,"HVAC"]
[]
[]
[]
[]
[null,"Table 1: Calculating Primary Energy Impact "]
[null,null,"Inputs",null,null,null,null,null,"Savings"]
[null,null,"Quantity","Steam Pressure",null,null,null,null,"kW","kWh","MMBtu"]
[null,1,{"$f":"'Hot Water Inputs'!P20","v":0},"Low Pressure (≤= 10 psig)",null,null,null,null,0,0,{"$f":"IFERROR(VLOOKUP(D25,$P$4:$S$5,4,FALSE),0)*C25","v":0}]
[null,2,{"$f":"'Hot Water Inputs'!Q20","v":0},"High Pressure (> 10 psig)",null,null,null,null,0,0,{"$f":"IFERROR(VLOOKUP(D26,$P$4:$S$5,4,FALSE),0)*C26","v":0}]
[null,null,null,null,null,null,null,"Totals:",{"$f":"SUM(I25:I26)","v":0},{"$f":"SUM(J25:J26)","v":0},{"$f":"SUM(K25:K26)","v":0}]

{"sheet":"HW3-WaterHeater","index":17,"n_rows":32,"n_cols":16,"rows_kept":32,"cut":false,"hidden":true,"merged":[[26,3,26,6],[27,3,27,6],[28,3,28,6],[29,3,29,6],[30,3,30,6],[21,1,21,9],[22,8,22,9],[24,3,24,6],[25,3,25,6],[22,1,22,7],[0,1,1,9],[3,1,3,4],[3,6,3,9],[4,6,12,9],[14,1,14,2],[13,6,16,9],[5,1,7,2],[14,3,14,4],[16,1,16,2],[16,3,16,4],[8,1,8,2],[12,1,12,4],[13,3,13,4],[15,3,15,4],[13,1,13,2],[15,1,15,2],[9,12,10,12],[9,13,10,13],[9,14,10,14],[9,15,10,15],[5,12,5,15],[1,12,1,14],[7,12,8,12],[7,13,8,13],[7,14,8,14],[7,15,8,15],[11,12,12,12],[11,13,12,13],[11,14,12,14],[11,15,12,15],[13,12,14,12],[13,13,14,13],[13,14,14,14],[13,15,14,15],[19,12,20,12],[19,13,20,13],[19,14,20,14],[19,15,20,15],[15,12,16,12],[15,13,16,13],[15,14,16,14],[15,15,16,15],[17,12,18,12],[17,13,18,13],[17,14,18,14],[17,15,18,15]]}
[null,"Measure: Water Heaters"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Table 2: Coincidence Factors"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Program","CFsp","CFwp"]
[null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,"LBES, SBES, Muni",0.43099999999999999,0.747]
[null,null,null,"Value","Unit",null,"Installation of a heat pump hot water heater, indirect water heater, on demand tankless water heater, volume water heater or condensing water heater through the midstream channel. \n\n"]
[null,"Total Savings",null,{"$f":"IFERROR(I32/'Hot Water Inputs'!S25,0)","v":0},"kW",null,null,null,null,null,null,null,"Table 3: Coincidence Factors"]
[null,null,null,{"$f":"I32","v":0},"kWh",null,null,null,null,null,null,null,"Measure Name ","ΔkWh ","ΔMMBtu ","ΔMMBtu / Mbtuh "]
[null,null,null,{"$f":"J32","v":0},"MMBtu",null,null,null,null,null,null,null,"Midstream Heat Pump Water Heater, 120 gallons",2082,0,0]
[null,"Measure Life:\n Heat Pump WH",null,{"$f":"IFERROR(SUMPRODUCT(H25:H31,C25:C31)/SUM(C25:C31),AVERAGE(H25:H31))","v":14.857142857142858},"Years"]
[null,"CFsp",null,{"$f":"N4*100","v":43.1},"%",null,null,null,null,null,null,null,"Midstream Heat Pump Water Heater, 55-80 gallons",1171,0,0]
[null,"CFwp",null,{"$f":"O4*100","v":74.7},"%"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Midstream Heat Pump Water Heater, <55 gallons",4556,0,0]
[null,"HVAC - Boiler Reset Controls"]
[null,"Measure Code",null,"COM-HW-WH",null,null,"NOTE: For more information on this measure refer to the NH TRM. ",null,null,null,null,null,"Midstream Indirect Water Heater",0,19,0]
[null,"Markets ",null,"Commercial"]
[null,"Program Types ",null,"Lost Opportunity",null,null,null,null,null,null,null,null,"Midstream on Demand Tankless Water Heater",0,8.9,0]
[null,"Categories ",null,"Hot Water"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Midstream Volume Water Heater",0,0,0.60770000000000002]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,"Midstream Condensing Gas Water Heater",0,0,0.14410000000000001]
[]
[null,"Table 1: Calculating Primary Energy Impact "]
[null,null,null,null,null,null,null,null,"Savings"]
[null,null,"Quantity","Measure Name",null,null,null,"Measure Life","kWh","MMBtu"]
[null,1,{"$f":"IF('Hot Water Inputs'!$P$25=D25,'Hot Water Inputs'!$Q$25,0)","v":0},"Midstream Heat Pump Water Heater, 120 gallons",null,null,null,13,{"$f":"N8*C25","v":0},{"$f":"O8*C25","v":0}]
[null,2,{"$f":"IF('Hot Water Inputs'!$P$25=D26,'Hot Water Inputs'!$Q$25,0)","v":0},"Midstream Heat Pump Water Heater, 55-80 gallons",null,null,null,13,{"$f":"N10*C26","v":0},{"$f":"O8*C26","v":0}]
[null,3,{"$f":"IF('Hot Water Inputs'!$P$25=D27,'Hot Water Inputs'!$Q$25,0)","v":0},"Midstream Heat Pump Water Heater, <55 gallons",null,null,null,13,{"$f":"N12*C27","v":0},{"$f":"O12*C27","v":0}]
[null,4,{"$f":"IF('Hot Water Inputs'!$P$25=D28,'Hot Water Inputs'!$Q$25,0)","v":0},"Midstream Indirect Water Heater",null,null,null,15,{"$f":"N14*C28","v":0},{"$f":"O14*C28","v":0}]
[null,5,{"$f":"IF('Hot Water Inputs'!$P$25=D29,'Hot Water Inputs'!$Q$25,0)","v":0},"Midstream on Demand Tankless Water Heater",null,null,null,20,{"$f":"N16*C29","v":0},{"$f":"O16*C29","v":0}]
[null,6,{"$f":"IF('Hot Water Inputs'!$P$25=D30,'Hot Water Inputs'!$Q$25,0)","v":0},"Midstream Volume Water Heater",null,null,null,15,{"$f":"N18*C30","v":0},{"$f":"IF('Hot Water Inputs'!$P$25=D30,P18*C30*'Hot Water Inputs'!$S$25,0)","v":0}]
[null,7,{"$f":"IF('Hot Water Inputs'!$P$25=D31,'Hot Water Inputs'!$Q$25,0)","v":0},"Midstream Condensing Gas Water Heater",null,null,null,15,{"$f":"N20*C31","v":0},{"$f":"IF('Hot Water Inputs'!$P$25=D31,P20*C31*'Hot Water Inputs'!$S$25,0)","v":0}]
[null,null,null,null,null,null,null,"Totals:",{"$f":"SUM(I25:I31)","v":0},{"$f":"SUM(J25:J31)","v":0}]

{"sheet":"HVAC Inputs","index":18,"n_rows":138,"n_cols":31,"rows_kept":138,"cut":false,"hidden":false,"merged":[[0,1,1,22],[3,10,3,16],[4,10,7,16],[12,8,12,12],[3,1,3,5],[3,7,3,8],[12,14,12,19],[62,13,62,18],[41,16,42,16],[41,17,42,17],[63,14,63,18],[41,13,42,13],[41,14,42,14],[41,15,42,15],[18,1,18,5],[4,3,10,3],[41,12,42,12],[41,19,42,19],[41,18,42,18],[13,15,13,19]]}
[null,"HVAC, Building & Equipment Control & Pipe Insulation Measures: Input Sheet"]
[]
[]
[null,"Input Tables for HVAC, Control & Pipe Insulation Measures",null,null,null,null,null,"Key",null,null,"Instructions"]
[null,1,"Boiler Reset Controls",null,1,"Wifi Thermostats",null,null,"Input Cells",null,"Please fill out all ORANGE cells on this Input Sheet with the facility's building and equipment control, duct insulation & sealing, and/or HVAC information relative to the customer measures selected on the \"Measure Summary\" tab. All aforementioned measures will reference this sheet for the calculations."]
[null,"1 &2","Demand Control Ventilation",null,1,"Programmable Thermostats",null,null,"Guidance/ Information Cells"]
[null,"1 & 2","Dual Enthalpy Economizer",null,3,"Circulator Pumps",null,null,"Calculation Cells"]
[null,"1 & 5","Duct Insulation & Sealing",null,4,"Heat Pumps"]
[null,1,"Hotel Occupancy Sensors",null,8,"Unitary & Split AC"]
[null,"1 & 6","Pipe Insulation: Domestic Hot Water ",null,9,"Chillers"]
[null,"1 & 7","Pipe Insulation: Space Heating Steam & Hot Water",null,10,"Packaged Terminal Heat Pumps"]
[]
[null,"Table 1: General ECM Questions",null,null,null,null,null,null,"Table 2: DCV and Dual Enthalpy Economizer Measures",null,null,null,null,null,"Table 4: Heat Pumps",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Yes"]
[null,"HVAC ECM1 - Boiler Reset Controls",null,null,null,null,null,null,"HVAC Unit","Area","Capacity","Add","Add Dual Enthalpy",null,"Operating Profile:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,"Quantity of boilers (on which reset is to be implemented)",null,null,null,null,null,null,"ID","Served","(tons)","DCV","Economizer",null,"Unit Types for Install:",1,2,3,4,5]
[null,"Cut sheet for proposed controller provided to NHSaves?",null,null,null,null,null,null,null,null,null,null,null,null,"Equipment Tag:"]
[null,"Hot Water temperature set point prior to hot water reset:",null,null,null,null,null,null,null,null,null,null,null,null,"Model Numbers:"]
[null,"Outdoor air temperature at which boiler will shut off:",null,null,null,null,null,null,null,null,null,null,null,null,"Quantity Units Installed:"]
[null,"Sequence of operation for temp reset (new temp setpoints and correlating outside temperatures) provided to NHSaves?",null,null,null,null,null,null,null,null,null,null,null,null,"Equipment Type:"]
[null,"HVAC ECM2 - Demand Control Ventilation (DCV)- Table 3",null,null,null,null,null,null,null,null,null,null,null,null,"Suplemental Electric Resistance?:"]
[null,"Table 2 has been completed?",null,null,null,null,null,null,null,null,null,null,null,null,"Cooling Capacity - TONS:"]
[null,"Mechanical Schedule provided to NHSaves?",null,null,null,null,null,null,null,null,null,null,null,null,"If Air to Air Heat Pump < 5.4 tons, Split or Packaged?:"]
[null,"New control sequence of operation provided to NHSaves?",null,null,null,null,null,null,null,null,null,null,null,null,"If VRF,  Heat Recovery or No Heat Recovery?:"]
[null,"HVAC ECM3 - Dual Enthalpy Economizer Controls - Table 3",null,null,null,null,null,null,null,null,null,null,null,null,"Cooling Efficiency (EER2):"]
[null,"Table 2 has been completed?",null,null,null,null,null,null,null,null,null,null,null,null,"Cooling Efficiency IEER (SEER2 if < 5.4 tons):"]
[null,"Mechanical Schedule provided to NHSaves?",null,null,null,null,null,null,null,null,null,null,null,null,"Heating Efficiency  COP (HSPF2 if < 5.4 tons):"]
[null,"New control sequence of operation provided to NHSaves?",null,null,null,null,null,null,"Table 3: Circulator Pump"]
[null,"HVAC ECM4 - Duct Insulation- Table 5",null,null,null,null,null,null,"Quantity","Pump","Pump"]
[null,"Table 5 has been completed?",null,null,null,null,null,null,"#","Type","hp"]
[null,"Pictures of ductwork to be insulated provided to NHSaves?",null,null,null,null,null,null,null,null,null,null,null,null,"HVAC Measure 5: Duct Sealing"]
[null,"Cut sheet(s) of insulation installed provided to NHSaves?",null,null,null,null,null,null,null,null,null,null,null,null,"Duct","Insulated ","Cool Cap","Heat Cap"]
[null,"HVAC ECM5 - Duct Sealing- Table 5",null,null,null,null,null,null,null,null,null,null,null,null,"Location","(Yes/No)","kBtu/hr","kBtu/hr"]
[null,"Table 5 completed?"]
[null,"Pictures of ductwork to be sealed provided to NHSaves?"]
[null,"Cut sheet(s) of air sealing product installed provided to NHSaves?"]
[null,"HVAC ECM6 - Hotel Occupancy Sensors",null,null,null,null,null,null,null,null,null,{"$f":"IF(AND(L38=\"Qualifies\",L39=\"Qualifies\",L40=\"Qualifies\",L41=\"Qualifies\",L42=\"Qualifies\"),\"Measure qualifies for savings\",\"Measure does not qualify for savings\")","v":"Measure does not qualify for savings"}]
[null,"# of Rooms where occupancy sensors are being installed:"]
[null,"Are the sensors controlled by a front desk system?",null,null,null,null,null,null,null,null,null,{"$f":"IF(K38=\"Yes\", \"Does not qualify; sensors controlled by a front desk system are not eligible\", IF(K38=\"No\",\"Qualifies\",\"\"))","v":""}]
[null,"Does the hotel operate 12 months/year?",null,null,null,null,null,null,null,null,null,{"$f":"IF(K39=\"Yes\", \"Qualifies\", IF(K39=\"No\",\"Does not qualify; hotel must operate all 12 months to be eligible\",\"\"))","v":""}]
[null,"Do the new controls include a) occupancy sensors?",null,null,null,null,null,null,null,null,null,{"$f":"IF(K40=\"Yes\", \"Qualifies\", IF(K40=\"No\",\"Does not qualify\",\"\"))","v":""}]
[null,"… b) window/door switches for rooms that have operable window or patio doors?",null,null,null,null,null,null,null,null,null,{"$f":"IF(K41=\"Yes\", \"Qualifies\", IF(K41=\"No\",\"Does not qualify\",\"\"))","v":""},null,"Table 6: Domestic Hot Water Pipe Insulation"]
[null,"… c) temperature set backs to 65F in the heating mode and 78F in the cooling mode when occupancy sensor is in unoccupied mode?",null,null,null,null,null,null,null,null,null,{"$f":"IF(K42=\"Yes\", \"Qualifies\", IF(K42=\"No\",\"Does not qualify; adjust set backs to be eligible for savings\",\"\"))","v":""},null,"Pipe Location","In Conditioned Space?","Nominal Pipe Size (in)","Linear feet of pipe to be insulated","Pipe Material","Insulation","Annual Operating Hours"]
[null,"If temperature set backs are included but are not set to the above temperatures, list the unoccupied heating setpoint: (˚ F)"]
[null,"If temperature set backs are included but are not set to the above temperatures, list the unoccupied cooling setpoint: (˚ F)",null,null,null,null,null,null,null,null,null,null,1,null,null,null,null,null,null,null,{"$f":"IF(O44=\"Yes\",\"No savings result from conditioned space\",\"\")","v":""}]
[null,"New temperature control sequence with setpoints provided to NHSaves?",null,null,null,null,null,null,null,null,null,null,2,null,null,null,null,null,null,null,{"$f":"IF(O45=\"Yes\",\"No savings result from conditioned space\",\"\")","v":""}]
[null,"HVAC ECM7 - Domestic Hot Water Pipe Insulation- Table 6",null,null,null,null,null,null,null,null,null,null,3,null,null,null,null,null,null,null,{"$f":"IF(O46=\"Yes\",\"No savings result from conditioned space\",\"\")","v":""}]
[null,"Table 6 completed?"]
[null,"Inventory of pipe to be insulated provided to NHSaves?"]
[null,"Picture of existing un-insulated piping provided to NHSaves?",null,null,null,null,null,null,null,null,null,null,null,"Table 7: Space Heating Steam or Hot Water Pipe Insulation",null,null,null,null,null,null,null,"Table 8: Unitary and split measures"]
[null,"Cut sheet of insulation to be installed provided to NHSaves?",null,null,null,null,null,null,null,null,null,null,null,"Pipe","In Conditioned","Linear Feet of Pipe",null,null,null,null,null,"Operating Profile:"]
[null,"HVAC ECM8 - Space Heating Steam or Hot Water Pipe Insulation- Table 7",null,null,null,null,null,null,null,null,null,null,null,"Location","Space?","to be insulated",null,null,null,null,null,"Unit Types for Install:",1,2,3,4,5,6]
[null,"Table 7 completed?",null,null,null,null,null,null,null,null,null,null,1,null,null,null,null,null,null,null,null,"Equipment Tag:"]
[null,"Inventory of pipe to be insulated provided to NHSaves?",null,null,null,null,null,null,null,null,null,null,2,null,null,null,null,null,null,null,null,"Model Numbers:"]
[null,"Picture of existing un-insulated piping provided to NHSaves?",null,null,null,null,null,null,null,null,null,null,3,null,null,null,null,null,null,null,null,"Quantity Units Installed:"]
[null,"Cut sheet of insulation to be installed provided to NHSaves?",null,null,null,null,null,null,null,null,null,{"$f":"IF(G55=\"\",\"\",IF(G55=\"Yes\",\"Qualifies\",\"Does not qualify\"))","v":""},4,null,null,null,null,null,null,null,null,"Condenser Type:"]
[null,"HVAC ECM9 - Wifi Thermostat",null,null,null,null,null,null,null,null,null,null,5,null,null,null,null,null,null,null,null,"Cooling Capacity - TONS:"]
[null,"Quantity of thermostats to be installed",null,null,null,null,null,null,null,null,null,{"$f":"IF(L59=\"Qualifies\",\"Measure qualifies for savings\",\"Measure does not qualify for savings\")","v":"Measure does not qualify for savings"},6,null,null,null,null,null,null,null,null,"If < 5.4 tons, Split or Packaged?:"]
[null,"Thermostat cut sheet provided to NHSaves?",null,null,null,null,null,null,null,null,null,null,7,null,null,null,null,null,null,null,null,"Unit Heat Source:"]
[null,"Thermostat includes an outdoor air temperature algorithm in the control logic to operate heating and cooling system?",null,null,null,null,null,null,null,null,null,{"$f":"IF(K59=\"Yes\", \"Qualifies\", IF(K59=\"No\",\"Does not qualify; measure requires outdoor air temp algorithm\",\"\"))","v":""},8,null,null,null,null,null,null,null,null,"Cooling Efficiency (EER/EER2):"]
[null,"HVAC ECM10 - Programmable Thermostat",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Cooling Efficiency (IEER/SEER2):"]
[null,"Thermostat cut sheet provided to NHSaves?"]
[null,"Quantity of Programmable Thermostats?"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 9: Chillers",null,null,null,null,null,null,"Table 10: Packaged Terminal Heat Pumps"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Operating Profile",null,null,null,null,null,null,"Quantity","Capacity","Proposed"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Unit ID-Opt. (1)",null,null,null,null,null,null,"#","Btu/hr","EER","COP"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Model Numbers"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Quantity Units Installed (2)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Chiller Type (3)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Compressor Type (4)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Cooling Capacity - TONS (5)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Air Cooled New Efficiency - EER (6)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Air Cooled New Efficiency - IPLV "]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Water Cooled New Efficiency FL - kW/Ton (7)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Water Cooled New Efficiency IPLV - kW/Ton"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"Midstream Heat Pump Water Heater, 120 gallons"]
[null,"Midstream Heat Pump Water Heater, 55-80 gallons"]
[null,"Midstream Heat Pump Water Heater, <55 gallons"]
[null,"Midstream Indirect Water Heater"]
[null,"Midstream on Demand Tankless Water Heater"]
[null,"Midstream Volume Water Heater"]
[null,"Midstream Condensing Gas Water Heater"]
[]
[]
[]
[null,"TRM Appendix 2 - Cooling EFLH",null,null,null,null,null,null,null,"TRM Appendix 2 - Heating EFLH"]
[null,"Building Type","HVAC Type","Bldg & HVAC","Berlin","Concord","Manchester",null,null,"Building Type","HVAC Type","Bldg & HVAC","Berlin","Concord","Manchester"]
[null,"Community College","CV Econ",{"$f":"CONCATENATE(B96,C96)","v":"Community CollegeCV Econ"},412,627,581,null,null,"Community College","CV Econ",{"$f":"CONCATENATE(J96,K96)","v":"Community CollegeCV Econ"},1103,1098,939,null,"Building Type",{"$f":"'Project Info'!$D$20","v":0}]
[null,"Community College","CV nonecon",{"$f":"CONCATENATE(B97,C97)","v":"Community CollegeCV nonecon"},612,874,789,null,null,"Community College","CV nonecon",{"$f":"CONCATENATE(J97,K97)","v":"Community CollegeCV nonecon"},982,1014,863,null,"HVAC Type",{"$f":"'Project Info'!$D$22","v":0}]
[null,"Community College","VAV",{"$f":"CONCATENATE(B98,C98)","v":"Community CollegeVAV"},299,489,460,null,null,"Community College","VAV","Community CollegeVAV",704,462,642,null,"Building Type & HVAC Type",{"$f":"_xlfn.CONCAT(R96,R97)","v":"00"}]
[null,"Community College","Unknown","Community CollegeUnknown",365,570,530,null,null,"Community College","Unknown","Community CollegeUnknown",809,646,723,null,"Location",{"$f":"IF('Project Info'!$D$21=\"Berlin\",\"Berlin\",IF(OR('Project Info'!$D$21=\"Concord\",'Project Info'!$D$21=\"Lebanon\",'Project Info'!$D$21=\"Keene\",'Project Info'!$D$21=\"Laconia\"),\"Concord\",\"Manchester\"))","v":"Manchester"}]
[null,"High School","CV Econ","High SchoolCV Econ",252,398,330,null,null,"High School","CV Econ","High SchoolCV Econ",806,744,724,null,"Cooling EFLH",{"$f":"IF(COUNTIF(B124:B138,$R$96)>0,OFFSET($B$123,MATCH($R$96,$B$124:$B$138),MATCH($R$99,$E$95:$G$95)+2),OFFSET($D$95,MATCH($R$98,$D$96:$D$123,0),MATCH($R$99,$E$95:$G$95)))","v":{"$error":"#N/A"}}]
[null,"High School","CV nonecon","High SchoolCV nonecon",707,837,741,null,null,"High School","CV nonecon","High SchoolCV nonecon",721,699,652,null,"Heating EFLH",{"$f":"IF(COUNTIF(J124:J138,$R$96)>0,OFFSET($J$123,MATCH($R$96,$J$124:$J$138),MATCH($R$99,$M$95:$O$95)+2),OFFSET($L$95,MATCH($R$98,$L$96:$L$123,0),MATCH($R$99,$M$95:$O$95)))","v":{"$error":"#N/A"}}]
[null,"High School","VAV","High SchoolVAV",148,255,196,null,null,"High School","VAV","High SchoolVAV",383,289,274]
[null,"High School","Unknown","High SchoolUnknown",251,368,301,null,null,"High School","Unknown","High SchoolUnknown",501,423,402]
[null,"Hospital","CV Econ","HospitalCV Econ",1037,1132,1115,null,null,"Hospital","CV Econ","HospitalCV Econ",1140,1052,703]
[null,"Hospital","CV nonecon","HospitalCV nonecon",2248,2117,1865,null,null,"Hospital","CV nonecon","HospitalCV nonecon",1068,971,641]
[null,"Hospital","VAV","HospitalVAV",1014,1089,1079,null,null,"Hospital","VAV","HospitalVAV",738,781,437]
[null,"Hospital","Unknown","HospitalUnknown",1115,1175,1145,null,null,"Hospital","Unknown","HospitalUnknown",797,818,474]
[null,"Hotel","CV Econ","HotelCV Econ",2838,3033,2763,null,null,"Hotel","CV Econ","HotelCV Econ",1111,955,909]
[null,"Hotel","CV nonecon","HotelCV nonecon",3035,3219,2983,null,null,"Hotel","CV nonecon","HotelCV nonecon",917,771,671]
[null,"Hotel","VAV","HotelVAV",2811,3014,2726,null,null,"Hotel","VAV","HotelVAV",571,432,350]
[null,"Hotel","Unknown","HotelUnknown",2937,3126,2873,null,null,"Hotel","Unknown","HotelUnknown",1014,863,790]
[null,"Large Office","CV Econ","Large OfficeCV Econ",885,1095,1002,null,null,"Large Office","CV Econ","Large OfficeCV Econ",2140,2046,1683]
[null,"Large Office","CV nonecon","Large OfficeCV nonecon",2500,2541,2276,null,null,"Large Office","CV nonecon","Large OfficeCV nonecon",2046,1985,1620]
[null,"Large Office","VAV","Large OfficeVAV",584,758,675,null,null,"Large Office","VAV","Large OfficeVAV",518,428,309]
[null,"Large Office","Unknown","Large OfficeUnknown",739,906,810,null,null,"Large Office","Unknown","Large OfficeUnknown",739,651,497]
[null,"Large Retail","CV Econ","Large RetailCV Econ",701,848,832,null,null,"Large Retail","CV Econ","Large RetailCV Econ",1878,1827,1735]
[null,"Large Retail","CV nonecon","Large RetailCV nonecon",1695,1654,1665,null,null,"Large Retail","CV nonecon","Large RetailCV nonecon",1755,1728,1620]
[null,"Large Retail","VAV","Large RetailVAV",560,662,656,null,null,"Large Retail","VAV","Large RetailVAV",775,681,549]
[null,"Large Retail","Unknown","Large RetailUnknown",662,756,750,null,null,"Large Retail","Unknown","Large RetailUnknown",942,856,729]
[null,"University","CV Econ","UniversityCV Econ",566,722,760,null,null,"University","CV Econ","UniversityCV Econ",1515,1404,1342]
[null,"University","CV nonecon","UniversityCV nonecon",1334,1543,1689,null,null,"University","CV nonecon","UniversityCV nonecon",1279,1195,1135]
[null,"University","VAV","UniversityVAV",413,592,619,null,null,"University","VAV","UniversityVAV",615,852,797]
[null,"University","Unknown","UniversityUnknown",579,760,807,null,null,"University","Unknown","UniversityUnknown",858,991,933]
[null,"Assembly",null,null,448,538,492,null,null,"Assembly",null,null,1234,960,908]
[null,"Auto Repair",null,null,186,304,341,null,null,"Auto Repair",null,null,4173,3370,3379]
[null,"Big Box Retail",null,null,734,841,786,null,null,"Big Box Retail",null,null,744,602,474]
[null,"Dormitory",null,null,638,698,705,null,null,"Dormatory",null,null,686,544,452]
[null,"Fast Food Restaurant",null,null,427,539,521,null,null,"Fast Food Restaurant",null,null,1837,1400,1249]
[null,"Full Service Restaurant",null,null,391,512,479,null,null,"Full Service Restaurant",null,null,1886,1303,1275]
[null,"Grocery",null,null,2143,2188,2028,null,null,"Grocery",null,null,951,1064,988]
[null,"Light Industrial",null,null,350,435,419,null,null,"Light Industrial",null,null,1379,1265,949]
[null,"Motel",null,null,670,900,909,null,null,"Motel",null,null,736,626,499]
[null,"Primary School",null,null,167,304,278,null,null,"Primary School",null,null,1551,1309,1094]
[null,"Religious",null,null,171,220,261,null,null,"Religious",null,null,1129,1012,928]
[null,"Small Office",null,null,563,786,758,null,null,"Small Office",null,null,894,760,588]
[null,"Small Retail",null,null,575,716,685,null,null,"Small Retail",null,null,1264,1052,795]
[null,"Warehouse",null,null,172,249,275,null,null,"Warehouse",null,null,1172,920,829]
[null,"Other",null,null,545,659,638,null,null,"Other",null,null,1403,1156,1029]

{"sheet":"HVAC1-BoilerReset","index":19,"n_rows":26,"n_cols":15,"rows_kept":26,"cut":false,"hidden":true,"merged":[[24,8,24,9],[25,8,25,9],[22,2,22,3],[3,6,3,9],[4,6,12,9],[5,1,7,2],[8,1,8,2],[9,1,9,2],[10,1,10,2],[12,1,12,4],[21,1,21,9],[22,8,22,9],[1,12,1,14],[5,12,5,14],[23,8,23,9],[13,1,13,2],[13,3,13,4],[13,6,16,9],[14,1,14,2],[14,3,14,4],[15,1,15,2],[15,3,15,4],[16,1,16,2],[16,3,16,4],[0,1,1,9],[3,1,3,4]]}
[null,"Measure: Boiler Reset Controls"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Table 2: Coincidence Factors"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Program","CFsp","CFwp"]
[null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,"LBES, SBES, Muni",0,0]
[null,null,null,"Value","Unit",null,"This measure involves the installation of reset controls to automatically control boiler water temperature.\n\nDefinitions:\nBoiler Reset Controls: devices that automatically control boiler water temperature based on outdoor or return water temperature using a software program."]
[null,"Total Savings",null,0,"kW",null,null,null,null,null,null,null,"Table 3: MMBtu/unit savings"]
[null,null,null,0,"kWh",null,null,null,null,null,null,null,"Measure Name","Fuel Type","MMbtu/unit"]
[null,null,null,{"$f":"I26","v":0},"MMBtu",null,null,null,null,null,null,null,"Boiler Reset Controls","Gas",35.5]
[null,"Measure Life",null,15,"Years",null,null,null,null,null,null,null,"Boiler Reset Controls","Oil",35.5]
[null,"CFsp",null,{"$f":"N4","v":0},"%",null,null,null,null,null,null,null,"Boiler Reset Controls","Propane",35.5]
[null,"CFwp",null,{"$f":"O4","v":0},"%"]
[]
[null,"HVAC - Boiler Reset Controls"]
[null,"Measure Code",null,"COM-HVAC-BRC",null,null,"NOTE: For more information on this measure refer to the NH TRM. "]
[null,"Market",null,"Commercial"]
[null,"Program Type",null,"Retrofit"]
[null,"Category",null,"HVAC"]
[]
[]
[]
[]
[null,"Table 1: Calculating Primary Energy Impact "]
[null,null,"Inputs",null,null,null,null,null,"Savings"]
[null,null,"No. of units",null,null,null,null,null,"MMBtu"]
[null,1,{"$f":"+'HVAC Inputs'!G15","v":0},null,null,null,null,null,{"$f":"$O$8*C25","v":0}]
[null,null,null,null,null,null,null,"Totals:",{"$f":"SUM(I25:J25)","v":0}]

{"sheet":"HVAC2-DCV","index":20,"n_rows":35,"n_cols":15,"rows_kept":35,"cut":false,"hidden":true,"merged":[[4,6,12,9],[5,1,7,2],[8,1,8,2],[9,1,9,2],[10,1,10,2],[12,1,12,4],[1,12,1,14],[13,1,13,2],[13,3,13,4],[13,6,16,9],[14,1,14,2],[14,3,14,4],[15,1,15,2],[15,3,15,4],[16,1,16,2],[16,3,16,4],[0,1,1,9],[3,1,3,4],[3,6,3,9]]}
[null,"Measure: Demand Control Ventilation (DCV)"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Table 2: Coincidence Factors"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Program","CFsp","CFwp"]
[null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,"LBES, SBES, Muni",0.82,0.05]
[null,null,null,"Value","Unit",null,"This measure controls the quantity of outside air to an air handling system based on detected space CO2 levels. The installed systems monitor the CO2 in the spaces or return air and reduce the outside air use when possible to save energy while meeting indoor air quality standards. Measure is applicable to situations where not required by the 2018 IECC Energy and Conservation Code section 403.7 Ventilation and Exhaust Systems. 1"]
[null,"Total Savings",null,{"$f":"I35","v":0},"kW"]
[null,null,null,{"$f":"J35","v":0},"kWh"]
[null,null,null,0,"MMBtu"]
[null,"Measure Life",null,10,"Years"]
[null,"CFsp",null,{"$f":"N4*100","v":82},"%"]
[null,"CFwp",null,{"$f":"O4*100","v":5},"%"]
[]
[null,"HVAC - Demand Control Ventilation"]
[null,"Measure Code",null,"COM-HVAC-DCV",null,null,"NOTE: For more information on this measure refer to the NH TRM."]
[null,"Market",null,"Commercial"]
[null,"Program Type",null,"Retrofit"]
[null,"Category",null,"HVAC"]
[]
[]
[]
[null,"Table 1: Calculating Primary Energy Impact "]
[null,null,"Inputs",null,null,null,null,null,"Savings"]
[null,null,"AHU","Cooling Cap","SAVEkW","SAVEkWh",null,null,"Demand","Energy"]
[null,null,"Tag","kBtu/hr","kW/ton","kWh/ton",null,null,"kW","kWh"]
[null,1,{"$f":"IF('HVAC Inputs'!L16=\"Yes\",'HVAC Inputs'!I16,\"\")","v":""},{"$f":"IF(C25=\"\",\"\",IFERROR(IF(OR(ISBLANK(C25)),\"\",'HVAC Inputs'!K16*12),\"Error: fill in ID / Tag # and Input Sheet\"))","v":""},{"$f":"IF(OR(ISBLANK(C25),ISBLANK(D25)),\"\",0.15)","v":0.15},{"$f":"IF(OR(ISBLANK(C25),ISBLANK(D25)),\"\",170)","v":170},null,null,{"$f":"IFERROR(D25*1/12*E25,\"\")","v":""},{"$f":"IFERROR(D25*1/12*F25, \"\")","v":""}]
[null,2,{"$f":"IF('HVAC Inputs'!L17=\"Yes\",'HVAC Inputs'!I17,\"\")","v":""},{"$f":"IF(C26=\"\",\"\",IFERROR(IF(OR(ISBLANK(C26)),\"\",'HVAC Inputs'!K17*12),\"Error: fill in ID / Tag # and Input Sheet\"))","v":""},{"$f":"IF(OR(ISBLANK(#REF!),ISBLANK(D26)),\"\",0.15)","v":0.15},{"$f":"IF(OR(ISBLANK(#REF!),ISBLANK(D26)),\"\",170)","v":170},null,null,"",""]
[null,3,{"$f":"IF('HVAC Inputs'!L18=\"Yes\",'HVAC Inputs'!I18,\"\")","v":""},{"$f":"IF(C27=\"\",\"\",IFERROR(IF(OR(ISBLANK(C27)),\"\",'HVAC Inputs'!K18*12),\"Error: fill in ID / Tag # and Input Sheet\"))","v":""},{"$f":"IF(OR(ISBLANK(#REF!),ISBLANK(D27)),\"\",0.15)","v":0.15},{"$f":"IF(OR(ISBLANK(#REF!),ISBLANK(D27)),\"\",170)","v":170},null,null,"",""]
[null,4,{"$f":"IF('HVAC Inputs'!L19=\"Yes\",'HVAC Inputs'!I19,\"\")","v":""},{"$f":"IF(C28=\"\",\"\",IFERROR(IF(OR(ISBLANK(C28)),\"\",'HVAC Inputs'!K19*12),\"Error: fill in ID / Tag # and Input Sheet\"))","v":""},{"$f":"IF(OR(ISBLANK(#REF!),ISBLANK(D28)),\"\",0.15)","v":0.15},{"$f":"IF(OR(ISBLANK(#REF!),ISBLANK(D28)),\"\",170)","v":170},null,null,"",""]
[null,5,{"$f":"IF('HVAC Inputs'!L20=\"Yes\",'HVAC Inputs'!I20,\"\")","v":""},{"$f":"IF(C29=\"\",\"\",IFERROR(IF(OR(ISBLANK(C29)),\"\",'HVAC Inputs'!K20*12),\"Error: fill in ID / Tag # and Input Sheet\"))","v":""},{"$f":"IF(OR(ISBLANK(#REF!),ISBLANK(D29)),\"\",0.15)","v":0.15},{"$f":"IF(OR(ISBLANK(#REF!),ISBLANK(D29)),\"\",170)","v":170},null,null,"",""]
[null,6,{"$f":"IF('HVAC Inputs'!L21=\"Yes\",'HVAC Inputs'!I21,\"\")","v":""},{"$f":"IF(C30=\"\",\"\",IFERROR(IF(OR(ISBLANK(C30)),\"\",'HVAC Inputs'!K21*12),\"Error: fill in ID / Tag # and Input Sheet\"))","v":""},{"$f":"IF(OR(ISBLANK(#REF!),ISBLANK(D30)),\"\",0.15)","v":0.15},{"$f":"IF(OR(ISBLANK(#REF!),ISBLANK(D30)),\"\",170)","v":170},null,null,"",""]
[null,7,{"$f":"IF('HVAC Inputs'!L22=\"Yes\",'HVAC Inputs'!I22,\"\")","v":""},{"$f":"IF(C31=\"\",\"\",IFERROR(IF(OR(ISBLANK(C31)),\"\",'HVAC Inputs'!K22*12),\"Error: fill in ID / Tag # and Input Sheet\"))","v":""},{"$f":"IF(OR(ISBLANK(#REF!),ISBLANK(D31)),\"\",0.15)","v":0.15},{"$f":"IF(OR(ISBLANK(#REF!),ISBLANK(D31)),\"\",170)","v":170},null,null,"",""]
[null,8,{"$f":"IF('HVAC Inputs'!L23=\"Yes\",'HVAC Inputs'!I23,\"\")","v":""},{"$f":"IF(C32=\"\",\"\",IFERROR(IF(OR(ISBLANK(C32)),\"\",'HVAC Inputs'!K23*12),\"Error: fill in ID / Tag # and Input Sheet\"))","v":""},{"$f":"IF(OR(ISBLANK(#REF!),ISBLANK(D32)),\"\",0.15)","v":0.15},{"$f":"IF(OR(ISBLANK(#REF!),ISBLANK(D32)),\"\",170)","v":170},null,null,"",""]
[null,9,{"$f":"IF('HVAC Inputs'!L24=\"Yes\",'HVAC Inputs'!I24,\"\")","v":""},{"$f":"IF(C33=\"\",\"\",IFERROR(IF(OR(ISBLANK(C33)),\"\",'HVAC Inputs'!K24*12),\"Error: fill in ID / Tag # and Input Sheet\"))","v":""},{"$f":"IF(OR(ISBLANK(#REF!),ISBLANK(D33)),\"\",0.15)","v":0.15},{"$f":"IF(OR(ISBLANK(#REF!),ISBLANK(D33)),\"\",170)","v":170},null,null,"",""]
[null,10,{"$f":"IF('HVAC Inputs'!L25=\"Yes\",'HVAC Inputs'!I25,\"\")","v":""},{"$f":"IF(C34=\"\",\"\",IFERROR(IF(OR(ISBLANK(C34)),\"\",'HVAC Inputs'!K25*12),\"Error: fill in ID / Tag # and Input Sheet\"))","v":""},{"$f":"IF(OR(ISBLANK(#REF!),ISBLANK(D34)),\"\",0.15)","v":0.15},{"$f":"IF(OR(ISBLANK(#REF!),ISBLANK(D34)),\"\",170)","v":170},null,null,"",""]
[null,null,null,null,null,null,null,"Totals:",{"$f":"SUM(I25:I34)","v":0},{"$f":"SUM(J25:J34)","v":0}]

{"sheet":"HVAC3-Economizer","index":21,"n_rows":36,"n_cols":15,"rows_kept":36,"cut":false,"hidden":true,"merged":[[23,8,23,9],[0,12,0,14],[13,1,13,2],[13,3,13,4],[13,6,16,9],[14,1,14,2],[14,3,14,4],[15,1,15,2],[15,3,15,4],[16,1,16,2],[16,3,16,4],[0,1,1,9],[3,1,3,4],[3,6,3,9],[4,6,12,9],[5,1,7,2],[8,1,8,2],[9,1,9,2],[10,1,10,2],[12,1,12,4]]}
[null,"Measure: Dual Enthalpy Economizer Controls",null,null,null,null,null,null,null,null,null,null,"Table 2: Coincidence Factors"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Program","CFsp","CFwp"]
[null,null,null,null,null,null,null,null,null,null,null,null,"LBES, SBES, Muni",0.34200000000000003,0]
[null,"Measure Summary",null,null,null,null,"Measure Description"]
[null,null,null,"Value","Unit",null,"This measure is to upgrade the outside-air dry-bulb economizer to a dual enthalpy economizer. The system will continuously monitor the enthalpy of both the outside air and return air. The system will control the system dampers adjust the outside quantity based on the two readings."]
[null,"Total Savings",null,{"$f":"I36","v":0},"kW"]
[null,null,null,{"$f":"J36","v":0},"kWh"]
[null,null,null,0,"MMBtu"]
[null,"Measure Life",null,10,"Years"]
[null,"CFsp",null,{"$f":"N3*100","v":34.200000000000003},"%"]
[null,"CFwp",null,{"$f":"O3*100","v":0},"%"]
[]
[null,"HVAC - Dual Enthalpy Economizer Controls"]
[null,"Measure Code",null,"COM-HVAC-DEEC",null,null,"NOTE: For more information on this measure refer to the NH TRM."]
[null,"Market",null,"Commercial"]
[null,"Program Type",null,"Retrofit"]
[null,"Category",null,"HVAC"]
[]
[]
[]
[]
[null,"Table 1: Calculating Primary Energy Impact "]
[null,null,"Inputs"]
[null,null,"AHU","Cooling Cap","SAVEkW","SAVEkWh",null,null,"Savings"]
[null,null,"Tag","kBtu/hr","kW/ton","kWh/ton",null,null,"kW","kWh"]
[null,1,{"$f":"IF('HVAC Inputs'!M16=\"Yes\",'HVAC Inputs'!I16,\"\")","v":""},{"$f":"IF(C26=\"\",\"\",IFERROR(IF(OR(ISBLANK(C26)),\"\",'HVAC Inputs'!K16)*12,\"Error: fill in all info\"))","v":""},{"$f":"IF(OR(ISBLANK(C26),ISBLANK(D26)),\"\",0.289)","v":0.28899999999999998},{"$f":"IF(OR(ISBLANK(C26),ISBLANK(D26)),\"\",289)","v":289},null,null,{"$f":"IFERROR(D26*1/12*E26,\"\")","v":""},{"$f":"IFERROR(D26*1/12*F26,\"\")","v":""}]
[null,2,{"$f":"IF('HVAC Inputs'!M17=\"Yes\",'HVAC Inputs'!I17,\"\")","v":""},{"$f":"IF(C27=\"\",\"\",IFERROR(IF(OR(ISBLANK(C27)),\"\",'HVAC Inputs'!K17)*12,\"Error: fill in all info\"))","v":""},{"$f":"IF(OR(ISBLANK(C27),ISBLANK(D27)),\"\",0.289)","v":0.28899999999999998},{"$f":"IF(OR(ISBLANK(C27),ISBLANK(D27)),\"\",289)","v":289},null,null,{"$f":"IFERROR(D27*1/12*E27,\"\")","v":""},{"$f":"IFERROR(D27*1/12*F27,\"\")","v":""}]
[null,3,{"$f":"IF('HVAC Inputs'!M18=\"Yes\",'HVAC Inputs'!I18,\"\")","v":""},{"$f":"IF(C28=\"\",\"\",IFERROR(IF(OR(ISBLANK(C28)),\"\",'HVAC Inputs'!K18)*12,\"Error: fill in all info\"))","v":""},0.28899999999999998,289,null,null,"",""]
[null,4,{"$f":"IF('HVAC Inputs'!M19=\"Yes\",'HVAC Inputs'!I19,\"\")","v":""},{"$f":"IF(C29=\"\",\"\",IFERROR(IF(OR(ISBLANK(C29)),\"\",'HVAC Inputs'!K19)*12,\"Error: fill in all info\"))","v":""},0.28899999999999998,289,null,null,"",""]
[null,5,{"$f":"IF('HVAC Inputs'!M20=\"Yes\",'HVAC Inputs'!I20,\"\")","v":""},{"$f":"IF(C30=\"\",\"\",IFERROR(IF(OR(ISBLANK(C30)),\"\",'HVAC Inputs'!K20)*12,\"Error: fill in all info\"))","v":""},0.28899999999999998,289,null,null,"",""]
[null,6,{"$f":"IF('HVAC Inputs'!M21=\"Yes\",'HVAC Inputs'!I21,\"\")","v":""},{"$f":"IF(C31=\"\",\"\",IFERROR(IF(OR(ISBLANK(C31)),\"\",'HVAC Inputs'!K21)*12,\"Error: fill in all info\"))","v":""},0.28899999999999998,289,null,null,"",""]
[null,7,{"$f":"IF('HVAC Inputs'!M22=\"Yes\",'HVAC Inputs'!I22,\"\")","v":""},{"$f":"IF(C32=\"\",\"\",IFERROR(IF(OR(ISBLANK(C32)),\"\",'HVAC Inputs'!K22)*12,\"Error: fill in all info\"))","v":""},0.28899999999999998,289,null,null,"",""]
[null,8,{"$f":"IF('HVAC Inputs'!M23=\"Yes\",'HVAC Inputs'!I23,\"\")","v":""},{"$f":"IF(C33=\"\",\"\",IFERROR(IF(OR(ISBLANK(C33)),\"\",'HVAC Inputs'!K23)*12,\"Error: fill in all info\"))","v":""},0.28899999999999998,289,null,null,"",""]
[null,9,{"$f":"IF('HVAC Inputs'!M24=\"Yes\",'HVAC Inputs'!I24,\"\")","v":""},{"$f":"IF(C34=\"\",\"\",IFERROR(IF(OR(ISBLANK(C34)),\"\",'HVAC Inputs'!K24)*12,\"Error: fill in all info\"))","v":""},0.28899999999999998,289,null,null,"",""]
[null,10,{"$f":"IF('HVAC Inputs'!M25=\"Yes\",'HVAC Inputs'!I25,\"\")","v":""},{"$f":"IF(C35=\"\",\"\",IFERROR(IF(OR(ISBLANK(C35)),\"\",'HVAC Inputs'!K25)*12,\"Error: fill in all info\"))","v":""},0.28899999999999998,289,null,null,"",""]
[null,null,null,null,null,null,null,"Totals:",{"$f":"SUM(I26:I35)","v":0},{"$f":"SUM(J26:J35)","v":0}]

{"sheet":"HVAC4-DuctInsulation","index":22,"n_rows":26,"n_cols":14,"rows_kept":26,"cut":false,"hidden":true,"merged":[[21,1,21,8],[1,11,1,13],[23,2,23,3],[24,2,24,3],[13,1,13,2],[13,3,13,4],[13,6,16,8],[14,1,14,2],[14,3,14,4],[15,1,15,2],[15,3,15,4],[16,1,16,2],[16,3,16,4],[22,2,22,3],[0,1,1,8],[3,1,3,4],[3,6,3,8],[4,6,12,8],[5,1,7,2],[8,1,8,2],[9,1,9,2],[10,1,10,2],[12,1,12,4]]}
[null,"Measure: Duct Insulation"]
[null,null,null,null,null,null,null,null,null,null,null,"Table 2: Coincidence Factors"]
[null,null,null,null,null,null,null,null,null,null,null,"Fuel Type","CFsp","CFwp"]
[null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,"Electric",0.35,0]
[null,null,null,"Value","Unit",null,"This measure is for existing ductwork in non-conditioned spaces, insulate ductwork. This could include replacing un-insulated flexible duct with rigid insulated ductwork and installing 1\" to 2\" of duct-wrap insulation.",null,null,null,null,"Gas",0,0]
[null,"Total Savings",null,0,"kW",null,null,null,null,null,null,"Oil",0,0]
[null,null,null,0,"kWh"]
[null,null,null,{"$f":"I26","v":0},"MMBtu"]
[null,"Measure Life",null,20,"Years"]
[null,"CFsp",null,{"$f":"IFERROR(VLOOKUP('Project Info'!$D$24,L4:N6,2,FALSE)*100,0)","v":0},"%"]
[null,"CFwp",null,{"$f":"IFERROR(VLOOKUP('Project Info'!$D$24,L4:N6,3,FALSE)*100,0)","v":0},"%"]
[]
[null,"HVAC - Duct Insulation"]
[null,"Measure Code",null,"COM-HVAC-DI",null,null,"NOTE: For more information on this measure refer to the NH TRM. "]
[null,"Market",null,"Commercial"]
[null,"Program Type",null,"Retrofit"]
[null,"Category",null,"HVAC"]
[]
[]
[]
[]
[null,"Table 1: Calculating Primary Energy Impact "]
[null,null,"Inputs",null,null,null,null,null,"Savings"]
[null,null,"Ductwork Area (ft2)",null,null,null,null,null,"MMBtu"]
[null,1,{"$f":"SUM(IF('HVAC Inputs'!$V$31=\"YES\",'HVAC Inputs'!$U$31,0),IF('HVAC Inputs'!$V$32=\"YES\",'HVAC Inputs'!$U$32,0),IF('HVAC Inputs'!$V$33=\"YES\",'HVAC Inputs'!$U$33,0),IF('HVAC Inputs'!$V$34=\"YES\",'HVAC Inputs'!$U$34,0),IF('HVAC Inputs'!$V$35=\"YES\",'HVAC Inputs'!$U$35,0),IF('HVAC Inputs'!$V$36=\"YES\",'HVAC Inputs'!$U$36,0),IF('HVAC Inputs'!$V$37=\"YES\",'HVAC Inputs'!$U$37,0),IF('HVAC Inputs'!$V$38=\"YES\",'HVAC Inputs'!$U$38,0))","v":0},null,null,null,null,null,{"$f":"0.035*C25","v":0}]
[null,null,null,null,null,null,null,"Total:",{"$f":"SUM(I25:I25)","v":0}]

{"sheet":"HVAC5-DuctSealing","index":23,"n_rows":101,"n_cols":30,"rows_kept":101,"cut":false,"hidden":true,"merged":[[8,27,8,29],[0,1,1,8],[3,1,3,4],[3,6,3,8],[4,6,12,8],[5,1,7,2],[8,1,8,2],[9,1,9,2],[10,1,10,2],[12,1,12,4],[32,1,32,8],[13,1,13,2],[13,3,13,4],[13,6,16,8],[14,1,14,2],[14,3,14,4],[15,1,15,2],[15,3,15,4],[16,1,16,2],[16,3,16,4]]}
[null,"Measure: Duct Sealing"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 2: Coincidence Factors"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Fuel Type","CFsp","CFwp"]
[null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,null,null,null,null,null,null,null,null,"Electric",0.35,0]
[null,null,null,"Value","Unit",null,"This measure is for sealing existing ductwork in non-conditioned spaces. This could include sealing ductwork with mastic or aerosol.",null,null,null,null,null,null,null,null,null,null,null,null,null,"Gas",0,0]
[null,"Total Savings:",null,{"$f":"+S24","v":{"$error":"#N/A"}},"kW",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Oil",0,0]
[null,null,null,{"$f":"+P24+R24","v":0},"kWh"]
[null,null,null,{"$f":"+Q24","v":{"$error":"#N/A"}},"MMBtu"]
[null,"Measure Life:",null,20,"Years",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Heating distribution Efficiency",null,null,null,null,null,null,"Thermal Regain Factors"]
[null,"CFsp:",null,{"$f":"+V4","v":0.35},"%",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Duct total leakage (%)","Assembly","Fast food","Full Service","Small Retail","Other",null,"Duct Location","TRFcooling","TRFheating"]
[null,"CFwp:",null,{"$f":"+W4","v":0},"%",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"8% Uninsulated",0.90900000000000003,0.80900000000000005,0.81599999999999995,0.65700000000000003,0.79800000000000004,null,"Attic",0.1,0.1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15% Uninsulated",0.879,0.78400000000000003,0.78900000000000003,0.624,0.76900000000000002,null,"Garage",0.1,0.1]
[null,"HVAC - Duct Sealing",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20% uninsulated",0.85799999999999998,0.76600000000000001,0.77,0.60199999999999998,0.749,null,"Crawl Space, unvented, uninsulated",0.6,0.6]
[null,"Measure Code",null,"COM-HVAC-DS",null,null,"NOTE: For more information on this measure refer to the NH TRM. ",null,null,null,null,null,null,null,null,null,null,null,null,null,"25% Uninsulated",0.83499999999999996,0.75,0.753,0.58199999999999996,0.73,null,"Crawl Space, Unvented, Insulated \nBuilding Floor and Crawl Space Walls",0.6,0.3]
[null,"Market",null,"Commercial",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"30% Uninsulated",0.81599999999999995,0.73399999999999999,0.73599999999999999,0.56299999999999994,0.71199999999999997,null,"Crawl Space, Unvented, Insulated\n Floor Only",0.3,0.3]
[null,"Program Type",null,"Retrofit",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"8% R-6",0.95099999999999996,0.90100000000000002,0.90400000000000003,0.79200000000000004,0.88700000000000001,null,"Crawl Space, Vented, Uninsulated",0.6,0.55000000000000004]
[null,"Category",null,"HVAC",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15% R-6",0.91700000000000004,0.86199999999999999,0.86599999999999999,0.74199999999999999,0.84699999999999998,null,"Crawl Space, Insulated Building \nFloor and Crawl Space Walls",0.63,0.6]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20% R-6",0.89500000000000002,0.83599999999999997,0.84,0.71,0.82,null,"Crawl Space, Vented, Insulated Floor Only",0.3,0.3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"25% R-6",0.871,0.81299999999999994,0.81599999999999995,0.68,0.79500000000000004,null,"Basement, Uninsulated",0.5,0.5]
[null,"Table 1: Calculating Primary Energy Impact ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"30% R-6",0.84899999999999998,0.79100000000000004,0.79400000000000004,0.65200000000000002,0.77200000000000002,null,"Basement, uninsulated Walls",0.6,0.6]
[null,"Inputs",null,null,null,null,null,null,null,null,null,null,null,null,null,"Savings",null,null,null,null,null,null,null,null,null,null,null,"Under-slab",0.2,0.2]
[null,"Building","Insulated","DE Heat","DE Heat","TRF","Capheat","Heating","Boiler","Heating","DE Cool","DE Cool","TRF","Capcool","Cooling","Heating",null,"Cooling"]
[null,"Type","Y/N","Base","Prop","Heat","MBH","System","Type","COP","Base","Prop","Cool","MBH","EER","kWh","MMBtu","kWh","kW",null,"Cooling Distribution Efficiency"]
[null,{"$f":"IF(ISERROR(MATCH('Project Info'!$D$20,$V$24:$Z$24,0)),\"Other\",'Project Info'!$D$20)","v":"Other"},{"$f":"'HVAC Inputs'!P33","v":0},{"$f":"OFFSET($U$10,IF(C24=\"Yes\",9,4),MATCH(B24,$V$10:$Z$10,0))","v":0.73},{"$f":"OFFSET($U$10,IF(C24=\"Yes\",6,1),MATCH(B24,$V$10:$Z$10,0))","v":0.79800000000000004},{"$f":"LOOKUP('HVAC Inputs'!O33,$AB$11:$AB$21,$AD$11:$AD$21)","v":{"$error":"#N/A"}},{"$f":"'HVAC Inputs'!R33","v":0},{"$f":"IF(C24=\"\",\"\",+'Project Info'!$D$25)","v":0},{"$f":"IF(C24=\"\",\"\",+'Project Info'!$D$26)","v":0},{"$f":"IF(C24=\"\",\"\",IF(H24=$U$38,$V$38,IF(H24=$U$41,$V$41,IF(H24=$U$42,$V$42,IF(I24=$U$39,$V$39,$V$40)))))","v":0.85},{"$f":"OFFSET($U$24,IF(C24=\"Yes\",9,4),MATCH(B24,$V$24:$Z$24,0))","v":0.82299999999999995},{"$f":"OFFSET($U$24,IF(C24=\"Yes\",6,1),MATCH(B24,$V$24:$Z$24,0))","v":0.84399999999999997},{"$f":"LOOKUP('HVAC Inputs'!O33,$AB$11:$AB$21,$AC$11:$AC$21)","v":{"$error":"#N/A"}},{"$f":"'HVAC Inputs'!Q33","v":0},{"$f":"'HVAC11-Unitary&Split'!V9","v":14.6},{"$f":"IF('Project Info'!D24=\"electric\",(E24-D24)/E24*(1-F24)*'HVAC Inputs'!R101*G24/J24/3.412,0)","v":0},{"$f":"IF('Project Info'!D24=\"Electric\",\"\",(E24-D24)/E24*'HVAC Inputs'!R101*G24/J24/1000)","v":{"$error":"#N/A"}},{"$f":"IF(C24=0,0,(L24-K24)/L24*(1-M24)*'HVAC Inputs'!$R$100*N24/O24)","v":0},{"$f":"+R24/'HVAC Inputs'!$R$100","v":{"$error":"#N/A"}},null,"Duct total leakage (%)","Assembly","Fast food Restaurant","Full Service Restaurant","Small Retail","Other"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"8% Uninsulated",0.87,0.85299999999999998,0.82699999999999996,0.82499999999999996,0.84399999999999997]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15% Uninsulated",0.85899999999999999,0.84299999999999997,0.82499999999999996,0.81799999999999995,0.83599999999999997]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,null,null,"20% uninsulated",0.85,0.83599999999999997,0.82099999999999995,0.81200000000000006,0.83]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"25% Uninsulated",0.84,0.82699999999999996,0.81799999999999995,0.80500000000000005,0.82299999999999995]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"30% Uninsulated",0.82899999999999996,0.81799999999999995,0.81299999999999994,0.79800000000000004,0.81499999999999995]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"8% R-6",0.94799999999999995,0.95,0.95899999999999996,0.93200000000000005,0.94699999999999995]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15% R-6",0.93200000000000005,0.93300000000000005,0.95499999999999996,0.92100000000000004,0.93500000000000005]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20% R-6",0.92,0.92100000000000004,0.95,0.91200000000000003,0.92600000000000005]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"25% R-6",0.90600000000000003,0.90800000000000003,0.94299999999999995,0.90300000000000002,0.91500000000000004]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"30% R-6",0.89200000000000002,0.89500000000000002,0.93400000000000005,0.89200000000000002,0.90300000000000002]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Heating Efficiency"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Boiler Type","Efficiency %"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Gas-fired",0.82]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Condensing",0.85]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Non-Condensing",0.85]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Electric Resistance",1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Heat Pump",3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"See Table 28 and Figure 68of the 2024 Commercial Existing Building Baseline Study"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Manchester"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,908]
[null,null,null,null,"Small Commercial Cooling Full Load Hours",null,null,null,null,null,"Small Commercial Heating Full Load Hours",null,null,null,null,null,null,null,null,null,3379]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,474]
[null,null,null,null,"Building Type","Berlin","Concord","Manchester",null,null,"Building Type","Berlin",null,null,null,null,null,null,null,"Concord",452]
[null,null,null,null,"Assembly",448,538,492,null,null,"Assembly",1234,null,null,null,null,null,null,null,960,1249]
[null,null,null,null,"Auto Repair",186,304,341,null,null,"Auto Repair",4173,null,null,null,null,null,null,null,3370,1275]
[null,null,null,null,"Big Box Retail",734,841,786,null,null,"Big Box Retail",744,null,null,null,null,null,null,null,602,988]
[null,null,null,null,"Dormitory",638,698,705,null,null,"Dormitory",686,null,null,null,null,null,null,null,544,949]
[null,null,null,null,"Fast food",427,539,521,null,null,"Fast food",1837,null,null,null,null,null,null,null,1400,499]
[null,null,null,null,"Full Service",391,512,479,null,null,"Full Service",1886,null,null,null,null,null,null,null,1303,1094]
[null,null,null,null,"Grocery",2143,2188,2028,null,null,"Grocery",951,null,null,null,null,null,null,null,1064,928]
[null,null,null,null,"Light Industrial",350,435,419,null,null,"Light Industrial",1379,null,null,null,null,null,null,null,1265,588]
[null,null,null,null,"Motel",670,900,909,null,null,"Motel",736,null,null,null,null,null,null,null,626,795]
[null,null,null,null,"Primary School",167,304,278,null,null,"Primary School",1551,null,null,null,null,null,null,null,1309,829]
[null,null,null,null,"Religious",171,220,261,null,null,"Religious",1129,null,null,null,null,null,null,null,1012,1029]
[null,null,null,null,"Small Office",563,786,758,null,null,"Small Office",894,null,null,null,null,null,null,null,760,939]
[null,null,null,null,"Small Retail",575,716,685,null,null,"Small Retail",1264,null,null,null,null,null,null,null,1052,863]
[null,null,null,null,"Warehouse",172,249,275,null,null,"Warehouse",1172,null,null,null,null,null,null,null,920,642]
[null,null,null,null,"Other Small building",545,659,638,null,null,"Other Small building",1403,null,null,null,null,null,null,null,1156,723]
[null,null,null,null,"Community College (CV econ HVAC)",412,627,581,null,null,"Community College (CV econ HVAC)",1103,null,null,null,null,null,null,null,1098,724]
[null,null,null,null,"Community College (CV noecon HVAC)",612,874,789,null,null,"Community College (CV noecon HVAC)",982,null,null,null,null,null,null,null,1014,652]
[null,null,null,null,"Community College (VAV HVAC)",299,489,460,null,null,"Community College (VAV HVAC)",704,null,null,null,null,null,null,null,462,274]
[null,null,null,null,"Community College (Unknown HVAC)",365,570,530,null,null,"Community College (Unknown HVAC)",809,null,null,null,null,null,null,null,646,402]
[null,null,null,null,"High School (CV econ HVAC)",252,398,330,null,null,"High School (CV econ HVAC)",806,null,null,null,null,null,null,null,744,703]
[null,null,null,null,"High School (CV noecon HVAC)",707,837,741,null,null,"High School (CV noecon HVAC)",721,null,null,null,null,null,null,null,699,641]
[null,null,null,null,"High School (VAV HVAC)",148,255,196,null,null,"High School (VAV HVAC)",383,null,null,null,null,null,null,null,289,437]
[null,null,null,null,"High School (Unknown HVAC)",251,368,301,null,null,"High School (Unknown HVAC)",501,null,null,null,null,null,null,null,423,474]
[null,null,null,null,"Hospital (CV econ HVAC)",1037,1132,1115,null,null,"Hospital (CV econ HVAC)",1140,null,null,null,null,null,null,null,1052,909]
[null,null,null,null,"Hospital (CV noecon HVAC)",2248,2117,1865,null,null,"Hospital (CV noecon HVAC)",1068,null,null,null,null,null,null,null,971,671]
[null,null,null,null,"Hospital (VAV HVAC)",1014,1089,1079,null,null,"Hospital (VAV HVAC)",738,null,null,null,null,null,null,null,781,350]
[null,null,null,null,"Hospital (Unknown HVAC)",1115,1175,1145,null,null,"Hospital (Unknown HVAC)",797,null,null,null,null,null,null,null,818,790]
[null,null,null,null,"Hotel (CV econ HVAC)",2838,3033,2763,null,null,"Hotel (CV econ HVAC)",1111,null,null,null,null,null,null,null,955,1683]
[null,null,null,null,"Hotel (CV noecon HVAC)",3035,3219,2983,null,null,"Hotel (CV noecon HVAC)",917,null,null,null,null,null,null,null,771,1620]
[null,null,null,null,"Hotel (VAV HVAC)",2811,3014,2726,null,null,"Hotel (VAV HVAC)",571,null,null,null,null,null,null,null,432,309]
[null,null,null,null,"Hotel (Unknown HVAC)",2937,3126,2873,null,null,"Hotel (Unknown HVAC)",1014,null,null,null,null,null,null,null,863,497]
[null,null,null,null,"Large Office (CV econ HVAC)",885,1095,1002,null,null,"Large Office (CV econ HVAC)",2140,null,null,null,null,null,null,null,2046,1735]
[null,null,null,null,"Large Office (CV noecon HVAC)",2500,2541,2276,null,null,"Large Office (CV noecon HVAC)",2046,null,null,null,null,null,null,null,1985,1620]
[null,null,null,null,"Large Office (VAV HVAC)",584,758,675,null,null,"Large Office (VAV HVAC)",518,null,null,null,null,null,null,null,428,549]
[null,null,null,null,"Large Office (Unknown HVAC)",739,906,810,null,null,"Large Office (Unknown HVAC)",739,null,null,null,null,null,null,null,651,729]
[null,null,null,null,"Large Retail (CV econ HVAC)",701,848,832,null,null,"Large Retail (CV econ HVAC)",1878,null,null,null,null,null,null,null,1827,1342]
[null,null,null,null,"Large Retail (CV noecon HVAC)",1695,1654,1665,null,null,"Large Retail (CV noecon HVAC)",1755,null,null,null,null,null,null,null,1728,1135]
[null,null,null,null,"Large Retail (VAV HVAC)",560,662,656,null,null,"Large Retail (VAV HVAC)",775,null,null,null,null,null,null,null,681,797]
[null,null,null,null,"Large Retail (Unknown HVAC)",662,756,750,null,null,"Large Retail (Unknown HVAC)",942,null,null,null,null,null,null,null,856,933]
[null,null,null,null,"University (CV econ HVAC)",566,722,760,null,null,"University (CV econ HVAC)",1515,null,null,null,null,null,null,null,1404]
[null,null,null,null,"University (CV noecon HVAC)",1334,1543,1689,null,null,"University (CV noecon HVAC)",1279,null,null,null,null,null,null,null,1195]
[null,null,null,null,"University (VAV HVAC)",413,592,619,null,null,"University (VAV HVAC)",615,null,null,null,null,null,null,null,852]
[null,null,null,null,"University (Unknown HVAC)",579,760,807,null,null,"University (Unknown HVAC)",858,null,null,null,null,null,null,null,991]

{"sheet":"HVAC6-HotelOccSensor","index":24,"n_rows":26,"n_cols":14,"rows_kept":26,"cut":false,"hidden":true,"merged":[[1,11,1,13],[22,7,22,8],[21,1,21,8],[13,6,16,8],[0,1,1,8],[3,1,3,4],[3,6,3,8],[4,6,12,8],[5,1,7,2],[8,1,8,2],[9,1,9,2],[10,1,10,2],[12,1,12,4],[16,1,16,2],[16,3,16,4],[13,1,13,2],[13,3,13,4],[14,1,14,2],[14,3,14,4],[15,1,15,2],[15,3,15,4]]}
[null,"Measure: Hotel Occupancy Sensor"]
[null,null,null,null,null,null,null,null,null,null,null,"Table 3: Coincidence Factors"]
[null,null,null,null,null,null,null,null,null,null,null,"Fuel Type","CFsp","CFwp"]
[null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,"LBES, SBES, Muni",0.82,0.05]
[null,null,null,"Value","Unit",null,"This measure includes the installation of hotel occupancy sensors (HOS) to control packaged terminal AC units (PTACs) with electric heat, heat pump units and/or fan coil units in hotels that operate all 12 months of the year."]
[null,"Total Savings",null,{"$f":"+H26","v":0},"kW"]
[null,null,null,{"$f":"+I26","v":0},"kWh"]
[null,null,null,0,"MMBtu"]
[null,"Measure Life",null,10,"Years"]
[null,"CFsp",null,{"$f":"M4*100","v":82},"%"]
[null,"CFwp",null,{"$f":"N4*100","v":5},"%"]
[]
[null,"HVAC - Hotel Occupancy Sensor"]
[null,"Measure Code",null,"COM-HVAC-HOS",null,null,"NOTE: For more information on this measure refer to the NH TRM. "]
[null,"Market",null,"Commercial"]
[null,"Program Type",null,"Retrofit"]
[null,"Category",null,"HVAC"]
[]
[]
[]
[]
[null,"Table 1: Calculating Primary Energy Impact "]
[null,null,"Inputs",null,null,null,null,"Savings"]
[null,null,"Quantity",null,null,null,null,"kW","kWh"]
[null,1,{"$f":"IF('HVAC Inputs'!L36=\"Measure qualifies for savings\",'HVAC Inputs'!K37,0)","v":0},null,null,null,null,{"$f":"0.09*C25","v":0},{"$f":"438*C25","v":0}]
[null,null,null,null,null,null,"Totals:",{"$f":"SUM(H25:H25)","v":0},{"$f":"SUM(I25:I25)","v":0}]

{"sheet":"HVAC7-DHW_PipeInsulation","index":25,"n_rows":28,"n_cols":30,"rows_kept":28,"cut":false,"hidden":true,"merged":[[23,22,23,24],[7,22,7,29],[7,14,7,20],[21,1,21,11],[13,1,13,2],[13,3,13,4],[13,7,16,11],[14,1,14,2],[22,9,22,11],[22,1,22,8],[1,15,1,18],[14,3,14,4],[15,1,15,2],[15,3,15,4],[16,1,16,2],[16,3,16,4],[0,1,1,11],[3,1,3,4],[3,7,3,11],[4,7,12,11],[5,1,7,2],[8,1,8,2],[9,1,9,2],[10,1,10,2],[12,1,12,4]]}
[null,"Measure: Pipe Wrap (Domestic Hot Water Pipe)",null,null,null,null,null,null,null,null,null,null,null,null,null,"Additional Information:"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 2: Coincidence Factors"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Fuel Type","Measure","CFsp","CFwp"]
[null,"Measure Summary",null,null,null,null,null,"Measure Description",null,null,null,null,null,null,null,"Gas, Oil, Propane","All",0,0]
[null,null,null,"Value","Unit",null,null,"This measure includes both steam and hot water heating pipes.\n\nDefinitions:\nPipe Wrap – Heating: Install insulation on steam pipes located in non-conditioned spaces.\nPipe Wrap – Hot Water: Install insulation on hot water located in non-conditioned spaces. ",null,null,null,null,null,null,null,"Electric","Heating",0,0.433]
[null,"Total Savings",null,{"$f":"J25","v":0},"kW",null,null,null,null,null,null,null,null,null,null,"Electric","Hot Water",0.312,0.80800000000000005]
[null,null,null,{"$f":"K25","v":0},"kWh"]
[null,null,null,{"$f":"L28","v":0},"MMBtu",null,null,null,null,null,null,null,null,null,"Table 3: Savings Values",null,null,null,null,null,null,null,"Table 6: Heating pipes, Electric Calculations"]
[null,"Measure Life",null,15,"Years",null,null,null,null,null,null,null,null,null,"Helper Column","Measure Name","Fuel Type","Program","kWh","kW","MMBtu/ft",null,"No.","Measure","Fuel Type","UAbase","UAee","kWh","kW","MMBtu"]
[null,"CFsp",null,{"$f":"IF(P6='Project Info'!D27,R6,R4)*100","v":0},"%",null,null,null,null,null,null,null,null,null,{"$f":"P10&Q10&R10","v":"HeatingGasCommercial"},"Heating","Gas","Commercial",0,0,0.28999999999999998,null,1,"Heating","Electric",{"$f":"IFERROR(VLOOKUP(G25,$W$15:$Z$20,2,FALSE),0)","v":0},{"$f":"IFERROR(VLOOKUP(H25,$W$21:$Z$22,3,FALSE),0)","v":0},{"$f":"(Z10-AA10)/($X$27*3412)*C25*$X$26*I25","v":{"$error":"#VALUE!"}},{"$f":"AB10/8760","v":{"$error":"#VALUE!"}},0]
[null,"CFwp",null,{"$f":"IF(P6='Project Info'!D27,S6,S4)*100","v":0},"%",null,null,null,null,null,null,null,null,null,{"$f":"P11&Q11&R11","v":"Hot WaterGasCommercial"},"Hot Water","Gas","Commercial",0,0,0.28999999999999998]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"P12&Q12&R12","v":"HeatingGasMunicipal"},"Heating","Gas","Municipal",0,0,"calculate"]
[null,"HVAC - Pipe Wrap",null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"P13&Q13&R13","v":"Hot WaterGasMunicipal"},"Hot Water","Gas","Municipal",0,0,"calculate",null,"Table 4: Pipe types for UA/L (Heating, Electric Only)"]
[null,"Measure Code",null,"COM-HVAC-PW",null,null,null,"NOTE: For more information on this measure refer to the NH TRM. ",null,null,null,null,null,null,{"$f":"P14&Q14","v":"HeatingOil"},"Heating","Oil","Municipal",0,0,"calculate",null,"Type of Pipe","Diameter","(UA/L)base","(UA/L)EE"]
[null,"Market",null,"Commercial",null,null,null,null,null,null,null,null,null,null,"Hot WaterOil","Hot Water","Oil","Municipal",0,0,"calculate",null,"Copper",1.5,0.97]
[null,"Program Type",null,"Retrofit",null,null,null,null,null,null,null,null,null,null,"HeatingPropane","Heating","Propane","Municipal",0,0,"calculate",null,"Copper",2,1.19]
[null,"Category",null,"HVAC",null,null,null,null,null,null,null,null,null,null,"Hot WaterPropane","Hot Water","Propane","Municipal",0,0,"calculate",null,"Copper",3,1.7]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"HeatingElectric","Heating","Electric","Commercial",{"$f":"AB10","v":{"$error":"#VALUE!"}},{"$f":"AC10","v":{"$error":"#VALUE!"}},0,null,"Steel",1.5,1.23]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hot WaterElectric","Hot Water","Electric","Commercial","calc from kW demand impact model","demand impact model",0,null,"Steel",2,1.51]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Steel",3,2.16]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Fiber glass",null,"-",0.12]
[null,"Table 1: Calculating Primary Energy Impact ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Rigid foam/cellular glass",null,"-",0.46]
[null,"Inputs",null,null,null,null,null,null,null,"Savings"]
[null,null,"ft","Pipe Material","Diameter","(UA/L)base","Insulation","(UA/L)EE","Hours","kW","kWh","MMBtu",null,null,null,null,null,null,null,null,null,null,"Table 5: Additional numbers (Heating, Electric only)"]
[null,1,{"$f":"IF('Measure Summary'!$E$27=\"Yes\",'HVAC Inputs'!Q44,0)","v":0},{"$f":"IF('HVAC Inputs'!R44=\"\",\"\",'HVAC Inputs'!R44)","v":""},{"$f":"IF('HVAC Inputs'!P44=\"\",\"\",'HVAC Inputs'!P44)","v":""},{"$f":"IF(D25=$W$15,LOOKUP(E25,$X$15:$X$17,$Y$15:$Y$17),LOOKUP(E25,$X$18:$X$20,$Y$18:$Y$20))","v":{"$error":"#N/A"}},{"$f":"IF('HVAC Inputs'!S44=\"\",\"\",'HVAC Inputs'!S44)","v":""},{"$f":"IF(G25=\"\",\"\",IF(G25=$W$21,$Z$21,$Z$22))","v":""},{"$f":"IF('HVAC Inputs'!T44=\"\",\"\",'HVAC Inputs'!T44)","v":""},{"$f":"K25/8760","v":0},{"$f":"IFERROR(IF('HVAC Inputs'!O44=\"Yes\",0,IF('Project Info'!$D$27=\"Electric\",((F25-H25)/($X$27*3412))*C25*$X$26*I25,0)),0)","v":0},{"$f":"IF('Project Info'!$D$27=\"Electric\",0,IF('HVAC Inputs'!O44=\"Yes\",0,C25*$U$10))","v":0},null,null,null,null,null,null,null,null,null,null,"Name","Value","Units"]
[null,2,{"$f":"IF('Measure Summary'!$E$27=\"Yes\",'HVAC Inputs'!Q45,0)","v":0},{"$f":"IF('HVAC Inputs'!R45=\"\",\"\",'HVAC Inputs'!R45)","v":""},{"$f":"IF('HVAC Inputs'!P45=\"\",\"\",'HVAC Inputs'!P45)","v":""},null,{"$f":"IF('HVAC Inputs'!S45=\"\",\"\",'HVAC Inputs'!S45)","v":""},{"$f":"IF(G26=\"\",\"\",IF(G26=$W$21,$Z$21,$Z$22))","v":""},{"$f":"IF('HVAC Inputs'!T45=\"\",\"\",'HVAC Inputs'!T45)","v":""},{"$f":"K26/8760","v":0},{"$f":"IFERROR(IF('HVAC Inputs'!O45=\"Yes\",0,IF('Project Info'!$D$27=\"Electric\",((F26-H26)/($X$27*3412))*C26*$X$26*I26,0)),0)","v":0},{"$f":"IF('Project Info'!$D$27=\"Electric\",0,IF('HVAC Inputs'!O45=\"Yes\",0,C26*$U$10))","v":0},null,null,null,null,null,null,null,null,null,null,"Temperature Delta (Fluid - Ambient)",45,"*F"]
[null,3,{"$f":"IF('Measure Summary'!$E$27=\"Yes\",'HVAC Inputs'!Q46,0)","v":0},{"$f":"IF('HVAC Inputs'!R46=\"\",\"\",'HVAC Inputs'!R46)","v":""},{"$f":"IF('HVAC Inputs'!P46=\"\",\"\",'HVAC Inputs'!P46)","v":""},null,{"$f":"IF('HVAC Inputs'!S46=\"\",\"\",'HVAC Inputs'!S46)","v":""},"",{"$f":"IF('HVAC Inputs'!T46=\"\",\"\",'HVAC Inputs'!T46)","v":""},0,{"$f":"IFERROR(IF('HVAC Inputs'!O46=\"Yes\",0,IF('Project Info'!$D$27=\"Electric\",((F27-H27)/($X$27*3412))*C27*$X$26*I27,0)),0)","v":0},{"$f":"IF('Project Info'!$D$27=\"Electric\",0,IF('HVAC Inputs'!O46=\"Yes\",0,C27*$U$10))","v":0},null,null,null,null,null,null,null,null,null,null,"Et (electric heater thermal eff)",0.98,"-"]
[null,null,null,null,null,null,null,null,"Totals:",0,0,{"$f":"SUM(L25:L27)","v":0}]

{"sheet":"HVAC8-SpaceHtgPipeInsulation","index":26,"n_rows":33,"n_cols":19,"rows_kept":33,"cut":false,"hidden":true,"merged":[[0,1,1,11],[1,15,1,18],[3,1,3,4],[3,7,3,11],[4,7,12,11],[5,1,7,2],[8,1,8,2],[9,1,9,2],[10,1,10,2],[12,1,12,4],[21,1,21,11],[22,9,22,11],[13,1,13,2],[13,3,13,4],[13,7,16,11],[14,1,14,2],[14,3,14,4],[15,1,15,2],[15,3,15,4],[16,1,16,2],[16,3,16,4]]}
[null,"Measure: Pipe Wrap (Space Heating Steam or Hot Water Pipe - Non-electric heating only)",null,null,null,null,null,null,null,null,null,null,null,null,null,"Additional Information:"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 2: Coincidence Factors"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Fuel Type","Measure","CFsp","CFwp"]
[null,"Measure Summary",null,null,null,null,null,"Measure Description",null,null,null,null,null,null,null,"Gas, Oil, Propane","All",0,0]
[null,null,null,"Value","Unit",null,null,"This measure includes both steam and hot water heating pipes.\n\nDefinitions:\nHeating: Install insulation on steam pipes located in non-conditioned spaces.\nHot Water: Install insulation on hot water heating pipes located in unconditioned spaces.",null,null,null,null,null,null,null,"Electric","Heating",0,0.433]
[null,"Total Savings",null,0,"kW",null,null,null,null,null,null,null,null,null,null,"Electric","Hot Water",0.312,0.80800000000000005]
[null,null,null,0,"kWh"]
[null,null,null,{"$f":"L33","v":0},"MMBtu"]
[null,"Measure Life",null,15,"Years"]
[null,"CFsp",null,{"$f":"R4*100","v":0},"%"]
[null,"CFwp",null,{"$f":"S4*100","v":0},"%"]
[]
[null,"HVAC - Pipe Wrap"]
[null,"Measure Code",null,"TBD",null,null,null,"Calculations assume that heating source is fossil fuel.\nTRM provides 0.29 MMBtu/ft for gas heating. Same factor is used for oil and propane heating."]
[null,"Market",null,"Commercial"]
[null,"Program Type",null,"Retrofit"]
[null,"Category",null,"HVAC"]
[]
[]
[]
[]
[null,"Table 1: Calculating Primary Energy Impact "]
[null,null,"Inputs","Pipe","Pipe ",null,null,null,null,"Savings"]
[null,null,"ft","Material","Diameter",null,null,null,null,"kW","kWh","MMBtu"]
[null,1,{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!P52,0)","v":0},{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!Q52)","v":false},{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!R52)","v":false},null,null,null,null,0,0,{"$f":"IF('HVAC Inputs'!O52=\"Yes\",0,C25*0.29)","v":0}]
[null,2,{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!P53,0)","v":0},{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!Q53)","v":false},{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!R53)","v":false},null,null,null,null,0,0,{"$f":"IF('HVAC Inputs'!O53=\"Yes\",0,C26*0.29)","v":0}]
[null,3,{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!P54,0)","v":0},{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!Q54)","v":false},{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!R54)","v":false},null,null,null,null,0,0,{"$f":"IF('HVAC Inputs'!O54=\"Yes\",0,C27*0.29)","v":0}]
[null,4,{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!P55,0)","v":0},{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!Q55)","v":false},{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!R55)","v":false},null,null,null,null,0,0,{"$f":"IF('HVAC Inputs'!O55=\"Yes\",0,C28*0.29)","v":0}]
[null,5,{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!P56,0)","v":0},{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!Q56)","v":false},{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!R56)","v":false},null,null,null,null,0,0,{"$f":"IF('HVAC Inputs'!O56=\"Yes\",0,C29*0.29)","v":0}]
[null,6,{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!P57,0)","v":0},{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!Q57)","v":false},{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!R57)","v":false},null,null,null,null,0,0,{"$f":"IF('HVAC Inputs'!O57=\"Yes\",0,C30*0.29)","v":0}]
[null,7,{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!P58,0)","v":0},{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!Q58)","v":false},{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!R58)","v":false},null,null,null,null,0,0,{"$f":"IF('HVAC Inputs'!O58=\"Yes\",0,C31*0.29)","v":0}]
[null,8,{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!P59,0)","v":0},{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!Q59)","v":false},{"$f":"IF('Measure Summary'!$E$28=\"Yes\",'HVAC Inputs'!R59)","v":false},null,null,null,null,0,0,{"$f":"IF('HVAC Inputs'!O59=\"Yes\",0,C32*0.29)","v":0}]
[null,null,null,null,null,null,null,null,"Totals:",0,0,{"$f":"SUM(L25:L32)","v":0}]

{"sheet":"HVAC9-WifiTstat","index":27,"n_rows":26,"n_cols":16,"rows_kept":26,"cut":false,"hidden":true,"merged":[[3,1,3,4],[3,6,3,9],[4,6,12,9],[5,1,7,2],[8,1,8,2],[9,1,9,2],[10,1,10,2],[12,1,12,4],[23,3,23,6],[8,12,8,15],[21,1,21,9],[22,7,22,9],[1,12,1,14],[22,2,22,3],[13,1,13,2],[13,3,13,4],[13,6,16,9],[14,1,14,2],[14,3,14,4],[15,1,15,2],[15,3,15,4],[16,1,16,2],[16,3,16,4],[0,1,1,9]]}
[null,"Measure: Thermostat - Wifi Communicating"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Table 2: Coincidence Factors"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Fuel Type","CFsp","CFwp"]
[null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,"Electric",0.34599999999999997,0]
[null,null,null,"Value","Unit",null,"This measure is for a Wi-Fi enabled communicating thermostat which allows remote set point adjustment and control via remote application. System requires an outdoor air temperature algorithm in the control logic to operate heating and cooling system.",null,null,null,null,null,"Gas",0,0]
[null,"Total Savings",null,{"$f":"H26","v":0},"kW",null,null,null,null,null,null,null,"Oil",0,0]
[null,null,null,{"$f":"I26","v":0},"kWh",null,null,null,null,null,null,null,"Propane",0,0]
[null,null,null,{"$f":"J26","v":0},"MMBtu"]
[null,"Measure Life",null,15,"Years",null,null,null,null,null,null,null,"Table 3: Savings Values"]
[null,"CFsp",null,{"$f":"IFERROR(VLOOKUP('Project Info'!$D$24,$M$4:$O$7,2,FALSE),0)*100","v":0},"%",null,null,null,null,null,null,null,"Fuel Type","kWh","kW","MMBtu"]
[null,"CFwp",null,{"$f":"IFERROR(VLOOKUP('Project Info'!$D$24,$M$4:$O$7,3,FALSE),0)*100","v":0},"%",null,null,null,null,null,null,null,"Electric",160.9,0.25600000000000001,0]
[null,null,null,null,null,null,null,null,null,null,null,null,"Gas",0,0,3.11]
[null,"HVAC - Thermostat - Wifi Communicating",null,null,null,null,null,null,null,null,null,null,"Oil",0,0,3.11]
[null,"Measure Code",null,"COM-HVAC-WIFI",null,null,"NOTE: For more information on this measure refer to the NH TRM.",null,null,null,null,null,"Propane",0,0,3.11]
[null,"Market",null,"Commercial",null,null,null,null,null,null,null,null,"OMP Gas",0,0,3.11]
[null,"Program Type",null,"Retrofit"]
[null,"Category",null,"HVAC"]
[]
[]
[]
[]
[null,"Table 1: Calculating Primary Energy Impact "]
[null,null,"Inputs",null,null,null,null,"Savings"]
[null,null,"Quantity",null,null,null,null,"kW","kWh","MMBtu"]
[null,1,{"$f":"+'HVAC Inputs'!K57","v":0},{"$f":"IF('Project Info'!D24=\"\",\"Select Space Heating Fuel on 'Project Info' tab\",\"\")","v":"Select Space Heating Fuel on 'Project Info' tab"},null,null,null,{"$f":"IFERROR(VLOOKUP('Project Info'!$D$24,$M$11:$P$14,3,FALSE),0)*C25","v":0},{"$f":"IFERROR(VLOOKUP('Project Info'!$D$24,$M$11:$P$14,2,FALSE),0)*C25","v":0},{"$f":"IFERROR(VLOOKUP('Project Info'!$D$24,$M$11:$P$14,4,FALSE),0)*C25","v":0}]
[null,null,null,null,null,null,"Totals:",{"$f":"SUM(H25:H25)","v":0},{"$f":"SUM(I25:I25)","v":0},{"$f":"SUM(J25:J25)","v":0}]

{"sheet":"HVAC10-HeatPumps","index":28,"n_rows":45,"n_cols":31,"rows_kept":45,"cut":false,"hidden":true,"merged":[[49,4,51,9],[20,13,21,13],[8,0,8,1],[0,5,0,9],[1,5,1,9],[6,0,6,1],[7,0,7,1],[1,0,1,3],[3,0,5,1]]}
[null,null,null,null,null,"HVAC Prescriptive Rebate"]
["Measure Summary",null,null,null,null,"Air & Water Source Heat Pumps (Including VRF)",null,null,null,null,null,null,null,"HVAC Lookup Tables: From NH TRM 2026"]
[null,null,"Value","Unit"]
["Total Savings",null,{"$f":"K43*(C8/100)","v":0},"Summer kW","Operating Profile",{"$f":"'HVAC Inputs'!P14","v":0},null,null,null,null,null,null,null,"Air to Air Heat Pumps",null,null,null,null,null,null,"Air to Air Heat Pumps",null,null,null,null,null,null,null,null,null,"Heat Pump Categories"]
[null,null,{"$f":"K44*(C9/100)","v":0},"Winter kW",null,null,null,null,null,null,null,null,null,"Capacity Range",null,null,"NH TRM 2026",null,null,null,"Capacity Range",null,null,"NH TRM 2026",null,null,null,null,null,null,"Air to Air Heat Pump"]
[null,null,{"$f":"K42","v":0},"kWh",null,null,null,null,null,null,null,null,null,"Min","Max","Elec","Cooling","Cooling","Heating",null,"Min","Max","Elec","Cooling","Cooling","Heating",null,null,null,null,"Water Source Heat Pump"]
["Measure Life",null,{"$f":"IFERROR(SUMPRODUCT(F42:J42,F20:J20)/SUM(F42:J42),12)","v":12},"Years","Equipment Tag",{"$f":"IF(+'HVAC Inputs'!P16=\"\",\"\",'HVAC Inputs'!P16)","v":""},{"$f":"IF(+'HVAC Inputs'!Q16=\"\",\"\",'HVAC Inputs'!Q16)","v":""},{"$f":"IF(+'HVAC Inputs'!R16=\"\",\"\",'HVAC Inputs'!R16)","v":""},{"$f":"IF(+'HVAC Inputs'!S16=\"\",\"\",'HVAC Inputs'!S16)","v":""},{"$f":"IF(+'HVAC Inputs'!T16=\"\",\"\",'HVAC Inputs'!T16)","v":""},"Totals:",null,null,"tons","tons","Resistance","EER2","IEER/SEER2","COP/HSPF2",null,"tons","tons","Resistance","EER2","IEER/SEER2","COP/HSPF2",null,null,null,null,"Open Loop Ground Water Heat Pump"]
["CFsp",null,{"$f":"IFERROR(34.2, \"\")","v":34.200000000000003},"%","Model Numbers",{"$f":"IF(+'HVAC Inputs'!P17=\"\",\"\",'HVAC Inputs'!P17)","v":""},{"$f":"IF(+'HVAC Inputs'!Q17=\"\",\"\",'HVAC Inputs'!Q17)","v":""},{"$f":"IF(+'HVAC Inputs'!R17=\"\",\"\",'HVAC Inputs'!R17)","v":""},{"$f":"IF(+'HVAC Inputs'!S17=\"\",\"\",'HVAC Inputs'!S17)","v":""},{"$f":"IF(+'HVAC Inputs'!T17=\"\",\"\",'HVAC Inputs'!T17)","v":""},"-",null,"Ductless Split","None",5.4,"No",11.9,14.3,7.5,null,5.4,11.24,"Yes",10.3,14.1,3.4,null,null,null,null,"Closed Loop Ground Water Heat Pump"]
["CFwp",null,{"$f":"IFERROR(IF(OR(F10 = \"Air to Air Heat Pump\", F10 = \"Air Cooled VRF Heat Pump\"), 0, 34.2), \"\")","v":34.200000000000003},"%","Quantity Units Installed",{"$f":"IF(+'HVAC Inputs'!P18=\"\",\"\",'HVAC Inputs'!P18)","v":""},{"$f":"IF(+'HVAC Inputs'!Q18=\"\",\"\",'HVAC Inputs'!Q18)","v":""},{"$f":"IF(+'HVAC Inputs'!R18=\"\",\"\",'HVAC Inputs'!R18)","v":""},{"$f":"IF(+'HVAC Inputs'!S18=\"\",\"\",'HVAC Inputs'!S18)","v":""},{"$f":"IF(+'HVAC Inputs'!T18=\"\",\"\",'HVAC Inputs'!T18)","v":""},{"$f":"SUM(F9:J9)","v":0},null,"Split","None",5.4,"No",11.9,14.3,7.5,null,11.25,19.899999999999999,"Yes",9.8800000000000008,13.5,3.3,null,null,null,null,"Air Cooled VRF Heat Pump"]
[null,null,null,null,"Equipment Type",{"$f":"IF(+'HVAC Inputs'!P19=\"\",\"\",'HVAC Inputs'!P19)","v":""},{"$f":"IF(+'HVAC Inputs'!Q19=\"\",\"\",'HVAC Inputs'!Q19)","v":""},{"$f":"IF(+'HVAC Inputs'!R19=\"\",\"\",'HVAC Inputs'!R19)","v":""},{"$f":"IF(+'HVAC Inputs'!S19=\"\",\"\",'HVAC Inputs'!S19)","v":""},{"$f":"IF(+'HVAC Inputs'!T19=\"\",\"\",'HVAC Inputs'!T19)","v":""},"-",null,"Packaged","None",5.4,"No",11.4,13.4,6.7,null,20,63.33,"Yes",8.8000000000000007,12.5,3.2,null,null,null,null,"Water Cooled VRF Heat Pump"]
[null,null,null,null,"Supplemental Electric Resistance?",{"$f":"IF(+'HVAC Inputs'!P20=\"\",\"\",'HVAC Inputs'!P20)","v":""},null,null,null,null,null,null,null,5.4,11.24,"No",10.3,13.9,3.4]
[null,null,null,null,"Cooling Capacity - TONS",{"$f":"IF(+'HVAC Inputs'!P21=\"\",\"\",'HVAC Inputs'!P21)","v":""},{"$f":"IF(+'HVAC Inputs'!Q21=\"\",\"\",'HVAC Inputs'!Q21)","v":""},{"$f":"IF(+'HVAC Inputs'!R21=\"\",\"\",'HVAC Inputs'!R21)","v":""},{"$f":"IF(+'HVAC Inputs'!S21=\"\",\"\",'HVAC Inputs'!S21)","v":""},{"$f":"IF(+'HVAC Inputs'!T21=\"\",\"\",'HVAC Inputs'!T21)","v":""},{"$f":"SUM(F12:J12)","v":0},null,null,11.25,19.899999999999999,"No",9.8800000000000008,13.3,3.3]
[null,null,null,null,"Air to Air HP < 5.4 tons, Split or Packaged?",{"$f":"IF(+'HVAC Inputs'!P22=\"\",\"\",'HVAC Inputs'!P22)","v":""},{"$f":"IF(+'HVAC Inputs'!Q22=\"\",\"\",'HVAC Inputs'!Q22)","v":""},{"$f":"IF(+'HVAC Inputs'!R22=\"\",\"\",'HVAC Inputs'!R22)","v":""},{"$f":"IF(+'HVAC Inputs'!S22=\"\",\"\",'HVAC Inputs'!S22)","v":""},{"$f":"IF(+'HVAC Inputs'!T22=\"\",\"\",'HVAC Inputs'!T22)","v":""},"-",null,null,20,63.33,"No",8.8000000000000007,12.3,3.2,null,"Air Cooled VRF Heat Pump (No Heat Recovery)",null,null,null,null,null,"Air Cooled VRF Heat Pump (Heat Recovery)"]
[null,null,null,null,"VRF Heat Recovery or No Heat Recovery?",{"$f":"IF(+'HVAC Inputs'!P23=\"\",\"\",'HVAC Inputs'!P23)","v":""},{"$f":"IF(+'HVAC Inputs'!Q23=\"\",\"\",'HVAC Inputs'!Q23)","v":""},{"$f":"IF(+'HVAC Inputs'!R23=\"\",\"\",'HVAC Inputs'!R23)","v":""},{"$f":"IF(+'HVAC Inputs'!S23=\"\",\"\",'HVAC Inputs'!S23)","v":""},{"$f":"IF(+'HVAC Inputs'!T23=\"\",\"\",'HVAC Inputs'!T23)","v":""},"-",null,null,"Table C403.3.2(2)",null,null,null,null,null,null,"Min","Max","NH TRM 2026",null,null,null,"Min","Max","NH TRM 2026"]
[null,null,null,null,"Cooling Efficiency EER2",{"$f":"IF(+'HVAC Inputs'!P24=\"\",\"\",'HVAC Inputs'!P24)","v":""},{"$f":"IF(+'HVAC Inputs'!Q24=\"\",\"\",'HVAC Inputs'!Q24)","v":""},{"$f":"IF(+'HVAC Inputs'!R24=\"\",\"\",'HVAC Inputs'!R24)","v":""},{"$f":"IF(+'HVAC Inputs'!S24=\"\",\"\",'HVAC Inputs'!S24)","v":""},{"$f":"IF(+'HVAC Inputs'!T24=\"\",\"\",'HVAC Inputs'!T24)","v":""},"-",null,null,"Heat pump ratings for units under 5.4 tons are based on SEER and HSPF",null,null,null,null,null,null,"Capacity","Capacity","Cooling","Cooling ","Heating",null,"Capacity","Capacity","Cooling","Cooling ","Heating"]
[null,null,null,null,"Cooling Efficiency IEER (SEER2 if < 5.4 tons)",{"$f":"IF(+'HVAC Inputs'!P25=\"\",\"\",'HVAC Inputs'!P25)","v":""},{"$f":"IF(+'HVAC Inputs'!Q25=\"\",\"\",'HVAC Inputs'!Q25)","v":""},{"$f":"IF(+'HVAC Inputs'!R25=\"\",\"\",'HVAC Inputs'!R25)","v":""},{"$f":"IF(+'HVAC Inputs'!S25=\"\",\"\",'HVAC Inputs'!S25)","v":""},{"$f":"IF(+'HVAC Inputs'!T25=\"\",\"\",'HVAC Inputs'!T25)","v":""},"-",null,null,null,null,null,null,null,null,null,"Tons","Tons","EER2","IEER/SEER2","COP/HSPF2",null,"Tons","Tons","EER2","IEER/SEER2","COP"]
[null,null,null,null,"Heating Efficiency  COP (HSPF2 if < 5.4 tons)",{"$f":"IF(+'HVAC Inputs'!P26=\"\",\"\",'HVAC Inputs'!P26)","v":""},{"$f":"IF(+'HVAC Inputs'!Q26=\"\",\"\",'HVAC Inputs'!Q26)","v":""},{"$f":"IF(+'HVAC Inputs'!R26=\"\",\"\",'HVAC Inputs'!R26)","v":""},{"$f":"IF(+'HVAC Inputs'!S26=\"\",\"\",'HVAC Inputs'!S26)","v":""},{"$f":"IF(+'HVAC Inputs'!T26=\"\",\"\",'HVAC Inputs'!T26)","v":""},"-",null,null,"Water Source Heat Pumps",null,null,null,null,null,null,0,{"$f":"65/12","v":5.416666666666667},11.9,14.3,7.5,null,0,{"$f":"65/12","v":5.416666666666667},11.9,14.3,7.5]
[null,null,null,null,"Equivalent Full Load Cooling Hours",{"$f":"IF(F9=\"\",\"\",'HVAC Inputs'!$R$100)","v":""},{"$f":"IF(G9=\"\",\"\",'HVAC Inputs'!$R$100)","v":""},{"$f":"IF(H9=\"\",\"\",'HVAC Inputs'!$R$100)","v":""},{"$f":"IF(I9=\"\",\"\",'HVAC Inputs'!$R$100)","v":""},{"$f":"IF(J9=\"\",\"\",'HVAC Inputs'!$R$100)","v":""},"-",null,null,null,"Min","Max","NH TRM 2026",null,null,null,{"$f":"V17","v":5.416666666666667},{"$f":"135/12","v":11.25},11,14.6,3.3,null,{"$f":"AB17","v":5.416666666666667},{"$f":"135/12","v":11.25},10.8,14.4,3.3]
[null,null,null,null,"Equivalent Full Load Heating Hours",{"$f":"IF(F9=\"\",\"\",'HVAC Inputs'!$R$101)","v":""},{"$f":"IF(G9=\"\",\"\",'HVAC Inputs'!$R$101)","v":""},{"$f":"IF(H9=\"\",\"\",'HVAC Inputs'!$R$101)","v":""},{"$f":"IF(I9=\"\",\"\",'HVAC Inputs'!$R$101)","v":""},{"$f":"IF(J9=\"\",\"\",'HVAC Inputs'!$R$101)","v":""},"-",null,null,"Equipment","Capacity","Capacity","Cooling","Heating",null,null,{"$f":"V18","v":11.25},{"$f":"240/12","v":20},10.6,13.9,3.2,null,{"$f":"AB18","v":11.25},{"$f":"240/12","v":20},10.4,13.7,3.2]
[null,null,null,null,"Measure Life",{"$f":"IF(F10=\"\",\"\",IF(OR(F$10=$AE$7,F$10=$AE$8),25,IF(F$10=$AE$6,12,IF(F$10=0,0,20))))","v":""},{"$f":"IF(G10=\"\",\"\",IF(OR(G$10=$AE$7,G$10=$AE$8),25,IF(G$10=$AE$6,12,IF(G$10=0,0,20))))","v":""},{"$f":"IF(H10=\"\",\"\",IF(OR(H$10=$AE$7,H$10=$AE$8),25,IF(H$10=$AE$6,12,IF(H$10=0,0,20))))","v":""},{"$f":"IF(I10=\"\",\"\",IF(OR(I$10=$AE$7,I$10=$AE$8),25,IF(I$10=$AE$6,12,IF(I$10=0,0,20))))","v":""},{"$f":"IF(J10=\"\",\"\",IF(OR(J$10=$AE$7,J$10=$AE$8),25,IF(J$10=$AE$6,12,IF(J$10=0,0,20))))","v":""},"-",null,null,"Type","Tons","Tons","EER2","COP",null,null,{"$f":"V19","v":20},63.33,9.5,12.7,3.2,null,{"$f":"AB19","v":20},63.33,9.3000000000000007,12.5,3.2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Water Source Heat Pump",0,{"$f":"O22","v":1.4166666666666667},11.6,4.3]
[null,null,null,null,null,"Below Sections for Baseline Performance Calculate Automatically Based on Inputs",null,null,null,null,null,null,null,null,{"$f":"17/12","v":1.4166666666666667},{"$f":"135/12","v":11.25},12.4,4.3,null,null,"Water Cooled VRF Heat Pump (No Heat Recovery)",null,null,null,null,null,"Water Cooled VRF Heat Pump (Heat Recovery)"]
[null,null,null,null,"Base Cooling EER2",{"$f":"IF(F10=\"\",\"\",IF(F10=$AE$5, IF(F11=\"Yes\", IF(F12<V8, X8, IF(F12<V9, X9, X10)), IF(F12<$O$8,IF(F13=\"Split\",$Q$8,IF(F13=\"Packaged\",$Q$10,\"SPLIT OR PACKAGED?\")),OFFSET($N$7,MATCH(F12,$N$8:$N$13,1),3))),IF(F10=$AE$6,IF(F12>$P$22,\"CUSTOM\",OFFSET($O$20,MATCH(F12,$O$21:$O$22,1),2)),IF(F10=$AE$7,IF(F12>$P$23,\"CUSTOM\",$Q$23),IF(F10=$AE$8,IF(F12>$P$24,\"CUSTOM\",$Q$24),IF(F10=$AE$9,IF(F14=\"Heat Recovery\",OFFSET($AA$16,MATCH(F12,$AA$17:$AA$20,1),2),OFFSET($U$16,MATCH(F12,$U$17:$U$20,1),2)),IF(F10=$AE$10,IF(F14=\"Heat Recovery\",OFFSET($AA$25,MATCH(F12,$AA$26:$AA$29,1),2),OFFSET($U$25,MATCH(F12,$U$26:$U$29,1),2)))))))))","v":""},{"$f":"IF(G10=\"\",\"\",IF(G10=$AE$5,IF(G12<$O$8,IF(G13=\"Split\",$Q$8,IF(G13=\"Packaged\",$Q$10,\"SPLIT OR PACKAGED?\")),OFFSET($N$7,MATCH(G12,$N$8:$N$13,1),3)),IF(G10=$AE$6,IF(G12>$P$22,\"CUSTOM\",OFFSET($O$20,MATCH(G12,$O$21:$O$22,1),2)),IF(G10=$AE$7,IF(G12>$P$23,\"CUSTOM\",$Q$23),IF(G10=$AE$8,IF(G12>$P$24,\"CUSTOM\",$Q$24),IF(G10=$AE$9,IF(G14=\"Heat Recovery\",OFFSET($AA$16,MATCH(G12,$AA$17:$AA$20,1),2),OFFSET($U$16,MATCH(G12,$U$17:$U$20,1),2)),IF(G10=$AE$10,IF(G14=\"Heat Recovery\",OFFSET($AA$25,MATCH(G12,$AA$26:$AA$28,1),2),OFFSET($U$25,MATCH(G12,$U$26:$U$28,1),2)))))))))","v":""},{"$f":"IF(H10=\"\",\"\",IF(H10=$AE$5,IF(H12<$O$8,IF(H13=\"Split\",$Q$8,IF(H13=\"Packaged\",$Q$10,\"SPLIT OR PACKAGED?\")),OFFSET($N$7,MATCH(H12,$N$8:$N$13,1),3)),IF(H10=$AE$6,IF(H12>$P$22,\"CUSTOM\",OFFSET($O$20,MATCH(H12,$O$21:$O$22,1),2)),IF(H10=$AE$7,IF(H12>$P$23,\"CUSTOM\",$Q$23),IF(H10=$AE$8,IF(H12>$P$24,\"CUSTOM\",$Q$24),IF(H10=$AE$9,IF(H14=\"Heat Recovery\",OFFSET($AA$16,MATCH(H12,$AA$17:$AA$20,1),2),OFFSET($U$16,MATCH(H12,$U$17:$U$20,1),2)),IF(H10=$AE$10,IF(H14=\"Heat Recovery\",OFFSET($AA$25,MATCH(H12,$AA$26:$AA$28,1),2),OFFSET($U$25,MATCH(H12,$U$26:$U$28,1),2)))))))))","v":""},{"$f":"IF(I10=\"\",\"\",IF(I10=$AE$5,IF(I12<$O$8,IF(I13=\"Split\",$Q$8,IF(I13=\"Packaged\",$Q$10,\"SPLIT OR PACKAGED?\")),OFFSET($N$7,MATCH(I12,$N$8:$N$13,1),3)),IF(I10=$AE$6,IF(I12>$P$22,\"CUSTOM\",OFFSET($O$20,MATCH(I12,$O$21:$O$22,1),2)),IF(I10=$AE$7,IF(I12>$P$23,\"CUSTOM\",$Q$23),IF(I10=$AE$8,IF(I12>$P$24,\"CUSTOM\",$Q$24),IF(I10=$AE$9,IF(I14=\"Heat Recovery\",OFFSET($AA$16,MATCH(I12,$AA$17:$AA$20,1),2),OFFSET($U$16,MATCH(I12,$U$17:$U$20,1),2)),IF(I10=$AE$10,IF(I14=\"Heat Recovery\",OFFSET($AA$25,MATCH(I12,$AA$26:$AA$28,1),2),OFFSET($U$25,MATCH(I12,$U$26:$U$28,1),2)))))))))","v":""},{"$f":"IF(J10=\"\",\"\",IF(J10=$AE$5,IF(J12<$O$8,IF(J13=\"Split\",$Q$8,IF(J13=\"Packaged\",$Q$10,\"SPLIT OR PACKAGED?\")),OFFSET($N$7,MATCH(J12,$N$8:$N$13,1),3)),IF(J10=$AE$6,IF(J12>$P$22,\"CUSTOM\",OFFSET($O$20,MATCH(J12,$O$21:$O$22,1),2)),IF(J10=$AE$7,IF(J12>$P$23,\"CUSTOM\",$Q$23),IF(J10=$AE$8,IF(J12>$P$24,\"CUSTOM\",$Q$24),IF(J10=$AE$9,IF(J14=\"Heat Recovery\",OFFSET($AA$16,MATCH(J12,$AA$17:$AA$20,1),2),OFFSET($U$16,MATCH(J12,$U$17:$U$20,1),2)),IF(J10=$AE$10,IF(J14=\"Heat Recovery\",OFFSET($AA$25,MATCH(J12,$AA$26:$AA$28,1),2),OFFSET($U$25,MATCH(J12,$U$26:$U$28,1),2)))))))))","v":""},"-",null,null,"Open Loop Ground Water Heat Pump",0,{"$f":"135/12","v":11.25},17.100000000000001,3.7,null,null,"Min","Max","NH TRM 2026",null,null,null,"Min","Max","NH TRM 2026"]
[null,null,null,null,"Base Cooling IEER (SEER2 if < 5.4 tons)",{"$f":"IF(F10=\"\",\"\",IF(F10=$AE$5, IF(F11=\"Yes\", IF(F12<V8, Y8, IF(F12<V9, Y9, Y10)), IF(F12<$O$8,IF(F13=\"Packaged\",$R$10,IF(F13=\"Split\",$R$9,\"SPLIT OR PACKAGED?\")),OFFSET($N$7,MATCH(F12,$N$8:$N$13,1),4))),IF(OR(F10=$AE$6,F10=$AE$7,F10=$AE$8),\"n/a\",IF(F10=$AE$9,IF(F14=\"Heat Recovery\",OFFSET($AA$16,MATCH(F12,$AA$17:$AA$20,1),3),OFFSET($U$16,MATCH(F12,$U$17:$U$20,1),3)),IF(F10=$AE$10,IF(F14=\"Heat Recovery\",OFFSET($AA$25,MATCH(F12,$AA$26:$AA$29,1),3),OFFSET($U$25,MATCH(F12,$U$26:$U$29,1),3)))))))","v":""},{"$f":"IF(G10=\"\",\"\",IF(G10=$AE$5,IF(G12<$O$8,IF(G13=\"Packaged\",$R$10,IF(G13=\"Split\",$R$9,\"SPLIT OR PACKAGED?\")),OFFSET($N$7,MATCH(G12,$N$8:$N$13,1),4)),IF(OR(G10=$AE$6,G10=$AE$7,G10=$AE$8),\"n/a\",IF(G10=$AE$9,IF(G14=\"Heat Recovery\",OFFSET($AA$16,MATCH(G12,$AA$17:$AA$20,1),3),OFFSET($U$16,MATCH(G12,$U$17:$U$20,1),3)),IF(G10=$AE$10,IF(G14=\"Heat Recovery\",OFFSET($AA$25,MATCH(G12,$AA$26:$AA$29,1),3),OFFSET($U$25,MATCH(G12,$U$26:$U$29,1),3)))))))","v":""},{"$f":"IF(H10=\"\",\"\",IF(H10=$AE$5,IF(H12<$O$8,IF(H13=\"Packaged\",$R$10,IF(H13=\"Split\",$R$9,\"SPLIT OR PACKAGED?\")),OFFSET($N$7,MATCH(H12,$N$8:$N$13,1),4)),IF(OR(H10=$AE$6,H10=$AE$7,H10=$AE$8),\"n/a\",IF(H10=$AE$9,IF(H14=\"Heat Recovery\",OFFSET($AA$16,MATCH(H12,$AA$17:$AA$20,1),3),OFFSET($U$16,MATCH(H12,$U$17:$U$20,1),3)),IF(H10=$AE$10,IF(H14=\"Heat Recovery\",OFFSET($AA$25,MATCH(H12,$AA$26:$AA$29,1),3),OFFSET($U$25,MATCH(H12,$U$26:$U$29,1),3)))))))","v":""},{"$f":"IF(I10=\"\",\"\",IF(I10=$AE$5,IF(I12<$O$8,IF(I13=\"Packaged\",$R$10,IF(I13=\"Split\",$R$9,\"SPLIT OR PACKAGED?\")),OFFSET($N$7,MATCH(I12,$N$8:$N$13,1),4)),IF(OR(I10=$AE$6,I10=$AE$7,I10=$AE$8),\"n/a\",IF(I10=$AE$9,IF(I14=\"Heat Recovery\",OFFSET($AA$16,MATCH(I12,$AA$17:$AA$20,1),3),OFFSET($U$16,MATCH(I12,$U$17:$U$20,1),3)),IF(I10=$AE$10,IF(I14=\"Heat Recovery\",OFFSET($AA$25,MATCH(I12,$AA$26:$AA$29,1),3),OFFSET($U$25,MATCH(I12,$U$26:$U$29,1),3)))))))","v":""},{"$f":"IF(J10=\"\",\"\",IF(J10=$AE$5,IF(J12<$O$8,IF(J13=\"Packaged\",$R$10,IF(J13=\"Split\",$R$9,\"SPLIT OR PACKAGED?\")),OFFSET($N$7,MATCH(J12,$N$8:$N$13,1),4)),IF(OR(J10=$AE$6,J10=$AE$7,J10=$AE$8),\"n/a\",IF(J10=$AE$9,IF(J14=\"Heat Recovery\",OFFSET($AA$16,MATCH(J12,$AA$17:$AA$20,1),3),OFFSET($U$16,MATCH(J12,$U$17:$U$20,1),3)),IF(J10=$AE$10,IF(J14=\"Heat Recovery\",OFFSET($AA$25,MATCH(J12,$AA$26:$AA$29,1),3),OFFSET($U$25,MATCH(J12,$U$26:$U$29,1),3)))))))","v":""},"-",null,null,"Closed Loop Ground Water Heat Pump",0,{"$f":"135/12","v":11.25},13.4,3.2,null,null,"Capacity","Capacity","Cooling","Cooling ","Heating",null,"Capacity","Capacity","Cooling","Cooling ","Heating"]
[null,null,null,null,"Base Heating COP (HSFP2 if < 5.4 tons)",{"$f":"IF(F10=\"\",\"\",IF(F10=$AE$5, IF(F11=\"Yes\", IF(F12<V8, Z8, IF(F12<V9, Z9, Z10)), IF(F12<$O$8,(IF(F13=\"SPLIT\",$S$9,IF(F13=\"PACKAGED\",$S$10,\"SPLIT OR PACKAGED?\"))),OFFSET($N$7,MATCH(F12,$N$8:$N$13,1),5))),IF(F10=$AE$6,IF(F12>$P$22,\"CUSTOM\",OFFSET($O$20,MATCH(F12,$O$21:$O$22,1),3)),IF(F10=$AE$7,IF(F12>$P$23,\"CUSTOM\",$R$23),IF(F10=$AE$8,IF(F12>$P$24,\"CUSTOM\",$R$24),IF(F10=$AE$9,IF(F14=\"Heat Recovery\",OFFSET($AA$16,MATCH(F12,$AA$17:$AA$20,1),4),OFFSET($U$16,MATCH(F12,$U$17:$U$20,1),4)),IF(F10=$AE$10,IF(F14=\"Heat Recovery\",OFFSET($AA$25,MATCH(F12,$AA$26:$AA$29,1),4),OFFSET($U$25,MATCH(F12,$U$26:$U$29,1),4)))))))))","v":""},{"$f":"IF(G10=\"\",\"\",IF(G10=$AE$5,IF(G12<$O$8,(IF(G13=\"SPLIT\",$S$9,IF(G13=\"PACKAGED\",$S$10,\"SPLIT OR PACKAGED?\"))),OFFSET($N$7,MATCH(G12,$N$8:$N$13,1),5)),IF(G10=$AE$6,IF(G12>$P$22,\"CUSTOM\",OFFSET($O$20,MATCH(G12,$O$21:$O$22,1),3)),IF(G10=$AE$7,IF(G12>$P$23,\"CUSTOM\",$R$23),IF(G10=$AE$8,IF(G12>$P$24,\"CUSTOM\",$R$24),IF(G10=$AE$9,IF(G14=\"Heat Recovery\",OFFSET($AA$16,MATCH(G12,$AA$17:$AA$20,1),4),OFFSET($U$16,MATCH(G12,$U$17:$U$20,1),4)),IF(G10=$AE$10,IF(G14=\"Heat Recovery\",OFFSET($AA$25,MATCH(G12,$AA$26:$AA$29,1),4),OFFSET($U$25,MATCH(G12,$U$26:$U$29,1),4)))))))))","v":""},{"$f":"IF(H10=\"\",\"\",IF(H10=$AE$5,IF(H12<$O$8,(IF(H13=\"SPLIT\",$S$9,IF(H13=\"PACKAGED\",$S$10,\"SPLIT OR PACKAGED?\"))),OFFSET($N$7,MATCH(H12,$N$8:$N$13,1),5)),IF(H10=$AE$6,IF(H12>$P$22,\"CUSTOM\",OFFSET($O$20,MATCH(H12,$O$21:$O$22,1),3)),IF(H10=$AE$7,IF(H12>$P$23,\"CUSTOM\",$R$23),IF(H10=$AE$8,IF(H12>$P$24,\"CUSTOM\",$R$24),IF(H10=$AE$9,IF(H14=\"Heat Recovery\",OFFSET($AA$16,MATCH(H12,$AA$17:$AA$20,1),4),OFFSET($U$16,MATCH(H12,$U$17:$U$20,1),4)),IF(H10=$AE$10,IF(H14=\"Heat Recovery\",OFFSET($AA$25,MATCH(H12,$AA$26:$AA$29,1),4),OFFSET($U$25,MATCH(H12,$U$26:$U$29,1),4)))))))))","v":""},{"$f":"IF(I10=\"\",\"\",IF(I10=$AE$5,IF(I12<$O$8,(IF(I13=\"SPLIT\",$S$9,IF(I13=\"PACKAGED\",$S$10,\"SPLIT OR PACKAGED?\"))),OFFSET($N$7,MATCH(I12,$N$8:$N$13,1),5)),IF(I10=$AE$6,IF(I12>$P$22,\"CUSTOM\",OFFSET($O$20,MATCH(I12,$O$21:$O$22,1),3)),IF(I10=$AE$7,IF(I12>$P$23,\"CUSTOM\",$R$23),IF(I10=$AE$8,IF(I12>$P$24,\"CUSTOM\",$R$24),IF(I10=$AE$9,IF(I14=\"Heat Recovery\",OFFSET($AA$16,MATCH(I12,$AA$17:$AA$20,1),4),OFFSET($U$16,MATCH(I12,$U$17:$U$20,1),4)),IF(I10=$AE$10,IF(I14=\"Heat Recovery\",OFFSET($AA$25,MATCH(I12,$AA$26:$AA$29,1),4),OFFSET($U$25,MATCH(I12,$U$26:$U$29,1),4)))))))))","v":""},{"$f":"IF(J10=\"\",\"\",IF(J10=$AE$5,IF(J12<$O$8,(IF(J13=\"SPLIT\",$S$9,IF(J13=\"PACKAGED\",$S$10,\"SPLIT OR PACKAGED?\"))),OFFSET($N$7,MATCH(J12,$N$8:$N$13,1),5)),IF(J10=$AE$6,IF(J12>$P$22,\"CUSTOM\",OFFSET($O$20,MATCH(J12,$O$21:$O$22,1),3)),IF(J10=$AE$7,IF(J12>$P$23,\"CUSTOM\",$R$23),IF(J10=$AE$8,IF(J12>$P$24,\"CUSTOM\",$R$24),IF(J10=$AE$9,IF(J14=\"Heat Recovery\",OFFSET($AA$16,MATCH(J12,$AA$17:$AA$20,1),4),OFFSET($U$16,MATCH(J12,$U$17:$U$20,1),4)),IF(J10=$AE$10,IF(J14=\"Heat Recovery\",OFFSET($AA$25,MATCH(J12,$AA$26:$AA$29,1),4),OFFSET($U$25,MATCH(J12,$U$26:$U$29,1),4)))))))))","v":""},"-",null,null,"Table C403.3.2(2)",null,null,null,null,null,null,"Tons","Tons","EER2","IEER","COP",null,"Tons","Tons","EER2","IEER","COP"]
[null,null,null,null,null,{"$f":"IF(ISERROR((12/F$9-12/F$12)*F$10*F$15/12),\"\",(12/F$9-12/F$12)*F$10*F$15/12)","v":""},{"$f":"IF(ISERROR((12/G$9-12/G$12)*G$10*G$15/12),\"\",(12/G$9-12/G$12)*G$10*G$15/12)","v":""},{"$f":"IF(ISERROR((12/H$9-12/H$12)*H$10*H$15/12),\"\",(12/H$9-12/H$12)*H$10*H$15/12)","v":""},{"$f":"IF(ISERROR((12/I$9-12/I$12)*I$10*I$15/12),\"\",(12/I$9-12/I$12)*I$10*I$15/12)","v":""},{"$f":"IF(ISERROR((12/J$9-12/J$12)*J$10*J$15/12),\"\",(12/J$9-12/J$12)*J$10*J$15/12)","v":""},null,null,null,null,null,null,null,null,null,null,0,{"$f":"65/12","v":5.416666666666667},12,16,4.3,null,0,{"$f":"65/12","v":5.416666666666667},11.8,15.8,4.3]
[null,null,null,null,null,"Below Sections for Energy Savings Calculate Automatically Based on Inputs",null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"V26","v":5.416666666666667},{"$f":"135/12","v":11.25},12,16,4.3,null,{"$f":"AB26","v":5.416666666666667},{"$f":"135/12","v":11.25},11.8,15.8,4.3]
[null,null,null,null,null,"Cooling Energy Savings Summary - Based on EER2",null,null,null,null," ",null,null,null,null,null,null,null,null,null,{"$f":"V27","v":11.25},{"$f":"240/12","v":20},10,14,4,null,{"$f":"AB27","v":11.25},{"$f":"240/12","v":20},9.8000000000000007,13.8,4]
[null,null,null,null,"Annual Cooling kWh Savings based on EER2",{"$f":"IF(F15<F23, 0, IFERROR(F9*F12*F18*(12/F23-12/F15),\"\"))","v":""},{"$f":"IFERROR(G9*G12*G18*(12/G23-12/G15),\"\")","v":""},{"$f":"IFERROR(H9*H12*H18*(12/H23-12/H15),\"\")","v":""},{"$f":"IFERROR(I9*I12*I18*(12/I23-12/I15),\"\")","v":""},{"$f":"IFERROR(J9*J12*J18*(12/J23-12/J15),\"\")","v":""},"-",null,null,null,null,null,null,null,null,null,{"$f":"V28","v":20},63.33,10,12,3.9,null,{"$f":"AB28","v":20},63.33,9.8000000000000007,11.8,3.9]
[null,null,null,null,"Avg. Summer kW Savings Based on EER2",{"$f":"IFERROR(F29/F18,\"\")","v":""},{"$f":"IFERROR(G29/G18,\"\")","v":""},{"$f":"IFERROR(H29/H18,\"\")","v":""},{"$f":"IFERROR(I29/I18,\"\")","v":""},{"$f":"IFERROR(J29/J18,\"\")","v":""},"-"]
[null,null,null,null,null,{"$f":"IF(ISERROR((12/F$9-12/F$12)*F$10*F$15/12),\"\",(12/F$9-12/F$12)*F$10*F$15/12)","v":""},{"$f":"IF(ISERROR((12/G$9-12/G$12)*G$10*G$15/12),\"\",(12/G$9-12/G$12)*G$10*G$15/12)","v":""},{"$f":"IF(ISERROR((12/H$9-12/H$12)*H$10*H$15/12),\"\",(12/H$9-12/H$12)*H$10*H$15/12)","v":""},{"$f":"IF(ISERROR((12/I$9-12/I$12)*I$10*I$15/12),\"\",(12/I$9-12/I$12)*I$10*I$15/12)","v":""},{"$f":"IF(ISERROR((12/J$9-12/J$12)*J$10*J$15/12),\"\",(12/J$9-12/J$12)*J$10*J$15/12)","v":""},null,null,null,null,null,"On Peak"]
[null,null,null,null,null,"Cooling Energy Savings Summary - Based on IEER/SEER2",null,null,null,null,null,null,null,null,"Schools",0.85]
[null,null,null,null,"Annual Cooling kWh Savings based on IEER/SEER2",{"$f":"IF(F16<F24, 0, IFERROR(F9*F12*F18*(12/F24-12/F16),\"\"))","v":""},{"$f":"IFERROR(G9*G12*G18*(12/G24-12/G16),\"\")","v":""},{"$f":"IFERROR(H9*H12*H18*(12/H24-12/H16),\"\")","v":""},{"$f":"IFERROR(I9*I12*I18*(12/I24-12/I16),\"\")","v":""},{"$f":"IFERROR(J9*J12*J18*(12/J24-12/J16),\"\")","v":""},"-",null,null,null,"1 Shift",0.85]
[null,null,null,null,"Avg. Summer kW Savings Based on IEER/SEER2",{"$f":"IFERROR(F33/F18,\"\")","v":""},{"$f":"IFERROR(G33/G18,\"\")","v":""},{"$f":"IFERROR(H33/H18,\"\")","v":""},{"$f":"IFERROR(I33/I18,\"\")","v":""},{"$f":"IFERROR(J33/J18,\"\")","v":""},"-",null,null,null,"2 Shift",0.65]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3 Shift",0.35]
[null,null,null,null,null,"Heating Energy Savings"]
[null,null,null,null,"Annual Heating Savings, kWh",{"$f":"IF(F17<F25, 0, IFERROR((1/F$25-1/F$17)*(F9*F$12*12000/3412)*F$19,\"\"))","v":""},{"$f":"IFERROR((1/G$25-1/G$17)*(G9*G$12*12000/3412)*G$19,\"\")","v":""},{"$f":"IFERROR((1/H$25-1/H$17)*(H9*H$12*12000/3412)*H$19,\"\")","v":""},{"$f":"IFERROR((1/I$25-1/I$17)*(I9*I$12*12000/3412)*I$19,\"\")","v":""},{"$f":"IFERROR((1/J$25-1/J$17)*(J9*J$12*12000/3412)*J$19,\"\")","v":""},"-"]
[null,null,null,null,"Average Winter kW Demand Savings",{"$f":"IFERROR(F37/F19,\"\")","v":""},{"$f":"IFERROR(G37/G19,\"\")","v":""},{"$f":"IFERROR(H37/H19,\"\")","v":""},{"$f":"IFERROR(I37/I19,\"\")","v":""},{"$f":"IFERROR(J37/J19,\"\")","v":""},"-"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Equipment Type","CF sp","CF wp"]
[null,null,null,null,null,"Total Energy Savings (Heating + Cooling)",null,null,null,null,null,null,null,"Air to Air",0.34200000000000003,0]
[null,null,null,null,"Qualifies?",{"$f":"IFERROR(IF(OR(F10=N21,F10=N22,F10=N23),IF(OR(F15<F23,F17<F25),\"DNQ\",\"Yes\"),IF(OR(F15<F23, F16<F24, F17<F25), \"DNQ\", \"Yes\")), \"\")","v":"Yes"},{"$f":"IFERROR(IF(OR(G10=O21,G10=O22,G10=O23),IF(OR(G15<G23,G17<G25),\"DNQ\",\"Yes\"),IF(OR(G15<G23, G16<G24, G17<G25), \"DNQ\", \"Yes\")), \"\")","v":"Yes"},"Yes","Yes","Yes",null,null,null,"Water Source",0.34200000000000003,0.34200000000000003]
[null,null,null,null,"Annual Savings (kWh)",{"$f":"(IFERROR(IF(F41=\"Yes\",IF(OR(F10=N21,F10=N22,F10=N23),F29+F37,F33+F37),\"\"), 0))","v":0},{"$f":"(IFERROR(IF(G41=\"Yes\",IF(OR(G10=O21,G10=O22,G10=O23),G29+G37,G33+G37),\"\"), 0))","v":0},0,0,0,{"$f":"SUM(F42:J42)","v":0}]
[null,null,null,null,"Average Summer kW Demand Savings",{"$f":"F30","v":""},{"$f":"G30","v":""},"","","",{"$f":"SUM(F43:J43)","v":0}]
[null,null,null,null,"Average Winter kW Demand Savings",{"$f":"F38","v":""},{"$f":"G38","v":""},"","","",{"$f":"SUM(F44:J44)","v":0}]
[null,null,null,null,"On Peak Energy  Savings, kWh",{"$f":"IFERROR(F42*VLOOKUP($F$4,O32:P35,2),\"\")","v":""},{"$f":"IFERROR(G42*VLOOKUP($F$4,O122:P125,2),\"\")","v":""},{"$f":"IFERROR(H42*VLOOKUP($F$4,O122:P125,2),\"\")","v":""},{"$f":"IFERROR(I42*VLOOKUP($F$4,O122:P125,2),\"\")","v":""},{"$f":"IFERROR(J42*VLOOKUP($F$4,O122:P125,2),\"\")","v":""},{"$f":"SUM(F45:J45)","v":0}]

{"sheet":"HVAC11-Unitary&Split","index":29,"n_rows":41,"n_cols":22,"rows_kept":41,"cut":false,"hidden":true,"merged":[[7,1,7,2],[8,1,8,2],[0,6,0,12],[1,6,1,12],[1,1,1,4],[3,1,5,2],[6,1,6,2]]}
[null,null,null,null,null,null,"HVAC Prescriptive Rebate",null,null,null,null,null,null,null,null,null,null,"HVAC Lookup Tables: From NH TRM 2026"]
[null,"Measure Summary",null,null,null,null,"Unitary & Split Systems"]
[null,null,null,"Value","Unit",null,null,null,null,null,null,null,null,null,null,null,null,"Unitary AC and Split Systems"]
[null,"Total Savings",null,{"$f":"M40*(D8/100)","v":0},"Summer kW",null,null,null,null,null,null,null,null,null,null,null,null,"Capacity Range",null,null,"NH TRM 2026"]
[null,null,null,{"$f":"M41*(D9/100)","v":0},"Winter kW","Operating Profile",{"$f":"IF('HVAC Inputs'!W50=\"\",\"\",'HVAC Inputs'!W50)","v":""},null,null,null,null,null,null,null,null,null,null,"Min","Max","Electric ","Full Load","Part Load"]
[null,null,null,{"$f":"+M38","v":0},"kWh",null,null,null,null,null,null,null,null,null,null,null,null,"tons","tons","Resistance?","EER/EER2","IEER/SEER2"]
[null,"Measure Life",null,20,"Years",null,"Equipment Description",null,null,null,null,null,"Totals:",null,null,null,null,"Split",5.4,null,11.4,13.4]
[null,"CFsp",null,{"$f":"IFERROR(34.2,0)","v":34.200000000000003},"%","Equipment Tag",{"$f":"IF('HVAC Inputs'!W52=\"\",\"\",'HVAC Inputs'!W52)","v":""},{"$f":"IF('HVAC Inputs'!X52=\"\",\"\",'HVAC Inputs'!X52)","v":""},{"$f":"IF('HVAC Inputs'!Y52=\"\",\"\",'HVAC Inputs'!Y52)","v":""},{"$f":"IF('HVAC Inputs'!Z52=\"\",\"\",'HVAC Inputs'!Z52)","v":""},{"$f":"IF('HVAC Inputs'!AA52=\"\",\"\",'HVAC Inputs'!AA52)","v":""},{"$f":"IF('HVAC Inputs'!AB52=\"\",\"\",'HVAC Inputs'!AB52)","v":""},"-",null,null,null,null,"Packaged",5.4,null,11.4,13.4]
[null,"CFwp",null,{"$f":"IFERROR(IF(G11 = \"Water Cooled\", 34.2, 0), \"\")","v":0},"%","Model Numbers",{"$f":"IF('HVAC Inputs'!W53=\"\",\"\",'HVAC Inputs'!W53)","v":""},{"$f":"IF('HVAC Inputs'!X53=\"\",\"\",'HVAC Inputs'!X53)","v":""},{"$f":"IF('HVAC Inputs'!Y53=\"\",\"\",'HVAC Inputs'!Y53)","v":""},{"$f":"IF('HVAC Inputs'!Z53=\"\",\"\",'HVAC Inputs'!Z53)","v":""},{"$f":"IF('HVAC Inputs'!AA53=\"\",\"\",'HVAC Inputs'!AA53)","v":""},{"$f":"IF('HVAC Inputs'!AB53=\"\",\"\",'HVAC Inputs'!AB53)","v":""},"-",null,null,null,null,5.4,11.24,"No",11,14.6]
[null,null,null,null,null,"Quantity Units Installed",{"$f":"IF('HVAC Inputs'!W54=\"\",\"\",'HVAC Inputs'!W54)","v":""},{"$f":"IF('HVAC Inputs'!X54=\"\",\"\",'HVAC Inputs'!X54)","v":""},{"$f":"IF('HVAC Inputs'!Y54=\"\",\"\",'HVAC Inputs'!Y54)","v":""},{"$f":"IF('HVAC Inputs'!Z54=\"\",\"\",'HVAC Inputs'!Z54)","v":""},{"$f":"IF('HVAC Inputs'!AA54=\"\",\"\",'HVAC Inputs'!AA54)","v":""},{"$f":"IF('HVAC Inputs'!AB54=\"\",\"\",'HVAC Inputs'!AB54)","v":""},{"$f":"SUM(G10:L10)","v":0},null,null,null,null,11.25,19.899999999999999,"No",10.8,14]
[null,null,null,null,null,"Condenser Type",{"$f":"IF('HVAC Inputs'!W55=\"\",\"\",'HVAC Inputs'!W55)","v":""},{"$f":"IF('HVAC Inputs'!X55=\"\",\"\",'HVAC Inputs'!X55)","v":""},{"$f":"IF('HVAC Inputs'!Y55=\"\",\"\",'HVAC Inputs'!Y55)","v":""},{"$f":"IF('HVAC Inputs'!Z55=\"\",\"\",'HVAC Inputs'!Z55)","v":""},{"$f":"IF('HVAC Inputs'!AA55=\"\",\"\",'HVAC Inputs'!AA55)","v":""},{"$f":"IF('HVAC Inputs'!AB55=\"\",\"\",'HVAC Inputs'!AB55)","v":""},"-",null,null,null,null,20,"None","No",10,13]
[null,null,null,null,null,"Cooling Capacity - TONS",{"$f":"IF('HVAC Inputs'!W56=\"\",\"\",'HVAC Inputs'!W56)","v":""},{"$f":"IF('HVAC Inputs'!X56=\"\",\"\",'HVAC Inputs'!X56)","v":""},{"$f":"IF('HVAC Inputs'!Y56=\"\",\"\",'HVAC Inputs'!Y56)","v":""},{"$f":"IF('HVAC Inputs'!Z56=\"\",\"\",'HVAC Inputs'!Z56)","v":""},{"$f":"IF('HVAC Inputs'!AA56=\"\",\"\",'HVAC Inputs'!AA56)","v":""},{"$f":"IF('HVAC Inputs'!AB56=\"\",\"\",'HVAC Inputs'!AB56)","v":""},{"$f":"SUM(G12:L12)","v":0}]
[null,null,null,null,null,"If < 5.4 tons, Split or Packaged?",{"$f":"IF('HVAC Inputs'!W57=\"\",\"\",'HVAC Inputs'!W57)","v":""},{"$f":"IF('HVAC Inputs'!X57=\"\",\"\",'HVAC Inputs'!X57)","v":""},{"$f":"IF('HVAC Inputs'!Y57=\"\",\"\",'HVAC Inputs'!Y57)","v":""},{"$f":"IF('HVAC Inputs'!Z57=\"\",\"\",'HVAC Inputs'!Z57)","v":""},{"$f":"IF('HVAC Inputs'!AA57=\"\",\"\",'HVAC Inputs'!AA57)","v":""},{"$f":"IF('HVAC Inputs'!AB57=\"\",\"\",'HVAC Inputs'!AB57)","v":""}]
[null,null,null,null,null,"Unit Heat Source",{"$f":"IF('HVAC Inputs'!W58=\"\",\"\",'HVAC Inputs'!W58)","v":""},{"$f":"IF('HVAC Inputs'!X58=\"\",\"\",'HVAC Inputs'!X58)","v":""},{"$f":"IF('HVAC Inputs'!Y58=\"\",\"\",'HVAC Inputs'!Y58)","v":""},{"$f":"IF('HVAC Inputs'!Z58=\"\",\"\",'HVAC Inputs'!Z58)","v":""},{"$f":"IF('HVAC Inputs'!AA58=\"\",\"\",'HVAC Inputs'!AA58)","v":""},{"$f":"IF('HVAC Inputs'!AB58=\"\",\"\",'HVAC Inputs'!AB58)","v":""},"-"]
[null,null,null,null,null,"Cooling Efficiency : EER/EER2",{"$f":"IF('HVAC Inputs'!W59=\"\",\"\",'HVAC Inputs'!W59)","v":""},{"$f":"IF('HVAC Inputs'!X59=\"\",\"\",'HVAC Inputs'!X59)","v":""},{"$f":"IF('HVAC Inputs'!Y59=\"\",\"\",'HVAC Inputs'!Y59)","v":""},{"$f":"IF('HVAC Inputs'!Z59=\"\",\"\",'HVAC Inputs'!Z59)","v":""},{"$f":"IF('HVAC Inputs'!AA59=\"\",\"\",'HVAC Inputs'!AA59)","v":""},{"$f":"IF('HVAC Inputs'!AB59=\"\",\"\",'HVAC Inputs'!AB59)","v":""},"-"]
[null,null,null,null,null,"Cooling Efficiency : IEER/SEER2",{"$f":"IF('HVAC Inputs'!W60=\"\",\"\",'HVAC Inputs'!W60)","v":""},{"$f":"IF('HVAC Inputs'!X60=\"\",\"\",'HVAC Inputs'!X60)","v":""},{"$f":"IF('HVAC Inputs'!Y60=\"\",\"\",'HVAC Inputs'!Y60)","v":""},{"$f":"IF('HVAC Inputs'!Z60=\"\",\"\",'HVAC Inputs'!Z60)","v":""},{"$f":"IF('HVAC Inputs'!AA60=\"\",\"\",'HVAC Inputs'!AA60)","v":""},{"$f":"IF('HVAC Inputs'!AB60=\"\",\"\",'HVAC Inputs'!AB60)","v":""},"-",null,null,null,null,"Unitary AC and Split Systems"]
[null,null,null,null,null,"Equivalent Full Load Cooling Hours",{"$f":"IF(G10=\"\",\"\",'HVAC Inputs'!$R$100)","v":""},{"$f":"IF(H10=\"\",\"\",'HVAC Inputs'!$R$100)","v":""},{"$f":"IF(I10=\"\",\"\",'HVAC Inputs'!$R$100)","v":""},{"$f":"IF(J10=\"\",\"\",'HVAC Inputs'!$R$100)","v":""},{"$f":"IF(K10=\"\",\"\",'HVAC Inputs'!$R$100)","v":""},{"$f":"IF(L10=\"\",\"\",'HVAC Inputs'!$R$100)","v":""},"-",null,null,null,null,"Capacity Range",null,null,"NH TRM 2026"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Min","Max","Electric ","Full Load","Part Load"]
[null,null,null,null,null,null,"Below Sections for Baseline Performance Calculate Automatically Based on Inputs",null,null,null,null,null,null,null,null,null,null,"tons","tons","Resistance?","EER","IEER"]
[null,null,null,null,null,"Baseline Cooling Efficiency: EER/EER2",{"$f":"IF(G12<$S$7,IF(G13=\"Split\",$U$7,IF(G13=\"Packaged\",$U$8,\"Select Split or Packaged\")),IF(G14=\"Other\",OFFSET($R$6,MATCH(G12,$R$7:$R$11,1),3),OFFSET($R$19,MATCH(G12,$R$20:$R$22,1),3)))","v":{"$error":"#N/A"}},{"$f":"IF(H12<$S$7,IF(H13=\"Split\",$U$7,IF(H13=\"Packaged\",$U$8,\"Select Split or Packaged\")),IF(H14=\"Other\",OFFSET($R$6,MATCH(H12,$R$7:$R$11,1),3),OFFSET($R$19,MATCH(H12,$R$20:$R$22,1),3)))","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$f":"IF(L12<$S$7,IF(L13=\"Split\",$U$7,IF(L13=\"Packaged\",$U$8,\"Select Split or Packaged\")),IF(L14=\"Other\",OFFSET($R$6,MATCH(L12,$R$7:$R$11,1),3),OFFSET($R$19,MATCH(L12,$R$20:$R$22,1),3)))","v":{"$error":"#N/A"}},"-",null,null,null,null,5.4,11.24,"Yes",11,14.8]
[null,null,null,null,null,"Baseline Cooling Efficiency: IEER/SEER2",{"$f":"IF(G12<$S$7,IF(G13=\"Split\",$V$7,IF(G13=\"Packaged\",$V$8,\"Select Split or Packaged\")),IF(G14=\"Other\",OFFSET($R$6,MATCH(G12,$R$7:$R$11,1),4),OFFSET($R$19,MATCH(G12,$R$20:$R$22,1),4)))","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},"-",null,null,null,null,11.25,19.899999999999999,"Yes",10.8,14.2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,20,"None","Yes",10,13.2]
[null,null,null,null,null,null,"Below Sections for Energy Savings Calculate Automatically Based on Inputs"]
[null,null,null,null,null,null,"Energy Savings Summary - Based on EER/EER2"]
[null,null,null,null,null,"Annual kWh Savings based on EER/EER2",{"$f":"IF(G15<G20,0,IFERROR((12/G$20-12/G$15)*G10*G$12*G$17,\"\"))","v":{"$error":"#N/A"}},{"$f":"IFERROR((12/H$20-12/H$15)*H10*H$12*H$17,\"\")","v":""},"","","","",{"$f":"SUM(G25:L25)","v":{"$error":"#N/A"}}]
[null,null,null,null,null,"Avg. Summer kW Savings Based on EER/EER2",{"$f":"IFERROR(G25/G17,\"\")","v":""},"","","","","",{"$f":"SUM(G26:L26)","v":0}]
[null,null,null,null,null,"Avg.  Winter kW Savings Based on EER/EER2",{"$f":"IF(G25=\"\",\"\",0)","v":{"$error":"#N/A"}},{"$f":"IF(H25=\"\",\"\",0)","v":""},"","","","",{"$f":"SUM(G27:L27)","v":{"$error":"#N/A"}}]
[null,null,null,null,null,"On Peak Energy  Savings, kWh",{"$f":"IFERROR(G25*VLOOKUP($G$5,R31:S34,2),\"\")","v":""},{"$f":"IFERROR(H25*VLOOKUP($G$5,R31:S34,2),\"\")","v":""},{"$f":"IFERROR(I25*VLOOKUP($G$5,R31:S34,2),\"\")","v":""},{"$f":"IFERROR(J25*VLOOKUP($G$5,R31:S34,2),\"\")","v":""},{"$f":"IFERROR(K25*VLOOKUP($G$5,R31:S34,2),\"\")","v":""},{"$f":"IFERROR(L25*VLOOKUP($G$5,R31:S34,2),\"\")","v":""},{"$f":"SUM(G28:L28)","v":0}]
[]
[null,null,null,null,null,null,"Energy Savings Summary - Based on IEER/SEER2",null,null,null,null,null,null,null,null,null,null,null,"On Peak"]
[null,null,null,null,null,"Annual kWh Savings based on IEER/SEER2",{"$f":"IF(G16<G21,0,IFERROR((12/G$21-12/G$16)*G10*G$12*G$17,\"\"))","v":{"$error":"#N/A"}},{"$f":"IFERROR((12/H$21-12/H$16)*H10*H$12*H$17,\"\")","v":""},"","","","",{"$f":"SUM(G31:L31)","v":{"$error":"#N/A"}},null,null,null,null,"Schools",0.85]
[null,null,null,null,null,"Average Summer kW Demand Savings",{"$f":"IFERROR(G31/G17,\"\")","v":""},"","","","","",{"$f":"SUM(G32:L32)","v":0},null,null,null,null,"1 Shift",0.85]
[null,null,null,null,null,"Average Winter kW Demand Savings",{"$f":"IF(G31=\"\",\"\",0)","v":{"$error":"#N/A"}},{"$f":"IF(H31=\"\",\"\",0)","v":""},"","","","",{"$f":"SUM(G33:L33)","v":{"$error":"#N/A"}},null,null,null,null,"2 Shift",0.65]
[null,null,null,null,null,"On Peak Energy  Savings, kWh",{"$f":"IFERROR(G31*VLOOKUP($G$5,$R$31:$S$34,2),\"\")","v":""},"","","","","",{"$f":"SUM(G34:L34)","v":0},null,null,null,null,"3 Shift",0.35]
[]
[]
[null,null,null,null,null,null,"Energy Savings Summary"]
[null,null,null,null,null,"Qualifies?",{"$f":"IFERROR(IF(OR(G15<G20, G16<G21), \"DNQ\", \"Yes\"), \"\")","v":""},{"$f":"IFERROR(MAX(H25,H31), \"\")","v":0},0,0,0,0,{"$f":"SUM(G38:L38)","v":0}]
[null,null,null,null,null,"Annual kWh Savings based on IEER/SEER2",{"$f":"IFERROR(IF(G38=\"Yes\", G31, 0), \"\")","v":0},{"$f":"IFERROR(IF(H38=\"Yes\", H31, 0), \"\")","v":0},0,0,0,0,{"$f":"SUM(G39:L39)","v":0}]
[null,null,null,null,null,"Summer kW",{"$f":"IFERROR(G26, \"\")","v":""},{"$f":"IFERROR(H26, \"\")","v":""},"","","","",{"$f":"SUM(G40:L40)","v":0}]
[null,null,null,null,null,"Winter kW",{"$f":"IFERROR(G27, \"\")","v":""},{"$f":"IFERROR(H27, \"\")","v":""},"","","","",{"$f":"SUM(G41:L41)","v":0}]

{"sheet":"HVAC12-Chillers","index":30,"n_rows":44,"n_cols":21,"rows_kept":44,"cut":false,"hidden":true,"merged":[[7,1,7,2],[8,1,8,2],[0,6,0,10],[1,6,1,10],[1,1,1,4],[3,1,5,2],[6,1,6,2]]}
[null,null,null,null,null,null,"HVAC Prescriptive Rebate",null,null,null,null,null,null,null,null,"Chiller Lookup Tables: From IECC 2018 / NH TRM 2026"]
[null,"Measure Summary",null,null,null,null,"Air & Water Cooled Chillers"]
[null,null,null,"Value","Unit",null,null,null,null,null,null,null,null,null,null,"Air Cooled Chillers"]
[null,"Total Savings",null,{"$f":"IFERROR(SUM(G41:K41)*D8/100, 0)","v":0},"Summer kW",null,null,null,null,null,null,null,null,null,null,"Equipment Size","Path A",null,"Path B"]
[null,null,null,{"$f":"IFERROR(SUM(G41:K41)*(D9/100),0)","v":0},"Winter kW",null,null,null,null,null,null,null,null,null,null,"TONS","EER","IPLV","EER","IPLV"]
[null,null,null,{"$f":"IFERROR(SUM(G39:K39),0)","v":0},"kWh",null,null,null,null,null,null,null,null,null,null,"  <150 ",10.1,13.7,9.6999999999999993,15.8]
[null,"Measure Life",null,23,"Years","Operating Profile",{"$f":"'HVAC Inputs'!O64","v":0},null,null,null,null,null,null,null,null,"  >150 ",10.1,14,9.6999999999999993,16.100000000000001]
[null,"CFsp",null,{"$f":"IFERROR(49, 0)","v":49},"%",null,null,null,null,null,null,null,null,null,null,"* Reference 2018 IECC Code Table C403.3.2(7) "]
[null,"CFwp",null,{"$f":"IFERROR(6, 0)","v":6},"%",null,"Equipment Description"]
[null,null,null,null,null,"Unit ID-Opt. (1)",{"$f":"IF('HVAC Inputs'!O65=\"\",\"\",'HVAC Inputs'!O65)","v":""},{"$f":"IF('HVAC Inputs'!P65=\"\",\"\",'HVAC Inputs'!P65)","v":""},{"$f":"IF('HVAC Inputs'!Q65=\"\",\"\",'HVAC Inputs'!Q65)","v":""},{"$f":"IF('HVAC Inputs'!R65=\"\",\"\",'HVAC Inputs'!R65)","v":""},{"$f":"IF('HVAC Inputs'!S65=\"\",\"\",'HVAC Inputs'!S65)","v":""}]
[null,null,null,null,null,"Model Numbers",{"$f":"IF('HVAC Inputs'!O66=\"\",\"\",'HVAC Inputs'!O66)","v":""},{"$f":"IF('HVAC Inputs'!P66=\"\",\"\",'HVAC Inputs'!P66)","v":""},{"$f":"IF('HVAC Inputs'!Q66=\"\",\"\",'HVAC Inputs'!Q66)","v":""},{"$f":"IF('HVAC Inputs'!R66=\"\",\"\",'HVAC Inputs'!R66)","v":""},{"$f":"IF('HVAC Inputs'!S66=\"\",\"\",'HVAC Inputs'!S66)","v":""}]
[null,null,null,null,null,"Quantity Units Installed (2)",{"$f":"IF('HVAC Inputs'!O67=\"\",\"\",'HVAC Inputs'!O67)","v":""},{"$f":"IF('HVAC Inputs'!P67=\"\",\"\",'HVAC Inputs'!P67)","v":""},{"$f":"IF('HVAC Inputs'!Q67=\"\",\"\",'HVAC Inputs'!Q67)","v":""},{"$f":"IF('HVAC Inputs'!R67=\"\",\"\",'HVAC Inputs'!R67)","v":""},{"$f":"IF('HVAC Inputs'!S67=\"\",\"\",'HVAC Inputs'!S67)","v":""},null,null,null,null,"Water Cooled Chillers"]
[null,null,null,null,null,"Chiller Type (3)",{"$f":"IF('HVAC Inputs'!O68=\"\",\"\",'HVAC Inputs'!O68)","v":""},{"$f":"IF('HVAC Inputs'!P68=\"\",\"\",'HVAC Inputs'!P68)","v":""},{"$f":"IF('HVAC Inputs'!Q68=\"\",\"\",'HVAC Inputs'!Q68)","v":""},{"$f":"IF('HVAC Inputs'!R68=\"\",\"\",'HVAC Inputs'!R68)","v":""},{"$f":"IF('HVAC Inputs'!S68=\"\",\"\",'HVAC Inputs'!S68)","v":""},null,null,null,null,"Min Tons for Category","Equipment Size","Path A",null,"Path B"]
[null,null,null,null,null,"Compressor Type (4)",{"$f":"IF('HVAC Inputs'!O69=\"\",\"\",'HVAC Inputs'!O69)","v":""},{"$f":"IF('HVAC Inputs'!P69=\"\",\"\",'HVAC Inputs'!P69)","v":""},{"$f":"IF('HVAC Inputs'!Q69=\"\",\"\",'HVAC Inputs'!Q69)","v":""},{"$f":"IF('HVAC Inputs'!R69=\"\",\"\",'HVAC Inputs'!R69)","v":""},{"$f":"IF('HVAC Inputs'!S69=\"\",\"\",'HVAC Inputs'!S69)","v":""},null,null,null,null,"(used in lookup)","TONS","kW/ton","IPLV","kW/ton","IPLV"]
[null,null,null,null,null,"Cooling Capacity - TONS (5)",{"$f":"IF('HVAC Inputs'!O70=\"\",\"\",'HVAC Inputs'!O70)","v":""},{"$f":"IF('HVAC Inputs'!P70=\"\",\"\",'HVAC Inputs'!P70)","v":""},{"$f":"IF('HVAC Inputs'!Q70=\"\",\"\",'HVAC Inputs'!Q70)","v":""},{"$f":"IF('HVAC Inputs'!R70=\"\",\"\",'HVAC Inputs'!R70)","v":""},{"$f":"IF('HVAC Inputs'!S70=\"\",\"\",'HVAC Inputs'!S70)","v":""},null,null,null,null,"Reciprocating, rotary-screw & scroll"]
[null,null,null,null,null,"Air Cooled New Efficiency - EER (6)",{"$f":"IF('HVAC Inputs'!O71=\"\",\"\",'HVAC Inputs'!O71)","v":""},{"$f":"IF('HVAC Inputs'!P71=\"\",\"\",'HVAC Inputs'!P71)","v":""},{"$f":"IF('HVAC Inputs'!Q71=\"\",\"\",'HVAC Inputs'!Q71)","v":""},{"$f":"IF('HVAC Inputs'!R71=\"\",\"\",'HVAC Inputs'!R71)","v":""},{"$f":"IF('HVAC Inputs'!S71=\"\",\"\",'HVAC Inputs'!S71)","v":""},null,null,null,null,0,"<75 ",0.75,0.6,0.78,0.5]
[null,null,null,null,null,"Air Cooled New Efficiency - IPLV ",{"$f":"IF('HVAC Inputs'!O72=\"\",\"\",'HVAC Inputs'!O72)","v":""},{"$f":"IF('HVAC Inputs'!P72=\"\",\"\",'HVAC Inputs'!P72)","v":""},{"$f":"IF('HVAC Inputs'!Q72=\"\",\"\",'HVAC Inputs'!Q72)","v":""},{"$f":"IF('HVAC Inputs'!R72=\"\",\"\",'HVAC Inputs'!R72)","v":""},{"$f":"IF('HVAC Inputs'!S72=\"\",\"\",'HVAC Inputs'!S72)","v":""},null,null,null,null,75,">75 and <150 ",0.72,0.56000000000000005,0.75,0.49]
[null,null,null,null,null,"Water Cooled New Efficiency FL - kW/Ton (7)",{"$f":"IF('HVAC Inputs'!O73=\"\",\"\",'HVAC Inputs'!O73)","v":""},{"$f":"IF('HVAC Inputs'!P73=\"\",\"\",'HVAC Inputs'!P73)","v":""},{"$f":"IF('HVAC Inputs'!Q73=\"\",\"\",'HVAC Inputs'!Q73)","v":""},{"$f":"IF('HVAC Inputs'!R73=\"\",\"\",'HVAC Inputs'!R73)","v":""},{"$f":"IF('HVAC Inputs'!S73=\"\",\"\",'HVAC Inputs'!S73)","v":""},null,null,null,null,150,">150 and <300 ",0.66,0.54,0.68,0.44]
[null,null,null,null,null,"Water Cooled New Efficiency IPLV - kW/Ton",{"$f":"IF('HVAC Inputs'!O74=\"\",\"\",'HVAC Inputs'!O74)","v":""},{"$f":"IF('HVAC Inputs'!P74=\"\",\"\",'HVAC Inputs'!P74)","v":""},{"$f":"IF('HVAC Inputs'!Q74=\"\",\"\",'HVAC Inputs'!Q74)","v":""},{"$f":"IF('HVAC Inputs'!R74=\"\",\"\",'HVAC Inputs'!R74)","v":""},{"$f":"IF('HVAC Inputs'!S74=\"\",\"\",'HVAC Inputs'!S74)","v":""},null,null,null,null,300,">300 and < 600",0.61,0.52,0.625,0.41]
[null,null,null,null,null,"Equivalent Full Load Cooling Hours (8)",{"$f":"IF(G12=\"\",\"\",'HVAC Inputs'!$R$100)","v":""},{"$f":"IF(H12=\"\",\"\",'HVAC Inputs'!$R$100)","v":""},{"$f":"IF(I12=\"\",\"\",'HVAC Inputs'!$R$100)","v":""},{"$f":"IF(J12=\"\",\"\",'HVAC Inputs'!$R$100)","v":""},{"$f":"IF(K12=\"\",\"\",'HVAC Inputs'!$R$100)","v":""},null,null,null,null,600,"> 600",0.56000000000000005,0.5,0.58499999999999996,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Centrifugal"]
[null,null,null,null,null,"Below Sections for Baseline Performance Calculate Automatically Based on Inputs",null,null,null,null,null,null,null,null,null,0,"<150 ",0.61,0.55000000000000004,0.69499999999999995,0.44]
[null,null,null,null,null,null,"Baseline Performance, Path A",null,null,null,null,null,null,null,null,150,">150 and <300",0.61,0.55000000000000004,0.63500000000000001,0.4]
[null,null,null,null,null,"Air Cooled Base Efficiency - EER (9)",{"$f":"IF(G13=\"Air Cooled\",IF(G15<150,$Q$6,$Q$7),\"\")","v":""},{"$f":"IF(H13=\"Air Cooled\",IF(H15<150,$Q$6,$Q$7),\"\")","v":""},"","","",null,null,null,null,300,">300 and <400",0.56000000000000005,0.52,0.59499999999999997,0.39]
[null,null,null,null,null,"Air Cooled Base Efficiency - IPLV",{"$f":"IF(G13=\"Air Cooled\",IF(G15<150,$R$6,$R$7),\"\")","v":""},{"$f":"IF(H13=\"Air Cooled\",IF(H15<150,$R$6,$R$7),\"\")","v":""},"","","",null,null,null,null,400,"> 400 and <600",0.56000000000000005,0.5,0.58499999999999996,0.38]
[null,null,null,null,null,"Water Cooled Base Efficiency - kW/Ton (10)",{"$f":"IF(G13<>\"Water Cooled\",\"\",IF(G14=\"Centrifugal\",OFFSET($P$21,MATCH(G15,$P$22:$P$26,1),2),OFFSET($P$15,MATCH(G15,$P$16:$P$20,1),2)))","v":""},{"$f":"IF(H13<>\"Water Cooled\",\"\",IF(H14=\"Centrifugal\",OFFSET($P$21,MATCH(H15,$P$22:$P$26,1),2),OFFSET($P$15,MATCH(H15,$P$16:$P$20,1),2)))","v":""},"","","",null,null,null,null,600,">600 ",0.56000000000000005,0.5,0.58499999999999996,0.38]
[null,null,null,null,null,"Water Cooled Base Efficiency - IPLV",{"$f":"IF(G13<>\"Water Cooled\",\"\",IF(G14=\"Centrifugal\",OFFSET($P$21,MATCH(G15,$P$22:$P$26,1),3),OFFSET($P$15,MATCH(G15,$P$16:$P$20,1),3)))","v":""},{"$f":"IF(H13<>\"Water Cooled\",\"\",IF(H14=\"Centrifugal\",OFFSET($P$21,MATCH(H15,$P$22:$P$26,1),3),OFFSET($P$15,MATCH(H15,$P$16:$P$20,1),3)))","v":""},"","","",null,null,null,null,"* Reference 2018 IECC Code Table C403.3.2(7) "]
[null,null,null,null,null,"Path A Savings (kWh)",{"$f":"IF(G13=\"Air Cooled\",IF(OR(G16<G24,G17<G25),\"DNQ\",(12/G25-12/G17)*G15*G20*G12),IF(G13=\"Water Cooled\",IF(OR(G18>G26,G19>G27),\"DNQ\",(G27-G19)*G15*G20*G12)))","v":false},{"$f":"IF(H13=\"Air Cooled\",IF(OR(H16<H24,H17<H25),\"DNQ\",(12/H25-12/H17)*H15*H20),IF(H13=\"Water Cooled\",IF(OR(H18>H26,H19>H27),\"DNQ\",(H27-H19)*H15*H20)))","v":false},false,false,false]
[]
[null,null,null,null,null,null,"Baseline Performance, Path B"]
[null,null,null,null,null,"Air Cooled Base Efficiency - EER (9)",{"$f":"IF(G13=\"Air Cooled\",IF(G15<150,$S$6,$S$7),\"\")","v":""},{"$f":"IF(H13=\"Air Cooled\",IF(H15<150,$S$6,$S$7),\"\")","v":""},"","",""]
[null,null,null,null,null,"Air Cooled Base Efficiency - IPLV",{"$f":"IF(G13=\"Air Cooled\",IF(G15<150,$T$6,$T$7),\"\")","v":""},{"$f":"IF(H13=\"Air Cooled\",IF(H15<150,$T$6,$T$7),\"\")","v":""},"","",""]
[null,null,null,null,null,"Water Cooled Base Efficiency - kW/Ton (10)",{"$f":"IF(G13<>\"Water Cooled\",\"\",IF(G14=\"Centrifugal\",OFFSET($P$21,MATCH(G15,$P$22:$P$26,1),4),OFFSET($P$15,MATCH(G15,$P$16:$P$20,1),4)))","v":""},{"$f":"IF(H13<>\"Water Cooled\",\"\",IF(H14=\"Centrifugal\",OFFSET($P$21,MATCH(H15,$P$22:$P$26,1),4),OFFSET($P$15,MATCH(H15,$P$16:$P$20,1),4)))","v":""},"","","",null,null,null,null,null,"On Peak"]
[null,null,null,null,null,"Water Cooled Base Efficiency - IPLV",{"$f":"IF(G13<>\"Water Cooled\",\"\",IF(G14=\"Centrifugal\",OFFSET($P$21,MATCH(G15,$P$22:$P$26,1),5),OFFSET($P$15,MATCH(G15,$P$16:$P$20,1),5)))","v":""},{"$f":"IF(H13<>\"Water Cooled\",\"\",IF(H14=\"Centrifugal\",OFFSET($P$21,MATCH(H15,$P$22:$P$26,1),5),OFFSET($P$15,MATCH(H15,$P$16:$P$20,1),5)))","v":""},"","","",null,null,null,null,"Schools",0.85]
[null,null,null,null,null,"Path B Savings (kWh)",{"$f":"IF(G13=\"Air Cooled\",IF(OR(G16<G31,G17<G32),\"DNQ\",(12/G32-12/G17)*G15*G20*G12),IF(G13=\"Water Cooled\",IF(OR(G18>G33,G19>G34),\"DNQ\",(G34-G19)*G15*G20*G12)))","v":false},{"$f":"IF(H13=\"Air Cooled\",IF(OR(H16<H31,H17<H32),\"DNQ\",(12/H32-12/H17)*H15*H20*H12),IF(H13=\"Water Cooled\",IF(OR(H18>H33,H19>H34),\"DNQ\",(H34-H19)*H15*H20*H12)))","v":false},false,false,false,null,null,null,null,"1 Shift",0.85]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"2 Shift",0.65]
[null,null,null,null,null,"Below Sections for Energy Savings Calculate Automatically Based on Inputs",null,null,null,null,null,null,null,null,null,"3 Shift",0.35]
[null,null,null,null,null,null,"Total Energy Savings (kWh)"]
[null,null,null,null,null,"Average Annual  kWh Savings ",{"$f":"MAX(G35,G28)","v":0},{"$f":"MAX(H35,H28)","v":0},0,0,0]
[null,null,null,null,null,"Compliance Path",{"$f":"IF(G39=G28,\"Path A\",IF(G39=G35,\"Path B\",\"DNQ\"))","v":"DNQ"},{"$f":"IF(H39=H28,\"Path A\",IF(H39=H35,\"Path B\",\"DNQ\"))","v":"DNQ"},"DNQ","DNQ","DNQ"]
[null,null,null,null,null,"Peak Demand Reduction",{"$f":"G39/G20","v":{"$error":"#VALUE!"}},{"$f":"H39/H20","v":{"$error":"#VALUE!"}},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[null,null,null,null,null,"On Peak Energy  Savings, kWh",{"$f":"IFERROR(G39*VLOOKUP($G$7,$P$34:$Q$37,2),\"\")","v":""},{"$f":"IFERROR(H39*VLOOKUP($G$7,$P$34:$Q$37,2),\"\")","v":""},{"$f":"IFERROR(I39*VLOOKUP($G$7,$P$34:$Q$37,2),\"\")","v":""},{"$f":"IFERROR(J39*VLOOKUP($G$7,$P$34:$Q$37,2),\"\")","v":""},{"$f":"IFERROR(K39*VLOOKUP($G$7,$P$34:$Q$37,2),\"\")","v":""},null,null,null,null,"Equipment Type","CF sp","CF wp"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"IPLV",0.49,0.06]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"FL",0.86,0.1]

{"sheet":"HVAC13-ProgTstats","index":31,"n_rows":26,"n_cols":16,"rows_kept":26,"cut":false,"hidden":true,"merged":[[0,1,1,9],[1,12,1,14],[3,1,3,4],[3,6,3,9],[4,6,12,9],[5,1,7,2],[8,1,8,2],[8,12,8,15],[9,1,9,2],[10,1,10,2],[21,1,21,9],[22,2,22,3],[22,7,22,9],[12,1,12,4],[13,1,13,2],[13,3,13,4],[13,6,16,9],[14,1,14,2],[14,3,14,4],[15,1,15,2],[15,3,15,4],[16,1,16,2],[16,3,16,4]]}
[null,"Measure: Thermostat - Progammable Thermostat"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Table 2: Coincidence Factors"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Fuel Type","CFsp","CFwp"]
[null,"Measure Summary",null,null,null,null,"Measure Description",null,null,null,null,null,"Electric",0,0]
[null,null,null,"Value","Unit",null,"Installation of a programmable thermostat, which gives the ability to adjust heating or air-conditioning operating times according to a pre-set schedule.",null,null,null,null,null,"Gas",0,0]
[null,"Total Savings",null,{"$f":"H25","v":0},"kW",null,null,null,null,null,null,null,"Oil",0,0]
[null,null,null,{"$f":"I25","v":0},"kWh",null,null,null,null,null,null,null,"Propane",0,0]
[null,null,null,{"$f":"J25","v":0},"MMBtu"]
[null,"Measure Life",null,15,"Years",null,null,null,null,null,null,null,"Table 3: Savings Values"]
[null,"CFsp",null,{"$f":"IFERROR(VLOOKUP('Project Info'!$D$24,$M$4:$O$7,2,FALSE),0)*100","v":0},"%",null,null,null,null,null,null,null,"Fuel Type","kWh","kW","MMBtu"]
[null,"CFwp",null,{"$f":"IFERROR(VLOOKUP('Project Info'!$D$24,$M$4:$O$7,3,FALSE),0)*100","v":0},"%",null,null,null,null,null,null,null,"Gas",0,0,2.0699999999999998]
[]
[null,"HVAC - Thermostat - Wifi Communicating"]
[null,"Measure Code",null,"COM-HVAC-PGM",null,null,"NOTE: For more information on this measure refer to the NH TRM."]
[null,"Market",null,"Commercial"]
[null,"Program Type",null,"Retrofit"]
[null,"Category",null,"HVAC"]
[]
[]
[]
[]
[null,"Table 1: Calculating Primary Energy Impact "]
[null,null,"Inputs",null,null,null,null,"Savings"]
[null,null,"Quantity",null,null,null,null,"kW","kWh","MMBtu"]
[null,1,{"$f":"'HVAC Inputs'!K62","v":0},{"$f":"IF(AND(C25>0,J26=0),\"Confirm Fuel Entered in 'Project Info'tab\",\"\")","v":""},null,null,null,0,0,{"$f":"P11*C25","v":0}]
[null,null,null,null,null,null,"Total (MMBTU only):",null,null,{"$f":"SUM(J25:J25)","v":0}]

{"sheet":"HVAC14-PTHP","index":32,"n_rows":27,"n_cols":14,"rows_kept":27,"cut":false,"hidden":true,"merged":[[11,8,15,11],[3,1,3,4],[5,1,7,2],[8,1,8,2],[9,1,9,2],[10,1,10,2]]}
[null,"Measure: Packaged Terminal Heat Pumps (PTHP)"]
[]
[]
[null,"Measure Summary",null,null,null,null,null,null,"PTHP"]
[null,null,null,"Value","Unit",null,null,null,"Measure Code",null,"COM-HVAC-PTHP"]
[null,"Total Savings",null,{"$f":"I27*D10/100","v":0},"Summer kW",null,null,null,"Markets ",null,"Commercial"]
[null,null,null,{"$f":"I27*D11/100","v":0},"Winter kW",null,null,null,"Program Types ",null,"Lost Opportunity"]
[null,null,null,{"$f":"H27","v":{"$error":"#VALUE!"}},"kWh",null,null,null,"Categories ",null,"HVAC"]
[null,"Measure Life",null,{"$f":"IFERROR(SUMPRODUCT(H14:L14,H24:L24)/SUM(H14:L14),12)","v":12},"Years"]
[null,"CFsp",null,34,"%"]
[null,"CFwp",null,42,"%",null,null,null,"Measure Description"]
[null,null,null,null,null,null,null,null,"Installation of a Packaged Terminal Heat Pump (PTHP) in a commercial and industrial scenario. A PTHP is purchased to replace a package terminal air conditioner (PTAC) with electric resistance heat."]
[]
[]
[]
[]
[]
[]
[]
[null,"Packaged Terminal Heat Pumps Savings",null,null,null,null,null,null,null,null,"Minimum Efficiency Requirements from TRM"]
[null,"Quantity","Capacity","Proposed",null,"Annual","Qualifies","Saved",null,null,"Btu/hr Threshold",null,"EER","COP"]
[null,"#","Btu/hr","EER","COP","Hours","(Y or N)","kWh","kW",null,"Less than",10000,12.1,3.5]
[null,{"$f":"IF('HVAC Inputs'!U66=\"\",\"\",'HVAC Inputs'!U66)","v":""},{"$f":"IF('HVAC Inputs'!V66=\"\",\"\",'HVAC Inputs'!V66)","v":""},{"$f":"IF('HVAC Inputs'!W66=\"\",\"\",'HVAC Inputs'!W66)","v":""},{"$f":"IF('HVAC Inputs'!X66=\"\",\"\",'HVAC Inputs'!X66)","v":""},{"$f":"IF('HVAC Inputs'!U66=\"\",\"\",'HVAC Inputs'!$R$101)","v":""},{"$f":"IF(C23<$L$22,IF(AND(D23>$M$22,E23>$N$22),\"Yes\",\"No\"),IF(AND(D23>$M$23,E23>$N$23),\"Yes\",\"No\"))","v":"Yes"},{"$f":"IF(G23=\"Yes\",B23*$M$25)","v":{"$error":"#VALUE!"}},{"$f":"IF('HVAC Inputs'!U66=\"\",\"\",H23/F23)","v":""},null,"Greater than",10000,10.7,3.1]
[null,{"$f":"IF('HVAC Inputs'!U67=\"\",\"\",'HVAC Inputs'!U67)","v":""},{"$f":"IF('HVAC Inputs'!V67=\"\",\"\",'HVAC Inputs'!V67)","v":""},{"$f":"IF('HVAC Inputs'!W67=\"\",\"\",'HVAC Inputs'!W67)","v":""},{"$f":"IF('HVAC Inputs'!X67=\"\",\"\",'HVAC Inputs'!X67)","v":""},{"$f":"IF('HVAC Inputs'!U67=\"\",\"\",'HVAC Inputs'!$R$101)","v":""},null,{"$f":"IF('HVAC Inputs'!U67=\"\",\"\",IF(AND('HVAC Inputs'!V67<$L$22,'HVAC Inputs'!W67>$M$22,'HVAC Inputs'!X67>$N$22),'HVAC Inputs'!U67*'HVAC Inputs'!V67/12000*$M$25,IF(AND('HVAC Inputs'!V67>=$L$22,'HVAC Inputs'!W67>$M$23,'HVAC Inputs'!X67>$N$23),'HVAC Inputs'!U67*'HVAC Inputs'!V67/12000*$M$25,0)))","v":""},{"$f":"IF('HVAC Inputs'!U67=\"\",\"\",H24/F24)","v":""}]
[null,{"$f":"IF('HVAC Inputs'!U68=\"\",\"\",'HVAC Inputs'!U68)","v":""},{"$f":"IF('HVAC Inputs'!V68=\"\",\"\",'HVAC Inputs'!V68)","v":""},{"$f":"IF('HVAC Inputs'!W68=\"\",\"\",'HVAC Inputs'!W68)","v":""},{"$f":"IF('HVAC Inputs'!X68=\"\",\"\",'HVAC Inputs'!X68)","v":""},{"$f":"IF('HVAC Inputs'!U68=\"\",\"\",'HVAC Inputs'!$R$101)","v":""},null,{"$f":"IF('HVAC Inputs'!U68=\"\",\"\",IF(AND('HVAC Inputs'!V68<$L$22,'HVAC Inputs'!W68>$M$22,'HVAC Inputs'!X68>$N$22),'HVAC Inputs'!U68*'HVAC Inputs'!V68/12000*$M$25,IF(AND('HVAC Inputs'!V68>=$L$22,'HVAC Inputs'!W68>$M$23,'HVAC Inputs'!X68>$N$23),'HVAC Inputs'!U68*'HVAC Inputs'!V68/12000*$M$25,0)))","v":""},{"$f":"IF('HVAC Inputs'!U68=\"\",\"\",H25/F25)","v":""},null,"Savings Factor",null,1126,"kWh/ton"]
[null,{"$f":"IF('HVAC Inputs'!U69=\"\",\"\",'HVAC Inputs'!U69)","v":""},{"$f":"IF('HVAC Inputs'!V69=\"\",\"\",'HVAC Inputs'!V69)","v":""},{"$f":"IF('HVAC Inputs'!W69=\"\",\"\",'HVAC Inputs'!W69)","v":""},{"$f":"IF('HVAC Inputs'!X69=\"\",\"\",'HVAC Inputs'!X69)","v":""},{"$f":"IF('HVAC Inputs'!U69=\"\",\"\",'HVAC Inputs'!$R$101)","v":""},null,{"$f":"IF('HVAC Inputs'!U69=\"\",\"\",IF(AND('HVAC Inputs'!V69<$L$22,'HVAC Inputs'!W69>$M$22,'HVAC Inputs'!X69>$N$22),'HVAC Inputs'!U69*'HVAC Inputs'!V69/12000*$M$25,IF(AND('HVAC Inputs'!V69>=$L$22,'HVAC Inputs'!W69>$M$23,'HVAC Inputs'!X69>$N$23),'HVAC Inputs'!U69*'HVAC Inputs'!V69/12000*$M$25,0)))","v":""},{"$f":"IF('HVAC Inputs'!U69=\"\",\"\",H26/F26)","v":""}]
["Totals:",{"$f":"SUM(B23:B26)","v":0},{"$f":"SUMPRODUCT(C23:C26,B23:B26)","v":0},null,null,null,null,{"$f":"SUM(H23:H26)","v":{"$error":"#VALUE!"}},{"$f":"SUM(I23:I26)","v":0}]

{"sheet":"HVAC15-CircPumps","index":33,"n_rows":26,"n_cols":14,"rows_kept":26,"cut":false,"hidden":true,"merged":[[11,8,14,10],[3,1,3,4],[5,1,7,2],[8,1,8,2],[9,1,9,2],[10,1,10,2],[12,1,12,3]]}
[null,"Measure: Circulator Pump"]
[]
[]
[null,"Measure Summary",null,null,null,null,null,null,"Circulator Pump"]
[null,null,null,"Value","Unit",null,null,null,"Measure Code",null,"COM-HVAC-CP"]
[null,"Total Savings",null,0,"MMBtu",null,null,null,"Markets ",null,"Commercial"]
[null,null,null,{"$f":"F25","v":0},"kW",null,null,null,"Program Types ",null,"Lost Opportunity"]
[null,null,null,{"$f":"E25","v":0},"kWh",null,null,null,"Categories ",null,"HVAC"]
[null,"Measure Life",null,20,"Years"]
[null,"CFsp",null,{"$f":"C15*100","v":82},"%"]
[null,"CFwp",null,{"$f":"D15*100","v":5},"%",null,null,null,"Measure Description"]
[null,null,null,null,null,null,null,null,"Installation of a hydronic hot water or service hot water single phase circulator pump with an ECM."]
[null,"Table 2: Coincidence Factors"]
[null,"Measure","CFsp","CFwp"]
[null,"Circulator Pump",0.82,0.05]
[]
[]
[null,"Energy Savings",null,null,null,null,null,"TRM Savings Calculations"]
[null,"Quantity","Pump","Pump","Saved",null,null,"Pump","Pump hp",null,"kW Coefficients",null,"kWh Coefficients"]
[null,"#","Type","hp","kWh","kW",null,"Type","Thresholds",null,"a","b","a","b"]
[null,{"$f":"IF('HVAC Inputs'!I30=\"\",\"\",'HVAC Inputs'!I30)","v":""},{"$f":"IF('HVAC Inputs'!J30=\"\",\"\",'HVAC Inputs'!J30)","v":""},{"$f":"IF('HVAC Inputs'!K30=\"\",\"\",'HVAC Inputs'!K30)","v":""},{"$f":"IF($B21=\"\",\"\",IF(AND($C21=$H$21,$D21<=$J$21),$M$21*$D21+$N$21,IF(AND($C21=$H$21,$D21>$J$21),$N$23,IF(AND($C21=$H$22,$D21<=$J$22),$M$22*$D21+$N$22,$N$24)))*$B21)","v":""},{"$f":"IF($B21=\"\",\"\",IF(AND($C21=$H$21,$D21<=$J$21),$K$21*$D21+$L$21,IF(AND($C21=$H$21,$D21>$J$21),$L$23,IF(AND($C21=$H$22,$D21<=$J$22),$K$22*$D21+$L$22,$L$24)))*$B21)","v":""},null,"Hydronic Heating","Less than",1,0.245,0.02,1325,111]
[null,{"$f":"IF('HVAC Inputs'!I31=\"\",\"\",'HVAC Inputs'!I31)","v":""},{"$f":"IF('HVAC Inputs'!J31=\"\",\"\",'HVAC Inputs'!J31)","v":""},{"$f":"IF('HVAC Inputs'!K31=\"\",\"\",'HVAC Inputs'!K31)","v":""},{"$f":"IF($B22=\"\",\"\",IF(AND($C22=$H$21,$D22<=$J$21),$M$21*$D22+$N$21,IF(AND($C22=$H$21,$D22>$J$21),$N$23,IF(AND($C22=$H$22,$D22<=$J$22),$M$22*$D22+$N$22,$N$24)))*$B22)","v":""},{"$f":"IF($B22=\"\",\"\",IF(AND($C22=$H$21,$D22<=$J$21),$K$21*$D22+$L$21,IF(AND($C22=$H$21,$D22>$J$21),$L$23,IF(AND($C22=$H$22,$D22<=$J$22),$K$22*$D22+$L$22,$L$24)))*$B22)","v":""},null,"Service Hot Water","Less than",1,0.245,0.02,2780,233]
[null,{"$f":"IF('HVAC Inputs'!I32=\"\",\"\",'HVAC Inputs'!I32)","v":""},{"$f":"IF('HVAC Inputs'!J32=\"\",\"\",'HVAC Inputs'!J32)","v":""},{"$f":"IF('HVAC Inputs'!K32=\"\",\"\",'HVAC Inputs'!K32)","v":""},{"$f":"IF($B23=\"\",\"\",IF(AND($C23=$H$21,$D23<=$J$21),$M$21*$D23+$N$21,IF(AND($C23=$H$21,$D23>$J$21),$N$23,IF(AND($C23=$H$22,$D23<=$J$22),$M$22*$D23+$N$22,$N$24)))*$B23)","v":""},{"$f":"IF($B23=\"\",\"\",IF(AND($C23=$H$21,$D23<=$J$21),$K$21*$D23+$L$21,IF(AND($C23=$H$21,$D23>$J$21),$L$23,IF(AND($C23=$H$22,$D23<=$J$22),$K$22*$D23+$L$22,$L$24)))*$B23)","v":""},null,"Hydronic Heating","Greater than",1,0,0.26500000000000001,0,1436]
[null,{"$f":"IF('HVAC Inputs'!I33=\"\",\"\",'HVAC Inputs'!I33)","v":""},{"$f":"IF('HVAC Inputs'!J33=\"\",\"\",'HVAC Inputs'!J33)","v":""},{"$f":"IF('HVAC Inputs'!K33=\"\",\"\",'HVAC Inputs'!K33)","v":""},{"$f":"IF($B24=\"\",\"\",IF(AND($C24=$H$21,$D24<=$J$21),$M$21*$D24+$N$21,IF(AND($C24=$H$21,$D24>$J$21),$N$23,IF(AND($C24=$H$22,$D24<=$J$22),$M$22*$D24+$N$22,$N$24)))*$B24)","v":""},{"$f":"IF($B24=\"\",\"\",IF(AND($C24=$H$21,$D24<=$J$21),$K$21*$D24+$L$21,IF(AND($C24=$H$21,$D24>$J$21),$L$23,IF(AND($C24=$H$22,$D24<=$J$22),$K$22*$D24+$L$22,$L$24)))*$B24)","v":""},null,"Service Hot Water","Greater than",1,0,0.26500000000000001,0,3013]
["Totals:",{"$f":"SUM(B21:B24)","v":0},null,{"$f":"SUMPRODUCT(D21:D24,B21:B24)","v":0},{"$f":"SUM(E21:E24)","v":0},{"$f":"SUM(F21:F24)","v":0}]
[null,null,null,null,null,null,null,"Formaula:","a x hp + b"]

{"sheet":"Motors and Drives Inputs","index":34,"n_rows":78,"n_cols":26,"rows_kept":78,"cut":false,"hidden":false,"merged":[[7,14,7,23],[43,14,43,23],[31,2,33,3],[34,2,34,3],[7,10,7,11],[35,2,35,3],[36,2,36,3],[4,4,8,6],[10,4,10,6],[3,1,3,2],[29,2,29,5],[4,8,4,9],[4,10,4,11],[5,8,5,9],[5,10,5,11],[6,8,6,9],[6,10,6,11],[7,8,7,9],[3,8,3,11]]}
[null,"Measure: Variable Frequency Drives (Inputs and Calculation Sheet)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 2: Coincidence Factors - Summer/Winter Peak"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Measure Name","CFsp","CFwp"]
[null,"Key",null,null,"Measure Description",null,null,null,"Motors & Drives - Variable Frequency Drives",null,null,null,null,null,"Variable Frequency Drive",1,1]
[null,null,"Input Cells",null,"After selecting \"Yes\" on the \"Measure Summary\" tab, please fill out the ORANGE cells to determine the savings associated with this measure that covers the installation of variable speed drives according to the terms and conditions stated on the statewide application and worksheet. The measure covers multiple end use types and building types. The installation of this measure saves energy because the power required to rotate a pump or fan at lower speeds requires less power than when rotated at full speed.",null,null,null,"Measure Code",null,"COM-MND-VFD",null,null,null,"Variable Frequency Drive w/ Motor",1,1]
[null,null,"Calculation Cells",null,null,null,null,null,"Market",null,"Commercial"]
[null,null,"Guidance/ Information Cells",null,null,null,null,null,"Program Type",null,"Retrofit",null,null,null,"Without"]
[null,null,null,null,null,null,null,null,"Category",null,"Motors and Drives",null,null,null,"Table 3: Savings Factors, VFDs without motor replacements"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Building Type","Building Exhaust Fan","Cooling Tower Fan","Chilled Water Pump","Boiler Feed Water Pump","Hot Water Circulating Pump","MAF - Make up Air Fan","Return Fan","Supply Fan","WS Heat",null,"kWh/HP value"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Annual Energy Savings Factors (kWh/HP)",null,null,null,null,null,null,null,null,null,1,{"$f":"IFERROR(VLOOKUP(F17,$O$9:$X$20,MATCH(G17,$O$9:$X$9,0),FALSE),\"\")","v":""}]
[null,null,null,null,"NOTE: For more information on this measure refer to the NH TRM. ",null,null,null,null,null,null,null,null,null,"University / College",3641,449,745,2316,2344,3220,1067,1023,3061,2,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Elem/High School",3563,365,628,1933,1957,3402,879,840,2561,3,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Multi-Family",3202,889,1374,2340,2400,3082,1374,1319,3713,4,""]
[null,null,"Table 1: Calculating Primary Energy Impact ",null,null,null,null,null,null,null,null,null,null,null,"Hotel/Motel",3151,809,1239,2195,2239,3368,1334,1290,3433,5,""]
[null,null,null,"Inputs",null,null,null,null,null,"Savings",null,null,null,null,"Health",3375,1705,2427,2349,2406,3002,1577,1487,3670,6,""]
[null,null,null,"Quantity","HP","Building Type","Equipment Type","Motor Replacement?",null,"kWwp","kWsp","kWh",null,null,"Warehouse",3310,455,816,2002,2087,3229,1253,1205,2818,7,""]
[null,null,1,null,null,null,null,null,null,{"$f":"IFERROR(IF(H17=\"\",\"\",IF(H17=$O$7,E17*Z33*D17,E17*Z69*D17)),\"\")","v":""},{"$f":"IFERROR(IF(H17=\"\",\"\",IF(H17=$O$7,E17*Z22*D17,E17*Z58*D17)),\"\")","v":""},{"$f":"IFERROR(IF(H17=\"\",\"\",IF(H17=$O$7,E17*Z10*D17,E17*Z46*D17)),\"\")","v":""},null,null,"Restaurant",3440,993,1566,1977,2047,2628,1425,1363,3542,8,""]
[null,null,2,null,null,null,null,null,null,{"$f":"IFERROR(IF(H18=\"\",\"\",IF(H18=$O$7,E18*Z34*D18,E18*Z70*D18)),\"\")","v":""},{"$f":"IFERROR(IF(H18=\"\",\"\",IF(H18=$O$7,E18*Z23*D18,E18*Z59*D18)),\"\")","v":""},{"$f":"IFERROR(IF(H18=\"\",\"\",IF(H18=$O$7,E18*Z11*D18,E18*Z47*D18)),\"\")","v":""},null,null,"Retail",3092,633,1049,1949,2000,2392,1206,1146,2998,9,""]
[null,null,3,null,null,null,null,null,null,{"$f":"IFERROR(IF(H19=\"\",\"\",IF(H19=$O$7,E19*Z35*D19,E19*Z71*D19)),\"\")","v":""},{"$f":"IFERROR(IF(H19=\"\",\"\",IF(H19=$O$7,E19*Z24*D19,E19*Z60*D19)),\"\")","v":""},{"$f":"IFERROR(IF(H19=\"\",\"\",IF(H19=$O$7,E19*Z12*D19,E19*Z48*D19)),\"\")","v":""},null,null,"Grocery",3126,918,1632,1653,1681,2230,1408,1297,3285,10,""]
[null,null,4,null,null,null,null,null,null,{"$f":"IFERROR(IF(H20=\"\",\"\",IF(H20=$O$7,E20*Z36*D20,E20*Z72*D20)),\"\")","v":""},"","",null,null,"Offices",3332,950,1370,1866,1896,3346,1135,1076,3235]
[null,null,5,null,null,null,null,null,null,"","","",null,null,"Summer Demand Savings Factors (kW/HPsp)",null,null,null,null,null,null,null,null,null,null,"kW/HPsp value"]
[null,null,6,null,null,null,null,null,null,"","","",null,null,"University / College",0.109,-2.3E-2,0.17399999999999999,0.45700000000000002,9.0999999999999998E-2,0.109,0.28699999999999998,0.27400000000000002,0.218,1,{"$f":"IFERROR(VLOOKUP(F17,$O$22:$X$31,MATCH(G17,$O$9:$X$9,0),FALSE),\"\")","v":""}]
[null,null,7,null,null,null,null,null,null,"","","",null,null,"Elem/High School",0.377,-2.3E-2,0.17399999999999999,0.45700000000000002,9.0999999999999998E-2,0.109,0.28699999999999998,0.27400000000000002,0.218,2,""]
[null,null,8,null,null,null,null,null,null,"","","",null,null,"Multi-Family",0.109,-2.3E-2,0.17399999999999999,0.45700000000000002,9.0999999999999998E-2,0.109,0.28699999999999998,0.27400000000000002,0.218,3,""]
[null,null,9,null,null,null,null,null,null,"","","",null,null,"Hotel/Motel",0.109,-2.3E-2,0.17399999999999999,0.45700000000000002,9.0999999999999998E-2,0.109,0.28699999999999998,0.27400000000000002,0.218,4,""]
[null,null,10,null,null,null,null,null,null,"","","",null,null,"Health",0.109,-2.3E-2,0.17399999999999999,0.45700000000000002,9.0999999999999998E-2,0.109,0.28699999999999998,0.27400000000000002,0.218,5,""]
[null,null,null,null,null,null,null,null,"Totals: ",{"$f":"SUM(J17:J26)","v":0},{"$f":"SUM(K17:K26)","v":0},{"$f":"SUM(L17:L26)","v":0},null,null,"Warehouse",0.109,-2.3E-2,0.17399999999999999,0.45700000000000002,9.0999999999999998E-2,0.26100000000000001,0.28699999999999998,0.27400000000000002,0.218,6,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Restaurant",0.26100000000000001,-2.3E-2,0.17399999999999999,0.45700000000000002,9.0999999999999998E-2,0.109,0.28699999999999998,0.27400000000000002,0.218,7,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Retail",0.109,-2.3E-2,0.17399999999999999,0.45700000000000002,9.0999999999999998E-2,0.109,0.28699999999999998,0.27400000000000002,0.218,8,""]
[null,null,"Measure Summary",null,null,null,null,null,null,null,null,null,null,null,"Grocery",0.26100000000000001,-2.3E-2,0.17399999999999999,0.45700000000000002,9.0999999999999998E-2,0.109,0.28699999999999998,0.27400000000000002,0.218,9,""]
[null,null,null,null,"Value","Unit",null,null,null,null,null,null,null,null,"Offices",0.109,-2.3E-2,0.17399999999999999,0.45700000000000002,9.0999999999999998E-2,0.109,0.28699999999999998,0.27400000000000002,0.218,10,""]
[null,null,"Total Savings",null,null,"kW",null,null,null,null,null,null,null,null,"Winter Demand Savings Factors (kW/HPwp)",null,null,null,null,null,null,null,null,null,null,"kW/HPwp value"]
[null,null,null,null,{"$f":"L27","v":0},"kWh",null,null,null,null,null,null,null,null,"University / College",0.377,-6.0000000000000001E-3,0.184,0.45700000000000002,0.21,0.109,0.26,0.252,0.28199999999999997,1,{"$f":"IFERROR(VLOOKUP(F17,$O$33:$X$42,MATCH(G17,$O$9:$X$9,0),FALSE),\"\")","v":""}]
[null,null,null,null,0,"MMBtu",null,null,null,null,null,null,null,null,"Elem/High School",0.45700000000000002,-6.0000000000000001E-3,0.184,0.45700000000000002,0.21,0.109,0.26,0.252,0.28199999999999997,2,{"$f":"IFERROR(VLOOKUP(F18,$O$33:$X$42,MATCH(G18,$O$9:$X$9,0),FALSE),\"\")","v":""}]
[null,null,"Measure Life",null,15,"Years",null,null,null,null,null,null,null,null,"Multi-Family",0.109,-6.0000000000000001E-3,0.184,0.35499999999999998,0.21,0.109,0.26,0.252,0.28199999999999997,3,""]
[null,null,"CFsp",null,{"$f":"P4*100","v":100},"%",null,null,null,null,null,null,null,null,"Hotel/Motel",0.109,-6.0000000000000001E-3,0.184,0.41799999999999998,0.21,0.109,0.26,0.252,0.28199999999999997,4,""]
[null,null,"CFwp",null,{"$f":"P5*100","v":100},"%",null,null,null,null,null,null,null,null,"Health",0.377,-6.0000000000000001E-3,0.184,0.27500000000000002,0.21,0.109,0.26,0.252,0.28199999999999997,5,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Warehouse",0.377,-6.0000000000000001E-3,0.184,0.17799999999999999,0.21,0.26100000000000001,0.26,0.252,0.28199999999999997,6,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Restaurant",0.109,-6.0000000000000001E-3,0.184,0.35499999999999998,0.21,0.109,0.26,0.252,0.28199999999999997,7,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Retail",0.109,-6.0000000000000001E-3,0.184,0.27500000000000002,0.21,0.109,0.26,0.252,0.28199999999999997,8,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Grocery",0.45700000000000002,-6.0000000000000001E-3,0.184,0.41799999999999998,0.21,0.109,0.26,0.252,0.28199999999999997,9,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Offices",0.45700000000000002,-6.0000000000000001E-3,0.184,0.41799999999999998,0.21,0.109,0.26,0.252,0.28199999999999997,10,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"With"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 4: Savings Factors, VFDs with motor replacements"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Building Type","Building Exhaust Fan","Cooling Tower Fan","Chilled Water Pump","Boiler Feed Water Pump","Hot Water Circulating Pump","MAF - Make up Air Fan","Return Fan","Supply Fan",null,null,"kWh/HP value"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Annual Energy Savings Factors (kWh/HP)",null,null,null,null,null,null,null,null,null,1,{"$f":"IFERROR(VLOOKUP(F17,$O$45:$W$56,MATCH(G17,$O$45:$W$45,0),FALSE),\"\")","v":""}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"University / College",3802,486,780,2415,2442,3381,1143,1100,null,2,{"$f":"IFERROR(VLOOKUP(F18,$O$45:$W$56,MATCH(G18,$O$45:$W$45,0),FALSE),\"\")","v":""}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Elem/High School",3721,396,657,2015,2040,3561,941,903,null,3,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Multi-Family",3368,954,1435,2443,2504,3248,1466,1412,null,4,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hotel/Motel",3317,866,1294,2291,2335,3534,1425,1381,null,5,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Health",3541,1815,2535,2453,2510,3168,1676,1586,null,6,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Warehouse",3476,496,853,2098,2183,3396,1342,1294,null,7,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Restaurant",3606,1066,1636,2067,2138,2794,1519,1457,null,8,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Retail",3258,685,1097,2036,2087,2558,1288,1229,null,9,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Grocery",3292,1001,1710,1724,1753,2396,1498,1386,null,10,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Offices",3498,1014,1432,1947,1977,3512,1210,1151]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Summer Demand Savings Factors (kW/HPsp)",null,null,null,null,null,null,null,null,null,null,"kW/HPsp value"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"University / College",0.25700000000000001,-4.0000000000000001E-3,0.46500000000000002,0.95199999999999996,0.19,0.25700000000000001,0.67900000000000005,0.70599999999999996,null,1,{"$f":"IFERROR(VLOOKUP(F17,$O$58:$W$67,MATCH(G17,$O$45:$W$45,0),FALSE),\"\")","v":""}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Elem/High School",1.1870000000000001,-6.0000000000000001E-3,0.69699999999999995,1.4279999999999999,0.28599999999999998,0.38500000000000001,1.0189999999999999,1.0580000000000001,null,2,{"$f":"IFERROR(VLOOKUP(F18,$O$58:$W$67,MATCH(G18,$O$45:$W$45,0),FALSE),\"\")","v":""}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Multi-Family",0.38500000000000001,-6.0000000000000001E-3,0.69699999999999995,1.4279999999999999,0.28599999999999998,0.38500000000000001,1.0189999999999999,1.0580000000000001,null,3,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hotel/Motel",0.25700000000000001,-4.0000000000000001E-3,0.46500000000000002,0.95199999999999996,0.19,0.25700000000000001,0.67900000000000005,0.70599999999999996,null,4,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Health",0.128,-2E-3,0.23200000000000001,0.47599999999999998,9.5000000000000001E-2,0.128,0.34,0.35299999999999998,null,5,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Warehouse",0.77,-1.2E-2,1.3939999999999999,2.855,0.57099999999999995,1.677,2.0379999999999998,2.117,null,6,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Restaurant",0.83899999999999997,-6.0000000000000001E-3,0.69699999999999995,1.4279999999999999,0.28599999999999998,0.38500000000000001,1.0189999999999999,1.0580000000000001,null,7,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Retail",0.51400000000000001,-8.0000000000000002E-3,0.93,1.9039999999999999,0.38100000000000001,0.51400000000000001,1.3580000000000001,1.411,null,8,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Grocery",0.28000000000000003,-2E-3,0.23200000000000001,0.47599999999999998,9.5000000000000001E-2,0.128,0.34,0.35299999999999998,null,9,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Offices",0.25700000000000001,-4.0000000000000001E-3,0.46500000000000002,0.95199999999999996,0.19,0.25700000000000001,0.67900000000000005,0.70599999999999996,null,10,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Winter Demand Savings Factors (kW/HPwp)",null,null,null,null,null,null,null,null,null,null,"kW/HPwp value"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"University / College",0.79100000000000004,-1E-3,0.38400000000000001,0.95199999999999996,0.437,0.25700000000000001,0.56299999999999994,0.54400000000000004,null,1,{"$f":"IFERROR(VLOOKUP(F17,$O$69:$W$78,MATCH(G17,$O$45:$W$45,0),FALSE),\"\")","v":""}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Elem/High School",1.4279999999999999,-2E-3,0.57499999999999996,1.4279999999999999,0.65500000000000003,0.38500000000000001,0.84399999999999997,0.81599999999999995,null,2,{"$f":"IFERROR(VLOOKUP(F18,$O$69:$W$78,MATCH(G18,$O$45:$W$45,0),FALSE),\"\")","v":""}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Multi-Family",0.38500000000000001,-2E-3,0.57499999999999996,1.123,0.66100000000000003,0.38500000000000001,0.84399999999999997,0.81599999999999995,null,3,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hotel/Motel",0.25700000000000001,-1E-3,0.38400000000000001,0.874,0.438,0.25700000000000001,0.56299999999999994,0.54400000000000004,null,4,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Health",0.39600000000000002,-1E-3,0.192,0.29399999999999998,0.223,0.128,0.28100000000000003,0.27200000000000002,null,5,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Warehouse",2.3740000000000001,-3.0000000000000001E-3,1.151,1.181,1.3839999999999999,1.677,1.6879999999999999,1.6319999999999999,null,6,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Restaurant",0.38500000000000001,-2E-3,0.57499999999999996,1.123,0.66100000000000003,0.38500000000000001,0.84399999999999997,0.81599999999999995,null,7,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Retail",0.51400000000000001,-2E-3,0.76700000000000002,1.1779999999999999,0.89300000000000002,0.51400000000000001,1.125,1.0880000000000001,null,8,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Grocery",0.47599999999999998,-1E-3,0.192,0.437,0.219,0.128,0.28100000000000003,0.27200000000000002,null,9,""]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Offices",0.95199999999999996,-1E-3,0.38400000000000001,0.874,0.438,0.25700000000000001,0.56299999999999994,0.54400000000000004,null,10,""]

{"sheet":"Appliances Inputs","index":35,"n_rows":43,"n_cols":25,"rows_kept":43,"cut":false,"hidden":false,"merged":[[2,6,2,8],[14,7,14,9],[13,13,13,15],[40,1,40,2],[41,1,41,2],[4,13,9,17],[4,1,10,4],[3,7,3,8],[4,7,4,8],[5,7,5,8],[42,1,42,2],[28,13,28,16],[30,13,32,14],[33,13,33,14],[34,13,34,14],[35,13,35,14],[22,21,22,22],[23,21,23,22],[24,21,24,22],[35,1,35,4],[37,1,39,2]]}
[null,"Measure: Air Purifiers (Input and Calculation Sheet)",null,null,null,null,null,null,null,null,null,null,null,"Measure: Dehumidifiers  (Input and Calculation Sheet)"]
[]
[null,null,null,null,null,null,"Key"]
[null,"Air Purifier Measure Description",null,null,null,null,null,"Input Cells",null,null,null,null,null,"Dehumidifier Measure Description"]
[null,"After selecting \"Yes\" on the \"Measure Summary\" tab, fill in the ORANGE cells to determine the energy savings for the installation of a room air purifiers with a performance exceeding the minimum qualfying efficiency established by ENERGY STAR.",null,null,null,null,null,"Guidance/ Information Cells",null,null,null,null,null,"After selecting \"Yes\" on the \"Measure Summary\" tab, fill in the ORANGE cells to determine the energy savings for the installation of a portable dehumidifier with an integrated energy factor exceeding the minimum qualfying efficiency established by ENERGY STAR."]
[null,null,null,null,null,null,null,"Calculation Cells"]
[]
[null,null,null,null,null,null,"Air Purifier",null,null,null,null,null,null,null,null,null,null,null,null,"Dehumidifier"]
[null,null,null,null,null,null,"Measure Code",null,"COM-APP-RAP",null,null,null,null,null,null,null,null,null,null,"Measure Code",null,"COM-APP-DEH"]
[null,null,null,null,null,null,"Markets ",null,"Commercial",null,null,null,null,null,null,null,null,null,null,"Markets ",null,"Commercial"]
[null,null,null,null,null,null,"Program Types ",null,"Lost Opportunity",null,null,null,null,null,null,null,null,null,null,"Program Types ",null,"Lost Opportunity"]
[null,null,null,null,null,null,"Categories ",null,"Appliances",null,null,null,null,null,null,null,null,null,null,"Categories ",null,"Appliances"]
[null,"CADR = Clean Air Delivery Rate",null,null,null,null,"Measure Life",null,3,"years",null,null,null,null,null,null,null,null,null,"Measure Life",null,12,"years"]
[null,"CADR/watt from TRM",null,null,null,null,null,null,null,null,null,null,null,"Dehumidifier Coincidence Factors"]
[null,"ENERGY STAR threshold varies by CADR",null,null,null,null,null,"Air Purifiers Coincidence Factors",null,null,null,null,null,"Measure","CFsp","CFwp"]
[null,"3.0 CADR/watt is greater than threshold for all sizes.",null,null,null,null,null,"Measure","CFsp","CFwp",null,null,null,"Dehumidifiers",0.82,0.17]
[null,"TRM provides baseline partial on watts, but not proposed.",null,null,null,null,null,"Air Purifiers",1,1,null,null,null,null,null,null,null,null,null,null,null,"Load",1520,"litres/year (TRM - Navigant Consulting, 2018. RES1 Demand Impact Model Update.)"]
[null,"Proposed partial on watts is from ENERGY STAR",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours",2851,"deemed hours/year"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Energy Savings"]
[null,"Energy Savings",null,null,null,null,null,null,null,null,null,null,null,"Quantity","Pints per","IEF",null,"Saved",null,null,null,"Integrated Energy Factor (Litres/kWh)"]
[null,"Bldg","Quantity","CADR","CADR/watt",null,"Partial On Watts",null,"Annual","Saved",null,null,null,"#","Unit","Base","Prop","kWh","kW",null,null,"Capacity Range",null,"2019 Fed","ENERGY"]
[null,"Type","#","cfm","Base","Prop","Base","Prop","Hours","kWh","kW",null,null,null,null,{"$f":"IF(N22=\"\",\"\",IF(O22<=$W$23,$X$23,IF(O22<=$W$24,$X$24,$X$25)))","v":""},{"$f":"IF(N22=\"\",\"\",IF(O22<=$W$23,$Y$23,IF(O22<=$W$24,$Y$24,$Y$25)))","v":""},{"$f":"IF(N22=\"\",\"\",(1/P22-1/Q22)*$W$17*N22)","v":""},{"$f":"IF(N22=\"\",\"\",R22/$W$18)","v":""},null,null,"Pints",null,"Standard","STAR"]
[null,null,null,null,{"$f":"IF($C23=\"\",\"\",$F$32)","v":""},{"$f":"IF($C23=\"\",\"\",$F$33)","v":""},{"$f":"IF($C23=\"\",\"\",$G$32)","v":""},{"$f":"IF($C23=\"\",\"\",$G$33)","v":""},{"$f":"IF(C23=\"\",\"\",LOOKUP(B23,$B$32:$B$34,$C$32:$C$34))","v":""},{"$f":"IF(C23=\"\",\"\",(1/E23-1/F23)*D23*C23*I23/1000+((8760-I23)*(G23-H23)/1000))","v":""},{"$f":"IF(C23=\"\",\"\",J23/I23)","v":""},null,null,null,null,{"$f":"IF(N23=\"\",\"\",IF(O23<=$W$23,$X$23,IF(O23<=$W$24,$X$24,$X$25)))","v":""},{"$f":"IF(N23=\"\",\"\",IF(O23<=$W$23,$Y$23,IF(O23<=$W$24,$Y$24,$Y$25)))","v":""},{"$f":"IF(N23=\"\",\"\",(1/P23-1/Q23)*$W$17*N23)","v":""},{"$f":"IF(N23=\"\",\"\",R23/$W$18)","v":""},null,null,"0-25",null,1.3,1.57]
[null,null,null,null,{"$f":"IF($C24=\"\",\"\",$F$32)","v":""},{"$f":"IF($C24=\"\",\"\",$F$33)","v":""},{"$f":"IF($C24=\"\",\"\",$G$32)","v":""},{"$f":"IF($C24=\"\",\"\",$G$33)","v":""},{"$f":"IF(C24=\"\",\"\",LOOKUP(B24,$B$32:$B$34,$C$32:$C$34))","v":""},{"$f":"IF(C24=\"\",\"\",(1/E24-1/F24)*D24*C24*I24/1000+((8760-I24)*(G24-H24)/1000))","v":""},{"$f":"IF(C24=\"\",\"\",J24/I24)","v":""},null,null,null,null,{"$f":"IF(N24=\"\",\"\",IF(O24<=$W$23,$X$23,IF(O24<=$W$24,$X$24,$X$25)))","v":""},{"$f":"IF(N24=\"\",\"\",IF(O24<=$W$23,$Y$23,IF(O24<=$W$24,$Y$24,$Y$25)))","v":""},{"$f":"IF(N24=\"\",\"\",(1/P24-1/Q24)*$W$17*N24)","v":""},{"$f":"IF(N24=\"\",\"\",R24/$W$18)","v":""},null,null,"26-50",null,1.6,1.8]
[null,null,null,null,{"$f":"IF($C25=\"\",\"\",$F$32)","v":""},{"$f":"IF($C25=\"\",\"\",$F$33)","v":""},{"$f":"IF($C25=\"\",\"\",$G$32)","v":""},{"$f":"IF($C25=\"\",\"\",$G$33)","v":""},{"$f":"IF(C25=\"\",\"\",LOOKUP(B25,$B$32:$B$34,$C$32:$C$34))","v":""},{"$f":"IF(C25=\"\",\"\",(1/E25-1/F25)*D25*C25*I25/1000+((8760-I25)*(G25-H25)/1000))","v":""},{"$f":"IF(C25=\"\",\"\",J25/I25)","v":""},null,null,null,null,{"$f":"IF(N25=\"\",\"\",IF(O25<=$W$23,$X$23,IF(O25<=$W$24,$X$24,$X$25)))","v":""},{"$f":"IF(N25=\"\",\"\",IF(O25<=$W$23,$Y$23,IF(O25<=$W$24,$Y$24,$Y$25)))","v":""},{"$f":"IF(N25=\"\",\"\",(1/P25-1/Q25)*$W$17*N25)","v":""},{"$f":"IF(N25=\"\",\"\",R25/$W$18)","v":""},null,null,"50-1,000",null,2.8,3.3]
[null,null,null,null,{"$f":"IF($C26=\"\",\"\",$F$32)","v":""},{"$f":"IF($C26=\"\",\"\",$F$33)","v":""},{"$f":"IF($C26=\"\",\"\",$G$32)","v":""},{"$f":"IF($C26=\"\",\"\",$G$33)","v":""},{"$f":"IF(C26=\"\",\"\",LOOKUP(B26,$B$32:$B$34,$C$32:$C$34))","v":""},{"$f":"IF(C26=\"\",\"\",(1/E26-1/F26)*D26*C26*I26/1000+((8760-I26)*(G26-H26)/1000))","v":""},{"$f":"IF(C26=\"\",\"\",J26/I26)","v":""},null,"Totals: ",{"$f":"SUM(N22:N25)","v":0},{"$f":"SUMPRODUCT(O22:O25,N22:N25)","v":0},{"$f":"(IF($N22=0,0,(1/P22*$N22))+IF($N23=0,0,(1/P23*$N23))+IF($N24=0,0,(1/P24*$N24))+IF($N25=0,0,(1/P25*$N25)))*$W$17","v":0},{"$f":"(IF($N22=0,0,(1/Q22*$N22))+IF($N23=0,0,(1/Q23*$N23))+IF($N24=0,0,(1/Q24*$N24))+IF($N25=0,0,(1/Q25*$N25)))*$W$17","v":0},{"$f":"SUM(R22:R25)","v":0},{"$f":"SUM(S22:S25)","v":0}]
[null,"Totals:",{"$f":"SUM(C23:C26)","v":0},{"$f":"SUMPRODUCT(D23:D26,C23:C26)","v":0},{"$f":"(IF($C23=0,0,(1/E23*$C23*$D23*$I23))+IF($C24=0,0,(1/E24*$C24*$D24*$I24))+IF($C25=0,0,(1/E25*$C25*$D25*$I25))+IF($C26=0,0,(1/E26*$C26*$D26*$I26)))/1000","v":0},{"$f":"(IF($C23=0,0,(1/F23*$C23*$D23*$I23))+IF($C24=0,0,(1/F24*$C24*$D24*$I24))+IF($C25=0,0,(1/F25*$C25*$D25*$I25))+IF($C26=0,0,(1/F26*$C26*$D26*$I26)))/1000","v":0},{"$f":"(IF($C23=0,0,($C23*G23*(8760-$I23)))+IF($C24=0,0,(G24*(8760-$I24)))+IF($C25=0,0,(G25*(1-$I25)))+IF($C26=0,0,(G26*(1-$I26))))/1000","v":0},{"$f":"(IF($C23=0,0,($C23*H23*(8760-$I23)))+IF($C24=0,0,(H24*(8760-$I24)))+IF($C25=0,0,(H25*(1-$I25)))+IF($C26=0,0,(H26*(1-$I26))))/1000","v":0},null,{"$f":"SUM(J23:J26)","v":0},{"$f":"SUM(K23:K26)","v":0}]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Dehumidifier Measure Summary"]
[null,"TRM Run Hours",null,null,"Model","CADR/","Partial",null,null,null,null,null,null,null,null,"Value","Unit"]
[null,"Building","Hrs",null,"Case","watt","On Watts",null,null,null,null,null,null,"Total Savings",null,{"$f":"S26","v":0},"kW"]
[null,"Education",2967,null,"Base:",2,2,null,null,null,null,null,null,null,null,{"$f":"R26","v":0},"kWh"]
[null,"Retail",4939,null,"Proposed:",3,1,null,null,null,null,null,null,null,null,0,"MMBtu"]
[null,"Small Office",3748,null,null,null,null,null,null,null,null,null,null,"Measure Life",null,12,"Years"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"CFsp",null,{"$f":"O16*100","v":82},"%"]
[null,"Air Purifier Measure Summary",null,null,null,null,null,null,null,null,null,null,null,"CFwp",null,{"$f":"P16*100","v":17},"%"]
[null,null,null,"Value","Unit"]
[null,"Total Savings",null,{"$f":"K27","v":0},"kW"]
[null,null,null,{"$f":"J27","v":0},"kWh"]
[null,null,null,0,"MMBtu"]
[null,"Measure Life",null,3,"Years"]
[null,"CFsp",null,{"$f":"I17*100","v":100},"%"]
[null,"CFwp",null,{"$f":"J17*100","v":100},"%"]