## Instructions
NHSaves Transformer Replacement Calculator
v1.2 6/18/2026
Calculator Background Info:
The term "low-voltage dry-type distribution transformer" means a distribution transformer that:
(A) has an input voltage of 600 volts or less;
(B) is air-cooled; and
(C) does not use oil as a coolant.
The NEMA TP-1 standard was first released in 1996, but was updated in 2002. The Energy Policy Act of 2005 mandated that all low-voltage dry-type transformers manufactured after January 1, 2007 must meet or exceed the NEMA TP-1-2002 standard efficiency levels (https://www1.eere.energy.gov/femp/pdfs/epact_2005.pdf).
In summary, all manufactured after January 1, 2007 are TP-1 compliant. Models between 2002 to 2007 may or may not be TP-1 compliant. Earlier models are very unlikely to be TP-1 compliant.
Calculator Use & Guidance:
- Applicable only to installation of new, replacement low-voltage dry-type distribution transformers under the NHSaves C&I Retrofit program in NH replacing existing pre-TP1 and TP1 transformers.
- Calculator is only applicable to transformer replacement sizes 15 to 500 kVA.
- Only equally sized transformer replacements (same kVA rating as existing transformer being replaced) should be used in this calculator.
- Single phase transformers and specialty transformers are not eligible to claim incentives using this calculator.
-- To apply for transformer incentives that are not eligible to use this calculator, a custom savings calculation is required.
- New replacement transformer must meet or exceed the US Department of Energy (DOE) 2016 minimum efficiency standard.
- A pre‑TP1 transformer refers to a distribution transformer manufactured before the NEMA TP1 energy efficiency standard was introduced - see background info above for details.
- If the age or TP-1 status of the existing unit cannot be determined, TP-1 compliance will be assumed by default.
Project Submission Instructions:
- In addition to this calculator, provide your NHSaves electric utility with a completed NHSaves custom retrofit project application and specification sheets for all proposed transformers. Submitted cut sheets must detail kVA ratings, efficiency data, and no‑load loss ratings. The “EfficiencyTables&NLL Links” tab provides access to specification resources from several common manufacturers.
- Photo(s) of each existing transformer are also required with project submission. Nameplates must be clearly legible and show the existing make, model, serial number, and electrical ratings.
Calculator Instructions:
STEP 1— Project Data tab.
Complete general project information in blue cells on the Project Data tab. Your utility will provide the NHSaves project number.
STEP 2—ECM Data tab.
Complete the inventory of existing transformers on the Energy Conservation Measure (ECM) Data tab by listing the inventory of existing transformers and the related parameters of this equipment as shown in the sections highlighted in blue. - Only include transformers sizes from 15 to 500 kVA - Only include replacement of existing pre-TP1/ pre-2000 and TP1 transformers - This calculator will not provide the energy savings for single phase transformers nor specialty transformers. Please do not include these in the calculator. -- Please use a custom savings calculation for other transformer applications to determine energy saved upon replacement.
STEP 3—Efficiency Tables tab
The EfficiencyTables&NLL Links tab provides information about the how the savings are dervied using baseline and proposed transformer parameters. Links to NLL information from common manufacturers is also provided.
STEP 4—Pre-Install Photos
Provide the electric utility with photos of the existing transformers. Photo(s) of each existing transformer are required with the project submission. Nameplates must be clearly legible and show the existing make, model, serial number, and electrical ratings.
STEP 5—Savings Summary tab
On the Summary tab, review project costs and view the estimated project savings. Submit the new transformer cut sheet(s) (highlighting the KVA and no load loss (Watts) information), existing transformer photo(s), a completed NHSaves retrofit custom project application, and this savings calculator to the NHSaves electric utility as noted in the Project Information section of the Project Data tab. All energy savings cacluations are required to be reviewed by the appropriate NHSaves electric utility prior to the customer receipt of an incentive offer.
STEP 6—Minimum Requirements Data (MRD) tab(s)
The Minimum Requirements Document (MRD) tab provides the verification information the site will need to provide to support the project energy savings projected. The project site should be reviewed for this information prior to incentive receipt.

## Project Data
NHSaves Transformer Replacement Calculator
v1.2 6/18/2026
Cell Color Key
Required Input
Table Header | Project Data
Project Information
Project Name:
Electric Utility:
Project Number:
Facility Information
Facility Name:
Electric Account Number:
Street Address:
City:
Zip Code:
State:
Customer Information
Company Name:
Contact Person:
Phone Number:
Email Address:
Vendor Information
Company Name:
Street Address:
City:
Zip Code:
State:
Contact Person:
Phone Number:
Email Address:

## ECM Data
NHSaves Transformer Replacement Calculator
v1.2 6/18/2026
Cell Color Key
Required Input
Calculated Result
| Table Header |  | Energy Conservation Measure (ECM) Data
| Transformer Identification |  |  | Quantity | Existing Transformer |  | Proposed Transformer |  |  | Energy | Peak Demand Reduction
Item # | Transformer Tag Numbers | Building Name | Location or Room ID No. |  | Rated kVA | Compliance Category | Manufacturer | Model No. | No Load Loss (Watts) | Annual Savings (kWh) | Summer (kW) | Winter (kW)
Example | T-001, T-003 | Murphy Bldg | 14th Fl Elec Rm | 2 | 30 | Pre-TP1 | REX | BA30H-M/Z3 | 79 | 6561 | 0.75 | 0.75
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
|  |  | Project Total Quantity: | 0 |  |  |  |  | Project Total Savings: | 0 | 0 | 0
Note on G11: Guidance: Replacement transformer must be the same Rated kVA as the existing transformer.
Note on K11: Guidance: No load losses should be entered by the vendor per the transformer cutsheet. No load losses can differ based on manufacturer and can also be dependent on whether the tranfsormer has an aluminum or copper core.
Note on G13: Guidance: Replacement transformer must be the same Rated kVA as the existing transformer.
Note on K13: Guidance: No load losses should be entered by the vendor per the transformer cutsheet. No load losses can differ based on manufacturer and can also be dependent on whether the tranfsormer has an aluminum or copper core.

## EfficiencyTables&NLL Links
Efficiency Tables & NLL Links
Pre-TP1 Table |  | TP-1 Table
Size (kVA) | Pre-TP1 NLL (Watts) | Size (kVA) | TP-1 Eff (%) | DOE 2016 Eff (%) | Annual Savings (kWh) | Demand Reduction (kW)
15 | 297.32 | 15 | 97 | 97.89 | 431.0656 | 0.049208
30 | 453.489 | 30 | 97.5 | 98.23 | 701.0799 | 0.080032
45 | 653.704 | 45 | 97.7 | 98.4 | 1004.5997 | 0.11468
75 | 856.923 | 75 | 98 | 98.6 | 1427.847 | 0.163
112.5 | 1164.255 | 112.5 | 98.2 | 98.74 | 1920.9401 | 0.21929
150 | 1510.628 | 150 | 98.3 | 98.83 | 2508.9787 | 0.28641
225 | 1818.96 | 225 | 98.5 | 98.94 | 3114.578 | 0.35555
300 | 2439.629 | 300 | 98.6 | 99.02 | 3956.7887 | 0.45169
500 | 3512.785 | 500 | 98.7 | 99.14 | 6893.3251 | 0.78691
NLL Data for Transformer Manufacturers
ABB Low Voltage Dry Type Transformers
Eaton Low-Voltage Dry-Type Distribution Transformers General Purpose
Hammond Power Solutions, Sentinel G
Siemens Series H
Square D EX

## Pre-Install Photos
Pre-Installation / Existing Transformer Photos
Instructions to add photos of existing transformer nameplate(s): |  | 0 | 0 | 0
Please upload photos of the transformer nameplate(s) and serial numbers |  | Click Here | Click Here | Click Here
1. Select a blue box to the right.
2. Click on the "Insert" menu at the top of the -----> left of the menu in the Excel workbook ribbon.
3. Under the "Text" group click on "Object." -----> |  | Click Here (if needed/multiple) | Click Here (if needed/multiple) | Click Here (if needed/multiple)
4. Select "Create From File" tab.
5. Select "Browse" button to find photo file location & select photo. |  | 0 | 0 | 0
6. Check the box to "Display as icon" | ------>
7. Click on "OK" so photo icon shows on spreadsheet. |  | 0 | 0 | 0
8. Enter description/location below photo. |  | Click Here | Click Here | Click Here
|  | Click Here (if needed) | Click Here (if needed) | Click Here (if needed)
|  | 0 | 0 | 0
|  | 0 | 0 | 0
|  | Click Here | Click Here | Click Here
|  | Click Here (if needed) | Click Here (if needed) | Click Here (if needed)
|  | 0 | 0 | 0
|  | 0 | 0 | 0
|  | Click Here | Click Here | Click Here
|  | Click Here (if needed) | Click Here (if needed) | Click Here (if needed)
|  | 0 | 0 | 0
|  | 0 | 0 | 0
|  | Click Here | Click Here | Click Here
|  | Click Here (if needed) | Click Here (if needed) | Click Here (if needed)
|  | 0 | 0 | 0
|  | 0 | 0 | 0
|  | Click Here | Click Here | Click Here
|  | Click Here (if needed) | Click Here (if needed) | Click Here (if needed)
|  | 0 | 0 | 0
|  | 0 | 0
|  | Click Here | Click Here
|  | Click Here (if needed) | Click Here (if needed)
|  | 0 | 0

## Savings Summary
NHSaves Transformer Replacement Calculator
v1.2 6/18/2026
Overall Project Savings Summary
Project cost:
Replaced Transformer Quantity: | 0
Energy Savings (kWh) | 0
Summer Peak (kW) | 0
Winter Peak (kW) | 0
Measure Life (Years) | 30

## MRD
Customer |  | 0
Facility |  | 0
Document: |  | Transformer Replacement Minimum Requirement Document (MRD)
This document specifies the agreed upon minimum equipment specifications and operational requirements of the proposed system. These requirements shall address the criteria necessary to be met to achieve the demand and energy savings estimated in the engineering analysis for this project. (Use additional sheets if necessary.)
Yes/No checkboxes are intended to be used during post-installation inspections to record site findings.
EQUIPMENT DESCRIPTION: Provide a list of equipment or materials installed as part of this project. Include mfr, model, HP, kW, efficiency ratings, etc.
Project Intent
N/A indicates an evaluated transformer is not included in the replacement scope
| 1. | Replaced the listed existing transformers with new units having the listed kVA and no-load ratings.
Replacement
|  | Building | Location | Transformer |  | Rated | No Load Loss | Comment
|  | Name | or Room ID | Tag No.(s) | Quantity | kVA | Watts | Ref No.
Yes □ No □
Refer to Page 2 MRD for projects with more transformers than listed in this table.
SEQUENCES OF OPERATION: Provide a description of equipment operating sequences, setpoints, operating schedules, balancing requirements (flow, velocity, head, etc.) or any other required operating parameters. Describe requirements separately.
Yes □ No □ | 2. | Removal of pre-retrofit transformers & installation of new.
DOCUMENTATION: List written documentation required to train, verify, operate, or maintain the equipment being installed or controlled. This may include specification sheets, test reports, construction drawings, etc.
Yes □ No □ | 3. | Provide pictures of installation and cut sheets documenting the NLL losses for each transformer
Yes □ No □ | 4. | Provide documentation of project costs such as transformer purchase costs, labor costs, and incidental costs.
The preapproved incentive is subject to the Companies' Post-Installation inspection of final specifications, drawings and operation of the proposed equipment. In the event the proposed system is altered from the above description, notify the Company of the change prior to the equipment purchase and installation as the change in design and operation may impact the incentive.
|  | Pre-Installation |  | Post-Installation
|  | Signature | Date | Signature |  |  |  | Date
Customer
Tech Rep

## Versions (hidden)
Version | Date | Author | Changes
1 | 2026-06-02 | Lisa Z./Amir | Original tool
1.1 | 2026-06-18 | Lisa Z. | Adjusted instructions language, MRDs